## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1057-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1057-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1057-1_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1057-1_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1057-1_0_4_node_56 | 0.4 | n |  | TRUE
5 | bus_LV_1057-1_0_4_node_55 | 0.4 | n |  | TRUE
6 | bus_LV_1057-1_0_4_node_54 | 0.4 | n |  | TRUE
7 | bus_LV_1057-1_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1057-1_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1057-1_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1057-1_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1057-1_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1057-1_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1057-1_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1057-1_0_4_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_1057-1_0_4_node_51 | 0.4 | n |  | TRUE
16 | bus_LV_1057-1_0_4_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_1057-1_0_4_node_49 | 0.4 | n |  | TRUE
18 | bus_LV_1057-1_0_4_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_1057-1_0_4_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_1057-1_0_4_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_1057-1_0_4_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_1057-1_0_4_node_69 | 0.4 | n |  | TRUE
23 | bus_LV_1057-1_0_4_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_1057-1_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1057-1_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1057-1_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1057-1_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1057-1_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1057-1_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1057-1_0_4_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_1057-1_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_1057-1_0_4_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_1057-1_0_4_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_1057-1_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1057-1_0_4_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_1057-1_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_1057-1_0_4_node_53 | 0.4 | n |  | TRUE
38 | bus_LV_1057-1_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1057-1_0_4_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_1057-1_0_4_node_48 | 0.4 | n |  | TRUE
41 | bus_LV_1057-1_0_4_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_1057-1_0_4_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_1057-1_0_4_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_1057-1_0_4_node_45 | 0.4 | n |  | TRUE
45 | bus_LV_1057-1_0_4_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_1057-1_0_4_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_1057-1_0_4_node_31 | 0.4 | n |  | TRUE
48 | bus_LV_1057-1_0_4_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_1057-1_0_4_node_77 | 0.4 | n |  | TRUE
50 | bus_LV_1057-1_0_4_node_72 | 0.4 | n |  | TRUE
51 | bus_LV_1057-1_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_1057-1_0_4_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_1057-1_0_4_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_1057-1_0_4_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_1057-1_0_4_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_1057-1_0_4_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_1057-1_0_4_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_1057-1_0_4_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_1057-1_0_4_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_1057-1_0_4_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_1057-1_0_4_node_126 | 0.4 | n |  | TRUE
62 | bus_LV_1057-1_0_4_node_98 | 0.4 | n |  | TRUE
63 | bus_LV_1057-1_0_4_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_1057-1_0_4_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_1057-1_0_4_node_127 | 0.4 | n |  | TRUE
66 | bus_LV_1057-1_0_4_node_134 | 0.4 | n |  | TRUE
67 | bus_LV_1057-1_0_4_node_96 | 0.4 | n |  | TRUE
68 | bus_LV_1057-1_0_4_node_95 | 0.4 | n |  | TRUE
69 | bus_LV_1057-1_0_4_node_74 | 0.4 | n |  | TRUE
70 | bus_LV_1057-1_0_4_node_131 | 0.4 | n |  | TRUE
71 | bus_LV_1057-1_0_4_node_97 | 0.4 | n |  | TRUE
72 | bus_LV_1057-1_0_4_node_70 | 0.4 | n |  | TRUE
73 | bus_LV_1057-1_0_4_node_104 | 0.4 | n |  | TRUE
74 | bus_LV_1057-1_0_4_node_102 | 0.4 | n |  | TRUE
75 | bus_LV_1057-1_0_4_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_1057-1_0_4_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_1057-1_0_4_node_63 | 0.4 | n |  | TRUE
78 | bus_LV_1057-1_0_4_node_64 | 0.4 | n |  | TRUE
79 | bus_LV_1057-1_0_4_node_65 | 0.4 | n |  | TRUE
80 | bus_LV_1057-1_0_4_node_66 | 0.4 | n |  | TRUE
81 | bus_LV_1057-1_0_4_node_67 | 0.4 | n |  | TRUE
82 | bus_LV_1057-1_0_4_node_68 | 0.4 | n |  | TRUE
83 | bus_LV_1057-1_0_4_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_1057-1_0_4_node_90 | 0.4 | n |  | TRUE
85 | bus_LV_1057-1_0_4_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_1057-1_0_4_node_88 | 0.4 | n |  | TRUE
87 | bus_LV_1057-1_0_4_node_71 | 0.4 | n |  | TRUE
88 | bus_LV_1057-1_0_4_node_75 | 0.4 | n |  | TRUE
89 | bus_LV_1057-1_0_4_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_1057-1_0_4_node_130 | 0.4 | n |  | TRUE
91 | bus_LV_1057-1_0_4_node_79 | 0.4 | n |  | TRUE
92 | bus_LV_1057-1_0_4_node_78 | 0.4 | n |  | TRUE
93 | bus_LV_1057-1_0_4_node_80 | 0.4 | n |  | TRUE
94 | bus_LV_1057-1_0_4_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_1057-1_0_4_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_1057-1_0_4_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_1057-1_0_4_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_1057-1_0_4_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_1057-1_0_4_node_111 | 0.4 | n |  | TRUE
100 | bus_LV_1057-1_0_4_node_137 | 0.4 | n |  | TRUE
101 | bus_LV_1057-1_0_4_node_109 | 0.4 | n |  | TRUE
102 | bus_LV_1057-1_0_4_node_138 | 0.4 | n |  | TRUE
103 | bus_LV_1057-1_0_4_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_1057-1_0_4_node_89 | 0.4 | n |  | TRUE
105 | bus_LV_1057-1_0_4_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_1057-1_0_4_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_1057-1_0_4_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_1057-1_0_4_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_1057-1_0_4_node_121 | 0.4 | n |  | TRUE
110 | bus_LV_1057-1_0_4_node_122 | 0.4 | n |  | TRUE
111 | bus_LV_1057-1_0_4_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_1057-1_0_4_node_123 | 0.4 | n |  | TRUE
113 | bus_LV_1057-1_0_4_node_135 | 0.4 | n |  | TRUE
114 | bus_LV_1057-1_0_4_node_99 | 0.4 | n |  | TRUE
115 | bus_LV_1057-1_0_4_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_1057-1_0_4_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_1057-1_0_4_node_103 | 0.4 | n |  | TRUE
118 | bus_LV_1057-1_0_4_node_106 | 0.4 | n |  | TRUE
119 | bus_LV_1057-1_0_4_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_1057-1_0_4_node_110 | 0.4 | n |  | TRUE
121 | bus_LV_1057-1_0_4_node_112 | 0.4 | n |  | TRUE
122 | bus_LV_1057-1_0_4_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_1057-1_0_4_node_114 | 0.4 | n |  | TRUE
124 | bus_LV_1057-1_0_4_node_115 | 0.4 | n |  | TRUE
125 | bus_LV_1057-1_0_4_node_116 | 0.4 | n |  | TRUE
126 | bus_LV_1057-1_0_4_node_117 | 0.4 | n |  | TRUE
127 | bus_LV_1057-1_0_4_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_1057-1_0_4_node_119 | 0.4 | n |  | TRUE
129 | bus_LV_1057-1_0_4_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_1057-1_0_4_node_128 | 0.4 | n |  | TRUE
131 | bus_LV_1057-1_0_4_node_129 | 0.4 | n |  | TRUE
132 | bus_LV_1057-1_0_4_node_132 | 0.4 | n |  | TRUE
133 | bus_LV_1057-1_0_4_node_125 | 0.4 | n |  | TRUE
134 | bus_LV_1057-1_0_4_node_124 | 0.4 | n |  | TRUE
135 | bus_LV_1057-1_0_4_node_133 | 0.4 | n |  | TRUE
136 | bus_LV_1057-1_0_4_node_136 | 0.4 | n |  | TRUE
137 | bus_LV_1057-1_0_4_node_139 | 0.4 | n |  | TRUE
138 | bus_LV_1057-1_0_4_node_140 | 0.4 | n |  | TRUE
139 | bus_LV_1057-1_0_4_node_141 | 0.4 | n |  | TRUE
140 | bus_LV_1057-1_0_4_node_142 | 0.4 | n |  | TRUE
141 | bus_MV_0_0_node_15 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1057-1_0_4_load_0 | 0 | 0.012511 | 0.0031356 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1057-1_0_4_load_1 | 1 | 0.030336 | 0.007603 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1057-1_0_4_load_56 | 4 | 0.017329 | 0.004343 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1057-1_0_4_load_54 | 6 | 0.0026998 | 0.00067662 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1057-1_0_4_load_5 | 7 | 0.0010242 | 0.00025669 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1057-1_0_4_load_8 | 9 | 0.0034514 | 0.000865 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1057-1_0_4_load_9 | 10 | 0.0022598 | 0.00056637 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1057-1_0_4_load_10 | 11 | 0.0011338 | 0.00028415 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1057-1_0_4_load_7 | 13 | 0.0015623 | 0.00039154 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1057-1_0_4_load_34 | 14 | 0.002248 | 0.0005634 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1057-1_0_4_load_51 | 15 | 0.0014272 | 0.00035768 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1057-1_0_4_load_33 | 16 | 0.0012463 | 0.00031236 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1057-1_0_4_load_32 | 18 | 0.0015245 | 0.00038208 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1057-1_0_4_load_46 | 20 | 0.0024275 | 0.0006084 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1057-1_0_4_load_35 | 21 | 0.0022017 | 0.00055179 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1057-1_0_4_load_30 | 23 | 0.00040943 | 0.00010261 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1057-1_0_4_load_12 | 24 | 0.0011054 | 0.00027704 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1057-1_0_4_load_17 | 28 | 0.0011732 | 0.00029403 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1057-1_0_4_load_18 | 29 | 0.0021016 | 0.0005267 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1057-1_0_4_load_15 | 30 | 0.0072064 | 0.0018061 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1057-1_0_4_load_20 | 32 | 0.0019254 | 0.00048254 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1057-1_0_4_load_22 | 33 | 0.0013829 | 0.00034659 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1057-1_0_4_load_50 | 35 | 0.0050692 | 0.0012705 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1057-1_0_4_load_53 | 37 | 0.0020349 | 0.00051 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1057-1_0_4_load_47 | 39 | 0.0018094 | 0.00045348 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1057-1_0_4_load_44 | 41 | 0.0023663 | 0.00059304 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1057-1_0_4_load_29 | 42 | 0.0020614 | 0.00051664 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1057-1_0_4_load_26 | 43 | 0.0027222 | 0.00068224 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1057-1_0_4_load_45 | 44 | 0.0005815 | 0.00014574 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1057-1_0_4_load_27 | 45 | 0.0094007 | 0.002356 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1057-1_0_4_load_28 | 46 | 0.0028131 | 0.00070503 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1057-1_0_4_load_31 | 47 | 0.0009248 | 0.00023178 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1057-1_0_4_load_77 | 49 | 0.0010014 | 0.00025097 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1057-1_0_4_load_36 | 51 | 0.0073832 | 0.0018504 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1057-1_0_4_load_38 | 53 | 0.0057435 | 0.0014395 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1057-1_0_4_load_40 | 55 | 0.0010194 | 0.00025548 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1057-1_0_4_load_42 | 56 | 0.0019174 | 0.00048055 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1057-1_0_4_load_57 | 59 | 0.0023431 | 0.00058725 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1057-1_0_4_load_58 | 60 | 0.0021303 | 0.00053391 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1057-1_0_4_load_126 | 61 | 0.0025547 | 0.00064027 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1057-1_0_4_load_98 | 62 | 0.0010189 | 0.00025536 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1057-1_0_4_load_59 | 63 | 0.0021334 | 0.00053468 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1057-1_0_4_load_60 | 64 | 0.0015565 | 0.00039011 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1057-1_0_4_load_127 | 65 | 0.0020801 | 0.00052133 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1057-1_0_4_load_134 | 66 | 0.0010219 | 0.00025611 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1057-1_0_4_load_96 | 67 | 0.00099273 | 0.0002488 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1057-1_0_4_load_95 | 68 | 0.0052794 | 0.0013231 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1057-1_0_4_load_131 | 70 | 0.0030354 | 0.00076074 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1057-1_0_4_load_97 | 71 | 0.001531 | 0.00038371 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1057-1_0_4_load_70 | 72 | 0.0048002 | 0.0012031 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1057-1_0_4_load_104 | 73 | 0.0026735 | 0.00067004 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1057-1_0_4_load_102 | 74 | 0.001811 | 0.00045387 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1057-1_0_4_load_61 | 75 | 0.0032498 | 0.00081448 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1057-1_0_4_load_62 | 76 | 0.0017851 | 0.00044738 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1057-1_0_4_load_63 | 77 | 0.0027308 | 0.0006844 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1057-1_0_4_load_64 | 78 | 0.0037612 | 0.00094265 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1057-1_0_4_load_67 | 81 | 0.0027655 | 0.00069309 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1057-1_0_4_load_68 | 82 | 0.0027686 | 0.00069388 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1057-1_0_4_load_76 | 83 | 0.0016467 | 0.00041269 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1057-1_0_4_load_90 | 84 | 0.0019796 | 0.00049613 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1057-1_0_4_load_88 | 86 | 0.0017202 | 0.00043112 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1057-1_0_4_load_71 | 87 | 0.0029624 | 0.00074245 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1057-1_0_4_load_75 | 88 | 0.0026311 | 0.00065943 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1057-1_0_4_load_81 | 89 | 0.0011779 | 0.0002952 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1057-1_0_4_load_130 | 90 | 0.0025774 | 0.00064597 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1057-1_0_4_load_79 | 91 | 0.00082529 | 0.00020684 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1057-1_0_4_load_78 | 92 | 0.0018445 | 0.00046228 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1057-1_0_4_load_83 | 95 | 0.00092614 | 0.00023211 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1057-1_0_4_load_84 | 96 | 0.0019386 | 0.00048585 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1057-1_0_4_load_85 | 97 | 0.0012108 | 0.00030346 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1057-1_0_4_load_86 | 98 | 0.00089786 | 0.00022502 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1057-1_0_4_load_111 | 99 | 0.0018483 | 0.00046322 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1057-1_0_4_load_137 | 100 | 0.00084239 | 0.00021112 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1057-1_0_4_load_109 | 101 | 0.0027563 | 0.0006908 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1057-1_0_4_load_138 | 102 | 0.0009007 | 0.00022574 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1057-1_0_4_load_87 | 103 | 0.0049084 | 0.0012302 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1057-1_0_4_load_91 | 105 | 0.00132 | 0.00033083 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1057-1_0_4_load_92 | 106 | 0.0010745 | 0.00026929 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1057-1_0_4_load_93 | 107 | 0.0031409 | 0.00078718 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1057-1_0_4_load_94 | 108 | 0.0012795 | 0.00032067 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1057-1_0_4_load_121 | 109 | 0.0033975 | 0.0008515 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1057-1_0_4_load_122 | 110 | 0.0012713 | 0.00031861 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1057-1_0_4_load_105 | 111 | 0.0044292 | 0.0011101 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1057-1_0_4_load_123 | 112 | 0.0021938 | 0.00054983 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1057-1_0_4_load_135 | 113 | 0.0014701 | 0.00036843 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1057-1_0_4_load_99 | 114 | 0.0031936 | 0.00080039 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1057-1_0_4_load_100 | 115 | 0.0024342 | 0.00061007 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1057-1_0_4_load_101 | 116 | 0.0025417 | 0.00063701 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1057-1_0_4_load_103 | 117 | 0.0015364 | 0.00038505 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1057-1_0_4_load_106 | 118 | 0.0026456 | 0.00066306 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1057-1_0_4_load_110 | 120 | 0.0025169 | 0.0006308 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1057-1_0_4_load_112 | 121 | 0.006718 | 0.0016837 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1057-1_0_4_load_113 | 122 | 0.0014694 | 0.00036827 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1057-1_0_4_load_114 | 123 | 0.0013639 | 0.00034183 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1057-1_0_4_load_115 | 124 | 0.0014694 | 0.00036827 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1057-1_0_4_load_116 | 125 | 0.0014967 | 0.00037511 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1057-1_0_4_load_118 | 127 | 0.0014594 | 0.00036575 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1057-1_0_4_load_119 | 128 | 0.0025055 | 0.00062793 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1057-1_0_4_load_120 | 129 | 0.0026256 | 0.00065803 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1057-1_0_4_load_128 | 130 | 0.002972 | 0.00074484 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1057-1_0_4_load_129 | 131 | 0.0029418 | 0.00073729 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1057-1_0_4_load_132 | 132 | 0.0015146 | 0.0003796 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1057-1_0_4_load_124 | 134 | 0.0022741 | 0.00056994 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1057-1_0_4_load_136 | 136 | 0.0041309 | 0.0010353 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1057-1_0_4_load_139 | 137 | 0.0012738 | 0.00031925 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1057-1_0_4_load_140 | 138 | 0.00062296 | 0.00015613 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1057-1_0_4_load_141 | 139 | 0.00077552 | 0.00019436 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1057-1_0_4_load_142 | 140 | 0.0060177 | 0.0015082 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 72 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1057-1_0_4_line_0 |  | 0 | 1 | 0.010476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1057-1_0_4_line_1 |  | 1 | 2 | 0.040026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1057-1_0_4_line_2 |  | 2 | 3 | 0.091858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1057-1_0_4_line_3 |  | 3 | 4 | 0.024488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1057-1_0_4_line_4 |  | 3 | 5 | 0.006653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1057-1_0_4_line_5 |  | 5 | 6 | 0.027491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1057-1_0_4_line_6 |  | 6 | 36 | 0.057568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1057-1_0_4_line_7 |  | 7 | 8 | 0.032868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1057-1_0_4_line_8 |  | 8 | 9 | 0.032543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1057-1_0_4_line_9 |  | 8 | 10 | 0.0080217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1057-1_0_4_line_10 |  | 9 | 11 | 0.032075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1057-1_0_4_line_11 |  | 10 | 12 | 0.063816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1057-1_0_4_line_12 |  | 11 | 17 | 0.0084324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1057-1_0_4_line_13 |  | 12 | 18 | 0.017887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1057-1_0_4_line_14 |  | 13 | 14 | 0.02466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1057-1_0_4_line_15 |  | 14 | 15 | 0.037801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1057-1_0_4_line_16 |  | 14 | 16 | 0.030678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1057-1_0_4_line_17 |  | 15 | 48 | 0.032762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1057-1_0_4_line_18 |  | 16 | 47 | 0.020402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1057-1_0_4_line_19 |  | 17 | 19 | 0.005733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1057-1_0_4_line_20 |  | 17 | 20 | 0.029135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1057-1_0_4_line_21 |  | 18 | 23 | 0.0013878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1057-1_0_4_line_22 |  | 19 | 37 | 0.025369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1057-1_0_4_line_23 |  | 19 | 27 | 0.024169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1057-1_0_4_line_24 |  | 19 | 36 | 0.037861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_1057-1_0_4_line_25 |  | 20 | 44 | 0.014848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1057-1_0_4_line_26 |  | 21 | 22 | 0.022142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1057-1_0_4_line_27 |  | 22 | 49 | 0.020863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_1057-1_0_4_line_28 |  | 22 | 50 | 0.021025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1057-1_0_4_line_29 |  | 23 | 47 | 0.0090553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_1057-1_0_4_line_30 |  | 24 | 25 | 0.0040099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1057-1_0_4_line_31 |  | 24 | 26 | 0.020263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1057-1_0_4_line_32 |  | 25 | 27 | 0.028882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1057-1_0_4_line_33 |  | 26 | 28 | 0.0055556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1057-1_0_4_line_34 |  | 26 | 29 | 0.020173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1057-1_0_4_line_35 |  | 27 | 33 | 0.048842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1057-1_0_4_line_36 |  | 30 | 31 | 0.014644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1057-1_0_4_line_37 |  | 30 | 32 | 0.013808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1057-1_0_4_line_38 |  | 31 | 34 | 0.027587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1057-1_0_4_line_39 |  | 32 | 35 | 0.0030642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1057-1_0_4_line_40 |  | 34 | 42 | 0.003166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1057-1_0_4_line_41 |  | 34 | 43 | 0.023778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1057-1_0_4_line_42 |  | 35 | 40 | 0.03019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1057-1_0_4_line_43 |  | 38 | 39 | 0.015089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1057-1_0_4_line_44 |  | 38 | 40 | 0.040444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1057-1_0_4_line_45 |  | 38 | 41 | 0.014062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1057-1_0_4_line_46 |  | 41 | 44 | 0.0075673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1057-1_0_4_line_47 |  | 43 | 45 | 0.017362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1057-1_0_4_line_48 |  | 45 | 46 | 0.06424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1057-1_0_4_line_49 |  | 48 | 49 | 0.005634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_1057-1_0_4_line_50 |  | 50 | 72 | 0.015755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_1057-1_0_4_line_51 |  | 51 | 52 | 0.021741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1057-1_0_4_line_52 |  | 51 | 53 | 0.02137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1057-1_0_4_line_53 |  | 52 | 54 | 0.021561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1057-1_0_4_line_54 |  | 52 | 55 | 0.016775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1057-1_0_4_line_55 |  | 54 | 56 | 0.015961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1057-1_0_4_line_56 |  | 55 | 57 | 0.01702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1057-1_0_4_line_57 |  | 56 | 61 | 0.0211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1057-1_0_4_line_58 |  | 57 | 62 | 0.019455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1057-1_0_4_line_59 |  | 58 | 59 | 0.0095851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1057-1_0_4_line_60 |  | 58 | 60 | 0.0035374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1057-1_0_4_line_61 |  | 59 | 63 | 0.005927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1057-1_0_4_line_62 |  | 60 | 64 | 0.016145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1057-1_0_4_line_63 |  | 61 | 65 | 0.013387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1057-1_0_4_line_64 |  | 62 | 66 | 0.017334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1057-1_0_4_line_65 |  | 63 | 73 | 0.021067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1057-1_0_4_line_66 |  | 66 | 113 | 0.0068031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1057-1_0_4_line_67 |  | 67 | 68 | 0.005249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1057-1_0_4_line_68 |  | 68 | 80 | 0.017971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1057-1_0_4_line_69 |  | 69 | 70 | 0.025113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1057-1_0_4_line_70 |  | 69 | 71 | 0.00699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1057-1_0_4_line_71 |  | 70 | 90 | 0.02331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1057-1_0_4_line_72 |  | 71 | 80 | 0.034722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1057-1_0_4_line_73 |  | 72 | 87 | 0.00059045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_1057-1_0_4_line_74 |  | 73 | 74 | 0.0011744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1057-1_0_4_line_75 |  | 74 | 115 | 0.02041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1057-1_0_4_line_76 |  | 75 | 76 | 0.0085121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1057-1_0_4_line_77 |  | 75 | 77 | 0.016566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1057-1_0_4_line_78 |  | 76 | 78 | 0.01776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1057-1_0_4_line_79 |  | 77 | 79 | 0.0096828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1057-1_0_4_line_80 |  | 78 | 80 | 0.037958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1057-1_0_4_line_81 |  | 79 | 81 | 0.0084858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1057-1_0_4_line_82 |  | 79 | 82 | 0.024551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1057-1_0_4_line_83 |  | 81 | 83 | 0.0201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1057-1_0_4_line_84 |  | 82 | 84 | 0.0047755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1057-1_0_4_line_85 |  | 83 | 85 | 0.012798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1057-1_0_4_line_86 |  | 84 | 86 | 0.016783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1057-1_0_4_line_87 |  | 85 | 88 | 0.0052964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1057-1_0_4_line_88 |  | 85 | 87 | 0.04527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_1057-1_0_4_line_89 |  | 86 | 103 | 0.014256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1057-1_0_4_line_90 |  | 88 | 89 | 0.029798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1057-1_0_4_line_91 |  | 89 | 91 | 0.016913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1057-1_0_4_line_92 |  | 90 | 133 | 0.0030638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1057-1_0_4_line_93 |  | 91 | 92 | 0.012755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1057-1_0_4_line_94 |  | 92 | 93 | 0.0096384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1057-1_0_4_line_95 |  | 93 | 94 | 0.030208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1057-1_0_4_line_96 |  | 93 | 95 | 0.018113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1057-1_0_4_line_97 |  | 94 | 96 | 0.093885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1057-1_0_4_line_98 |  | 94 | 97 | 0.010628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1057-1_0_4_line_99 |  | 95 | 98 | 0.0045585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1057-1_0_4_line_100 |  | 97 | 99 | 0.024192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1057-1_0_4_line_101 |  | 98 | 100 | 0.013722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1057-1_0_4_line_102 |  | 99 | 101 | 0.028057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1057-1_0_4_line_103 |  | 100 | 102 | 0.0098713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1057-1_0_4_line_104 |  | 101 | 119 | 0.021084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1057-1_0_4_line_105 |  | 102 | 137 | 0.02225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1057-1_0_4_line_106 |  | 103 | 104 | 0.0054195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1057-1_0_4_line_107 |  | 104 | 105 | 0.033913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1057-1_0_4_line_108 |  | 104 | 106 | 0.018385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1057-1_0_4_line_109 |  | 105 | 107 | 0.026525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1057-1_0_4_line_110 |  | 106 | 108 | 0.018242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1057-1_0_4_line_111 |  | 107 | 109 | 0.011941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1057-1_0_4_line_112 |  | 108 | 110 | 0.0051975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1057-1_0_4_line_113 |  | 109 | 111 | 0.019987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1057-1_0_4_line_114 |  | 110 | 112 | 0.019369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1057-1_0_4_line_115 |  | 111 | 117 | 0.0019066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1057-1_0_4_line_116 |  | 113 | 135 | 0.010775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1057-1_0_4_line_117 |  | 114 | 115 | 0.0053152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1057-1_0_4_line_118 |  | 114 | 116 | 0.016374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1057-1_0_4_line_119 |  | 116 | 117 | 0.022229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1057-1_0_4_line_120 |  | 118 | 119 | 0.039203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1057-1_0_4_line_121 |  | 119 | 120 | 0.015321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1057-1_0_4_line_122 |  | 120 | 121 | 0.01808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1057-1_0_4_line_123 |  | 122 | 123 | 5.7503e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1057-1_0_4_line_124 |  | 122 | 124 | 0.00022228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1057-1_0_4_line_125 |  | 123 | 125 | 0.000589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1057-1_0_4_line_126 |  | 124 | 126 | 0.015559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1057-1_0_4_line_127 |  | 125 | 127 | 0.0073577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1057-1_0_4_line_128 |  | 126 | 128 | 0.021134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1057-1_0_4_line_129 |  | 126 | 129 | 0.018437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1057-1_0_4_line_130 |  | 127 | 130 | 0.00046401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1057-1_0_4_line_131 |  | 129 | 131 | 0.0047595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1057-1_0_4_line_132 |  | 130 | 132 | 0.00056343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1057-1_0_4_line_133 |  | 131 | 133 | 0.017757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1057-1_0_4_line_134 |  | 132 | 135 | 0.018322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1057-1_0_4_line_135 |  | 133 | 134 | 0.042244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1057-1_0_4_line_136 |  | 135 | 136 | 0.002138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1057-1_0_4_line_137 |  | 137 | 138 | 0.0060638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1057-1_0_4_line_138 |  | 138 | 139 | 0.0089144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1057-1_0_4_line_139 |  | 139 | 140 | 0.012312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1057-1_0_4_trafo_70 | 0.63 MVA 20/0.4 kV | 141 | 72 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2673261.1088 | 1220533.2784 | 2673271.0908 | 1220536.4582
1 | 2673309.2285 | 1220548.607 | 2673271.0908 | 1220536.4582
2 | 2673309.2285 | 1220548.607 | 2673293.247 | 1220607.9489 | 2673300.119 | 1220609.9792 | 2673300.5608 | 1220616.6222 | 2673302.3325 | 1220621.8586 | 2673306.5121 | 1220626.2573 | 2673310.3271 | 1220629.4619
3 | 2673310.3271 | 1220629.4619 | 2673315.7877 | 1220633.9653 | 2673327.6837 | 1220640.8273 | 2673330.9566 | 1220642.5016
4 | 2673310.3271 | 1220629.4619 | 2673306.9559 | 1220635.2019
5 | 2673306.9559 | 1220635.2019 | 2673331.3584 | 1220647.8608
6 | 2673382.8195 | 1220673.6163 | 2673378.8703 | 1220672.0778 | 2673359.0746 | 1220662.2387 | 2673331.3584 | 1220647.8608
7 | 2673452.8569 | 1220611.0277 | 2673459.302 | 1220605.8371 | 2673466.0687 | 1220604.0972 | 2673483.6189 | 1220605.4994
8 | 2673452.8569 | 1220611.0277 | 2673438.6904 | 1220640.3251
9 | 2673452.8569 | 1220611.0277 | 2673452.6169 | 1220603.0096
10 | 2673438.6904 | 1220640.3251 | 2673435.4239 | 1220647.0806 | 2673422.9501 | 1220668.2498
11 | 2673455.5605 | 1220541.9495 | 2673450.8688 | 1220544.6156 | 2673452.6169 | 1220603.0096
12 | 2673418.6693 | 1220675.5148 | 2673422.9501 | 1220668.2498
13 | 2673455.5605 | 1220541.9495 | 2673471.3814 | 1220550.2937
14 | 2673523.6091 | 1220545.1134 | 2673545.3956 | 1220533.5608
15 | 2673523.6091 | 1220545.1134 | 2673525.6231 | 1220538.9451 | 2673521.4111 | 1220526.7296 | 2673510.5122 | 1220511.9161
16 | 2673500.0469 | 1220560.9549 | 2673513.0154 | 1220558.3799 | 2673521.9641 | 1220550.1517 | 2673523.6091 | 1220545.1134
17 | 2673489.757 | 1220486.6686 | 2673498.4121 | 1220495.47 | 2673510.5122 | 1220511.9161
18 | 2673500.0469 | 1220560.9549 | 2673500.0469 | 1220560.9549 | 2673485.1113 | 1220557.5351 | 2673480.6185 | 1220555.1655
19 | 2673418.6693 | 1220675.5148 | 2673415.763 | 1220680.46
20 | 2673418.6693 | 1220675.5148 | 2673433.8248 | 1220670.3093 | 2673442.6026 | 1220670.9846 | 2673446.7259 | 1220672.2293
21 | 2673471.3814 | 1220550.2937 | 2673472.6089 | 1220550.9411
22 | 2673415.763 | 1220680.46 | 2673391.9524 | 1220671.7059
23 | 2673407.3577 | 1220703.1044 | 2673414.582 | 1220684.5592 | 2673415.763 | 1220680.46
24 | 2673382.8195 | 1220673.6163 | 2673408.7651 | 1220682.4973 | 2673414.582 | 1220684.5592 | 2673415.763 | 1220680.46
25 | 2673460.894 | 1220676.6694 | 2673460.894 | 1220676.6694 | 2673453.624 | 1220674.3115 | 2673446.7259 | 1220672.2293
26 | 2673468.6968 | 1220472.9 | 2673463.0983 | 1220494.3226
27 | 2673468.6968 | 1220472.9 | 2673472.1581 | 1220478.3239 | 2673484.1306 | 1220486.3768
28 | 2673455.1191 | 1220460.2577 | 2673453.8035 | 1220462.9543 | 2673464.6565 | 1220468.892 | 2673468.6968 | 1220472.9
29 | 2673480.6185 | 1220555.1655 | 2673472.6089 | 1220550.9411
30 | 2673416.0775 | 1220730.6409 | 2673417.2503 | 1220734.4754
31 | 2673423.2041 | 1220753.8438 | 2673417.5726 | 1220735.5291 | 2673417.2503 | 1220734.4754
32 | 2673416.0775 | 1220730.6409 | 2673411.5927 | 1220715.9316 | 2673407.3577 | 1220703.1044
33 | 2673423.2041 | 1220753.8438 | 2673425.6375 | 1220758.8382
34 | 2673423.2041 | 1220753.8438 | 2673430.9437 | 1220758.7201 | 2673437.8896 | 1220767.283
35 | 2673407.3577 | 1220703.1044 | 2673398.8839 | 1220707.9254 | 2673381.6791 | 1220718.1312 | 2673372.0125 | 1220720.0022 | 2673362.8307 | 1220718.9435
36 | 2673472.7163 | 1220754.0432 | 2673468.5627 | 1220761.0743 | 2673465.2089 | 1220766.6255
37 | 2673472.7163 | 1220754.0432 | 2673479.7446 | 1220742.1578
38 | 2673465.2089 | 1220766.6255 | 2673459.64 | 1220775.8406 | 2673455.622 | 1220792.1794
39 | 2673479.7446 | 1220742.1578 | 2673481.3043 | 1220739.5202
40 | 2673455.622 | 1220792.1794 | 2673457.259 | 1220794.8894
41 | 2673455.622 | 1220792.1794 | 2673460.9224 | 1220793.6568 | 2673476.4183 | 1220803.3452
42 | 2673494.412 | 1220712.5616 | 2673491.7557 | 1220721.846 | 2673481.3043 | 1220739.5202
43 | 2673463.0114 | 1220696.9197 | 2673448.7624 | 1220691.9559
44 | 2673463.0114 | 1220696.9197 | 2673460.9113 | 1220701.7081 | 2673464.909 | 1220703.0027 | 2673494.412 | 1220712.5616
45 | 2673463.0114 | 1220696.9197 | 2673465.0349 | 1220692.1861 | 2673464.5754 | 1220683.308 | 2673464.5639 | 1220683.2872
46 | 2673460.894 | 1220676.6694 | 2673464.5639 | 1220683.2872
47 | 2673492.1591 | 1220810.2533 | 2673483.5625 | 1220807.8119 | 2673476.4183 | 1220803.3452
48 | 2673492.1591 | 1220810.2533 | 2673501.9804 | 1220813.0425 | 2673524.9855 | 1220816.0617 | 2673538.8534 | 1220819.8687 | 2673555.1591 | 1220822.023
49 | 2673489.757 | 1220486.6686 | 2673484.1306 | 1220486.3768
50 | 2673455.1191 | 1220460.2577 | 2673449.8439 | 1220457.3241 | 2673442.3221 | 1220451.1695
51 | 2673583.6283 | 1220342 | 2673581.4922 | 1220336.181 | 2673577.0676 | 1220328.8883 | 2673570.6451 | 1220326.0738
52 | 2673549.3641 | 1220328.0224 | 2673570.6451 | 1220326.0738
53 | 2673603.6712 | 1220334.3537 | 2673596.3005 | 1220335.8192 | 2673583.6283 | 1220342
54 | 2673583.6283 | 1220342 | 2673569.9672 | 1220350.8482 | 2673569.501 | 1220351.0254
55 | 2673603.6712 | 1220334.3537 | 2673609.7424 | 1220349.115
56 | 2673553.5917 | 1220357.0722 | 2673569.501 | 1220351.0254
57 | 2673609.7424 | 1220349.115 | 2673617.7684 | 1220368.6291
58 | 2673553.5917 | 1220357.0722 | 2673556.0799 | 1220365.7197 | 2673557.7151 | 1220376.0474
59 | 2673498.2878 | 1220337.7328 | 2673490.7677 | 1220331.7894
60 | 2673498.2878 | 1220337.7328 | 2673501.1895 | 1220339.756
61 | 2673486.1177 | 1220328.1143 | 2673490.7677 | 1220331.7894
62 | 2673514.7446 | 1220348.4389 | 2673511.6638 | 1220347.0594 | 2673501.1895 | 1220339.756
63 | 2673622.8606 | 1220381.01 | 2673617.7684 | 1220368.6291
64 | 2673560.269 | 1220393.1924 | 2673558.3252 | 1220379.9011 | 2673557.7151 | 1220376.0474
65 | 2673486.1177 | 1220328.1143 | 2673469.5897 | 1220315.0517
66 | 2673560.269 | 1220393.1924 | 2673561.2535 | 1220399.9239
67 | 2673527.4278 | 1220387.1243 | 2673525.5722 | 1220390.07 | 2673524.4823 | 1220391.4615
68 | 2673512.7838 | 1220405.0664 | 2673517.809 | 1220399.9807 | 2673524.4823 | 1220391.4615
69 | 2673485.6004 | 1220435.5286 | 2673491.7104 | 1220437.2162 | 2673503.9214 | 1220451.4772
70 | 2673485.6004 | 1220435.5286 | 2673487.5605 | 1220429.182 | 2673487.818 | 1220428.9486
71 | 2673503.9214 | 1220451.4772 | 2673517.3139 | 1220467.1181 | 2673519.0937 | 1220469.1737
72 | 2673512.7838 | 1220405.0664 | 2673505.9999 | 1220413.7105 | 2673494.2518 | 1220423.1162 | 2673487.818 | 1220428.9486
73 | 2673442.3221 | 1220451.1695 | 2673441.8651 | 1220450.7956
74 | 2673468.6683 | 1220314.3235 | 2673469.5897 | 1220315.0517
75 | 2673453.1805 | 1220301.06 | 2673459.8735 | 1220307.3726 | 2673468.6683 | 1220314.3235
76 | 2673456.286 | 1220386.1405 | 2673463.0259 | 1220391.3396
77 | 2673456.286 | 1220386.1405 | 2673446.9337 | 1220378.9262 | 2673442.3363 | 1220377.713
78 | 2673463.0259 | 1220391.3396 | 2673463.2364 | 1220391.502 | 2673477.1757 | 1220402.072
79 | 2673432.8015 | 1220378.007 | 2673439.8622 | 1220377.06 | 2673442.3363 | 1220377.713
80 | 2673512.7838 | 1220405.0664 | 2673507.8901 | 1220407.4965 | 2673493.1862 | 1220409.2496 | 2673480.4963 | 1220404.59 | 2673477.1757 | 1220402.072
81 | 2673432.8015 | 1220378.007 | 2673434.0684 | 1220386.3977
82 | 2673432.8015 | 1220378.007 | 2673417.0589 | 1220359.1671
83 | 2673434.0684 | 1220386.3977 | 2673434.7726 | 1220391.0619 | 2673429.4501 | 1220405.4946 | 2673429.4501 | 1220405.4946
84 | 2673417.0589 | 1220359.1671 | 2673415.8576 | 1220357.7294 | 2673414.1753 | 1220355.3648
85 | 2673418.8899 | 1220412.7247 | 2673429.4501 | 1220405.4946
86 | 2673404.4461 | 1220341.6895 | 2673414.1753 | 1220355.3648
87 | 2673418.8899 | 1220412.7247 | 2673415.0765 | 1220409.0492
88 | 2673418.8899 | 1220412.7247 | 2673425.5061 | 1220429.3615 | 2673434.392 | 1220444.6809 | 2673441.8651 | 1220450.7956
89 | 2673397.6901 | 1220329.1358 | 2673404.4461 | 1220341.6895 | 2673404.4461 | 1220341.6895
90 | 2673391.4386 | 1220391.4297 | 2673396.5843 | 1220393.4596 | 2673404.6575 | 1220399.0071 | 2673415.0765 | 1220409.0492
91 | 2673391.4386 | 1220391.4297 | 2673384.918 | 1220388.8574 | 2673375.0757 | 1220387.761
92 | 2673521.0993 | 1220471.4899 | 2673519.0937 | 1220469.1737
93 | 2673362.3995 | 1220386.349 | 2673375.0757 | 1220387.761
94 | 2673352.8203 | 1220385.282 | 2673362.3995 | 1220386.349
95 | 2673322.5931 | 1220383.2419 | 2673352.8203 | 1220385.282
96 | 2673352.8203 | 1220385.282 | 2673353.3247 | 1220378.8285 | 2673352.6668 | 1220373.1055 | 2673351.5975 | 1220367.3245
97 | 2673322.5931 | 1220383.2419 | 2673323.187 | 1220390.465 | 2673332.1414 | 1220405.1848 | 2673336.1449 | 1220415.8855 | 2673338.2847 | 1220424.5063 | 2673341.7806 | 1220434.5225 | 2673345.7904 | 1220444.7118 | 2673355.3274 | 1220454.6245 | 2673366.0778 | 1220463.3514
98 | 2673322.5931 | 1220383.2419 | 2673311.9787 | 1220382.7131
99 | 2673350.7683 | 1220362.8421 | 2673351.5975 | 1220367.3245
100 | 2673287.8162 | 1220381.5093 | 2673311.9787 | 1220382.7131
101 | 2673345.7863 | 1220350.1837 | 2673345.7863 | 1220350.1837 | 2673349.9706 | 1220358.5296 | 2673350.7683 | 1220362.8421
102 | 2673287.8162 | 1220381.5093 | 2673264.4989 | 1220380.3476 | 2673259.7931 | 1220380.1395
103 | 2673345.7863 | 1220350.1837 | 2673339.7669 | 1220342.3601 | 2673339.7669 | 1220342.3601
104 | 2673238.7298 | 1220379.2078 | 2673259.7931 | 1220380.1395
105 | 2673339.7669 | 1220342.3601 | 2673331.0422 | 1220334.8701 | 2673324.7866 | 1220331.4353 | 2673321.3349 | 1220330.3638
106 | 2673395.1218 | 1220324.3634 | 2673397.6901 | 1220329.1358
107 | 2673395.1218 | 1220324.3634 | 2673390.0946 | 1220301.2977 | 2673389.6094 | 1220291.0031
108 | 2673395.1218 | 1220324.3634 | 2673390.925 | 1220323.8003 | 2673379.8971 | 1220314.933
109 | 2673389.6094 | 1220291.0031 | 2673388.9879 | 1220277.8132 | 2673391.3272 | 1220264.7002 | 2673391.3272 | 1220264.7002
110 | 2673365.6808 | 1220303.5021 | 2673379.8971 | 1220314.933
111 | 2673402.2304 | 1220259.8314 | 2673402.2304 | 1220259.8314 | 2673391.3272 | 1220264.7002
112 | 2673365.6808 | 1220303.5021 | 2673361.6303 | 1220300.2453
113 | 2673402.2304 | 1220259.8314 | 2673419.0331 | 1220270.6541
114 | 2673346.5358 | 1220288.1083 | 2673361.6303 | 1220300.2453
115 | 2673420.636 | 1220271.6865 | 2673419.0331 | 1220270.6541
116 | 2673565.4422 | 1220409.4081 | 2673562.0474 | 1220405.3524 | 2673561.2535 | 1220399.9239
117 | 2673449.3138 | 1220297.413 | 2673453.1805 | 1220301.06
118 | 2673449.3138 | 1220297.413 | 2673437.402 | 1220286.1781
119 | 2673420.636 | 1220271.6865 | 2673425.0556 | 1220274.5333 | 2673437.402 | 1220286.1781
120 | 2673238.7298 | 1220379.2078 | 2673209.5751 | 1220377.5596 | 2673199.6138 | 1220376.6641
121 | 2673238.7298 | 1220379.2078 | 2673239.6453 | 1220363.9139
122 | 2673240.7258 | 1220345.8663 | 2673239.6453 | 1220363.9139
123 | 2673551.6804 | 1220431.0202 | 2673551.7319 | 1220430.9946
124 | 2673551.4813 | 1220431.119 | 2673551.6804 | 1220431.0202
125 | 2673551.7319 | 1220430.9946 | 2673552.2594 | 1220430.7327
126 | 2673537.5451 | 1220438.0378 | 2673551.4813 | 1220431.119
127 | 2673558.8497 | 1220427.4608 | 2673552.2594 | 1220430.7327
128 | 2673524.3702 | 1220431.4932 | 2673534.8966 | 1220428.2432 | 2673537.5451 | 1220438.0378
129 | 2673537.5451 | 1220438.0378 | 2673540.448 | 1220448.7362 | 2673535.6887 | 1220454.3398
130 | 2673558.8497 | 1220427.4608 | 2673559.2653 | 1220427.2545 | 2673559.2653 | 1220427.2545
131 | 2673532.6051 | 1220457.9652 | 2673534.7195 | 1220455.4809 | 2673535.6887 | 1220454.3398
132 | 2673559.2653 | 1220427.2545 | 2673559.4496 | 1220426.7221
133 | 2673521.0993 | 1220471.4899 | 2673526.7969 | 1220464.7892 | 2673532.6051 | 1220457.9652
134 | 2673565.4422 | 1220409.4081 | 2673559.4496 | 1220426.7221
135 | 2673521.0993 | 1220471.4899 | 2673524.6302 | 1220475.5695 | 2673535.8292 | 1220483.5907 | 2673553.1781 | 1220489.442 | 2673557.6478 | 1220491.0912
136 | 2673565.4422 | 1220409.4081 | 2673566.818 | 1220411.0484
137 | 2673315.5438 | 1220328.566 | 2673321.3349 | 1220330.3638
138 | 2673315.5438 | 1220328.566 | 2673308.4517 | 1220326.3644 | 2673306.9788 | 1220326.1496
139 | 2673294.7954 | 1220324.3728 | 2673306.9788 | 1220326.1496

## bus_geodata
| x | y | coords
0 | 2673261.1088 | 1220533.2784
1 | 2673271.0908 | 1220536.4582
2 | 2673309.2285 | 1220548.607
3 | 2673310.3271 | 1220629.4619
4 | 2673330.9566 | 1220642.5016
5 | 2673306.9559 | 1220635.2019
6 | 2673331.3584 | 1220647.8608
7 | 2673483.6189 | 1220605.4994
8 | 2673452.8569 | 1220611.0277
9 | 2673438.6904 | 1220640.3251
10 | 2673452.6169 | 1220603.0096
11 | 2673422.9501 | 1220668.2498
12 | 2673455.5605 | 1220541.9495
13 | 2673545.3956 | 1220533.5608
14 | 2673523.6091 | 1220545.1134
15 | 2673510.5122 | 1220511.9161
16 | 2673500.0469 | 1220560.9549
17 | 2673418.6693 | 1220675.5148
18 | 2673471.3814 | 1220550.2937
19 | 2673415.763 | 1220680.46
20 | 2673446.7259 | 1220672.2293
21 | 2673463.0983 | 1220494.3226
22 | 2673468.6968 | 1220472.9
23 | 2673472.6089 | 1220550.9411
24 | 2673417.2503 | 1220734.4754
25 | 2673416.0775 | 1220730.6409
26 | 2673423.2041 | 1220753.8438
27 | 2673407.3577 | 1220703.1044
28 | 2673425.6375 | 1220758.8382
29 | 2673437.8896 | 1220767.283
30 | 2673472.7163 | 1220754.0432
31 | 2673465.2089 | 1220766.6255
32 | 2673479.7446 | 1220742.1578
33 | 2673362.8307 | 1220718.9435
34 | 2673455.622 | 1220792.1794
35 | 2673481.3043 | 1220739.5202
36 | 2673382.8195 | 1220673.6163
37 | 2673391.9524 | 1220671.7059
38 | 2673463.0114 | 1220696.9197
39 | 2673448.7624 | 1220691.9559
40 | 2673494.412 | 1220712.5616
41 | 2673464.5639 | 1220683.2872
42 | 2673457.259 | 1220794.8894
43 | 2673476.4183 | 1220803.3452
44 | 2673460.894 | 1220676.6694
45 | 2673492.1591 | 1220810.2533
46 | 2673555.1591 | 1220822.023
47 | 2673480.6185 | 1220555.1655
48 | 2673489.757 | 1220486.6686
49 | 2673484.1306 | 1220486.3768
50 | 2673455.1191 | 1220460.2577
51 | 2673570.6451 | 1220326.0738
52 | 2673583.6283 | 1220342
53 | 2673549.3641 | 1220328.0224
54 | 2673603.6712 | 1220334.3537
55 | 2673569.501 | 1220351.0253
56 | 2673609.7424 | 1220349.115
57 | 2673553.5917 | 1220357.0722
58 | 2673498.2878 | 1220337.7328
59 | 2673490.7677 | 1220331.7894
60 | 2673501.1895 | 1220339.756
61 | 2673617.7684 | 1220368.6291
62 | 2673557.7151 | 1220376.0474
63 | 2673486.1177 | 1220328.1143
64 | 2673514.7446 | 1220348.4389
65 | 2673622.8606 | 1220381.01
66 | 2673560.269 | 1220393.1924
67 | 2673527.4278 | 1220387.1243
68 | 2673524.4823 | 1220391.4615
69 | 2673485.6004 | 1220435.5286
70 | 2673503.9214 | 1220451.4772
71 | 2673487.818 | 1220428.9486
72 | 2673442.3221 | 1220451.1695
73 | 2673469.5897 | 1220315.0517
74 | 2673468.6683 | 1220314.3235
75 | 2673456.286 | 1220386.1405
76 | 2673463.0259 | 1220391.3396
77 | 2673442.3363 | 1220377.713
78 | 2673477.1757 | 1220402.072
79 | 2673432.8015 | 1220378.007
80 | 2673512.7838 | 1220405.0664
81 | 2673434.0684 | 1220386.3977
82 | 2673417.0589 | 1220359.1671
83 | 2673429.4501 | 1220405.4946
84 | 2673414.1753 | 1220355.3648
85 | 2673418.8899 | 1220412.7247
86 | 2673404.4461 | 1220341.6895
87 | 2673441.8651 | 1220450.7956
88 | 2673415.0765 | 1220409.0492
89 | 2673391.4386 | 1220391.4297
90 | 2673519.0937 | 1220469.1737
91 | 2673375.0757 | 1220387.761
92 | 2673362.3995 | 1220386.349
93 | 2673352.8203 | 1220385.282
94 | 2673322.5931 | 1220383.2419
95 | 2673351.5975 | 1220367.3245
96 | 2673366.0778 | 1220463.3514
97 | 2673311.9787 | 1220382.7131
98 | 2673350.7683 | 1220362.8421
99 | 2673287.8162 | 1220381.5093
100 | 2673345.7863 | 1220350.1837
101 | 2673259.7931 | 1220380.1395
102 | 2673339.7669 | 1220342.3601
103 | 2673397.6901 | 1220329.1358
104 | 2673395.1218 | 1220324.3634
105 | 2673389.6094 | 1220291.0031
106 | 2673379.8971 | 1220314.933
107 | 2673391.3272 | 1220264.7002
108 | 2673365.6808 | 1220303.5021
109 | 2673402.2304 | 1220259.8314
110 | 2673361.6303 | 1220300.2453
111 | 2673419.0331 | 1220270.6541
112 | 2673346.5358 | 1220288.1083
113 | 2673561.2535 | 1220399.9239
114 | 2673449.3138 | 1220297.413
115 | 2673453.1805 | 1220301.06
116 | 2673437.402 | 1220286.1781
117 | 2673420.636 | 1220271.6865
118 | 2673199.6138 | 1220376.6641
119 | 2673238.7298 | 1220379.2078
120 | 2673239.6453 | 1220363.9139
121 | 2673240.7258 | 1220345.8663
122 | 2673551.6804 | 1220431.0202
123 | 2673551.7319 | 1220430.9946
124 | 2673551.4813 | 1220431.119
125 | 2673552.2594 | 1220430.7327
126 | 2673537.5451 | 1220438.0378
127 | 2673558.8497 | 1220427.4608
128 | 2673524.3702 | 1220431.4932
129 | 2673535.6887 | 1220454.3398
130 | 2673559.2653 | 1220427.2545
131 | 2673532.6051 | 1220457.9652
132 | 2673559.4496 | 1220426.7221
133 | 2673521.0993 | 1220471.4899
134 | 2673557.6478 | 1220491.0912
135 | 2673565.4422 | 1220409.4081
136 | 2673566.818 | 1220411.0484
137 | 2673321.3349 | 1220330.3638
138 | 2673315.5438 | 1220328.566
139 | 2673306.9788 | 1220326.1496
140 | 2673294.7954 | 1220324.3728
141 | 2673455.1191 | 1220460.2577

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97044 | -0.56977 | 0.012511 | 0.0031356
1 | 0.97056 | -0.56735 | 0.030336 | 0.007603
2 | 0.97216 | -0.53566 | 0 | 0
3 | 0.97584 | -0.46335 | 0 | 0
4 | 0.97544 | -0.47112 | 0.017329 | 0.004343
5 | 0.97621 | -0.45602 | 0 | 0
6 | 0.97698 | -0.4409 | 0.0026998 | 0.00067662
7 | 0.98374 | -0.30948 | 0.0010242 | 0.00025669
8 | 0.98377 | -0.30888 | 0 | 0
9 | 0.98205 | -0.34225 | 0.0034514 | 0.000865
10 | 0.9842 | -0.3006 | 0.0022598 | 0.00056637
11 | 0.9804 | -0.37425 | 0.0011338 | 0.00028415
12 | 0.98767 | -0.23368 | 0 | 0
13 | 0.99206 | -0.14994 | 0.0015623 | 0.00039154
14 | 0.99209 | -0.14925 | 0.002248 | 0.0005634
15 | 0.99429 | -0.10755 | 0.0014272 | 0.00035768
16 | 0.99036 | -0.1822 | 0.0012463 | 0.00031236
17 | 0.97997 | -0.38259 | 0 | 0
18 | 0.98865 | -0.21501 | 0.0015245 | 0.00038208
19 | 0.97978 | -0.38627 | 0 | 0
20 | 0.97893 | -0.40291 | 0.0024275 | 0.0006084
21 | 0.99774 | -0.042463 | 0.0022017 | 0.00055179
22 | 0.99778 | -0.041609 | 0 | 0
23 | 0.98872 | -0.21354 | 0.00040943 | 0.00010261
24 | 0.97952 | -0.39142 | 0.0011054 | 0.00027704
25 | 0.97954 | -0.3911 | 0 | 0
26 | 0.97946 | -0.39262 | 0 | 0
27 | 0.97965 | -0.3888 | 0 | 0
28 | 0.97945 | -0.39274 | 0.0011732 | 0.00029403
29 | 0.97942 | -0.39339 | 0.0021016 | 0.0005267
30 | 0.97532 | -0.47383 | 0.0072064 | 0.0018061
31 | 0.97509 | -0.47839 | 0 | 0
32 | 0.97563 | -0.4677 | 0.0019254 | 0.00048254
33 | 0.97959 | -0.39003 | 0.0013829 | 0.00034659
34 | 0.97465 | -0.48699 | 0 | 0
35 | 0.97571 | -0.46624 | 0.0050692 | 0.0012705
36 | 0.97867 | -0.40791 | 0 | 0
37 | 0.97974 | -0.38721 | 0.0020349 | 0.00051
38 | 0.97776 | -0.42597 | 0 | 0
39 | 0.97773 | -0.42647 | 0.0018094 | 0.00045348
40 | 0.97658 | -0.449 | 0 | 0
41 | 0.97819 | -0.41751 | 0.0023663 | 0.00059304
42 | 0.97465 | -0.48711 | 0.0020614 | 0.00051664
43 | 0.97432 | -0.49351 | 0.0027222 | 0.00068224
44 | 0.97844 | -0.41263 | 0.0005815 | 0.00014574
45 | 0.97412 | -0.4974 | 0.0094007 | 0.002356
46 | 0.97396 | -0.50073 | 0.0028131 | 0.00070503
47 | 0.98923 | -0.20395 | 0.0009248 | 0.00023178
48 | 0.99622 | -0.071137 | 0 | 0
49 | 0.99655 | -0.06489 | 0.0010014 | 0.00025097
50 | 0.99905 | -0.017801 | 0 | 0
51 | 0.97585 | -0.46607 | 0.0073832 | 0.0018504
52 | 0.97612 | -0.46085 | 0 | 0
53 | 0.97574 | -0.46832 | 0.0057435 | 0.0014395
54 | 0.97599 | -0.46343 | 0 | 0
55 | 0.97642 | -0.45481 | 0.0010194 | 0.00025548
56 | 0.97589 | -0.46535 | 0.0019174 | 0.00048055
57 | 0.97675 | -0.44837 | 0 | 0
58 | 0.98453 | -0.29734 | 0 | 0
59 | 0.98456 | -0.2967 | 0.0023431 | 0.00058725
60 | 0.98452 | -0.29757 | 0.0021303 | 0.00053391
61 | 0.9758 | -0.46714 | 0.0025547 | 0.00064027
62 | 0.97712 | -0.44101 | 0.0010189 | 0.00025536
63 | 0.9846 | -0.29606 | 0.0021334 | 0.00053468
64 | 0.9845 | -0.29803 | 0.0015565 | 0.00039011
65 | 0.97577 | -0.46765 | 0.0020801 | 0.00052133
66 | 0.97747 | -0.43414 | 0.0010219 | 0.00025611
67 | 0.98564 | -0.27489 | 0.00099273 | 0.0002488
68 | 0.98565 | -0.2748 | 0.0052794 | 0.0013231
69 | 0.98353 | -0.31577 | 0 | 0
70 | 0.98223 | -0.34117 | 0.0030354 | 0.00076074
71 | 0.98389 | -0.30871 | 0.001531 | 0.00038371
72 | 1 | 0 | -0.30925 | -0.079067
73 | 0.98475 | -0.29297 | 0.0026735 | 0.00067004
74 | 0.98477 | -0.29274 | 0.001811 | 0.00045387
75 | 0.98966 | -0.19745 | 0.0032498 | 0.00081448
76 | 0.98911 | -0.20797 | 0.0017851 | 0.00044738
77 | 0.99077 | -0.17605 | 0.0027308 | 0.0006844
78 | 0.988 | -0.22939 | 0.0037612 | 0.00094265
79 | 0.99145 | -0.1631 | 0 | 0
80 | 0.98575 | -0.27278 | 0 | 0
81 | 0.99244 | -0.14398 | 0.0027655 | 0.00069309
82 | 0.99028 | -0.1857 | 0.0027686 | 0.00069388
83 | 0.99485 | -0.097845 | 0.0016467 | 0.00041269
84 | 0.99006 | -0.18987 | 0.0019796 | 0.00049613
85 | 0.99641 | -0.068219 | 0 | 0
86 | 0.98933 | -0.20393 | 0.0017202 | 0.00043112
87 | 0.99995 | -0.00089026 | 0.0029624 | 0.00074245
88 | 0.99622 | -0.071789 | 0.0026311 | 0.00065943
89 | 0.99525 | -0.090517 | 0.0011779 | 0.0002952
90 | 0.98108 | -0.36352 | 0.0025774 | 0.00064597
91 | 0.99472 | -0.10081 | 0.00082529 | 0.00020684
92 | 0.99432 | -0.1084 | 0.0018445 | 0.00046228
93 | 0.99404 | -0.11382 | 0 | 0
94 | 0.9935 | -0.12429 | 0 | 0
95 | 0.99384 | -0.11774 | 0.00092614 | 0.00023211
96 | 0.99334 | -0.12751 | 0.0019386 | 0.00048585
97 | 0.99333 | -0.12762 | 0.0012108 | 0.00030346
98 | 0.99379 | -0.11865 | 0.00089786 | 0.00022502
99 | 0.99297 | -0.13466 | 0.0018483 | 0.00046322
100 | 0.99366 | -0.12118 | 0.00084239 | 0.00021112
101 | 0.99259 | -0.14193 | 0.0027563 | 0.0006908
102 | 0.99358 | -0.12285 | 0.0009007 | 0.00022574
103 | 0.98874 | -0.21546 | 0.0049084 | 0.0012302
104 | 0.98854 | -0.21937 | 0 | 0
105 | 0.98746 | -0.24035 | 0.00132 | 0.00033083
106 | 0.98844 | -0.22128 | 0.0010745 | 0.00026929
107 | 0.98664 | -0.25616 | 0.0031409 | 0.00078718
108 | 0.98836 | -0.22282 | 0.0012795 | 0.00032067
109 | 0.98631 | -0.26262 | 0.0033975 | 0.0008515
110 | 0.98834 | -0.22314 | 0.0012713 | 0.00031861
111 | 0.98582 | -0.27222 | 0.0044292 | 0.0011101
112 | 0.9883 | -0.2239 | 0.0021938 | 0.00054983
113 | 0.97762 | -0.43132 | 0.0014701 | 0.00036843
114 | 0.98508 | -0.28666 | 0.0031936 | 0.00080039
115 | 0.985 | -0.2881 | 0.0024342 | 0.00061007
116 | 0.98535 | -0.28129 | 0.0025417 | 0.00063701
117 | 0.98578 | -0.27298 | 0.0015364 | 0.00038505
118 | 0.99227 | -0.1482 | 0.0026456 | 0.00066306
119 | 0.99236 | -0.14636 | 0 | 0
120 | 0.99223 | -0.14887 | 0.0025169 | 0.0006308
121 | 0.99212 | -0.15102 | 0.006718 | 0.0016837
122 | 0.97863 | -0.4115 | 0.0014694 | 0.00036827
123 | 0.97863 | -0.41154 | 0.0013639 | 0.00034183
124 | 0.97864 | -0.41134 | 0.0014694 | 0.00036827
125 | 0.97861 | -0.41192 | 0.0014967 | 0.00037511
126 | 0.97921 | -0.4 | 0 | 0
127 | 0.97837 | -0.41652 | 0.0014594 | 0.00036575
128 | 0.97917 | -0.40096 | 0.0025055 | 0.00062793
129 | 0.97994 | -0.38573 | 0.0026256 | 0.00065803
130 | 0.97836 | -0.41679 | 0.002972 | 0.00074484
131 | 0.98014 | -0.38183 | 0.0029418 | 0.00073729
132 | 0.97834 | -0.4171 | 0.0015146 | 0.0003796
133 | 0.98094 | -0.36632 | 0 | 0
134 | 0.98085 | -0.36806 | 0.0022741 | 0.00056994
135 | 0.97786 | -0.42656 | 0 | 0
136 | 0.97785 | -0.42672 | 0.0041309 | 0.0010353
137 | 0.9934 | -0.12626 | 0.0012738 | 0.00031925
138 | 0.99336 | -0.12706 | 0.00062296 | 0.00015613
139 | 0.9933 | -0.12813 | 0.00077552 | 0.00019436
140 | 0.99324 | -0.12944 | 0.0060177 | 0.0015082
141 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012511 | -0.0031356 | 0.012513 | 0.0031364 | 1.4458e-06 | 7.9586e-07 | 0.019184 | 0.019184 | 0.019184 | 0.97044 | -0.56977 | 0.97056 | -0.56735 | 5.2703
1 | -0.042849 | -0.010739 | 0.042914 | 0.01078 | 6.4778e-05 | 4.0962e-05 | 0.065694 | 0.065694 | 0.065694 | 0.97056 | -0.56735 | 0.97216 | -0.53566 | 18.0479
2 | -0.042914 | -0.01078 | 0.043062 | 0.010874 | 0.00014866 | 9.4e-05 | 0.065694 | 0.065694 | 0.065694 | 0.97216 | -0.53566 | 0.97584 | -0.46335 | 18.0478
3 | 0.017335 | 0.0043468 | -0.017329 | -0.004343 | 6.417e-06 | 3.8011e-06 | 0.026435 | 0.026435 | 0.026435 | 0.97584 | -0.46335 | 0.97544 | -0.47112 | 7.2623
4 | -0.060398 | -0.015221 | 0.060419 | 0.015235 | 2.1176e-05 | 1.3469e-05 | 0.092128 | 0.092128 | 0.092128 | 0.97584 | -0.46335 | 0.97621 | -0.45602 | 25.31
5 | -0.060419 | -0.015235 | 0.060463 | 0.015262 | 4.3749e-05 | 2.7312e-05 | 0.092128 | 0.092128 | 0.092128 | 0.97621 | -0.45602 | 0.97698 | -0.4409 | 12.655
6 | -0.063162 | -0.015939 | 0.063262 | 0.016001 | 9.9975e-05 | 6.254e-05 | 0.09624 | 0.09624 | 0.09624 | 0.97698 | -0.4409 | 0.97867 | -0.40791 | 13.2198
7 | -0.0010242 | -0.00025669 | 0.0010242 | 0.00025629 | 2.9581e-08 | -3.9838e-07 | 0.0015492 | 0.0015491 | 0.0015492 | 0.98374 | -0.30948 | 0.98377 | -0.30888 | 0.42562
8 | 0.11467 | 0.029125 | -0.11449 | -0.029009 | 0.00018386 | 0.00011684 | 0.17358 | 0.17358 | 0.17358 | 0.98377 | -0.30888 | 0.98205 | -0.34225 | 23.844
9 | -0.11569 | -0.029382 | 0.11574 | 0.029411 | 4.6132e-05 | 2.9321e-05 | 0.17513 | 0.17513 | 0.17513 | 0.98377 | -0.30888 | 0.9842 | -0.3006 | 24.0568
10 | 0.11103 | 0.028144 | -0.11086 | -0.028035 | 0.00017046 | 0.00010828 | 0.16835 | 0.16836 | 0.16836 | 0.98205 | -0.34225 | 0.9804 | -0.37425 | 23.1257
11 | -0.118 | -0.029977 | 0.11838 | 0.03022 | 0.00038146 | 0.00024251 | 0.17855 | 0.17855 | 0.17855 | 0.9842 | -0.3006 | 0.98767 | -0.23368 | 24.5261
12 | 0.10973 | 0.027751 | -0.10969 | -0.027723 | 4.3902e-05 | 2.7884e-05 | 0.16663 | 0.16663 | 0.16663 | 0.9804 | -0.37425 | 0.97997 | -0.38259 | 22.8894
13 | -0.11838 | -0.03022 | 0.11849 | 0.030288 | 0.00010692 | 6.7968e-05 | 0.17855 | 0.17855 | 0.17855 | 0.98767 | -0.23368 | 0.98865 | -0.21501 | 24.526
14 | -0.0015623 | -0.00039154 | 0.0015623 | 0.00039126 | 5.0776e-08 | -2.8592e-07 | 0.0023433 | 0.0023432 | 0.0023433 | 0.99206 | -0.14994 | 0.99209 | -0.14925 | 0.64376
15 | -0.12679 | -0.032519 | 0.12705 | 0.032682 | 0.00025704 | 0.00016353 | 0.19044 | 0.19044 | 0.19044 | 0.99209 | -0.14925 | 0.99429 | -0.10755 | 26.159
16 | 0.12298 | 0.031564 | -0.12279 | -0.031439 | 0.00019628 | 0.00012483 | 0.18472 | 0.18472 | 0.18472 | 0.99209 | -0.14925 | 0.99036 | -0.1822 | 25.3741
17 | -0.12848 | -0.03304 | 0.1287 | 0.033185 | 0.0002278 | 0.00014494 | 0.19257 | 0.19257 | 0.19257 | 0.99429 | -0.10755 | 0.99622 | -0.071137 | 26.4524
18 | 0.12154 | 0.031127 | -0.12141 | -0.031045 | 0.0001279 | 8.1329e-05 | 0.18285 | 0.18285 | 0.18285 | 0.99036 | -0.1822 | 0.98923 | -0.20395 | 25.1169
19 | 0.07114 | 0.018003 | -0.071128 | -0.017995 | 1.2558e-05 | 7.8924e-06 | 0.10808 | 0.10808 | 0.10808 | 0.97997 | -0.38259 | 0.97978 | -0.38627 | 14.8467
20 | 0.038546 | 0.00972 | -0.038508 | -0.0096964 | 3.7455e-05 | 2.3605e-05 | 0.058551 | 0.058551 | 0.058551 | 0.97997 | -0.38259 | 0.97893 | -0.40291 | 16.0853
21 | -0.12001 | -0.03067 | 0.12002 | 0.030675 | 8.51e-06 | 5.4108e-06 | 0.18084 | 0.18084 | 0.18084 | 0.98865 | -0.21501 | 0.98872 | -0.21354 | 24.8412
22 | 0.002035 | 0.00050974 | -0.0020349 | -0.00051 | 9.0869e-08 | -2.6133e-07 | 0.0030905 | 0.0030907 | 0.0030907 | 0.97978 | -0.38627 | 0.97974 | -0.38721 | 0.84908
23 | 0.0057647 | 0.0014435 | -0.005764 | -0.0014433 | 6.9462e-07 | 1.4021e-07 | 0.0087544 | 0.0087546 | 0.0087546 | 0.97978 | -0.38627 | 0.97965 | -0.3888 | 2.4051
24 | 0.063328 | 0.016042 | -0.063262 | -0.016001 | 6.575e-05 | 4.1128e-05 | 0.096239 | 0.09624 | 0.09624 | 0.97978 | -0.38627 | 0.97867 | -0.40791 | 13.2197
25 | 0.036081 | 0.009088 | -0.036064 | -0.0090774 | 1.6758e-05 | 1.0539e-05 | 0.054861 | 0.054861 | 0.054861 | 0.97893 | -0.40291 | 0.97844 | -0.41263 | 15.0716
26 | -0.0022017 | -0.00055179 | 0.0022018 | 0.00055156 | 8.9521e-08 | -2.319e-07 | 0.0032836 | 0.0032835 | 0.0032836 | 0.99774 | -0.042463 | 0.99778 | -0.041609 | 0.90208
27 | 0.12989 | 0.033554 | -0.12974 | -0.033461 | 0.00014733 | 9.3746e-05 | 0.19407 | 0.19407 | 0.19407 | 0.99778 | -0.041609 | 0.99655 | -0.06489 | 26.6577
28 | -0.13209 | -0.034106 | 0.13225 | 0.034204 | 0.00015354 | 9.7715e-05 | 0.19735 | 0.19735 | 0.19735 | 0.99778 | -0.041609 | 0.99905 | -0.017801 | 27.1087
29 | -0.12043 | -0.030778 | 0.12049 | 0.030814 | 5.5907e-05 | 3.5548e-05 | 0.18146 | 0.18146 | 0.18146 | 0.98872 | -0.21354 | 0.98923 | -0.20395 | 24.9258
30 | -0.0043804 | -0.0010974 | 0.0043805 | 0.0010974 | 6.6583e-08 | -7.8618e-09 | 0.0066543 | 0.0066543 | 0.0066543 | 0.97952 | -0.39142 | 0.97954 | -0.3911 | 1.8281
31 | 0.003275 | 0.00082033 | -0.0032748 | -0.00082046 | 1.8807e-07 | -1.3467e-07 | 0.004975 | 0.0049751 | 0.0049751 | 0.97952 | -0.39142 | 0.97946 | -0.39262 | 1.3668
32 | -0.0043805 | -0.0010974 | 0.004381 | 0.0010973 | 4.7957e-07 | -5.6683e-08 | 0.0066543 | 0.0066541 | 0.0066543 | 0.97954 | -0.3911 | 0.97965 | -0.3888 | 1.8281
33 | 0.0011732 | 0.00029396 | -0.0011732 | -0.00029403 | 6.6183e-09 | -6.5687e-08 | 0.0017823 | 0.0017824 | 0.0017824 | 0.97946 | -0.39262 | 0.97945 | -0.39274 | 0.48966
34 | 0.0021016 | 0.0005265 | -0.0021016 | -0.0005267 | 7.712e-08 | -2.0453e-07 | 0.0031928 | 0.0031929 | 0.0031929 | 0.97946 | -0.39262 | 0.97942 | -0.39339 | 0.87716
35 | 0.001383 | 0.00034602 | -0.0013829 | -0.00034659 | 8.0813e-08 | -5.632e-07 | 0.0021004 | 0.0021006 | 0.0021006 | 0.97965 | -0.3888 | 0.97959 | -0.39003 | 0.5771
36 | 0.017015 | 0.0042696 | -0.017012 | -0.0042674 | 3.7014e-06 | 2.1862e-06 | 0.025962 | 0.025962 | 0.025962 | 0.97532 | -0.47383 | 0.97509 | -0.47839 | 7.1324
37 | -0.024222 | -0.0060757 | 0.024229 | 0.0060801 | 7.072e-06 | 4.3537e-06 | 0.036956 | 0.036956 | 0.036956 | 0.97532 | -0.47383 | 0.97563 | -0.4677 | 10.1529
38 | 0.017012 | 0.0042674 | -0.017005 | -0.0042633 | 6.9728e-06 | 4.1187e-06 | 0.025962 | 0.025962 | 0.025962 | 0.97509 | -0.47839 | 0.97465 | -0.48699 | 7.1324
39 | -0.026154 | -0.0065626 | 0.026156 | 0.0065637 | 1.8287e-06 | 1.1321e-06 | 0.039893 | 0.039893 | 0.039893 | 0.97563 | -0.4677 | 0.97571 | -0.46624 | 10.9596
40 | 0.0020614 | 0.00051661 | -0.0020614 | -0.00051664 | 1.176e-08 | -3.193e-08 | 0.0031472 | 0.0031472 | 0.0031472 | 0.97465 | -0.48699 | 0.97465 | -0.48711 | 0.86463
41 | 0.014943 | 0.0037467 | -0.014939 | -0.003744 | 4.6413e-06 | 2.6742e-06 | 0.022815 | 0.022815 | 0.022815 | 0.97465 | -0.48699 | 0.97432 | -0.49351 | 6.2678
42 | -0.031225 | -0.0078342 | 0.031251 | 0.0078502 | 2.5677e-05 | 1.6056e-05 | 0.047624 | 0.047623 | 0.047624 | 0.97571 | -0.46624 | 0.97658 | -0.449 | 13.0834
43 | 0.0018094 | 0.00045332 | -0.0018094 | -0.00045348 | 4.2907e-08 | -1.6178e-07 | 0.0027537 | 0.0027538 | 0.0027538 | 0.97776 | -0.42597 | 0.97773 | -0.42647 | 0.75653
44 | 0.031285 | 0.0078718 | -0.031251 | -0.0078502 | 3.4397e-05 | 2.1508e-05 | 0.047623 | 0.047623 | 0.047623 | 0.97776 | -0.42597 | 0.97658 | -0.449 | 13.0834
45 | -0.033095 | -0.0083251 | 0.033108 | 0.0083335 | 1.3382e-05 | 8.3883e-06 | 0.050377 | 0.050377 | 0.050377 | 0.97776 | -0.42597 | 0.97819 | -0.41751 | 13.8398
46 | -0.035474 | -0.0089265 | 0.035483 | 0.0089317 | 8.2677e-06 | 5.1963e-06 | 0.053976 | 0.053976 | 0.053976 | 0.97819 | -0.41751 | 0.97844 | -0.41263 | 14.8287
47 | 0.012217 | 0.0030618 | -0.012214 | -0.0030606 | 2.2664e-06 | 1.2343e-06 | 0.018657 | 0.018658 | 0.018658 | 0.97432 | -0.49351 | 0.97412 | -0.4974 | 5.1257
48 | 0.0028136 | 0.00070452 | -0.0028131 | -0.00070503 | 4.4496e-07 | -5.1482e-07 | 0.0042976 | 0.0042979 | 0.0042979 | 0.97412 | -0.4974 | 0.97396 | -0.50073 | 1.1807
49 | -0.1287 | -0.033185 | 0.12874 | 0.03321 | 3.9175e-05 | 2.4925e-05 | 0.19257 | 0.19257 | 0.19257 | 0.99622 | -0.071137 | 0.99655 | -0.06489 | 26.4523
50 | -0.13225 | -0.034204 | 0.13236 | 0.034277 | 0.00011505 | 7.3221e-05 | 0.19735 | 0.19735 | 0.19735 | 0.99905 | -0.017801 | 1 | 0 | 27.1087
51 | -0.013127 | -0.00329 | 0.013131 | 0.0032918 | 3.2667e-06 | 1.819e-06 | 0.020017 | 0.020017 | 0.020017 | 0.97585 | -0.46607 | 0.97612 | -0.46085 | 5.4992
52 | 0.0057441 | 0.0014396 | -0.0057435 | -0.0014395 | 6.148e-07 | 1.2652e-07 | 0.0087588 | 0.0087589 | 0.0087589 | 0.97585 | -0.46607 | 0.97574 | -0.46832 | 2.4063
53 | 0.0065541 | 0.0016424 | -0.0065533 | -0.0016422 | 8.0712e-07 | 2.4708e-07 | 0.0099912 | 0.0099913 | 0.0099913 | 0.97612 | -0.46085 | 0.97599 | -0.46343 | 2.7449
54 | -0.019685 | -0.0049342 | 0.01969 | 0.0049377 | 5.6646e-06 | 3.4156e-06 | 0.030008 | 0.030008 | 0.030008 | 0.97612 | -0.46085 | 0.97642 | -0.45481 | 8.244
55 | 0.0065533 | 0.0016422 | -0.0065527 | -0.001642 | 5.975e-07 | 1.8296e-07 | 0.0099913 | 0.0099913 | 0.0099913 | 0.97599 | -0.46343 | 0.97589 | -0.46535 | 2.7449
56 | -0.02071 | -0.0051931 | 0.020716 | 0.005197 | 6.3577e-06 | 3.856e-06 | 0.031562 | 0.031561 | 0.031562 | 0.97642 | -0.45481 | 0.97675 | -0.44837 | 8.6708
57 | 0.0046353 | 0.0011614 | -0.0046349 | -0.0011615 | 3.9525e-07 | -1.0645e-08 | 0.0070677 | 0.0070678 | 0.0070678 | 0.97589 | -0.46535 | 0.9758 | -0.46714 | 1.9417
58 | -0.020716 | -0.005197 | 0.020723 | 0.0052014 | 7.2672e-06 | 4.4074e-06 | 0.031561 | 0.031561 | 0.031561 | 0.97675 | -0.44837 | 0.97712 | -0.44101 | 8.6707
59 | -0.003687 | -0.00092382 | 0.0036871 | 0.00092377 | 1.1161e-07 | -5.0462e-08 | 0.0055724 | 0.0055723 | 0.0055724 | 0.98453 | -0.29734 | 0.98456 | -0.2967 | 1.5309
60 | 0.003687 | 0.00092382 | -0.0036869 | -0.00092384 | 4.1191e-08 | -1.8621e-08 | 0.0055724 | 0.0055724 | 0.0055724 | 0.98453 | -0.29734 | 0.98452 | -0.29757 | 1.5309
61 | -0.0060302 | -0.001511 | 0.0060304 | 0.0015111 | 1.8461e-07 | 4.277e-08 | 0.0091136 | 0.0091136 | 0.0091136 | 0.98456 | -0.2967 | 0.9846 | -0.29606 | 2.5037
62 | 0.0015566 | 0.00038992 | -0.0015565 | -0.00039011 | 3.3509e-08 | -1.8385e-07 | 0.0023526 | 0.0023526 | 0.0023526 | 0.98452 | -0.29757 | 0.9845 | -0.29803 | 0.64633
63 | 0.0020802 | 0.00052119 | -0.0020801 | -0.00052133 | 5.0514e-08 | -1.349e-07 | 0.0031721 | 0.0031721 | 0.0031721 | 0.9758 | -0.46714 | 0.97577 | -0.46765 | 0.87146
64 | -0.021742 | -0.0054568 | 0.021749 | 0.0054611 | 7.1275e-06 | 4.3444e-06 | 0.033113 | 0.033113 | 0.033113 | 0.97712 | -0.44101 | 0.97747 | -0.43414 | 9.097
65 | -0.0081638 | -0.0020457 | 0.008165 | 0.0020462 | 1.2025e-06 | 5.0165e-07 | 0.012338 | 0.012338 | 0.012338 | 0.9846 | -0.29606 | 0.98475 | -0.29297 | 3.3895
66 | -0.022771 | -0.0057172 | 0.022774 | 0.0057191 | 3.0663e-06 | 1.8771e-06 | 0.034669 | 0.034669 | 0.034669 | 0.97747 | -0.43414 | 0.97762 | -0.43132 | 9.5243
67 | -0.00099273 | -0.0002488 | 0.00099274 | 0.00024874 | 4.4213e-09 | -6.407e-08 | 0.0014987 | 0.0014987 | 0.0014987 | 0.98564 | -0.27489 | 0.98565 | -0.2748 | 0.41174
68 | -0.0062722 | -0.0015719 | 0.0062728 | 0.001572 | 6.0425e-07 | 1.5764e-07 | 0.009469 | 0.0094689 | 0.009469 | 0.98565 | -0.2748 | 0.98575 | -0.27278 | 2.6014
69 | 0.056336 | 0.014227 | -0.056267 | -0.014184 | 6.8476e-05 | 4.3506e-05 | 0.085271 | 0.085271 | 0.085271 | 0.98353 | -0.31577 | 0.98223 | -0.34117 | 23.4261
70 | -0.056336 | -0.014227 | 0.056355 | 0.014239 | 1.9059e-05 | 1.2109e-05 | 0.085271 | 0.085271 | 0.085271 | 0.98353 | -0.31577 | 0.98389 | -0.30871 | 23.4261
71 | 0.053232 | 0.013423 | -0.053175 | -0.013387 | 5.6889e-05 | 3.6114e-05 | 0.080673 | 0.080673 | 0.080673 | 0.98223 | -0.34117 | 0.98108 | -0.36352 | 22.1628
72 | -0.057886 | -0.014623 | 0.057986 | 0.014686 | 9.9885e-05 | 6.3485e-05 | 0.087586 | 0.087586 | 0.087586 | 0.98389 | -0.30871 | 0.98575 | -0.27278 | 24.0622
73 | 0.17524 | 0.04479 | -0.17523 | -0.044785 | 7.5457e-06 | 4.8137e-06 | 0.26107 | 0.26107 | 0.26107 | 1 | 0 | 0.99995 | -0.00089026 | 35.8612
74 | -0.010838 | -0.0027163 | 0.010839 | 0.0027163 | 1.1813e-07 | 6.0661e-08 | 0.016377 | 0.016377 | 0.016377 | 0.98475 | -0.29297 | 0.98477 | -0.29274 | 4.4993
75 | -0.01265 | -0.0031702 | 0.012652 | 0.0031717 | 2.7963e-06 | 1.5299e-06 | 0.019114 | 0.019114 | 0.019114 | 0.98477 | -0.29274 | 0.985 | -0.2881 | 5.2511
76 | 0.070045 | 0.017801 | -0.070009 | -0.017779 | 3.5464e-05 | 2.2588e-05 | 0.1054 | 0.1054 | 0.1054 | 0.98966 | -0.19745 | 0.98911 | -0.20797 | 28.9574
77 | -0.073294 | -0.018616 | 0.07337 | 0.018664 | 7.5568e-05 | 4.815e-05 | 0.11029 | 0.11029 | 0.11029 | 0.98966 | -0.19745 | 0.99077 | -0.17605 | 30.2998
78 | 0.068224 | 0.017331 | -0.068154 | -0.017286 | 7.027e-05 | 4.4745e-05 | 0.10272 | 0.10272 | 0.10272 | 0.98911 | -0.20797 | 0.988 | -0.22939 | 28.2197
79 | -0.076101 | -0.019348 | 0.076148 | 0.019378 | 4.7514e-05 | 3.0284e-05 | 0.11439 | 0.11439 | 0.11439 | 0.99077 | -0.17605 | 0.99145 | -0.1631 | 31.4265
80 | 0.064393 | 0.016344 | -0.064259 | -0.016258 | 0.00013408 | 8.5326e-05 | 0.097055 | 0.097055 | 0.097055 | 0.988 | -0.22939 | 0.98575 | -0.27278 | 26.6635
81 | -0.12822 | -0.032514 | 0.12834 | 0.03259 | 0.00011801 | 7.5416e-05 | 0.19257 | 0.19257 | 0.19257 | 0.99145 | -0.1631 | 0.99244 | -0.14398 | 52.9043
82 | 0.05207 | 0.013136 | -0.052013 | -0.0131 | 5.6272e-05 | 3.5698e-05 | 0.078179 | 0.07818 | 0.07818 | 0.99145 | -0.1631 | 0.99028 | -0.1857 | 21.4779
83 | -0.1311 | -0.033283 | 0.13139 | 0.033469 | 0.00029168 | 0.00018642 | 0.19672 | 0.19672 | 0.19672 | 0.99244 | -0.14398 | 0.99485 | -0.097845 | 54.0434
84 | 0.049245 | 0.012406 | -0.049235 | -0.0124 | 9.8116e-06 | 6.218e-06 | 0.074019 | 0.074019 | 0.074019 | 0.99028 | -0.1857 | 0.99006 | -0.18987 | 20.335
85 | -0.13304 | -0.033882 | 0.13323 | 0.034004 | 0.0001904 | 0.00012169 | 0.19918 | 0.19918 | 0.19918 | 0.99485 | -0.097845 | 0.99641 | -0.068219 | 54.72
86 | 0.047255 | 0.011904 | -0.047223 | -0.011884 | 3.1766e-05 | 2.0114e-05 | 0.071044 | 0.071044 | 0.071044 | 0.99006 | -0.18987 | 0.98933 | -0.20393 | 19.5176
87 | 0.038482 | 0.009682 | -0.038475 | -0.0096779 | 6.5624e-06 | 4.131e-06 | 0.057481 | 0.057481 | 0.057481 | 0.99641 | -0.068219 | 0.99622 | -0.071789 | 15.7916
88 | -0.17171 | -0.043686 | 0.17227 | 0.044042 | 0.00055916 | 0.00035668 | 0.25666 | 0.25666 | 0.25666 | 0.99641 | -0.068219 | 0.99995 | -0.00089026 | 35.2557
89 | 0.045503 | 0.011453 | -0.045478 | -0.011437 | 2.5054e-05 | 1.5851e-05 | 0.068457 | 0.068457 | 0.068457 | 0.98933 | -0.20393 | 0.98874 | -0.21546 | 18.8069
90 | 0.035844 | 0.0090185 | -0.035812 | -0.0089983 | 3.2045e-05 | 2.0121e-05 | 0.053551 | 0.053551 | 0.053551 | 0.99622 | -0.071789 | 0.99525 | -0.090517 | 14.7119
91 | 0.034634 | 0.0087031 | -0.034617 | -0.0086925 | 1.7012e-05 | 1.0668e-05 | 0.05179 | 0.051791 | 0.051791 | 0.99525 | -0.090517 | 0.99472 | -0.10081 | 14.2282
92 | 0.050598 | 0.012741 | -0.050591 | -0.012736 | 6.7702e-06 | 4.2942e-06 | 0.076763 | 0.076763 | 0.076763 | 0.98108 | -0.36352 | 0.98094 | -0.36632 | 21.0889
93 | 0.033792 | 0.0084856 | -0.03378 | -0.008478 | 1.2225e-05 | 7.6584e-06 | 0.050556 | 0.050556 | 0.050556 | 0.99472 | -0.10081 | 0.99432 | -0.1084 | 13.889
94 | 0.031935 | 0.0080157 | -0.031927 | -0.0080105 | 8.2569e-06 | 5.1594e-06 | 0.047796 | 0.047796 | 0.047796 | 0.99432 | -0.1084 | 0.99404 | -0.11382 | 13.1307
95 | 0.019663 | 0.0049352 | -0.019653 | -0.0049293 | 9.8157e-06 | 5.8906e-06 | 0.029436 | 0.029436 | 0.029436 | 0.99404 | -0.11382 | 0.9935 | -0.12429 | 8.0869
96 | 0.012264 | 0.0030753 | -0.012262 | -0.0030741 | 2.2895e-06 | 1.2305e-06 | 0.018359 | 0.01836 | 0.01836 | 0.99404 | -0.11382 | 0.99384 | -0.11774 | 5.0438
97 | 0.0019389 | 0.00048483 | -0.0019386 | -0.00048585 | 2.9686e-07 | -1.0256e-06 | 0.0029036 | 0.002904 | 0.002904 | 0.9935 | -0.12429 | 0.99334 | -0.12751 | 0.7978
98 | 0.017714 | 0.0044445 | -0.017711 | -0.0044428 | 2.8056e-06 | 1.658e-06 | 0.026533 | 0.026533 | 0.026533 | 0.9935 | -0.12429 | 0.99333 | -0.12762 | 7.2892
99 | 0.011336 | 0.002842 | -0.011335 | -0.0028417 | 4.9245e-07 | 2.561e-07 | 0.016973 | 0.016973 | 0.016973 | 0.99384 | -0.11774 | 0.99379 | -0.11865 | 4.6629
100 | 0.0165 | 0.0041394 | -0.016495 | -0.0041361 | 5.5434e-06 | 3.2347e-06 | 0.024719 | 0.024719 | 0.024719 | 0.99333 | -0.12762 | 0.99297 | -0.13466 | 6.791
101 | 0.010438 | 0.0026167 | -0.010436 | -0.0026161 | 1.2568e-06 | 6.266e-07 | 0.015629 | 0.015629 | 0.015629 | 0.99379 | -0.11865 | 0.99366 | -0.12118 | 4.2936
102 | 0.014647 | 0.0036729 | -0.014641 | -0.0036701 | 5.0689e-06 | 2.8813e-06 | 0.021949 | 0.02195 | 0.02195 | 0.99297 | -0.13466 | 0.99259 | -0.14193 | 6.0301
103 | 0.0095939 | 0.0024049 | -0.0095932 | -0.0024046 | 7.6409e-07 | 3.6116e-07 | 0.014367 | 0.014367 | 0.014367 | 0.99366 | -0.12118 | 0.99358 | -0.12285 | 3.947
104 | 0.011885 | 0.0029792 | -0.011883 | -0.0029779 | 2.51e-06 | 1.334e-06 | 0.017817 | 0.017818 | 0.017818 | 0.99259 | -0.14193 | 0.99236 | -0.14636 | 4.8949
105 | 0.0086925 | 0.0021788 | -0.008691 | -0.0021782 | 1.414e-06 | 6.1687e-07 | 0.013018 | 0.013018 | 0.013018 | 0.99358 | -0.12285 | 0.9934 | -0.12626 | 3.5765
106 | 0.04057 | 0.010207 | -0.040562 | -0.010202 | 7.5797e-06 | 4.7815e-06 | 0.06107 | 0.06107 | 0.06107 | 0.98874 | -0.21546 | 0.98854 | -0.21937 | 16.7775
107 | 0.034742 | 0.0087437 | -0.034707 | -0.0087219 | 3.4799e-05 | 2.1837e-05 | 0.052309 | 0.05231 | 0.05231 | 0.98854 | -0.21937 | 0.98746 | -0.24035 | 14.3708
108 | 0.0058201 | 0.0014583 | -0.0058196 | -0.0014582 | 5.2915e-07 | 1.0298e-07 | 0.0087607 | 0.0087608 | 0.0087608 | 0.98854 | -0.21937 | 0.98844 | -0.22128 | 2.4068
109 | 0.033387 | 0.008391 | -0.033362 | -0.0083753 | 2.5186e-05 | 1.578e-05 | 0.05032 | 0.05032 | 0.05032 | 0.98746 | -0.24035 | 0.98664 | -0.25616 | 13.8243
110 | 0.0047451 | 0.0011889 | -0.0047448 | -0.0011889 | 3.4906e-07 | -1.0402e-08 | 0.0071433 | 0.0071433 | 0.0071433 | 0.98844 | -0.22128 | 0.98836 | -0.22282 | 1.9625
111 | 0.030221 | 0.0075881 | -0.030212 | -0.0075823 | 9.3043e-06 | 5.8023e-06 | 0.045584 | 0.045584 | 0.045584 | 0.98664 | -0.25616 | 0.98631 | -0.26262 | 12.523
112 | 0.0034653 | 0.00086821 | -0.0034652 | -0.00086825 | 5.3048e-08 | -3.2657e-08 | 0.005217 | 0.005217 | 0.005217 | 0.98836 | -0.22282 | 0.98834 | -0.22314 | 1.4332
113 | 0.026814 | 0.0067308 | -0.026802 | -0.0067232 | 1.2268e-05 | 7.5966e-06 | 0.040458 | 0.040458 | 0.040458 | 0.98631 | -0.26262 | 0.98582 | -0.27222 | 11.1148
114 | 0.0021939 | 0.00054963 | -0.0021938 | -0.00054983 | 7.9244e-08 | -1.9749e-07 | 0.003303 | 0.0033031 | 0.0033031 | 0.98834 | -0.22314 | 0.9883 | -0.2239 | 0.90745
115 | 0.022373 | 0.0056131 | -0.022372 | -0.0056126 | 8.1548e-07 | 4.976e-07 | 0.033772 | 0.033772 | 0.033772 | 0.98582 | -0.27222 | 0.98578 | -0.27298 | 9.2781
116 | -0.024244 | -0.0060875 | 0.02425 | 0.0060909 | 5.5036e-06 | 3.3872e-06 | 0.036906 | 0.036906 | 0.036906 | 0.97762 | -0.43132 | 0.97786 | -0.42656 | 10.139
117 | 0.015088 | 0.0037824 | -0.015087 | -0.0037818 | 1.0353e-06 | 5.9495e-07 | 0.022791 | 0.022791 | 0.022791 | 0.98508 | -0.28666 | 0.985 | -0.2881 | 6.2613
118 | -0.018281 | -0.0045828 | 0.018286 | 0.0045856 | 4.6826e-06 | 2.7883e-06 | 0.027615 | 0.027615 | 0.027615 | 0.98508 | -0.28666 | 0.98535 | -0.28129 | 7.5866
119 | -0.020828 | -0.0052226 | 0.020836 | 0.0052276 | 8.2467e-06 | 4.9946e-06 | 0.031453 | 0.031453 | 0.031453 | 0.98535 | -0.28129 | 0.98578 | -0.27298 | 8.641
120 | -0.0026456 | -0.00066306 | 0.0026459 | 0.0006627 | 2.3139e-07 | -3.5835e-07 | 0.0039674 | 0.0039672 | 0.0039674 | 0.99227 | -0.1482 | 0.99236 | -0.14636 | 1.09
121 | 0.0092368 | 0.0023152 | -0.0092356 | -0.0023147 | 1.1022e-06 | 5.0747e-07 | 0.01385 | 0.01385 | 0.01385 | 0.99236 | -0.14636 | 0.99223 | -0.14887 | 3.8051
122 | 0.0067187 | 0.0016839 | -0.006718 | -0.0016837 | 6.8833e-07 | 2.0703e-07 | 0.010076 | 0.010076 | 0.010076 | 0.99223 | -0.14887 | 0.99212 | -0.15102 | 2.7681
123 | 0.037209 | 0.009347 | -0.037209 | -0.009347 | 6.9045e-08 | 4.3467e-08 | 0.056585 | 0.056585 | 0.056585 | 0.97863 | -0.4115 | 0.97863 | -0.41154 | 15.5453
124 | -0.038679 | -0.0097153 | 0.038679 | 0.0097155 | 2.8838e-07 | 1.8177e-07 | 0.058819 | 0.058819 | 0.058819 | 0.97863 | -0.4115 | 0.97864 | -0.41134 | 16.1591
125 | 0.035845 | 0.0090052 | -0.035845 | -0.0090048 | 6.5632e-07 | 4.1264e-07 | 0.054511 | 0.054511 | 0.054511 | 0.97863 | -0.41154 | 0.97861 | -0.41192 | 14.9756
126 | -0.040149 | -0.010084 | 0.04017 | 0.010097 | 2.1749e-05 | 1.3724e-05 | 0.061054 | 0.061053 | 0.061054 | 0.97864 | -0.41134 | 0.97921 | -0.4 | 16.773
127 | 0.034348 | 0.0086297 | -0.034341 | -0.0086249 | 7.5284e-06 | 4.7258e-06 | 0.052235 | 0.052235 | 0.052235 | 0.97861 | -0.41192 | 0.97837 | -0.41652 | 14.3504
128 | 0.0025056 | 0.00062774 | -0.0025055 | -0.00062793 | 1.1489e-07 | -1.9231e-07 | 0.0038074 | 0.0038075 | 0.0038075 | 0.97921 | -0.4 | 0.97917 | -0.40096 | 1.046
129 | -0.042676 | -0.010725 | 0.042705 | 0.010744 | 2.9086e-05 | 1.8383e-05 | 0.064861 | 0.064861 | 0.064861 | 0.97921 | -0.4 | 0.97994 | -0.38573 | 17.8189
130 | 0.032881 | 0.0082592 | -0.032881 | -0.0082589 | 4.3529e-07 | 2.7276e-07 | 0.050016 | 0.050016 | 0.050016 | 0.97837 | -0.41652 | 0.97836 | -0.41679 | 13.7406
131 | -0.04533 | -0.011402 | 0.045339 | 0.011407 | 8.46e-06 | 5.3544e-06 | 0.068848 | 0.068848 | 0.068848 | 0.97994 | -0.38573 | 0.98014 | -0.38183 | 18.9142
132 | 0.029909 | 0.0075141 | -0.029908 | -0.0075138 | 4.3733e-07 | 2.7282e-07 | 0.045496 | 0.045496 | 0.045496 | 0.97836 | -0.41679 | 0.97834 | -0.4171 | 12.4988
133 | -0.048281 | -0.012144 | 0.048317 | 0.012167 | 3.579e-05 | 2.2682e-05 | 0.073314 | 0.073314 | 0.073314 | 0.98014 | -0.38183 | 0.98094 | -0.36632 | 20.1411
134 | 0.028394 | 0.0071342 | -0.028381 | -0.0071262 | 1.2818e-05 | 7.9733e-06 | 0.043192 | 0.043192 | 0.043192 | 0.97834 | -0.4171 | 0.97786 | -0.42656 | 11.866
135 | 0.0022743 | 0.00056953 | -0.0022741 | -0.00056994 | 1.8854e-07 | -4.1257e-07 | 0.0034498 | 0.0034499 | 0.0034499 | 0.98094 | -0.36632 | 0.98085 | -0.36806 | 0.94779
136 | 0.004131 | 0.0010353 | -0.0041309 | -0.0010353 | 3.1681e-08 | -6.5445e-09 | 0.0062861 | 0.0062861 | 0.0062861 | 0.97786 | -0.42656 | 0.97785 | -0.42672 | 1.727
137 | 0.0074172 | 0.001859 | -0.0074169 | -0.0018589 | 2.8069e-07 | 1.0114e-07 | 0.01111 | 0.01111 | 0.01111 | 0.9934 | -0.12626 | 0.99336 | -0.12706 | 3.0523
138 | 0.006794 | 0.0017027 | -0.0067936 | -0.0017026 | 3.4624e-07 | 1.062e-07 | 0.010177 | 0.010177 | 0.010177 | 0.99336 | -0.12706 | 0.9933 | -0.12813 | 2.7959
139 | 0.0060181 | 0.0015083 | -0.0060177 | -0.0015082 | 3.7527e-07 | 8.0809e-08 | 0.0090154 | 0.0090154 | 0.0090154 | 0.9933 | -0.12813 | 0.99324 | -0.12944 | 2.4768

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31405 | 0.08027

## res_load
| p_mw | q_mvar
0 | 0.012511 | 0.0031356
1 | 0.030336 | 0.007603
2 | 0.017329 | 0.004343
3 | 0.0026998 | 0.00067662
4 | 0.0010242 | 0.00025669
5 | 0.0034514 | 0.000865
6 | 0.0022598 | 0.00056637
7 | 0.0011338 | 0.00028415
8 | 0.0015623 | 0.00039154
9 | 0.002248 | 0.0005634
10 | 0.0014272 | 0.00035768
11 | 0.0012463 | 0.00031236
12 | 0.0015245 | 0.00038208
13 | 0.0024275 | 0.0006084
14 | 0.0022017 | 0.00055179
15 | 0.00040943 | 0.00010261
16 | 0.0011054 | 0.00027704
17 | 0.0011732 | 0.00029403
18 | 0.0021016 | 0.0005267
19 | 0.0072064 | 0.0018061
20 | 0.0019254 | 0.00048254
21 | 0.0013829 | 0.00034659
22 | 0.0050692 | 0.0012705
23 | 0.0020349 | 0.00051
24 | 0.0018094 | 0.00045348
25 | 0.0023663 | 0.00059304
26 | 0.0020614 | 0.00051664
27 | 0.0027222 | 0.00068224
28 | 0.0005815 | 0.00014574
29 | 0.0094007 | 0.002356
30 | 0.0028131 | 0.00070503
31 | 0.0009248 | 0.00023178
32 | 0.0010014 | 0.00025097
33 | 0.0073832 | 0.0018504
34 | 0.0057435 | 0.0014395
35 | 0.0010194 | 0.00025548
36 | 0.0019174 | 0.00048055
37 | 0.0023431 | 0.00058725
38 | 0.0021303 | 0.00053391
39 | 0.0025547 | 0.00064027
40 | 0.0010189 | 0.00025536
41 | 0.0021334 | 0.00053468
42 | 0.0015565 | 0.00039011
43 | 0.0020801 | 0.00052133
44 | 0.0010219 | 0.00025611
45 | 0.00099273 | 0.0002488
46 | 0.0052794 | 0.0013231
47 | 0.0030354 | 0.00076074
48 | 0.001531 | 0.00038371
49 | 0.0048002 | 0.0012031
50 | 0.0026735 | 0.00067004
51 | 0.001811 | 0.00045387
52 | 0.0032498 | 0.00081448
53 | 0.0017851 | 0.00044738
54 | 0.0027308 | 0.0006844
55 | 0.0037612 | 0.00094265
56 | 0.0027655 | 0.00069309
57 | 0.0027686 | 0.00069388
58 | 0.0016467 | 0.00041269
59 | 0.0019796 | 0.00049613
60 | 0.0017202 | 0.00043112
61 | 0.0029624 | 0.00074245
62 | 0.0026311 | 0.00065943
63 | 0.0011779 | 0.0002952
64 | 0.0025774 | 0.00064597
65 | 0.00082529 | 0.00020684
66 | 0.0018445 | 0.00046228
67 | 0.00092614 | 0.00023211
68 | 0.0019386 | 0.00048585
69 | 0.0012108 | 0.00030346
70 | 0.00089786 | 0.00022502
71 | 0.0018483 | 0.00046322
72 | 0.00084239 | 0.00021112
73 | 0.0027563 | 0.0006908
74 | 0.0009007 | 0.00022574
75 | 0.0049084 | 0.0012302
76 | 0.00132 | 0.00033083
77 | 0.0010745 | 0.00026929
78 | 0.0031409 | 0.00078718
79 | 0.0012795 | 0.00032067
80 | 0.0033975 | 0.0008515
81 | 0.0012713 | 0.00031861
82 | 0.0044292 | 0.0011101
83 | 0.0021938 | 0.00054983
84 | 0.0014701 | 0.00036843
85 | 0.0031936 | 0.00080039
86 | 0.0024342 | 0.00061007
87 | 0.0025417 | 0.00063701
88 | 0.0015364 | 0.00038505
89 | 0.0026456 | 0.00066306
90 | 0.0025169 | 0.0006308
91 | 0.006718 | 0.0016837
92 | 0.0014694 | 0.00036827
93 | 0.0013639 | 0.00034183
94 | 0.0014694 | 0.00036827
95 | 0.0014967 | 0.00037511
96 | 0.0014594 | 0.00036575
97 | 0.0025055 | 0.00062793
98 | 0.0026256 | 0.00065803
99 | 0.002972 | 0.00074484
100 | 0.0029418 | 0.00073729
101 | 0.0015146 | 0.0003796
102 | 0.0022741 | 0.00056994
103 | 0.0041309 | 0.0010353
104 | 0.0012738 | 0.00031925
105 | 0.00062296 | 0.00015613
106 | 0.00077552 | 0.00019436
107 | 0.0060177 | 0.0015082

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1