## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1062-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1062-11_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1062-11_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1062-11_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1062-11_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1062-11_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_1062-11_0_4_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_1062-11_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1062-11_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1062-11_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1062-11_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1062-11_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1062-11_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1062-11_0_4_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1062-11_0_4_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1062-11_0_4_node_84 | 0.4 | n |  | TRUE
16 | bus_LV_1062-11_0_4_node_97 | 0.4 | n |  | TRUE
17 | bus_LV_1062-11_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1062-11_0_4_node_249 | 0.4 | n |  | TRUE
19 | bus_LV_1062-11_0_4_node_85 | 0.4 | n |  | TRUE
20 | bus_LV_1062-11_0_4_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_1062-11_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1062-11_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1062-11_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1062-11_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1062-11_0_4_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_1062-11_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1062-11_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1062-11_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1062-11_0_4_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1062-11_0_4_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_1062-11_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1062-11_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_1062-11_0_4_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_1062-11_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_1062-11_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_1062-11_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_1062-11_0_4_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_1062-11_0_4_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_1062-11_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1062-11_0_4_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_1062-11_0_4_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_1062-11_0_4_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_1062-11_0_4_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_1062-11_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_1062-11_0_4_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_1062-11_0_4_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_1062-11_0_4_node_114 | 0.4 | n |  | TRUE
48 | bus_LV_1062-11_0_4_node_75 | 0.4 | n |  | TRUE
49 | bus_LV_1062-11_0_4_node_299 | 0.4 | n |  | TRUE
50 | bus_LV_1062-11_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_1062-11_0_4_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_1062-11_0_4_node_71 | 0.4 | n |  | TRUE
53 | bus_LV_1062-11_0_4_node_70 | 0.4 | n |  | TRUE
54 | bus_LV_1062-11_0_4_node_108 | 0.4 | n |  | TRUE
55 | bus_LV_1062-11_0_4_node_94 | 0.4 | n |  | TRUE
56 | bus_LV_1062-11_0_4_node_95 | 0.4 | n |  | TRUE
57 | bus_LV_1062-11_0_4_node_96 | 0.4 | n |  | TRUE
58 | bus_LV_1062-11_0_4_node_98 | 0.4 | n |  | TRUE
59 | bus_LV_1062-11_0_4_node_211 | 0.4 | n |  | TRUE
60 | bus_LV_1062-11_0_4_node_209 | 0.4 | n |  | TRUE
61 | bus_LV_1062-11_0_4_node_178 | 0.4 | n |  | TRUE
62 | bus_LV_1062-11_0_4_node_179 | 0.4 | n |  | TRUE
63 | bus_LV_1062-11_0_4_node_180 | 0.4 | n |  | TRUE
64 | bus_LV_1062-11_0_4_node_181 | 0.4 | n |  | TRUE
65 | bus_LV_1062-11_0_4_node_182 | 0.4 | n |  | TRUE
66 | bus_LV_1062-11_0_4_node_183 | 0.4 | n |  | TRUE
67 | bus_LV_1062-11_0_4_node_203 | 0.4 | n |  | TRUE
68 | bus_LV_1062-11_0_4_node_217 | 0.4 | n |  | TRUE
69 | bus_LV_1062-11_0_4_node_220 | 0.4 | n |  | TRUE
70 | bus_LV_1062-11_0_4_node_201 | 0.4 | n |  | TRUE
71 | bus_LV_1062-11_0_4_node_202 | 0.4 | n |  | TRUE
72 | bus_LV_1062-11_0_4_node_204 | 0.4 | n |  | TRUE
73 | bus_LV_1062-11_0_4_node_205 | 0.4 | n |  | TRUE
74 | bus_LV_1062-11_0_4_node_235 | 0.4 | n |  | TRUE
75 | bus_LV_1062-11_0_4_node_259 | 0.4 | n |  | TRUE
76 | bus_LV_1062-11_0_4_node_258 | 0.4 | n |  | TRUE
77 | bus_LV_1062-11_0_4_node_210 | 0.4 | n |  | TRUE
78 | bus_LV_1062-11_0_4_node_212 | 0.4 | n |  | TRUE
79 | bus_LV_1062-11_0_4_node_213 | 0.4 | n |  | TRUE
80 | bus_LV_1062-11_0_4_node_254 | 0.4 | n |  | TRUE
81 | bus_LV_1062-11_0_4_node_245 | 0.4 | n |  | TRUE
82 | bus_LV_1062-11_0_4_node_246 | 0.4 | n |  | TRUE
83 | bus_LV_1062-11_0_4_node_247 | 0.4 | n |  | TRUE
84 | bus_LV_1062-11_0_4_node_248 | 0.4 | n |  | TRUE
85 | bus_LV_1062-11_0_4_node_260 | 0.4 | n |  | TRUE
86 | bus_LV_1062-11_0_4_node_255 | 0.4 | n |  | TRUE
87 | bus_LV_1062-11_0_4_node_256 | 0.4 | n |  | TRUE
88 | bus_LV_1062-11_0_4_node_257 | 0.4 | n |  | TRUE
89 | bus_MV_2_0_node_313 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1062-11_0_4_load_0 | 0 | 0.0039048 | 0.00097863 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1062-11_0_4_load_11 | 5 | 0.013974 | 0.0035021 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1062-11_0_4_load_28 | 6 | 0.010784 | 0.0027028 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1062-11_0_4_load_29 | 13 | 0.014119 | 0.0035386 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1062-11_0_4_load_15 | 14 | 0.012989 | 0.0032553 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1062-11_0_4_load_84 | 15 | 0.007062 | 0.0017699 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1062-11_0_4_load_97 | 16 | 0.0039713 | 0.00099529 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1062-11_0_4_load_249 | 18 | 0.0035568 | 0.00089142 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1062-11_0_4_load_85 | 19 | 0.0085268 | 0.002137 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1062-11_0_4_load_45 | 20 | 0.027498 | 0.0068916 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1062-11_0_4_load_12 | 21 | 0.011626 | 0.0029138 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1062-11_0_4_load_13 | 22 | 0.011626 | 0.0029139 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1062-11_0_4_load_14 | 23 | 0.010173 | 0.0025496 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1062-11_0_4_load_16 | 24 | 0.011925 | 0.0029888 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1062-11_0_4_load_25 | 25 | 0.010074 | 0.0025249 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1062-11_0_4_load_17 | 26 | 0.0078282 | 0.0019619 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1062-11_0_4_load_18 | 27 | 0.0062097 | 0.0015563 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1062-11_0_4_load_21 | 29 | 0.00354 | 0.00088722 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1062-11_0_4_load_22 | 31 | 0.013298 | 0.0033327 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1062-11_0_4_load_23 | 32 | 0.035435 | 0.0088808 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1062-11_0_4_load_32 | 33 | 0.010164 | 0.0025473 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1062-11_0_4_load_26 | 34 | 0.010889 | 0.0027291 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1062-11_0_4_load_27 | 35 | 0.033039 | 0.0082805 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1062-11_0_4_load_36 | 37 | 0.0062511 | 0.0015667 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1062-11_0_4_load_34 | 39 | 0.0018605 | 0.00046629 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1062-11_0_4_load_33 | 41 | 0.010101 | 0.0025315 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1062-11_0_4_load_41 | 44 | 0.010538 | 0.0026412 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1062-11_0_4_load_114 | 47 | 0.0019234 | 0.00048206 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1062-11_0_4_load_75 | 48 | 0.00093422 | 0.00023414 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1062-11_0_4_load_299 | 49 | 0.011216 | 0.0028111 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1062-11_0_4_load_42 | 50 | 0.014388 | 0.003606 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1062-11_0_4_load_44 | 51 | 0.001223 | 0.00030651 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1062-11_0_4_load_71 | 52 | 0.0025363 | 0.00063566 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1062-11_0_4_load_70 | 53 | 0.0022479 | 0.00056337 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1062-11_0_4_load_108 | 54 | 0.0046319 | 0.0011609 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1062-11_0_4_load_94 | 55 | 0.0025457 | 0.00063802 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1062-11_0_4_load_95 | 56 | 0.0027051 | 0.00067796 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1062-11_0_4_load_96 | 57 | 0.0018525 | 0.00046428 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1062-11_0_4_load_211 | 59 | 0.0021554 | 0.00054019 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1062-11_0_4_load_209 | 60 | 0.0019836 | 0.00049713 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1062-11_0_4_load_178 | 61 | 0.0012236 | 0.00030665 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1062-11_0_4_load_181 | 64 | 0.00091803 | 0.00023008 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1062-11_0_4_load_182 | 65 | 0.00091934 | 0.00023041 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1062-11_0_4_load_183 | 66 | 0.0028187 | 0.00070644 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1062-11_0_4_load_217 | 68 | 0.0010715 | 0.00026855 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1062-11_0_4_load_220 | 69 | 0.0037702 | 0.00094491 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1062-11_0_4_load_201 | 70 | 0.00098453 | 0.00024675 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1062-11_0_4_load_202 | 71 | 0.002094 | 0.00052481 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1062-11_0_4_load_204 | 72 | 0.002094 | 0.00052481 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1062-11_0_4_load_235 | 74 | 0.0022573 | 0.00056572 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1062-11_0_4_load_259 | 75 | 0.0021858 | 0.00054781 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1062-11_0_4_load_258 | 76 | 0.00082912 | 0.0002078 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1062-11_0_4_load_212 | 78 | 0.0027353 | 0.00068554 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1062-11_0_4_load_213 | 79 | 0.00077608 | 0.0001945 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1062-11_0_4_load_254 | 80 | 0.0016836 | 0.00042194 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1062-11_0_4_load_245 | 81 | 0.017542 | 0.0043965 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1062-11_0_4_load_247 | 83 | 0.007041 | 0.0017646 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1062-11_0_4_load_248 | 84 | 0.0015302 | 0.00038349 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1062-11_0_4_load_260 | 85 | 0.00091679 | 0.00022977 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1062-11_0_4_load_255 | 86 | 0.00086393 | 0.00021652 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1062-11_0_4_load_256 | 87 | 0.0022242 | 0.00055743 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1062-11_0_4_load_257 | 88 | 0.0016342 | 0.00040956 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1062-11_0_4_line_0 |  | 0 | 1 | 0.016822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_1062-11_0_4_line_1 |  | 0 | 2 | 0.075962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_1062-11_0_4_line_2 |  | 1 | 3 | 0.017567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1062-11_0_4_line_3 |  | 1 | 4 | 0.10232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1062-11_0_4_line_4 |  | 2 | 5 | 0.013245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1062-11_0_4_line_5 |  | 3 | 6 | 0.05889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1062-11_0_4_line_6 |  | 4 | 16 | 0.13478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1062-11_0_4_line_7 |  | 5 | 12 | 0.040841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1062-11_0_4_line_8 |  | 6 | 34 | 0.069834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1062-11_0_4_line_9 |  | 7 | 8 | 0.037848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1062-11_0_4_line_10 |  | 7 | 9 | 0.0074581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1062-11_0_4_line_11 |  | 8 | 20 | 0.02155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1062-11_0_4_line_12 |  | 9 | 14 | 0.030402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1062-11_0_4_line_13 |  | 9 | 15 | 0.039701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1062-11_0_4_line_14 |  | 10 | 11 | 0.017569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1062-11_0_4_line_15 |  | 10 | 12 | 0.010015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1062-11_0_4_line_16 |  | 10 | 13 | 0.023973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1062-11_0_4_line_17 |  | 11 | 19 | 0.029246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1062-11_0_4_line_18 |  | 11 | 15 | 0.045562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1062-11_0_4_line_19 |  | 11 | 17 | 0.058979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1062-11_0_4_line_20 |  | 12 | 31 | 0.023219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1062-11_0_4_line_21 |  | 14 | 22 | 0.04235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1062-11_0_4_line_22 |  | 16 | 56 | 0.0028734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1062-11_0_4_line_23 |  | 17 | 18 | 0.028061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1062-11_0_4_line_24 |  | 19 | 54 | 0.018732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1062-11_0_4_line_25 |  | 21 | 22 | 0.038655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1062-11_0_4_line_26 |  | 21 | 23 | 0.035179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1062-11_0_4_line_27 |  | 23 | 24 | 0.028277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1062-11_0_4_line_28 |  | 24 | 25 | 0.019499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1062-11_0_4_line_29 |  | 25 | 33 | 0.019536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1062-11_0_4_line_30 |  | 26 | 27 | 0.037919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1062-11_0_4_line_31 |  | 26 | 28 | 0.027286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1062-11_0_4_line_32 |  | 28 | 29 | 0.062864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1062-11_0_4_line_33 |  | 29 | 30 | 0.024949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1062-11_0_4_line_34 |  | 30 | 43 | 0.051764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1062-11_0_4_line_35 |  | 31 | 32 | 0.0091551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1062-11_0_4_line_36 |  | 33 | 41 | 0.020258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1062-11_0_4_line_37 |  | 34 | 35 | 0.082901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1062-11_0_4_line_38 |  | 36 | 37 | 0.019294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1062-11_0_4_line_39 |  | 36 | 38 | 0.049013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1062-11_0_4_line_40 |  | 36 | 39 | 0.049126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1062-11_0_4_line_41 |  | 38 | 40 | 0.13506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1062-11_0_4_line_42 |  | 38 | 41 | 0.036522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1062-11_0_4_line_43 |  | 39 | 42 | 0.079252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1062-11_0_4_line_44 |  | 40 | 46 | 0.066156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1062-11_0_4_line_45 |  | 40 | 48 | 0.059593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1062-11_0_4_line_46 |  | 42 | 43 | 0.00431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1062-11_0_4_line_47 |  | 42 | 44 | 0.018343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1062-11_0_4_line_48 |  | 43 | 49 | 0.0024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1062-11_0_4_line_49 |  | 45 | 46 | 0.002857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1062-11_0_4_line_50 |  | 45 | 47 | 0.022357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1062-11_0_4_line_51 |  | 46 | 51 | 0.20539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1062-11_0_4_line_52 |  | 46 | 50 | 0.04481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1062-11_0_4_line_53 |  | 51 | 52 | 0.039498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1062-11_0_4_line_54 |  | 52 | 53 | 0.054023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1062-11_0_4_line_55 |  | 55 | 56 | 0.04811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_1062-11_0_4_line_56 |  | 55 | 57 | 0.0063851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_1062-11_0_4_line_57 |  | 57 | 58 | 0.010166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_1062-11_0_4_line_58 |  | 58 | 59 | 0.023797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1062-11_0_4_line_59 |  | 58 | 60 | 0.0059264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_1062-11_0_4_line_60 |  | 60 | 77 | 0.022849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_1062-11_0_4_line_61 |  | 61 | 62 | 0.019498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1062-11_0_4_line_62 |  | 61 | 63 | 0.027627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1062-11_0_4_line_63 |  | 62 | 64 | 0.083794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1062-11_0_4_line_64 |  | 63 | 65 | 0.020289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1062-11_0_4_line_65 |  | 63 | 66 | 0.028528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1062-11_0_4_line_66 |  | 64 | 67 | 0.012765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1062-11_0_4_line_67 |  | 65 | 68 | 0.019125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1062-11_0_4_line_68 |  | 66 | 69 | 0.012093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1062-11_0_4_line_69 |  | 67 | 73 | 0.005921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1062-11_0_4_line_70 |  | 67 | 70 | 0.027635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1062-11_0_4_line_71 |  | 70 | 71 | 0.0012867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1062-11_0_4_line_72 |  | 71 | 72 | 0.0072703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1062-11_0_4_line_73 |  | 72 | 74 | 0.0022135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1062-11_0_4_line_74 |  | 73 | 75 | 0.01467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1062-11_0_4_line_75 |  | 73 | 76 | 0.016484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1062-11_0_4_line_76 |  | 76 | 79 | 0.020139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1062-11_0_4_line_77 |  | 77 | 78 | 0.011379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1062-11_0_4_line_78 |  | 77 | 79 | 0.01081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1062-11_0_4_line_79 |  | 78 | 80 | 0.025624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1062-11_0_4_line_80 |  | 80 | 86 | 0.0037644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1062-11_0_4_line_81 |  | 81 | 82 | 0.0098699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1062-11_0_4_line_82 |  | 82 | 83 | 0.030959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1062-11_0_4_line_83 |  | 82 | 84 | 0.022552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1062-11_0_4_line_84 |  | 84 | 85 | 0.0019617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1062-11_0_4_line_85 |  | 85 | 88 | 0.0079084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1062-11_0_4_line_86 |  | 86 | 87 | 0.00085882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1062-11_0_4_line_87 |  | 87 | 88 | 0.00023592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1062-11_0_4_trafo_10 | 0.63 MVA 20/0.4 kV | 89 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2656655.6081 | 1210560.3822 | 2656656.4068 | 1210569.1062 | 2656658.3503 | 1210576.9304
1 | 2656702.7471 | 1210636.62 | 2656700.669 | 1210635.3773 | 2656690.9746 | 1210627.8807 | 2656681.3543 | 1210618.1835 | 2656673.3253 | 1210608.1679 | 2656664.3077 | 1210592.6175 | 2656659.2469 | 1210580.54 | 2656658.3503 | 1210576.9304
2 | 2656655.6081 | 1210560.3822 | 2656655.8445 | 1210553.8917 | 2656658.1192 | 1210548.0431 | 2656662.1492 | 1210545.4243
3 | 2656604.4082 | 1210631.6614 | 2656606.8524 | 1210612.7511 | 2656610.7303 | 1210600.525 | 2656618.3341 | 1210592.092 | 2656632.4631 | 1210583.9767 | 2656643.6081 | 1210580.3803 | 2656642.8122 | 1210576.1591 | 2656642.3638 | 1210573.7646 | 2656645.4928 | 1210569.1804 | 2656645.146 | 1210560.8833 | 2656646.1498 | 1210560.815 | 2656650.6444 | 1210560.4908 | 2656654.4147 | 1210560.4043 | 2656655.6081 | 1210560.3822
4 | 2656702.7471 | 1210636.62 | 2656703.5818 | 1210635.1492 | 2656705.5348 | 1210635.9683 | 2656707.5934 | 1210632.0633 | 2656712.6047 | 1210631.744
5 | 2656662.1492 | 1210545.4243 | 2656720.6125 | 1210538.3457
6 | 2656604.4082 | 1210631.6614 | 2656604.62 | 1210663.0044 | 2656607.0162 | 1210674.7787 | 2656614.6689 | 1210687.6034 | 2656625.6152 | 1210697.7133 | 2656678.4916 | 1210729.2905
7 | 2656748.0854 | 1210651.9711 | 2656712.6047 | 1210631.744
8 | 2656720.6125 | 1210538.3457 | 2656744.1394 | 1210535.4972 | 2656789.9485 | 1210530.0202
9 | 2656840.1705 | 1210720.6107 | 2656819.0219 | 1210706.9233 | 2656808.1492 | 1210700.2936
10 | 2656804.8859 | 1210706.9999 | 2656805.2346 | 1210706.2917 | 2656806.4904 | 1210703.7021 | 2656807.7694 | 1210701.0683 | 2656808.1492 | 1210700.2936
11 | 2656842.7834 | 1210699.2227 | 2656841.1265 | 1210712.7929 | 2656840.1705 | 1210720.6107
12 | 2656804.8859 | 1210706.9999 | 2656826.7963 | 1210720.4944 | 2656830.6898 | 1210723.0714
13 | 2656804.8859 | 1210706.9999 | 2656770.8983 | 1210686.4821
14 | 2656731.8925 | 1210662.9349 | 2656733.619 | 1210659.5937 | 2656742.1059 | 1210664.5996 | 2656743.7966 | 1210661.0247
15 | 2656748.0854 | 1210651.9711 | 2656743.7966 | 1210661.0247
16 | 2656743.7966 | 1210661.0247 | 2656764.2603 | 1210673.5119
17 | 2656731.8925 | 1210662.9349 | 2656725.4369 | 1210691.459
18 | 2656731.8925 | 1210662.9349 | 2656770.8983 | 1210686.4821
19 | 2656731.8925 | 1210662.9349 | 2656696.2895 | 1210641.1836 | 2656690.3173 | 1210637.0688 | 2656682.4283 | 1210630.7234
20 | 2656748.0854 | 1210651.9711 | 2656753.0704 | 1210629.2932
21 | 2656830.6898 | 1210723.0714 | 2656840.0727 | 1210729.2816 | 2656861.354 | 1210744.9715 | 2656864.9935 | 1210747.8788
22 | 2656678.4916 | 1210729.2905 | 2656680.9586 | 1210730.7637
23 | 2656682.4283 | 1210630.7234 | 2656677.8686 | 1210643.4989 | 2656672.1733 | 1210648.6368 | 2656666.3206 | 1210652.1496
24 | 2656721.302 | 1210709.729 | 2656725.4369 | 1210691.459
25 | 2656895.1952 | 1210772.0048 | 2656864.9935 | 1210747.8788
26 | 2656895.1952 | 1210772.0048 | 2656922.6809 | 1210793.9613
27 | 2656944.7744 | 1210811.6103 | 2656922.6809 | 1210793.9613
28 | 2656960.1189 | 1210823.6394 | 2656954.9962 | 1210819.7758 | 2656944.7744 | 1210811.6103
29 | 2656960.1189 | 1210823.6394 | 2656975.7158 | 1210835.403
30 | 2657000.8588 | 1210661.7031 | 2657037.729 | 1210670.5602
31 | 2657064.2602 | 1210676.9337 | 2657037.729 | 1210670.5602
32 | 2657064.2602 | 1210676.9337 | 2657048.3692 | 1210737.7555
33 | 2657042.0623 | 1210761.8947 | 2657048.3692 | 1210737.7555
34 | 2657042.0623 | 1210761.8947 | 2656991.8563 | 1210748.7183
35 | 2656755.0359 | 1210620.3516 | 2656753.0704 | 1210629.2932
36 | 2656975.7158 | 1210835.403 | 2656985.1692 | 1210842.533 | 2656992.1072 | 1210847.2997
37 | 2656789.9485 | 1210530.0202 | 2656800.5565 | 1210528.7519 | 2656829.5231 | 1210525.9926 | 2656838.9439 | 1210527.9057 | 2656843.73 | 1210537.6682 | 2656861.8787 | 1210551.1936
38 | 2657000.4015 | 1210836.6527 | 2656996.5993 | 1210837.7059 | 2656992.5674 | 1210837.345 | 2656985.921 | 1210833.835 | 2656982.9578 | 1210831.4804
39 | 2657000.4015 | 1210836.6527 | 2657001.2939 | 1210837.1059 | 2657008.2211 | 1210840.652 | 2657004.2293 | 1210848.0294 | 2657003.0226 | 1210850.2525 | 2657024.8811 | 1210863.5026 | 2657022.9883 | 1210866.742
40 | 2657000.4015 | 1210836.6527 | 2657001.9025 | 1210836.2446 | 2657006.9787 | 1210833.0911 | 2657012.1279 | 1210827.8594 | 2657018.6646 | 1210816.6151 | 2657025.4103 | 1210803.3716 | 2657027.7023 | 1210797.4116
41 | 2657022.9883 | 1210866.742 | 2657024.8811 | 1210863.5026 | 2657035.2394 | 1210869.0382 | 2657050.8038 | 1210876.9028 | 2657063.7755 | 1210882.5191 | 2657084.4592 | 1210890.6551 | 2657101.9418 | 1210896.5925 | 2657138.9661 | 1210907.698 | 2657139.7224 | 1210904.9035 | 2657139.9508 | 1210904.0719 | 2657144.6259 | 1210905.4953
42 | 2657022.9883 | 1210866.742 | 2657007.2904 | 1210857.7311 | 2656992.1072 | 1210847.2997
43 | 2656990.7222 | 1210752.8767 | 2657031.5254 | 1210763.0947 | 2657034.088 | 1210765.3206 | 2657035.6975 | 1210768.6713 | 2657035.7837 | 1210772.3743 | 2657033.5465 | 1210782.2144 | 2657027.7023 | 1210797.4116
44 | 2657208.3762 | 1210923.8281 | 2657175.446 | 1210914.5403 | 2657154.8637 | 1210908.5284 | 2657144.6259 | 1210905.4953
45 | 2657144.6259 | 1210905.4953 | 2657144.6676 | 1210904.3172 | 2657143.6889 | 1210894.6353 | 2657142.9361 | 1210887.535 | 2657143.6288 | 1210874.7228 | 2657146.8331 | 1210862.3127 | 2657148.2468 | 1210857.5345 | 2657150.7341 | 1210846.9095
46 | 2656991.8563 | 1210748.7183 | 2656990.7222 | 1210752.8767
47 | 2656985.9022 | 1210770.5746 | 2656990.7222 | 1210752.8767
48 | 2656989.529 | 1210748.1069 | 2656991.8563 | 1210748.7183
49 | 2657207.6884 | 1210926.6009 | 2657208.3762 | 1210923.8281
50 | 2657207.6884 | 1210926.6009 | 2657212.4101 | 1210927.9247 | 2657229.2191 | 1210932.6215
51 | 2657208.3762 | 1210923.8281 | 2657217.8574 | 1210926.4983 | 2657311.3568 | 1210952.9223 | 2657383.4717 | 1210973.75 | 2657405.8803 | 1210980.183
52 | 2657208.3762 | 1210923.8281 | 2657212.7081 | 1210906.3702 | 2657186.8532 | 1210899.2311
53 | 2657405.8803 | 1210980.183 | 2657439.5895 | 1210959.5972
54 | 2657461.1587 | 1210910.7059 | 2657458.2713 | 1210923.2948 | 2657451.161 | 1210941.9487 | 2657440.5095 | 1210957.4444 | 2657439.5895 | 1210959.5972
55 | 2656680.9586 | 1210730.7637 | 2656716.6285 | 1210752.0655 | 2656720.9336 | 1210757.0201
56 | 2656721.8514 | 1210763.0445 | 2656721.8982 | 1210758.1303 | 2656720.9336 | 1210757.0201
57 | 2656719.4486 | 1210772.7825 | 2656721.8192 | 1210766.4345 | 2656721.8514 | 1210763.0445
58 | 2656719.4486 | 1210772.7825 | 2656696.3589 | 1210767.0226
59 | 2656719.4486 | 1210772.7825 | 2656724.0057 | 1210776.5713
60 | 2656744.5923 | 1210785.896 | 2656732.9453 | 1210782.3832 | 2656725.8198 | 1210778.0795 | 2656724.0057 | 1210776.5713
61 | 2656718.3378 | 1210917.581 | 2656721.3823 | 1210913.8855 | 2656722.8749 | 1210911.1536 | 2656724.9361 | 1210904.5803 | 2656725.4166 | 1210899.8973
62 | 2656721.128 | 1210872.6917 | 2656725.6564 | 1210897.5607 | 2656725.4166 | 1210899.8973
63 | 2656718.3378 | 1210917.581 | 2656721.1442 | 1210917.3408 | 2656724.4272 | 1210914.9373 | 2656727.9522 | 1210908.667 | 2656729.6651 | 1210900.3561 | 2656729.7365 | 1210892.8411 | 2656726.3933 | 1210880.0016 | 2656728.9049 | 1210867.6181 | 2656724.2046 | 1210856.0331 | 2656725.0048 | 1210840.7446
64 | 2656721.128 | 1210872.6917 | 2656724.4166 | 1210873.7013 | 2656734.4644 | 1210876.7542 | 2656740.537 | 1210878.6017
65 | 2656721.128 | 1210872.6917 | 2656693.7541 | 1210864.6607
66 | 2656725.6719 | 1210827.9969 | 2656725.0048 | 1210840.7446
67 | 2656758.8335 | 1210884.1681 | 2656740.537 | 1210878.6017
68 | 2656693.7541 | 1210864.6607 | 2656682.1499 | 1210861.2563
69 | 2656731.6048 | 1210828.2424 | 2656729.9867 | 1210828.1825 | 2656727.3279 | 1210828.0683 | 2656725.6719 | 1210827.9969
70 | 2656725.6719 | 1210827.9969 | 2656698.6135 | 1210822.3798
71 | 2656697.3537 | 1210822.1182 | 2656698.6135 | 1210822.3798
72 | 2656690.2352 | 1210820.6405 | 2656697.3537 | 1210822.1182
73 | 2656688.0679 | 1210820.1906 | 2656690.2352 | 1210820.6405
74 | 2656731.6048 | 1210828.2424 | 2656734.8443 | 1210831.2083 | 2656735.7656 | 1210837.4207 | 2656739.4204 | 1210839.0787
75 | 2656731.6048 | 1210828.2424 | 2656734.7606 | 1210821.6351 | 2656734.3174 | 1210812.4841
76 | 2656734.3174 | 1210812.4841 | 2656733.7506 | 1210800.7796 | 2656740.6588 | 1210795.9646
77 | 2656744.5923 | 1210785.896 | 2656755.1813 | 1210790.0618
78 | 2656744.5923 | 1210785.896 | 2656740.6588 | 1210795.9646
79 | 2656779.026 | 1210799.4427 | 2656755.1813 | 1210790.0618
80 | 2656779.026 | 1210799.4427 | 2656779.026 | 1210799.4427 | 2656782.2148 | 1210801.4433
81 | 2656808.1347 | 1210822.3222 | 2656814.827 | 1210829.5768
82 | 2656819.8346 | 1210848.994 | 2656819.0974 | 1210845.0069 | 2656807.9779 | 1210831.6041 | 2656807.0335 | 1210827.8262 | 2656808.1347 | 1210822.3222
83 | 2656808.1347 | 1210822.3222 | 2656796.4616 | 1210810.3818 | 2656791.5029 | 1210807.2707
84 | 2656791.5029 | 1210807.2707 | 2656789.8412 | 1210806.2281
85 | 2656783.1422 | 1210802.0251 | 2656789.8412 | 1210806.2281
86 | 2656782.2148 | 1210801.4433 | 2656782.9423 | 1210801.8997
87 | 2656782.9423 | 1210801.8997 | 2656783.1422 | 1210802.0251

## bus_geodata
| x | y | coords
0 | 2656658.3503 | 1210576.9304
1 | 2656655.6081 | 1210560.3822
2 | 2656702.7471 | 1210636.62
3 | 2656662.1492 | 1210545.4243
4 | 2656604.4082 | 1210631.6614
5 | 2656712.6047 | 1210631.744
6 | 2656720.6125 | 1210538.3457
7 | 2656808.1492 | 1210700.2936
8 | 2656840.1705 | 1210720.6107
9 | 2656804.8859 | 1210706.9999
10 | 2656743.7966 | 1210661.0247
11 | 2656731.8925 | 1210662.9349
12 | 2656748.0854 | 1210651.9711
13 | 2656764.2603 | 1210673.5119
14 | 2656830.6898 | 1210723.0714
15 | 2656770.8983 | 1210686.4821
16 | 2656678.4916 | 1210729.2905
17 | 2656682.4283 | 1210630.7234
18 | 2656666.3206 | 1210652.1496
19 | 2656725.4369 | 1210691.459
20 | 2656842.7834 | 1210699.2227
21 | 2656895.1952 | 1210772.0048
22 | 2656864.9935 | 1210747.8788
23 | 2656922.6809 | 1210793.9613
24 | 2656944.7744 | 1210811.6103
25 | 2656960.1189 | 1210823.6394
26 | 2657037.729 | 1210670.5602
27 | 2657000.8588 | 1210661.7031
28 | 2657064.2602 | 1210676.9337
29 | 2657048.3692 | 1210737.7555
30 | 2657042.0623 | 1210761.8947
31 | 2656753.0704 | 1210629.2932
32 | 2656755.0359 | 1210620.3516
33 | 2656975.7158 | 1210835.403
34 | 2656789.9485 | 1210530.0202
35 | 2656861.8787 | 1210551.1936
36 | 2657000.4015 | 1210836.6527
37 | 2656982.9578 | 1210831.4804
38 | 2657022.9883 | 1210866.742
39 | 2657027.7023 | 1210797.4116
40 | 2657144.6259 | 1210905.4953
41 | 2656992.1072 | 1210847.2997
42 | 2656990.7222 | 1210752.8767
43 | 2656991.8563 | 1210748.7183
44 | 2656985.9022 | 1210770.5746
45 | 2657207.6884 | 1210926.6009
46 | 2657208.3762 | 1210923.8281
47 | 2657229.2191 | 1210932.6215
48 | 2657150.7341 | 1210846.9095
49 | 2656989.529 | 1210748.1069
50 | 2657186.8532 | 1210899.2311
51 | 2657405.8803 | 1210980.183
52 | 2657439.5895 | 1210959.5972
53 | 2657461.1587 | 1210910.7059
54 | 2656721.302 | 1210709.729
55 | 2656720.9336 | 1210757.0201
56 | 2656680.9586 | 1210730.7637
57 | 2656721.8514 | 1210763.0445
58 | 2656719.4486 | 1210772.7825
59 | 2656696.3589 | 1210767.0226
60 | 2656724.0057 | 1210776.5713
61 | 2656725.4166 | 1210899.8973
62 | 2656718.3378 | 1210917.581
63 | 2656721.128 | 1210872.6917
64 | 2656725.0048 | 1210840.7446
65 | 2656740.537 | 1210878.6017
66 | 2656693.7541 | 1210864.6607
67 | 2656725.6719 | 1210827.9969
68 | 2656758.8335 | 1210884.1681
69 | 2656682.1499 | 1210861.2563
70 | 2656698.6135 | 1210822.3798
71 | 2656697.3537 | 1210822.1182
72 | 2656690.2352 | 1210820.6405
73 | 2656731.6048 | 1210828.2424
74 | 2656688.0679 | 1210820.1906
75 | 2656739.4204 | 1210839.0787
76 | 2656734.3174 | 1210812.4841
77 | 2656744.5923 | 1210785.896
78 | 2656755.1813 | 1210790.0618
79 | 2656740.6588 | 1210795.9646
80 | 2656779.026 | 1210799.4427
81 | 2656814.827 | 1210829.5768
82 | 2656808.1347 | 1210822.3222
83 | 2656819.8346 | 1210848.994
84 | 2656791.5029 | 1210807.2707
85 | 2656789.8412 | 1210806.2281
86 | 2656782.2148 | 1210801.4433
87 | 2656782.9423 | 1210801.8997
88 | 2656783.1422 | 1210802.0251
89 | 2656839.643 | 1210724.9305

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98123 | -0.359 | 0.0039048 | 0.00097863
1 | 0.98056 | -0.37201 | 0 | 0
2 | 0.98434 | -0.29868 | 0 | 0
3 | 0.97966 | -0.38945 | 0 | 0
4 | 0.97822 | -0.41748 | 0 | 0
5 | 0.98489 | -0.2882 | 0.013974 | 0.0035021
6 | 0.97666 | -0.44815 | 0.010784 | 0.0027028
7 | 0.99542 | -0.086608 | 0 | 0
8 | 1 | 0 | -0.42852 | -0.10983
9 | 0.99451 | -0.10377 | 0 | 0
10 | 0.98734 | -0.24093 | 0 | 0
11 | 0.98848 | -0.21909 | 0 | 0
12 | 0.98674 | -0.25256 | 0 | 0
13 | 0.98703 | -0.24698 | 0.014119 | 0.0035386
14 | 0.99302 | -0.13228 | 0.012989 | 0.0032553
15 | 0.99166 | -0.15818 | 0.007062 | 0.0017699
16 | 0.97515 | -0.4777 | 0.0039713 | 0.00099529
17 | 0.98829 | -0.22283 | 0 | 0
18 | 0.9882 | -0.22462 | 0.0035568 | 0.00089142
19 | 0.98813 | -0.22596 | 0.0085268 | 0.002137
20 | 0.99946 | -0.010334 | 0.027498 | 0.0068916
21 | 0.9895 | -0.19976 | 0.011626 | 0.0029138
22 | 0.9911 | -0.16889 | 0.011626 | 0.0029139
23 | 0.98816 | -0.22551 | 0.010173 | 0.0025496
24 | 0.98717 | -0.24454 | 0.011925 | 0.0029888
25 | 0.98534 | -0.27986 | 0.010074 | 0.0025249
26 | 0.97023 | -0.5753 | 0.0078282 | 0.0019619
27 | 0.97001 | -0.57966 | 0.0062097 | 0.0015563
28 | 0.97059 | -0.56821 | 0 | 0
29 | 0.97141 | -0.55189 | 0.00354 | 0.00088722
30 | 0.97182 | -0.54379 | 0 | 0
31 | 0.9857 | -0.27284 | 0.013298 | 0.0033327
32 | 0.9854 | -0.27866 | 0.035435 | 0.0088808
33 | 0.98368 | -0.31182 | 0.010164 | 0.0025473
34 | 0.97379 | -0.50438 | 0.010889 | 0.0027291
35 | 0.97124 | -0.55485 | 0.033039 | 0.0082805
36 | 0.97758 | -0.43048 | 0 | 0
37 | 0.97747 | -0.43268 | 0.0062511 | 0.0015667
38 | 0.97975 | -0.38815 | 0 | 0
39 | 0.97569 | -0.46747 | 0.0018605 | 0.00046629
40 | 0.97683 | -0.44539 | 0 | 0
41 | 0.98216 | -0.34136 | 0.010101 | 0.0025315
42 | 0.97279 | -0.52473 | 0 | 0
43 | 0.97267 | -0.52701 | 0 | 0
44 | 0.97261 | -0.52829 | 0.010538 | 0.0026412
45 | 0.97545 | -0.47252 | 0 | 0
46 | 0.97546 | -0.47242 | 0 | 0
47 | 0.97541 | -0.4733 | 0.0019234 | 0.00048206
48 | 0.97678 | -0.44641 | 0.00093422 | 0.00023414
49 | 0.97264 | -0.52751 | 0.011216 | 0.0028111
50 | 0.97486 | -0.48423 | 0.014388 | 0.003606
51 | 0.97431 | -0.49507 | 0.001223 | 0.00030651
52 | 0.97413 | -0.49854 | 0.0025363 | 0.00063566
53 | 0.97402 | -0.50077 | 0.0022479 | 0.00056337
54 | 0.98805 | -0.22751 | 0.0046319 | 0.0011609
55 | 0.97409 | -0.49854 | 0.0025457 | 0.00063802
56 | 0.97509 | -0.47892 | 0.0027051 | 0.00067796
57 | 0.97396 | -0.50104 | 0.0018525 | 0.00046428
58 | 0.97377 | -0.50492 | 0 | 0
59 | 0.97372 | -0.50586 | 0.0021554 | 0.00054019
60 | 0.97366 | -0.5071 | 0.0019836 | 0.00049713
61 | 0.97114 | -0.55686 | 0.0012236 | 0.00030665
62 | 0.97131 | -0.55333 | 0 | 0
63 | 0.97092 | -0.56125 | 0 | 0
64 | 0.97208 | -0.53816 | 0.00091803 | 0.00023008
65 | 0.97088 | -0.56199 | 0.00091934 | 0.00023041
66 | 0.97074 | -0.56472 | 0.0028187 | 0.00070644
67 | 0.97221 | -0.53563 | 0 | 0
68 | 0.97086 | -0.56237 | 0.0010715 | 0.00026855
69 | 0.9707 | -0.56557 | 0.0037702 | 0.00094491
70 | 0.97202 | -0.53942 | 0.00098453 | 0.00024675
71 | 0.97201 | -0.53957 | 0.002094 | 0.00052481
72 | 0.97198 | -0.54016 | 0.002094 | 0.00052481
73 | 0.97231 | -0.53365 | 0 | 0
74 | 0.97198 | -0.54025 | 0.0022573 | 0.00056572
75 | 0.97228 | -0.53424 | 0.0021858 | 0.00054781
76 | 0.97262 | -0.52747 | 0.00082912 | 0.0002078
77 | 0.97324 | -0.51525 | 0 | 0
78 | 0.97286 | -0.52282 | 0.0027353 | 0.00068554
79 | 0.97302 | -0.51961 | 0.00077608 | 0.0001945
80 | 0.97206 | -0.53862 | 0.0016836 | 0.00042194
81 | 0.97099 | -0.55977 | 0.017542 | 0.0043965
82 | 0.97115 | -0.55657 | 0 | 0
83 | 0.97095 | -0.5606 | 0.007041 | 0.0017646
84 | 0.97167 | -0.54633 | 0.0015302 | 0.00038349
85 | 0.97172 | -0.54538 | 0.00091679 | 0.00022977
86 | 0.97195 | -0.54082 | 0.00086393 | 0.00021652
87 | 0.97192 | -0.54131 | 0.0022242 | 0.00055743
88 | 0.97192 | -0.54144 | 0.0016342 | 0.00040956
89 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.12911 | 0.032751 | -0.12903 | -0.0327 | 8.0725e-05 | 5.1027e-05 | 0.19593 | 0.19593 | 0.19593 | 0.98123 | -0.359 | 0.98056 | -0.37201 | 17.9425
1 | -0.13301 | -0.03373 | 0.1334 | 0.033975 | 0.00038688 | 0.00024472 | 0.20185 | 0.20185 | 0.20185 | 0.98123 | -0.359 | 0.98434 | -0.29868 | 18.4848
2 | 0.055112 | 0.013965 | -0.055066 | -0.013936 | 4.6138e-05 | 2.9307e-05 | 0.083688 | 0.083688 | 0.083688 | 0.98056 | -0.37201 | 0.97966 | -0.38945 | 22.9913
3 | 0.073915 | 0.018736 | -0.073754 | -0.018636 | 0.00016114 | 9.9264e-05 | 0.11224 | 0.11225 | 0.11225 | 0.98056 | -0.37201 | 0.97822 | -0.41748 | 10.2789
4 | -0.1334 | -0.033975 | 0.13347 | 0.034017 | 6.7456e-05 | 4.2666e-05 | 0.20185 | 0.20185 | 0.20185 | 0.98434 | -0.29868 | 0.98489 | -0.2882 | 18.4847
5 | 0.055066 | 0.013936 | -0.054911 | -0.013837 | 0.00015467 | 9.825e-05 | 0.083688 | 0.083689 | 0.083689 | 0.97966 | -0.38945 | 0.97666 | -0.44815 | 22.9914
6 | 0.073754 | 0.018636 | -0.073542 | -0.018506 | 0.00021227 | 0.00013079 | 0.11225 | 0.11225 | 0.11225 | 0.97822 | -0.41748 | 0.97515 | -0.4777 | 10.279
7 | -0.14744 | -0.03752 | 0.14769 | 0.03768 | 0.00025379 | 0.00016087 | 0.22296 | 0.22296 | 0.22296 | 0.98489 | -0.2882 | 0.98674 | -0.25256 | 20.418
8 | 0.044127 | 0.011134 | -0.044008 | -0.01106 | 0.00011846 | 7.4946e-05 | 0.067258 | 0.067258 | 0.067258 | 0.97666 | -0.44815 | 0.97379 | -0.50438 | 18.4775
9 | -0.39768 | -0.10186 | 0.39936 | 0.10293 | 0.0016764 | 0.0010714 | 0.59527 | 0.59526 | 0.59527 | 0.99542 | -0.086608 | 1 | 0 | 54.5115
10 | 0.39768 | 0.10186 | -0.39735 | -0.10165 | 0.00033034 | 0.00021113 | 0.59527 | 0.59527 | 0.59527 | 0.99542 | -0.086608 | 0.99451 | -0.10377 | 54.5115
11 | 0.027511 | 0.0069 | -0.027498 | -0.0068916 | 1.3544e-05 | 8.3859e-06 | 0.040939 | 0.040939 | 0.040939 | 1 | 0 | 0.99946 | -0.010334 | 11.2471
12 | 0.16134 | 0.04118 | -0.16112 | -0.041039 | 0.00022194 | 0.00014086 | 0.24167 | 0.24167 | 0.24167 | 0.99451 | -0.10377 | 0.99302 | -0.13228 | 22.1307
13 | 0.23601 | 0.060466 | -0.23539 | -0.060071 | 0.00062048 | 0.00039557 | 0.3536 | 0.3536 | 0.3536 | 0.99451 | -0.10377 | 0.99166 | -0.15818 | 32.3808
14 | -0.21072 | -0.053541 | 0.21094 | 0.053682 | 0.00022184 | 0.0001413 | 0.31783 | 0.31783 | 0.31783 | 0.98734 | -0.24093 | 0.98848 | -0.21909 | 29.1055
15 | 0.19659 | 0.05 | -0.19648 | -0.04993 | 0.00011009 | 7.0073e-05 | 0.29655 | 0.29655 | 0.29655 | 0.98734 | -0.24093 | 0.98674 | -0.25256 | 27.1562
16 | 0.014123 | 0.0035409 | -0.014119 | -0.0035386 | 4.0731e-06 | 2.3003e-06 | 0.021286 | 0.021286 | 0.021286 | 0.98734 | -0.24093 | 0.98703 | -0.24698 | 5.8477
17 | 0.013163 | 0.0033003 | -0.013159 | -0.0032979 | 4.3066e-06 | 2.3814e-06 | 0.019816 | 0.019816 | 0.019816 | 0.98848 | -0.21909 | 0.98813 | -0.22596 | 5.444
18 | -0.22766 | -0.057874 | 0.22833 | 0.058301 | 0.00067005 | 0.00042708 | 0.343 | 0.343 | 0.343 | 0.98848 | -0.21909 | 0.99166 | -0.15818 | 31.4105
19 | 0.0035577 | 0.0008909 | -0.0035571 | -0.00089125 | 6.3436e-07 | -3.499e-07 | 0.0053554 | 0.0053557 | 0.0053557 | 0.98848 | -0.21909 | 0.98829 | -0.22283 | 1.4713
20 | 0.04879 | 0.01225 | -0.048742 | -0.01222 | 4.7145e-05 | 2.9877e-05 | 0.073583 | 0.073583 | 0.073583 | 0.98674 | -0.25256 | 0.9857 | -0.27284 | 20.2151
21 | 0.14813 | 0.037783 | -0.14787 | -0.037618 | 0.00026138 | 0.00016564 | 0.2222 | 0.2222 | 0.2222 | 0.99302 | -0.13228 | 0.9911 | -0.16889 | 20.3484
22 | 0.069571 | 0.01751 | -0.069567 | -0.017508 | 4.0499e-06 | 2.4844e-06 | 0.10619 | 0.10619 | 0.10619 | 0.97515 | -0.4777 | 0.97509 | -0.47892 | 9.7241
23 | 0.0035571 | 0.00089125 | -0.0035568 | -0.00089142 | 3.0184e-07 | -1.6636e-07 | 0.0053557 | 0.0053558 | 0.0053558 | 0.98829 | -0.22283 | 0.9882 | -0.22462 | 1.4714
24 | 0.0046323 | 0.0011609 | -0.0046319 | -0.0011609 | 3.4182e-07 | -2.1166e-08 | 0.0069757 | 0.0069758 | 0.0069758 | 0.98813 | -0.22596 | 0.98805 | -0.22751 | 1.9164
25 | -0.13604 | -0.034576 | 0.13624 | 0.034704 | 0.00020256 | 0.00012815 | 0.20475 | 0.20475 | 0.20475 | 0.9895 | -0.19976 | 0.9911 | -0.16889 | 18.75
26 | 0.12441 | 0.031662 | -0.12426 | -0.031565 | 0.00015421 | 9.734e-05 | 0.18727 | 0.18727 | 0.18727 | 0.9895 | -0.19976 | 0.98816 | -0.22551 | 17.149
27 | 0.11409 | 0.029015 | -0.11398 | -0.028949 | 0.00010451 | 6.5798e-05 | 0.17195 | 0.17195 | 0.17195 | 0.98816 | -0.22551 | 0.98717 | -0.24454 | 15.7462
28 | 0.10206 | 0.025961 | -0.10188 | -0.02585 | 0.00017335 | 0.0001107 | 0.15397 | 0.15397 | 0.15397 | 0.98717 | -0.24454 | 0.98534 | -0.27986 | 42.3002
29 | 0.091809 | 0.023325 | -0.091668 | -0.023235 | 0.00014105 | 9.0025e-05 | 0.13876 | 0.13876 | 0.13876 | 0.98534 | -0.27986 | 0.98368 | -0.31182 | 38.1206
30 | 0.006211 | 0.0015566 | -0.0062097 | -0.0015563 | 1.2903e-06 | 3.5759e-07 | 0.0095256 | 0.0095258 | 0.0095258 | 0.97023 | -0.5753 | 0.97001 | -0.57966 | 2.617
31 | -0.014039 | -0.0035186 | 0.014044 | 0.0035213 | 4.7437e-06 | 2.6989e-06 | 0.021531 | 0.021531 | 0.021531 | 0.97023 | -0.5753 | 0.97059 | -0.56821 | 5.9152
32 | -0.014044 | -0.0035213 | 0.014055 | 0.0035275 | 1.0929e-05 | 6.2168e-06 | 0.021531 | 0.021531 | 0.021531 | 0.97059 | -0.56821 | 0.97141 | -0.55189 | 5.9152
33 | -0.017595 | -0.0044147 | 0.017602 | 0.0044187 | 6.7972e-06 | 4.0412e-06 | 0.026954 | 0.026954 | 0.026954 | 0.97141 | -0.55189 | 0.97182 | -0.54379 | 7.4049
34 | -0.017602 | -0.0044187 | 0.017616 | 0.0044271 | 1.4102e-05 | 8.3836e-06 | 0.026954 | 0.026953 | 0.026954 | 0.97182 | -0.54379 | 0.97267 | -0.52701 | 7.4048
35 | 0.035445 | 0.008887 | -0.035435 | -0.0088808 | 9.8298e-06 | 6.1744e-06 | 0.053509 | 0.053509 | 0.053509 | 0.9857 | -0.27284 | 0.9854 | -0.27866 | 14.7003
36 | 0.081504 | 0.020688 | -0.081388 | -0.020614 | 0.00011565 | 7.3761e-05 | 0.12338 | 0.12338 | 0.12338 | 0.98368 | -0.31182 | 0.98216 | -0.34136 | 33.8967
37 | 0.033119 | 0.0083304 | -0.033039 | -0.0082805 | 7.9656e-05 | 4.9951e-05 | 0.050619 | 0.050619 | 0.050619 | 0.97379 | -0.50438 | 0.97124 | -0.55485 | 13.9064
38 | 0.0062518 | 0.0015669 | -0.0062511 | -0.0015667 | 6.5521e-07 | 1.7745e-07 | 0.009516 | 0.0095161 | 0.0095161 | 0.97758 | -0.43048 | 0.97747 | -0.43268 | 2.6143
39 | -0.047669 | -0.01203 | 0.047766 | 0.012091 | 9.6847e-05 | 6.1366e-05 | 0.072589 | 0.072589 | 0.072589 | 0.97758 | -0.43048 | 0.97975 | -0.38815 | 19.942
40 | 0.041417 | 0.010463 | -0.041344 | -0.010417 | 7.3288e-05 | 4.6289e-05 | 0.063073 | 0.063073 | 0.063073 | 0.97758 | -0.43048 | 0.97569 | -0.46747 | 17.3277
41 | 0.023361 | 0.0058892 | -0.023297 | -0.0058501 | 6.3802e-05 | 3.9138e-05 | 0.035493 | 0.035493 | 0.035493 | 0.97975 | -0.38815 | 0.97683 | -0.44539 | 9.7509
42 | -0.071127 | -0.01798 | 0.071287 | 0.018082 | 0.00015999 | 0.00010193 | 0.10808 | 0.10808 | 0.10808 | 0.97975 | -0.38815 | 0.98216 | -0.34136 | 29.6926
43 | 0.039484 | 0.0099504 | -0.039376 | -0.0098824 | 0.00010783 | 6.8026e-05 | 0.060236 | 0.060236 | 0.060236 | 0.97569 | -0.46747 | 0.97279 | -0.52473 | 16.5483
44 | 0.022363 | 0.0056166 | -0.022334 | -0.005599 | 2.8798e-05 | 1.7603e-05 | 0.03407 | 0.034071 | 0.034071 | 0.97683 | -0.44539 | 0.97546 | -0.47242 | 9.3601
45 | 0.00093427 | 0.00023342 | -0.00093422 | -0.00023414 | 4.5255e-08 | -7.1701e-07 | 0.0014229 | 0.0014232 | 0.0014232 | 0.97683 | -0.44539 | 0.97678 | -0.44641 | 0.39098
46 | 0.028836 | 0.0072403 | -0.028832 | -0.0072384 | 3.1451e-06 | 1.9594e-06 | 0.044113 | 0.044113 | 0.044113 | 0.97279 | -0.52473 | 0.97267 | -0.52701 | 12.1189
47 | 0.01054 | 0.0026421 | -0.010538 | -0.0026412 | 1.7881e-06 | 9.167e-07 | 0.016123 | 0.016123 | 0.016123 | 0.97279 | -0.52473 | 0.97261 | -0.52829 | 4.4294
48 | 0.011217 | 0.0028112 | -0.011216 | -0.0028111 | 2.6501e-07 | 1.3982e-07 | 0.01716 | 0.01716 | 0.01716 | 0.97267 | -0.52701 | 0.97264 | -0.52751 | 4.7142
49 | -0.0019235 | -0.00048182 | 0.0019235 | 0.00048179 | 9.2236e-09 | -2.9761e-08 | 0.0029341 | 0.0029341 | 0.0029341 | 0.97545 | -0.47252 | 0.97546 | -0.47242 | 0.80608
50 | 0.0019235 | 0.00048182 | -0.0019234 | -0.00048206 | 7.2179e-08 | -2.3287e-07 | 0.0029341 | 0.0029342 | 0.0029342 | 0.97545 | -0.47252 | 0.97541 | -0.4733 | 0.80611
51 | 0.0060147 | 0.0015066 | -0.0060082 | -0.001505 | 6.484e-06 | 1.5889e-06 | 0.0091748 | 0.0091758 | 0.0091758 | 0.97546 | -0.47242 | 0.97431 | -0.49507 | 2.5208
52 | 0.014396 | 0.0036106 | -0.014388 | -0.003606 | 8.1047e-06 | 4.628e-06 | 0.021962 | 0.021962 | 0.021962 | 0.97546 | -0.47242 | 0.97486 | -0.48423 | 6.0335
53 | 0.0047852 | 0.0011985 | -0.0047844 | -0.0011985 | 7.9105e-07 | 1.4461e-08 | 0.0073079 | 0.0073081 | 0.0073081 | 0.97431 | -0.49507 | 0.97413 | -0.49854 | 2.0077
54 | 0.0022481 | 0.00056285 | -0.0022479 | -0.00056337 | 2.3889e-07 | -5.1959e-07 | 0.0034338 | 0.0034341 | 0.0034341 | 0.97413 | -0.49854 | 0.97402 | -0.50077 | 0.94343
55 | -0.066799 | -0.016792 | 0.066862 | 0.01683 | 6.264e-05 | 3.8291e-05 | 0.10206 | 0.10206 | 0.10206 | 0.97409 | -0.49854 | 0.97509 | -0.47892 | 9.3461
56 | 0.064253 | 0.016154 | -0.064245 | -0.016149 | 7.6921e-06 | 4.6845e-06 | 0.098171 | 0.098171 | 0.098171 | 0.97409 | -0.49854 | 0.97396 | -0.50104 | 8.99
57 | 0.062393 | 0.015685 | -0.062381 | -0.015678 | 1.1551e-05 | 7.0134e-06 | 0.095341 | 0.095341 | 0.095341 | 0.97396 | -0.50104 | 0.97377 | -0.50492 | 8.7309
58 | 0.0021555 | 0.00053995 | -0.0021554 | -0.00054019 | 9.6814e-08 | -2.3406e-07 | 0.0032937 | 0.0032938 | 0.0032938 | 0.97377 | -0.50492 | 0.97372 | -0.50586 | 0.90489
59 | 0.060226 | 0.015138 | -0.06022 | -0.015134 | 6.2766e-06 | 3.7959e-06 | 0.092047 | 0.092047 | 0.092047 | 0.97377 | -0.50492 | 0.97366 | -0.5071 | 8.4292
60 | 0.058236 | 0.014637 | -0.058213 | -0.014623 | 2.2631e-05 | 1.3632e-05 | 0.089016 | 0.089016 | 0.089016 | 0.97366 | -0.5071 | 0.97324 | -0.51525 | 8.1517
61 | -0.0098065 | -0.0024576 | 0.0098082 | 0.0024584 | 1.6508e-06 | 8.1522e-07 | 0.015026 | 0.015026 | 0.015026 | 0.97114 | -0.55686 | 0.97131 | -0.55333 | 4.128
62 | 0.0085829 | 0.002151 | -0.0085811 | -0.0021502 | 1.7918e-06 | 8.0501e-07 | 0.013151 | 0.013151 | 0.013151 | 0.97114 | -0.55686 | 0.97092 | -0.56125 | 3.613
63 | -0.0098082 | -0.0024584 | 0.0098152 | 0.0024619 | 7.0943e-06 | 3.5024e-06 | 0.015026 | 0.015025 | 0.015026 | 0.97131 | -0.55333 | 0.97208 | -0.53816 | 4.128
64 | 0.001991 | 0.00049853 | -0.0019909 | -0.00049873 | 7.0832e-08 | -2.0557e-07 | 0.0030512 | 0.0030512 | 0.0030512 | 0.97092 | -0.56125 | 0.97088 | -0.56199 | 0.83825
65 | 0.0065902 | 0.0016516 | -0.0065891 | -0.0016513 | 1.0913e-06 | 3.457e-07 | 0.0101 | 0.0101 | 0.0101 | 0.97092 | -0.56125 | 0.97074 | -0.56472 | 2.7748
66 | -0.010733 | -0.002692 | 0.010735 | 0.0026927 | 1.2923e-06 | 6.6881e-07 | 0.016431 | 0.016431 | 0.016431 | 0.97208 | -0.53816 | 0.97221 | -0.53563 | 4.5139
67 | 0.0010715 | 0.00026833 | -0.0010715 | -0.00026855 | 1.9342e-08 | -2.2412e-07 | 0.0016422 | 0.0016423 | 0.0016423 | 0.97088 | -0.56199 | 0.97086 | -0.56237 | 0.45118
68 | 0.0037704 | 0.00094486 | -0.0037702 | -0.00094491 | 1.5148e-07 | -5.2552e-08 | 0.0057795 | 0.0057795 | 0.0057795 | 0.97074 | -0.56472 | 0.9707 | -0.56557 | 1.5878
69 | -0.018166 | -0.0045553 | 0.018168 | 0.0045563 | 1.7166e-06 | 1.0252e-06 | 0.027805 | 0.027805 | 0.027805 | 0.97221 | -0.53563 | 0.97231 | -0.53365 | 7.6387
70 | 0.0074313 | 0.0018626 | -0.00743 | -0.0018621 | 1.3407e-06 | 5.1543e-07 | 0.011374 | 0.011374 | 0.011374 | 0.97221 | -0.53563 | 0.97202 | -0.53942 | 3.1248
71 | 0.0064455 | 0.0016153 | -0.0064454 | -0.0016153 | 4.6978e-08 | 1.4116e-08 | 0.009867 | 0.009867 | 0.009867 | 0.97202 | -0.53942 | 0.97201 | -0.53957 | 2.7107
72 | 0.0043514 | 0.0010905 | -0.0043513 | -0.0010905 | 1.2098e-07 | -1.2686e-08 | 0.0066614 | 0.0066614 | 0.0066614 | 0.97201 | -0.53957 | 0.97198 | -0.54016 | 1.8301
73 | 0.0022573 | 0.0005657 | -0.0022573 | -0.00056572 | 9.9122e-09 | -2.1091e-08 | 0.0034557 | 0.0034557 | 0.0034557 | 0.97198 | -0.54016 | 0.97198 | -0.54025 | 0.94937
74 | 0.0021859 | 0.00054767 | -0.0021858 | -0.00054781 | 6.1561e-08 | -1.4254e-07 | 0.0033452 | 0.0033452 | 0.0033452 | 0.97231 | -0.53365 | 0.97228 | -0.53424 | 0.91902
75 | -0.020353 | -0.005104 | 0.020359 | 0.0051076 | 5.998e-06 | 3.6342e-06 | 0.03115 | 0.03115 | 0.03115 | 0.97231 | -0.53365 | 0.97262 | -0.52747 | 8.5577
76 | -0.021189 | -0.0053154 | 0.021197 | 0.0053202 | 7.9368e-06 | 4.8295e-06 | 0.032418 | 0.032418 | 0.032418 | 0.97262 | -0.52747 | 0.97302 | -0.51961 | 8.9061
77 | 0.036236 | 0.0091055 | -0.036223 | -0.0090973 | 1.3102e-05 | 8.2438e-06 | 0.055411 | 0.055411 | 0.055411 | 0.97324 | -0.51525 | 0.97286 | -0.52282 | 15.2229
78 | 0.021977 | 0.0055175 | -0.021973 | -0.0055147 | 4.5778e-06 | 2.7955e-06 | 0.033605 | 0.033605 | 0.033605 | 0.97324 | -0.51525 | 0.97302 | -0.51961 | 9.2321
79 | 0.033488 | 0.0084117 | -0.033463 | -0.0083959 | 2.5216e-05 | 1.582e-05 | 0.051228 | 0.051228 | 0.051228 | 0.97286 | -0.52282 | 0.97206 | -0.53862 | 14.0735
80 | 0.031779 | 0.007974 | -0.031776 | -0.0079719 | 3.3412e-06 | 2.0917e-06 | 0.04865 | 0.04865 | 0.04865 | 0.97206 | -0.53862 | 0.97195 | -0.54082 | 13.3655
81 | -0.017542 | -0.0043965 | 0.017545 | 0.0043981 | 2.6749e-06 | 1.5898e-06 | 0.026883 | 0.026883 | 0.026883 | 0.97099 | -0.55977 | 0.97115 | -0.55657 | 7.3855
82 | 0.0070424 | 0.0017651 | -0.007041 | -0.0017646 | 1.3518e-06 | 4.8216e-07 | 0.01079 | 0.010791 | 0.010791 | 0.97115 | -0.55657 | 0.97095 | -0.5606 | 2.9645
83 | -0.024587 | -0.0061632 | 0.024599 | 0.0061706 | 1.2003e-05 | 7.4028e-06 | 0.037674 | 0.037674 | 0.037674 | 0.97115 | -0.55657 | 0.97167 | -0.54633 | 10.3499
84 | -0.02613 | -0.0065541 | 0.026131 | 0.0065549 | 1.178e-06 | 7.2963e-07 | 0.040017 | 0.040017 | 0.040017 | 0.97167 | -0.54633 | 0.97172 | -0.54538 | 10.9936
85 | -0.027047 | -0.0067846 | 0.027053 | 0.0067878 | 5.0881e-06 | 3.1584e-06 | 0.041421 | 0.041421 | 0.041421 | 0.97172 | -0.54538 | 0.97192 | -0.54144 | 11.3793
86 | 0.030912 | 0.0077553 | -0.030911 | -0.0077549 | 7.2138e-07 | 4.5104e-07 | 0.047328 | 0.047328 | 0.047328 | 0.97195 | -0.54082 | 0.97192 | -0.54131 | 13.0022
87 | 0.028687 | 0.0071975 | -0.028687 | -0.0071973 | 1.7068e-07 | 1.0631e-07 | 0.043923 | 0.043923 | 0.043923 | 0.97192 | -0.54131 | 0.97192 | -0.54144 | 12.0667

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42852 | 0.10983

## res_load
| p_mw | q_mvar
0 | 0.0039048 | 0.00097863
1 | 0.013974 | 0.0035021
2 | 0.010784 | 0.0027028
3 | 0.014119 | 0.0035386
4 | 0.012989 | 0.0032553
5 | 0.007062 | 0.0017699
6 | 0.0039713 | 0.00099529
7 | 0.0035568 | 0.00089142
8 | 0.0085268 | 0.002137
9 | 0.027498 | 0.0068916
10 | 0.011626 | 0.0029138
11 | 0.011626 | 0.0029139
12 | 0.010173 | 0.0025496
13 | 0.011925 | 0.0029888
14 | 0.010074 | 0.0025249
15 | 0.0078282 | 0.0019619
16 | 0.0062097 | 0.0015563
17 | 0.00354 | 0.00088722
18 | 0.013298 | 0.0033327
19 | 0.035435 | 0.0088808
20 | 0.010164 | 0.0025473
21 | 0.010889 | 0.0027291
22 | 0.033039 | 0.0082805
23 | 0.0062511 | 0.0015667
24 | 0.0018605 | 0.00046629
25 | 0.010101 | 0.0025315
26 | 0.010538 | 0.0026412
27 | 0.0019234 | 0.00048206
28 | 0.00093422 | 0.00023414
29 | 0.011216 | 0.0028111
30 | 0.014388 | 0.003606
31 | 0.001223 | 0.00030651
32 | 0.0025363 | 0.00063566
33 | 0.0022479 | 0.00056337
34 | 0.0046319 | 0.0011609
35 | 0.0025457 | 0.00063802
36 | 0.0027051 | 0.00067796
37 | 0.0018525 | 0.00046428
38 | 0.0021554 | 0.00054019
39 | 0.0019836 | 0.00049713
40 | 0.0012236 | 0.00030665
41 | 0.00091803 | 0.00023008
42 | 0.00091934 | 0.00023041
43 | 0.0028187 | 0.00070644
44 | 0.0010715 | 0.00026855
45 | 0.0037702 | 0.00094491
46 | 0.00098453 | 0.00024675
47 | 0.002094 | 0.00052481
48 | 0.002094 | 0.00052481
49 | 0.0022573 | 0.00056572
50 | 0.0021858 | 0.00054781
51 | 0.00082912 | 0.0002078
52 | 0.0027353 | 0.00068554
53 | 0.00077608 | 0.0001945
54 | 0.0016836 | 0.00042194
55 | 0.017542 | 0.0043965
56 | 0.007041 | 0.0017646
57 | 0.0015302 | 0.00038349
58 | 0.00091679 | 0.00022977
59 | 0.00086393 | 0.00021652
60 | 0.0022242 | 0.00055743
61 | 0.0016342 | 0.00040956

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1