## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1062-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1062-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1062-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1062-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1062-1_0_4_node_46 | 0.4 | n |  | TRUE
5 | bus_LV_1062-1_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1062-1_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1062-1_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1062-1_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1062-1_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_1062-1_0_4_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_1062-1_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1062-1_0_4_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_1062-1_0_4_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1062-1_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_1062-1_0_4_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_1062-1_0_4_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_1062-1_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1062-1_0_4_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1062-1_0_4_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1062-1_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1062-1_0_4_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1062-1_0_4_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1062-1_0_4_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1062-1_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1062-1_0_4_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_1062-1_0_4_node_42 | 0.4 | n |  | TRUE
27 | bus_LV_1062-1_0_4_node_92 | 0.4 | n |  | TRUE
28 | bus_LV_1062-1_0_4_node_89 | 0.4 | n |  | TRUE
29 | bus_LV_1062-1_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1062-1_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1062-1_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1062-1_0_4_node_91 | 0.4 | n |  | TRUE
33 | bus_LV_1062-1_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1062-1_0_4_node_72 | 0.4 | n |  | TRUE
35 | bus_LV_1062-1_0_4_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_1062-1_0_4_node_73 | 0.4 | n |  | TRUE
37 | bus_LV_1062-1_0_4_node_116 | 0.4 | n |  | TRUE
38 | bus_LV_1062-1_0_4_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1062-1_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1062-1_0_4_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_1062-1_0_4_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1062-1_0_4_node_60 | 0.4 | n |  | TRUE
43 | bus_LV_1062-1_0_4_node_269 | 0.4 | n |  | TRUE
44 | bus_LV_1062-1_0_4_node_111 | 0.4 | n |  | TRUE
45 | bus_LV_1062-1_0_4_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_1062-1_0_4_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_1062-1_0_4_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_1062-1_0_4_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_1062-1_0_4_node_79 | 0.4 | n |  | TRUE
50 | bus_LV_1062-1_0_4_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_1062-1_0_4_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_1062-1_0_4_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_1062-1_0_4_node_69 | 0.4 | n |  | TRUE
54 | bus_LV_1062-1_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_1062-1_0_4_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_1062-1_0_4_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_1062-1_0_4_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_1062-1_0_4_node_52 | 0.4 | n |  | TRUE
59 | bus_LV_1062-1_0_4_node_101 | 0.4 | n |  | TRUE
60 | bus_LV_1062-1_0_4_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_1062-1_0_4_node_61 | 0.4 | n |  | TRUE
62 | bus_LV_1062-1_0_4_node_67 | 0.4 | n |  | TRUE
63 | bus_LV_1062-1_0_4_node_68 | 0.4 | n |  | TRUE
64 | bus_LV_1062-1_0_4_node_70 | 0.4 | n |  | TRUE
65 | bus_LV_1062-1_0_4_node_71 | 0.4 | n |  | TRUE
66 | bus_LV_1062-1_0_4_node_81 | 0.4 | n |  | TRUE
67 | bus_LV_1062-1_0_4_node_340 | 0.4 | n |  | TRUE
68 | bus_LV_1062-1_0_4_node_80 | 0.4 | n |  | TRUE
69 | bus_LV_1062-1_0_4_node_90 | 0.4 | n |  | TRUE
70 | bus_LV_1062-1_0_4_node_93 | 0.4 | n |  | TRUE
71 | bus_LV_1062-1_0_4_node_94 | 0.4 | n |  | TRUE
72 | bus_LV_1062-1_0_4_node_165 | 0.4 | n |  | TRUE
73 | bus_LV_1062-1_0_4_node_97 | 0.4 | n |  | TRUE
74 | bus_LV_1062-1_0_4_node_98 | 0.4 | n |  | TRUE
75 | bus_LV_1062-1_0_4_node_99 | 0.4 | n |  | TRUE
76 | bus_LV_1062-1_0_4_node_100 | 0.4 | n |  | TRUE
77 | bus_LV_1062-1_0_4_node_102 | 0.4 | n |  | TRUE
78 | bus_LV_1062-1_0_4_node_108 | 0.4 | n |  | TRUE
79 | bus_LV_1062-1_0_4_node_117 | 0.4 | n |  | TRUE
80 | bus_LV_1062-1_0_4_node_341 | 0.4 | n |  | TRUE
81 | bus_LV_1062-1_0_4_node_110 | 0.4 | n |  | TRUE
82 | bus_LV_1062-1_0_4_node_112 | 0.4 | n |  | TRUE
83 | bus_LV_1062-1_0_4_node_251 | 0.4 | n |  | TRUE
84 | bus_LV_1062-1_0_4_node_136 | 0.4 | n |  | TRUE
85 | bus_LV_1062-1_0_4_node_137 | 0.4 | n |  | TRUE
86 | bus_LV_1062-1_0_4_node_138 | 0.4 | n |  | TRUE
87 | bus_LV_1062-1_0_4_node_139 | 0.4 | n |  | TRUE
88 | bus_LV_1062-1_0_4_node_158 | 0.4 | n |  | TRUE
89 | bus_LV_1062-1_0_4_node_140 | 0.4 | n |  | TRUE
90 | bus_LV_1062-1_0_4_node_141 | 0.4 | n |  | TRUE
91 | bus_LV_1062-1_0_4_node_144 | 0.4 | n |  | TRUE
92 | bus_LV_1062-1_0_4_node_142 | 0.4 | n |  | TRUE
93 | bus_LV_1062-1_0_4_node_143 | 0.4 | n |  | TRUE
94 | bus_LV_1062-1_0_4_node_156 | 0.4 | n |  | TRUE
95 | bus_LV_1062-1_0_4_node_154 | 0.4 | n |  | TRUE
96 | bus_LV_1062-1_0_4_node_145 | 0.4 | n |  | TRUE
97 | bus_LV_1062-1_0_4_node_146 | 0.4 | n |  | TRUE
98 | bus_LV_1062-1_0_4_node_147 | 0.4 | n |  | TRUE
99 | bus_LV_1062-1_0_4_node_148 | 0.4 | n |  | TRUE
100 | bus_LV_1062-1_0_4_node_149 | 0.4 | n |  | TRUE
101 | bus_LV_1062-1_0_4_node_150 | 0.4 | n |  | TRUE
102 | bus_LV_1062-1_0_4_node_151 | 0.4 | n |  | TRUE
103 | bus_LV_1062-1_0_4_node_152 | 0.4 | n |  | TRUE
104 | bus_LV_1062-1_0_4_node_159 | 0.4 | n |  | TRUE
105 | bus_LV_1062-1_0_4_node_157 | 0.4 | n |  | TRUE
106 | bus_LV_1062-1_0_4_node_153 | 0.4 | n |  | TRUE
107 | bus_LV_1062-1_0_4_node_155 | 0.4 | n |  | TRUE
108 | bus_LV_1062-1_0_4_node_189 | 0.4 | n |  | TRUE
109 | bus_LV_1062-1_0_4_node_190 | 0.4 | n |  | TRUE
110 | bus_LV_1062-1_0_4_node_191 | 0.4 | n |  | TRUE
111 | bus_LV_1062-1_0_4_node_192 | 0.4 | n |  | TRUE
112 | bus_LV_1062-1_0_4_node_193 | 0.4 | n |  | TRUE
113 | bus_LV_1062-1_0_4_node_242 | 0.4 | n |  | TRUE
114 | bus_LV_1062-1_0_4_node_253 | 0.4 | n |  | TRUE
115 | bus_LV_1062-1_0_4_node_211 | 0.4 | n |  | TRUE
116 | bus_LV_1062-1_0_4_node_213 | 0.4 | n |  | TRUE
117 | bus_LV_1062-1_0_4_node_215 | 0.4 | n |  | TRUE
118 | bus_LV_1062-1_0_4_node_281 | 0.4 | n |  | TRUE
119 | bus_LV_1062-1_0_4_node_252 | 0.4 | n |  | TRUE
120 | bus_LV_1062-1_0_4_node_279 | 0.4 | n |  | TRUE
121 | bus_MV_3_0_node_82 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1062-1_0_4_load_0 | 0 | 0.0011012 | 0.00027599 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1062-1_0_4_load_1 | 1 | 0.008361 | 0.0020955 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1062-1_0_4_load_2 | 2 | 0.0019326 | 0.00048436 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1062-1_0_4_load_6 | 5 | 0.014881 | 0.0037296 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1062-1_0_4_load_7 | 6 | 0.011739 | 0.0029421 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1062-1_0_4_load_9 | 8 | 0.019616 | 0.0049161 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1062-1_0_4_load_10 | 9 | 0.047016 | 0.011783 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1062-1_0_4_load_12 | 11 | 0.0020408 | 0.00051147 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1062-1_0_4_load_13 | 12 | 0.0028616 | 0.00071719 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1062-1_0_4_load_39 | 16 | 0.014428 | 0.003616 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1062-1_0_4_load_17 | 17 | 0.022841 | 0.0057244 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1062-1_0_4_load_21 | 21 | 0.023194 | 0.0058129 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1062-1_0_4_load_22 | 22 | 0.0035838 | 0.00089819 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1062-1_0_4_load_23 | 23 | 0.0003801 | 9.5263e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1062-1_0_4_load_24 | 24 | 0.0057604 | 0.0014437 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1062-1_0_4_load_42 | 26 | 0.0021405 | 0.00053646 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1062-1_0_4_load_92 | 27 | 0.00052264 | 0.00013099 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1062-1_0_4_load_89 | 28 | 0.0012651 | 0.00031706 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1062-1_0_4_load_25 | 29 | 0.0024405 | 0.00061165 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1062-1_0_4_load_26 | 30 | 0.00026236 | 6.5753e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1062-1_0_4_load_28 | 31 | 0.00061404 | 0.00015389 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1062-1_0_4_load_91 | 32 | 0.00015998 | 4.0094e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1062-1_0_4_load_31 | 33 | 0.0040469 | 0.0010142 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1062-1_0_4_load_72 | 34 | 0.0068074 | 0.0017061 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1062-1_0_4_load_116 | 37 | 0.0021902 | 0.0005489 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1062-1_0_4_load_33 | 38 | 0.00045811 | 0.00011481 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1062-1_0_4_load_34 | 39 | 0.00042204 | 0.00010577 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1062-1_0_4_load_35 | 40 | 0.00034629 | 8.6787e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1062-1_0_4_load_60 | 42 | 0.0046718 | 0.0011709 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1062-1_0_4_load_269 | 43 | 0.00050672 | 0.000127 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1062-1_0_4_load_37 | 45 | 0.001951 | 0.00048896 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1062-1_0_4_load_40 | 47 | 0.00018934 | 4.7453e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1062-1_0_4_load_41 | 48 | 0.0016254 | 0.00040738 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1062-1_0_4_load_79 | 49 | 0.00029095 | 7.2919e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1062-1_0_4_load_44 | 50 | 0.0021103 | 0.0005289 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1062-1_0_4_load_45 | 51 | 0.00038376 | 9.6179e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1062-1_0_4_load_47 | 52 | 0.00042464 | 0.00010643 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1062-1_0_4_load_48 | 54 | 0.004082 | 0.0010231 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1062-1_0_4_load_49 | 55 | 0.017134 | 0.0042941 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1062-1_0_4_load_51 | 57 | 0.0047851 | 0.0011993 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1062-1_0_4_load_52 | 58 | 0.021101 | 0.0052884 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1062-1_0_4_load_101 | 59 | 0.0041897 | 0.00105 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1062-1_0_4_load_59 | 60 | 0.00081926 | 0.00020532 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1062-1_0_4_load_67 | 62 | 0.00040693 | 0.00010199 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1062-1_0_4_load_68 | 63 | 0.00059838 | 0.00014997 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1062-1_0_4_load_70 | 64 | 0.0019293 | 0.00048352 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1062-1_0_4_load_340 | 67 | 0.0004247 | 0.00010644 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1062-1_0_4_load_80 | 68 | 0.00077216 | 0.00019352 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1062-1_0_4_load_90 | 69 | 0.00015072 | 3.7773e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1062-1_0_4_load_93 | 70 | 0.0018943 | 0.00047476 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1062-1_0_4_load_94 | 71 | 0.0041789 | 0.0010473 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1062-1_0_4_load_165 | 72 | 0.00081747 | 0.00020488 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1062-1_0_4_load_97 | 73 | 0.00024181 | 6.0603e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1062-1_0_4_load_98 | 74 | 0.000361 | 9.0475e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1062-1_0_4_load_100 | 76 | 0.00043651 | 0.0001094 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1062-1_0_4_load_341 | 80 | 0.0012586 | 0.00031543 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1062-1_0_4_load_110 | 81 | 0.0044278 | 0.0011097 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1062-1_0_4_load_112 | 82 | 0.00020967 | 5.2549e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1062-1_0_4_load_251 | 83 | 0.00033837 | 8.4804e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1062-1_0_4_load_136 | 84 | 0.0010622 | 0.0002662 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1062-1_0_4_load_137 | 85 | 0.00044976 | 0.00011272 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1062-1_0_4_load_138 | 86 | 0.00024217 | 6.0694e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1062-1_0_4_load_139 | 87 | 0.00099597 | 0.00024961 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1062-1_0_4_load_140 | 89 | 0.0004989 | 0.00012504 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1062-1_0_4_load_144 | 91 | 0.00013929 | 3.491e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1062-1_0_4_load_142 | 92 | 0.0033325 | 0.00083521 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1062-1_0_4_load_156 | 94 | 0.0011303 | 0.00028329 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1062-1_0_4_load_154 | 95 | 0.0009829 | 0.00024634 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1062-1_0_4_load_146 | 97 | 0.0020146 | 0.00050491 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1062-1_0_4_load_147 | 98 | 0.0018852 | 0.00047249 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1062-1_0_4_load_148 | 99 | 0.0002093 | 5.2455e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1062-1_0_4_load_149 | 100 | 0.0015819 | 0.00039646 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1062-1_0_4_load_150 | 101 | 0.00063163 | 0.0001583 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1062-1_0_4_load_151 | 102 | 0.00055711 | 0.00013962 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1062-1_0_4_load_159 | 104 | 0.0021325 | 0.00053444 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1062-1_0_4_load_157 | 105 | 0.00065562 | 0.00016431 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1062-1_0_4_load_153 | 106 | 0.0010024 | 0.00025123 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1062-1_0_4_load_155 | 107 | 0.00031356 | 7.8587e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1062-1_0_4_load_189 | 108 | 0.0027513 | 0.00068955 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1062-1_0_4_load_190 | 109 | 0.00054696 | 0.00013708 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1062-1_0_4_load_253 | 114 | 0.0020171 | 0.00050554 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1062-1_0_4_load_211 | 115 | 0.00064167 | 0.00016082 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1062-1_0_4_load_215 | 117 | 0.00081967 | 0.00020543 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1062-1_0_4_load_281 | 118 | 0.00074513 | 0.00018675 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1062-1_0_4_load_279 | 120 | 0.001833 | 0.00045939 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1062-1_0_4_line_0 |  | 0 | 1 | 0.020321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1062-1_0_4_line_1 |  | 0 | 2 | 0.031699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1062-1_0_4_line_2 |  | 1 | 3 | 0.011203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1062-1_0_4_line_3 |  | 3 | 4 | 0.40514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1062-1_0_4_line_4 |  | 4 | 50 | 0.028752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1062-1_0_4_line_5 |  | 5 | 6 | 0.0031078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1062-1_0_4_line_6 |  | 6 | 7 | 0.07845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1062-1_0_4_line_7 |  | 7 | 8 | 0.047568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1062-1_0_4_line_8 |  | 7 | 9 | 0.064669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1062-1_0_4_line_9 |  | 9 | 10 | 0.054086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1062-1_0_4_line_10 |  | 10 | 15 | 0.005038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1062-1_0_4_line_11 |  | 10 | 12 | 0.022729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1062-1_0_4_line_12 |  | 11 | 12 | 0.00081044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1062-1_0_4_line_13 |  | 11 | 13 | 0.1117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1062-1_0_4_line_14 |  | 13 | 14 | 0.035088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1062-1_0_4_line_15 |  | 14 | 16 | 0.11963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1062-1_0_4_line_16 |  | 15 | 29 | 0.047632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1062-1_0_4_line_17 |  | 16 | 20 | 0.057169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1062-1_0_4_line_18 |  | 17 | 18 | 0.033497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1062-1_0_4_line_19 |  | 17 | 19 | 0.0099976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1062-1_0_4_line_20 |  | 18 | 20 | 0.033442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1062-1_0_4_line_21 |  | 18 | 21 | 0.029752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1062-1_0_4_line_22 |  | 18 | 22 | 0.026235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1062-1_0_4_line_23 |  | 19 | 23 | 0.13527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1062-1_0_4_line_24 |  | 19 | 24 | 0.059658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1062-1_0_4_line_25 |  | 21 | 25 | 0.23198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_1062-1_0_4_line_26 |  | 22 | 26 | 0.01199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1062-1_0_4_line_27 |  | 23 | 27 | 0.011213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_1062-1_0_4_line_28 |  | 24 | 28 | 0.10081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1062-1_0_4_line_29 |  | 25 | 33 | 0.067588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_1062-1_0_4_line_30 |  | 27 | 70 | 0.23248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1062-1_0_4_line_31 |  | 28 | 61 | 0.015077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1062-1_0_4_line_32 |  | 29 | 30 | 0.025845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_1062-1_0_4_line_33 |  | 30 | 31 | 0.011274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_1062-1_0_4_line_34 |  | 31 | 32 | 0.057681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_1062-1_0_4_line_35 |  | 32 | 48 | 0.0022182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1062-1_0_4_line_36 |  | 33 | 34 | 0.023297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1062-1_0_4_line_37 |  | 34 | 36 | 0.027338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1062-1_0_4_line_38 |  | 35 | 36 | 0.029684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1062-1_0_4_line_39 |  | 35 | 37 | 1.4825e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1062-1_0_4_line_40 |  | 36 | 58 | 0.019454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1062-1_0_4_line_41 |  | 38 | 39 | 0.011774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1062-1_0_4_line_42 |  | 38 | 40 | 0.0014732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1062-1_0_4_line_43 |  | 39 | 41 | 0.02764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1062-1_0_4_line_44 |  | 40 | 42 | 0.2437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1062-1_0_4_line_45 |  | 41 | 43 | 0.034763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1062-1_0_4_line_46 |  | 41 | 44 | 0.005356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1062-1_0_4_line_47 |  | 42 | 61 | 0.021883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1062-1_0_4_line_48 |  | 42 | 60 | 0.029918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1062-1_0_4_line_49 |  | 43 | 120 | 0.033503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1062-1_0_4_line_50 |  | 44 | 82 | 0.032361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1062-1_0_4_line_51 |  | 44 | 81 | 0.029066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1062-1_0_4_line_52 |  | 45 | 46 | 0.048103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1062-1_0_4_line_53 |  | 46 | 47 | 0.024274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_1062-1_0_4_line_54 |  | 46 | 48 | 0.014162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_1062-1_0_4_line_55 |  | 47 | 49 | 0.0082885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_1062-1_0_4_line_56 |  | 49 | 68 | 0.027446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_1062-1_0_4_line_57 |  | 50 | 51 | 0.070951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1062-1_0_4_line_58 |  | 51 | 52 | 0.021006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_1062-1_0_4_line_59 |  | 52 | 53 | 0.004605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_1062-1_0_4_line_60 |  | 53 | 65 | 0.01729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1062-1_0_4_line_61 |  | 53 | 62 | 0.015613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_1062-1_0_4_line_62 |  | 54 | 55 | 0.017146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1062-1_0_4_line_63 |  | 54 | 56 | 0.093383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1062-1_0_4_line_64 |  | 55 | 57 | 0.0017393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1062-1_0_4_line_65 |  | 56 | 58 | 0.063942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1062-1_0_4_line_66 |  | 57 | 59 | 0.021411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1062-1_0_4_line_67 |  | 59 | 77 | 0.094249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1062-1_0_4_line_68 |  | 62 | 63 | 0.027859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_1062-1_0_4_line_69 |  | 63 | 64 | 0.013736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_1062-1_0_4_line_70 |  | 64 | 66 | 0.092566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_1062-1_0_4_line_71 |  | 65 | 67 | 0.021874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1062-1_0_4_line_72 |  | 66 | 69 | 0.015011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1062-1_0_4_line_73 |  | 66 | 68 | 0.0096849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_1062-1_0_4_line_74 |  | 70 | 71 | 0.035748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_1062-1_0_4_line_75 |  | 71 | 72 | 0.067102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_1062-1_0_4_line_76 |  | 72 | 102 | 0.69897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_1062-1_0_4_line_77 |  | 73 | 74 | 0.020377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1062-1_0_4_line_78 |  | 73 | 75 | 0.032775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1062-1_0_4_line_79 |  | 75 | 76 | 0.043605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1062-1_0_4_line_80 |  | 76 | 77 | 0.083367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1062-1_0_4_line_81 |  | 77 | 78 | 0.078501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1062-1_0_4_line_82 |  | 78 | 79 | 0.050147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1062-1_0_4_line_83 |  | 78 | 80 | 0.05176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1062-1_0_4_line_84 |  | 79 | 83 | 0.019036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1062-1_0_4_line_85 |  | 83 | 119 | 0.00025032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1062-1_0_4_line_86 |  | 84 | 85 | 0.0070105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1062-1_0_4_line_87 |  | 84 | 86 | 0.027188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1062-1_0_4_line_88 |  | 85 | 87 | 0.039341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1062-1_0_4_line_89 |  | 85 | 88 | 0.41671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1062-1_0_4_line_90 |  | 86 | 89 | 0.017157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1062-1_0_4_line_91 |  | 87 | 90 | 0.035614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1062-1_0_4_line_92 |  | 88 | 105 | 0.077102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1062-1_0_4_line_93 |  | 89 | 91 | 0.31064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1062-1_0_4_line_94 |  | 90 | 92 | 0.042173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1062-1_0_4_line_95 |  | 90 | 93 | 0.1116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1062-1_0_4_line_96 |  | 91 | 96 | 0.021622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1062-1_0_4_line_97 |  | 92 | 94 | 0.0038082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1062-1_0_4_line_98 |  | 93 | 95 | 0.062008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1062-1_0_4_line_99 |  | 95 | 106 | 0.044302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1062-1_0_4_line_100 |  | 96 | 97 | 0.02406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1062-1_0_4_line_101 |  | 96 | 98 | 0.0099279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1062-1_0_4_line_102 |  | 99 | 100 | 0.01245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1062-1_0_4_line_103 |  | 99 | 101 | 0.067311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1062-1_0_4_line_104 |  | 100 | 102 | 0.045686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1062-1_0_4_line_105 |  | 101 | 103 | 0.0059359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1062-1_0_4_line_106 |  | 103 | 104 | 0.065533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1062-1_0_4_line_107 |  | 103 | 105 | 0.044071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1062-1_0_4_line_108 |  | 106 | 107 | 0.020848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1062-1_0_4_line_109 |  | 108 | 109 | 0.027477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1062-1_0_4_line_110 |  | 108 | 110 | 0.010923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1062-1_0_4_line_111 |  | 109 | 111 | 0.08966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1062-1_0_4_line_112 |  | 110 | 112 | 0.018793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1062-1_0_4_line_113 |  | 111 | 113 | 0.025055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1062-1_0_4_line_114 |  | 112 | 114 | 0.015309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1062-1_0_4_line_115 |  | 113 | 117 | 0.085855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1062-1_0_4_line_116 |  | 114 | 119 | 0.0024431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1062-1_0_4_line_117 |  | 115 | 116 | 0.088551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1062-1_0_4_line_118 |  | 116 | 117 | 0.057902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1062-1_0_4_line_119 |  | 116 | 118 | 0.27428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1062-1_0_4_trafo_20 | 0.63 MVA 20/0.4 kV | 121 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2661365.1798 | 1211503.3668 | 2661356.4301 | 1211500.3456 | 2661352.5775 | 1211498.8718 | 2661350.8187 | 1211497.7308 | 2661349.3992 | 1211496.1152 | 2661348.1853 | 1211493.7124 | 2661348.1853 | 1211493.7124
1 | 2661365.1798 | 1211503.3668 | 2661394.1983 | 1211513.3864 | 2661395.1632 | 1211513.6452
2 | 2661349.0966 | 1211482.6817 | 2661347.9155 | 1211488.1729 | 2661347.713 | 1211490.8725 | 2661348.1853 | 1211493.7124
3 | 2660966.4858 | 1211349.4687 | 2661349.0966 | 1211482.6817
4 | 2660966.4858 | 1211349.4687 | 2660959.8829 | 1211362.7982 | 2660954.2572 | 1211375.483
5 | 2660665.6206 | 1211087.6294 | 2660665.4767 | 1211090.7339
6 | 2660714.4308 | 1211135.8806 | 2660707.3893 | 1211128.1264 | 2660703.3984 | 1211125.2619 | 2660699.268 | 1211123.4188 | 2660671.4645 | 1211117.2545 | 2660667.8627 | 1211115.7392 | 2660665.4268 | 1211113.1573 | 2660664.5463 | 1211110.8136 | 2660665.4767 | 1211090.7339
7 | 2660714.4308 | 1211135.8806 | 2660715.187 | 1211124.3035 | 2660718.8165 | 1211088.5208
8 | 2660714.4308 | 1211135.8806 | 2660712.3624 | 1211151.6913 | 2660710.0787 | 1211161.0404 | 2660696.9152 | 1211197.857
9 | 2660678.7059 | 1211248.7857 | 2660696.9152 | 1211197.857
10 | 2660678.7059 | 1211248.7857 | 2660683.4764 | 1211250.4464
11 | 2660678.7059 | 1211248.7857 | 2660657.2483 | 1211241.2917
12 | 2660657.2483 | 1211241.2917 | 2660656.4832 | 1211241.0245
13 | 2660551.0312 | 1211204.1953 | 2660656.4832 | 1211241.0245
14 | 2660551.0312 | 1211204.1953 | 2660517.8428 | 1211192.5294
15 | 2660517.8428 | 1211192.5294 | 2660515.1437 | 1211198.6613 | 2660506.2839 | 1211211.3236 | 2660439.7471 | 1211282.5567
16 | 2660683.4764 | 1211250.4464 | 2660679.4968 | 1211263.6584 | 2660676.8444 | 1211274.9049 | 2660675.3519 | 1211287.9087 | 2660675.8127 | 1211297.0867
17 | 2660400.7581 | 1211324.3677 | 2660438.9628 | 1211283.3963 | 2660439.7471 | 1211282.5567
18 | 2660378.5663 | 1211349.4361 | 2660377.0021 | 1211350.8211 | 2660370.3842 | 1211358.2475 | 2660356.1234 | 1211373.7905 | 2660355.888 | 1211374.0715
19 | 2660350.5499 | 1211382.406 | 2660352.3467 | 1211378.2995 | 2660355.888 | 1211374.0715
20 | 2660378.5663 | 1211349.4361 | 2660400.7581 | 1211324.3677
21 | 2660378.5663 | 1211349.4361 | 2660352.1983 | 1211335.6557
22 | 2660378.5663 | 1211349.4361 | 2660387.5056 | 1211353.6402 | 2660398.9158 | 1211359.9706 | 2660401.9161 | 1211361.3625
23 | 2660350.5499 | 1211382.406 | 2660325.5732 | 1211393.5936 | 2660297.0057 | 1211406.7129 | 2660262.5435 | 1211421.9074 | 2660245.4709 | 1211433.0084 | 2660231.5756 | 1211445.1298
24 | 2660350.5499 | 1211382.406 | 2660350.6668 | 1211386.6209 | 2660351.6672 | 1211390.6334 | 2660355.9442 | 1211401.2609 | 2660360.6825 | 1211414.3612 | 2660366.5703 | 1211430.2526 | 2660370.1071 | 1211438.499
25 | 2660152.8352 | 1211221.1678 | 2660173.7482 | 1211245.2265 | 2660186.9157 | 1211252.9195 | 2660231.3909 | 1211274.1811 | 2660266.1285 | 1211291.2199 | 2660291.4491 | 1211303.9166 | 2660322.3806 | 1211320.0723 | 2660352.1983 | 1211335.6557
26 | 2660412.7931 | 1211366.4082 | 2660401.9161 | 1211361.3625
27 | 2660223.126 | 1211452.5006 | 2660231.5756 | 1211445.1298
28 | 2660432.3887 | 1211513.8513 | 2660432.1043 | 1211512.5547 | 2660427.6371 | 1211497.467 | 2660424.905 | 1211491.1355 | 2660421.5081 | 1211485.153 | 2660416.8135 | 1211479.7689 | 2660389.6174 | 1211458.0249 | 2660376.6217 | 1211447.6982 | 2660371.6852 | 1211442.1783 | 2660370.1071 | 1211438.499
29 | 2660152.8352 | 1211221.1678 | 2660154.6791 | 1211211.6361 | 2660153.6261 | 1211191.7246 | 2660148.3492 | 1211173.9495 | 2660142.5588 | 1211160.3718 | 2660141.9592 | 1211155.7733
30 | 2660065.1542 | 1211619.8892 | 2660069.3724 | 1211610.7188 | 2660077.312 | 1211596.479 | 2660089.7922 | 1211576.537 | 2660102.3364 | 1211560.8093 | 2660118.7198 | 1211542.6411 | 2660129.631 | 1211532.1336 | 2660149.6194 | 1211515.1692 | 2660183.3784 | 1211487.5038 | 2660214.2 | 1211460.2871 | 2660223.126 | 1211452.5006
31 | 2660435.6197 | 1211528.5778 | 2660432.3887 | 1211513.8513
32 | 2660683.238 | 1211321.436 | 2660682.9995 | 1211321.2178 | 2660679.5541 | 1211315.546 | 2660675.9964 | 1211300.7453 | 2660675.8127 | 1211297.0867
33 | 2660691.5559 | 1211329.0456 | 2660683.238 | 1211321.436
34 | 2660691.5559 | 1211329.0456 | 2660692.659 | 1211330.0547 | 2660708.5327 | 1211341.3008 | 2660718.3239 | 1211348.3936 | 2660721.6509 | 1211354.4978 | 2660723.0961 | 1211359.5823 | 2660723.2367 | 1211365.176 | 2660722.6833 | 1211371.0183 | 2660722.5274 | 1211371.9458
35 | 2660722.5274 | 1211371.9458 | 2660722.1596 | 1211374.1333
36 | 2660130.0968 | 1211141.5848 | 2660141.4757 | 1211144.1844 | 2660141.402 | 1211151.4992 | 2660141.9592 | 1211155.7733
37 | 2660103.4459 | 1211135.4961 | 2660130.0968 | 1211141.5848
38 | 2660074.571 | 1211128.5122 | 2660092.7402 | 1211133.8317 | 2660103.4459 | 1211135.4961
39 | 2660074.5568 | 1211128.5081 | 2660074.571 | 1211128.5122
40 | 2660103.4459 | 1211135.4961 | 2660107.6276 | 1211116.4972
41 | 2660474.1608 | 1211771.6832 | 2660476.1517 | 1211783.2876
42 | 2660474.1608 | 1211771.6832 | 2660473.9117 | 1211770.2312
43 | 2660483.7846 | 1211809.8477 | 2660480.8622 | 1211800.568 | 2660476.1517 | 1211783.2876
44 | 2660414.396 | 1211533.9071 | 2660473.9117 | 1211770.2312
45 | 2660483.7846 | 1211809.8477 | 2660460.5018 | 1211812.2577 | 2660449.1523 | 1211812.6369
46 | 2660483.7846 | 1211809.8477 | 2660485.3969 | 1211814.9561
47 | 2660435.6197 | 1211528.5778 | 2660414.396 | 1211533.9071
48 | 2660385.3789 | 1211541.1932 | 2660414.396 | 1211533.9071
49 | 2660449.1523 | 1211812.6369 | 2660438.292 | 1211812.9998 | 2660429.8123 | 1211811.5019 | 2660426.2812 | 1211811.2883 | 2660415.9639 | 1211813.1735
50 | 2660485.3969 | 1211814.9561 | 2660481.7243 | 1211818.2097 | 2660468.3775 | 1211832.1051 | 2660465.6222 | 1211834.0784 | 2660461.81 | 1211835.3628 | 2660461.0553 | 1211835.5435
51 | 2660485.3969 | 1211814.9561 | 2660507.8791 | 1211811.3262 | 2660513.8934 | 1211813.1772
52 | 2660719.8118 | 1211388.0995 | 2660700.2319 | 1211387.122 | 2660671.7642 | 1211385.8021
53 | 2660719.8118 | 1211388.0995 | 2660743.839 | 1211391.5505
54 | 2660719.8118 | 1211388.0995 | 2660722.1596 | 1211374.1333
55 | 2660752.1123 | 1211391.9769 | 2660744.7224 | 1211391.6774 | 2660743.839 | 1211391.5505
56 | 2660752.1123 | 1211391.9769 | 2660756.8148 | 1211392.1675 | 2660761.8561 | 1211387.3714 | 2660768.6741 | 1211379.7362 | 2660772.7656 | 1211375.9929
57 | 2660954.2572 | 1211375.483 | 2660947.7491 | 1211390.1576 | 2660937.9761 | 1211406.6011 | 2660927.4599 | 1211422.1587 | 2660916.1761 | 1211434.8614
58 | 2660902.653 | 1211450.9358 | 2660915.8523 | 1211435.2259 | 2660916.1761 | 1211434.8614
59 | 2660899.6908 | 1211454.4616 | 2660902.653 | 1211450.9358
60 | 2660899.6908 | 1211454.4616 | 2660894.8823 | 1211461.0054 | 2660893.1031 | 1211464.0891 | 2660892.4126 | 1211466.9727 | 2660892.1804 | 1211469.6164
61 | 2660899.6908 | 1211454.4616 | 2660886.7869 | 1211445.6723
62 | 2660033.106 | 1211023.5704 | 2660016.9504 | 1211017.8263
63 | 2660121.3726 | 1211054.0495 | 2660068.5786 | 1211036.1182 | 2660057.3863 | 1211032.2032 | 2660033.106 | 1211023.5704
64 | 2660015.3116 | 1211017.2436 | 2660016.9504 | 1211017.8263
65 | 2660121.3726 | 1211054.0495 | 2660107.6276 | 1211116.4972
66 | 2660015.3116 | 1211017.2436 | 2659995.1382 | 1211010.071
67 | 2659906.335 | 1210978.4971 | 2659995.1382 | 1211010.071
68 | 2660862.508 | 1211433.643 | 2660868.1779 | 1211435.9177 | 2660878.8822 | 1211438.3839 | 2660885.9036 | 1211445.0707 | 2660886.7869 | 1211445.6723
69 | 2660862.508 | 1211433.643 | 2660861.4955 | 1211433.2368 | 2660850.7981 | 1211426.4948
70 | 2660779.9112 | 1211369.4555 | 2660783.5742 | 1211370.171 | 2660788.7359 | 1211372.9475 | 2660804.2279 | 1211383.5896 | 2660820.0581 | 1211395.3469 | 2660824.8836 | 1211399.7877 | 2660830.4394 | 1211406.3928 | 2660835.1716 | 1211411.7887 | 2660837.7575 | 1211414.5501 | 2660840.8439 | 1211416.6606 | 2660844.1964 | 1211419.4965 | 2660845.3757 | 1211423.0774 | 2660850.7981 | 1211426.4948
71 | 2660892.1804 | 1211469.6164 | 2660911.4051 | 1211474.0931 | 2660913.5074 | 1211474.4632
72 | 2660779.9112 | 1211369.4555 | 2660782.3963 | 1211367.1906 | 2660788.3356 | 1211360.0356 | 2660789.4473 | 1211357.9652
73 | 2660779.9112 | 1211369.4555 | 2660772.7656 | 1211375.9929
74 | 2660065.1542 | 1211619.8892 | 2660051.9785 | 1211648.5334 | 2660050.6877 | 1211652.5499
75 | 2660024.4307 | 1211713.6638 | 2660025.3563 | 1211711.6594 | 2660033.1375 | 1211692.7373 | 2660035.6212 | 1211683.7791 | 2660042.0653 | 1211676.1726 | 2660046.5581 | 1211665.4002 | 2660050.6877 | 1211652.5499
76 | 2660024.4307 | 1211713.6638 | 2659804.2602 | 1212377.0547
77 | 2659902.7691 | 1210844.6777 | 2659890.9202 | 1210841.8264 | 2659882.9444 | 1210839.9681
78 | 2659933.3665 | 1210855.1494 | 2659931.8466 | 1210853.6443 | 2659929.349 | 1210851.8626 | 2659925.375 | 1210850.2996 | 2659921.4876 | 1210849.1821 | 2659902.7691 | 1210844.6777
79 | 2659933.3665 | 1210855.1494 | 2659934.2479 | 1210857.4374 | 2659934.683 | 1210859.5097 | 2659934.6013 | 1210862.355 | 2659933.0466 | 1210871.1114 | 2659931.2761 | 1210878.6537 | 2659926.7314 | 1210897.6662
80 | 2659906.335 | 1210978.4971 | 2659921.1696 | 1210920.9334 | 2659926.7314 | 1210897.6662
81 | 2659906.335 | 1210978.4971 | 2659903.8145 | 1210985.0535 | 2659901.6107 | 1210993.3809 | 2659891.5329 | 1211038.1402 | 2659875.4232 | 1211032.7642
82 | 2659865.886 | 1211081.9872 | 2659871.5684 | 1211051.1255 | 2659875.4232 | 1211032.7642
83 | 2659875.4232 | 1211032.7642 | 2659826.3301 | 1211016.3625
84 | 2659865.886 | 1211081.9872 | 2659847.1296 | 1211078.7373
85 | 2659847.1296 | 1211078.7373 | 2659846.8829 | 1211078.6946
86 | 2659204.7308 | 1212466.6663 | 2659203.9818 | 1212464.8329 | 2659201.7995 | 1212460.301
87 | 2659204.7308 | 1212466.6663 | 2659212.4374 | 1212485.5294 | 2659214.7195 | 1212491.9471
88 | 2659201.7995 | 1212460.301 | 2659197.6395 | 1212451.662 | 2659183.9844 | 1212426.6447 | 2659183.4597 | 1212425.509
89 | 2659201.7995 | 1212460.301 | 2659581.3115 | 1212288.1925
90 | 2659214.7195 | 1212491.9471 | 2659220.468 | 1212508.1125
91 | 2659170.4131 | 1212392.4116 | 2659173.7251 | 1212402.4171 | 2659178.1681 | 1212414.0572 | 2659183.4597 | 1212425.509
92 | 2659581.3115 | 1212288.1925 | 2659589.5398 | 1212295.7904 | 2659605.8403 | 1212315.2094 | 2659629.668 | 1212342.4085 | 2659633.3899 | 1212344.7342
93 | 2659220.468 | 1212508.1125 | 2659385.9944 | 1212770.9774
94 | 2659170.4131 | 1212392.4116 | 2659157.4842 | 1212400.6217 | 2659149.8064 | 1212405.6486 | 2659133.8782 | 1212413.3232
95 | 2659170.4131 | 1212392.4116 | 2659168.0895 | 1212385.3954 | 2659165.3885 | 1212375.0623 | 2659159.1853 | 1212353.2098 | 2659139.2927 | 1212285.2381
96 | 2659396.8595 | 1212789.6359 | 2659392.3161 | 1212782.8087 | 2659389.075 | 1212777.1842 | 2659385.9944 | 1212770.9774
97 | 2659130.4475 | 1212414.9763 | 2659133.8782 | 1212413.3232
98 | 2659139.2927 | 1212285.2381 | 2659133.8552 | 1212271.1979 | 2659128.7064 | 1212260.2291 | 2659123.694 | 1212250.8182 | 2659117.6556 | 1212241.4416 | 2659111.2627 | 1212233.34 | 2659109.4124 | 1212231.3752
99 | 2659077.5633 | 1212200.599 | 2659103.0298 | 1212224.5976 | 2659109.4124 | 1212231.3752
100 | 2659396.8595 | 1212789.6359 | 2659403.3331 | 1212796.4044 | 2659414.7694 | 1212805.6307
101 | 2659396.8595 | 1212789.6359 | 2659392.5038 | 1212788.3695 | 2659388.8115 | 1212786.8541 | 2659387.5412 | 1212786.264
102 | 2659747.6361 | 1212363.8936 | 2659759.7802 | 1212366.6388
103 | 2659747.6361 | 1212363.8936 | 2659736.2479 | 1212361.3193 | 2659717.2958 | 1212363.2085 | 2659692.3551 | 1212357.6778 | 2659681.4098 | 1212356.2161
104 | 2659759.7802 | 1212366.6388 | 2659790.9027 | 1212373.6742 | 2659804.2602 | 1212377.0547
105 | 2659675.5261 | 1212355.4304 | 2659681.4098 | 1212356.2161
106 | 2659675.5261 | 1212355.4304 | 2659694.3577 | 1212383.8026 | 2659694.2869 | 1212390.8729 | 2659688.9035 | 1212404.972 | 2659682.7364 | 1212411.9561
107 | 2659675.5261 | 1212355.4304 | 2659649.1186 | 1212352.2199 | 2659637.9131 | 1212347.5607 | 2659633.3899 | 1212344.7342
108 | 2659062.663 | 1212186.0187 | 2659075.976 | 1212199.1031 | 2659077.5633 | 1212200.599
109 | 2659800.0553 | 1211070.6014 | 2659772.9805 | 1211065.9195
110 | 2659810.8187 | 1211072.4626 | 2659800.0553 | 1211070.6014
111 | 2659684.6313 | 1211050.6418 | 2659772.9805 | 1211065.9195
112 | 2659810.8187 | 1211072.4626 | 2659829.3894 | 1211075.6729
113 | 2659684.6313 | 1211050.6418 | 2659659.8539 | 1211046.4693
114 | 2659829.3894 | 1211075.6729 | 2659844.4755 | 1211078.2788
115 | 2659659.8539 | 1211046.4693 | 2659652.646 | 1211074.9589 | 2659647.1341 | 1211099.5187 | 2659644.4999 | 1211105.3292 | 2659638.8064 | 1211113.0992 | 2659637.1384 | 1211115.762 | 2659636.277 | 1211119.8336 | 2659634.9978 | 1211127.711
116 | 2659846.8829 | 1211078.6946 | 2659844.4755 | 1211078.2788
117 | 2659627.3414 | 1211185.0949 | 2659623.2762 | 1211174.4256 | 2659615.1084 | 1211156.8112 | 2659609.3698 | 1211147.059 | 2659603.6201 | 1211139.1635 | 2659595.8314 | 1211130.7584 | 2659578.6344 | 1211114.7882 | 2659577.5371 | 1211113.4806
118 | 2659627.3414 | 1211185.0949 | 2659632.2848 | 1211144.4197 | 2659634.9978 | 1211127.711
119 | 2659627.3414 | 1211185.0949 | 2659544.6034 | 1211446.5972

## bus_geodata
| x | y | coords
0 | 2661365.1798 | 1211503.3668
1 | 2661348.1853 | 1211493.7124
2 | 2661395.1632 | 1211513.6452
3 | 2661349.0966 | 1211482.6817
4 | 2660966.4858 | 1211349.4687
5 | 2660665.6206 | 1211087.6294
6 | 2660665.4767 | 1211090.7339
7 | 2660714.4308 | 1211135.8806
8 | 2660718.8165 | 1211088.5208
9 | 2660696.9152 | 1211197.857
10 | 2660678.7059 | 1211248.7857
11 | 2660656.4832 | 1211241.0245
12 | 2660657.2483 | 1211241.2917
13 | 2660551.0312 | 1211204.1953
14 | 2660517.8428 | 1211192.5294
15 | 2660683.4764 | 1211250.4464
16 | 2660439.7471 | 1211282.5567
17 | 2660355.888 | 1211374.0715
18 | 2660378.5663 | 1211349.4361
19 | 2660350.5499 | 1211382.406
20 | 2660400.7581 | 1211324.3677
21 | 2660352.1983 | 1211335.6557
22 | 2660401.9161 | 1211361.3625
23 | 2660231.5756 | 1211445.1298
24 | 2660370.1071 | 1211438.499
25 | 2660152.8352 | 1211221.1678
26 | 2660412.7931 | 1211366.4082
27 | 2660223.126 | 1211452.5006
28 | 2660432.3887 | 1211513.8513
29 | 2660675.8127 | 1211297.0867
30 | 2660683.238 | 1211321.436
31 | 2660691.5559 | 1211329.0456
32 | 2660722.5274 | 1211371.9458
33 | 2660141.9592 | 1211155.7733
34 | 2660130.0968 | 1211141.5848
35 | 2660074.571 | 1211128.5122
36 | 2660103.4459 | 1211135.4961
37 | 2660074.5568 | 1211128.5081
38 | 2660474.1608 | 1211771.6832
39 | 2660476.1517 | 1211783.2876
40 | 2660473.9117 | 1211770.2312
41 | 2660483.7847 | 1211809.8477
42 | 2660414.396 | 1211533.9071
43 | 2660449.1523 | 1211812.6369
44 | 2660485.3969 | 1211814.9561
45 | 2660671.7642 | 1211385.8021
46 | 2660719.8118 | 1211388.0995
47 | 2660743.839 | 1211391.5505
48 | 2660722.1596 | 1211374.1333
49 | 2660752.1123 | 1211391.9769
50 | 2660954.2572 | 1211375.483
51 | 2660916.1761 | 1211434.8614
52 | 2660902.653 | 1211450.9358
53 | 2660899.6908 | 1211454.4616
54 | 2660033.106 | 1211023.5704
55 | 2660016.9504 | 1211017.8263
56 | 2660121.3726 | 1211054.0495
57 | 2660015.3116 | 1211017.2436
58 | 2660107.6276 | 1211116.4972
59 | 2659995.1382 | 1211010.071
60 | 2660385.3789 | 1211541.1932
61 | 2660435.6197 | 1211528.5778
62 | 2660886.7869 | 1211445.6723
63 | 2660862.508 | 1211433.643
64 | 2660850.7981 | 1211426.4948
65 | 2660892.1804 | 1211469.6164
66 | 2660779.9112 | 1211369.4555
67 | 2660913.5074 | 1211474.4632
68 | 2660772.7656 | 1211375.9929
69 | 2660789.4473 | 1211357.9652
70 | 2660065.1542 | 1211619.8892
71 | 2660050.6877 | 1211652.5499
72 | 2660024.4307 | 1211713.6638
73 | 2659902.7691 | 1210844.6777
74 | 2659882.9444 | 1210839.9681
75 | 2659933.3665 | 1210855.1494
76 | 2659926.7314 | 1210897.6662
77 | 2659906.335 | 1210978.4971
78 | 2659875.4232 | 1211032.7642
79 | 2659865.886 | 1211081.9872
80 | 2659826.3301 | 1211016.3625
81 | 2660513.8934 | 1211813.1772
82 | 2660461.0553 | 1211835.5435
83 | 2659847.1296 | 1211078.7373
84 | 2659204.7308 | 1212466.6663
85 | 2659201.7995 | 1212460.301
86 | 2659214.7195 | 1212491.9471
87 | 2659183.4597 | 1212425.509
88 | 2659581.3115 | 1212288.1925
89 | 2659220.468 | 1212508.1125
90 | 2659170.4131 | 1212392.4116
91 | 2659385.9944 | 1212770.9774
92 | 2659133.8782 | 1212413.3232
93 | 2659139.2927 | 1212285.2381
94 | 2659130.4475 | 1212414.9763
95 | 2659109.4124 | 1212231.3752
96 | 2659396.8595 | 1212789.6359
97 | 2659414.7694 | 1212805.6307
98 | 2659387.5412 | 1212786.264
99 | 2659747.6361 | 1212363.8936
100 | 2659759.7802 | 1212366.6388
101 | 2659681.4098 | 1212356.2161
102 | 2659804.2602 | 1212377.0547
103 | 2659675.5261 | 1212355.4304
104 | 2659682.7364 | 1212411.9561
105 | 2659633.3899 | 1212344.7342
106 | 2659077.5633 | 1212200.599
107 | 2659062.663 | 1212186.0187
108 | 2659800.0553 | 1211070.6014
109 | 2659772.9805 | 1211065.9195
110 | 2659810.8187 | 1211072.4626
111 | 2659684.6313 | 1211050.6418
112 | 2659829.3894 | 1211075.6729
113 | 2659659.8539 | 1211046.4693
114 | 2659844.4755 | 1211078.2788
115 | 2659577.5371 | 1211113.4806
116 | 2659627.3414 | 1211185.0949
117 | 2659634.9978 | 1211127.711
118 | 2659544.6035 | 1211446.5972
119 | 2659846.8829 | 1211078.6946
120 | 2660415.9639 | 1211813.1735
121 | 2660378.5663 | 1211349.4361

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97009 | -0.57641 | 0.0011012 | 0.00027599
1 | 0.97015 | -0.57527 | 0.008361 | 0.0020955
2 | 0.97003 | -0.57755 | 0.0019326 | 0.00048436
3 | 0.97027 | -0.5729 | 0 | 0
4 | 0.97458 | -0.48775 | 0 | 0
5 | 0.97006 | -0.57688 | 0.014881 | 0.0037296
6 | 0.9701 | -0.57602 | 0.011739 | 0.0029421
7 | 0.97205 | -0.53742 | 0 | 0
8 | 0.97118 | -0.55465 | 0.019616 | 0.0049161
9 | 0.97485 | -0.48242 | 0.047016 | 0.011783
10 | 0.97955 | -0.39035 | 0 | 0
11 | 0.98086 | -0.36483 | 0.0020408 | 0.00051147
12 | 0.98082 | -0.36573 | 0.0028616 | 0.00071719
13 | 0.98733 | -0.23985 | 0 | 0
14 | 0.98937 | -0.20092 | 0 | 0
15 | 0.97949 | -0.39155 | 0 | 0
16 | 0.99631 | -0.069402 | 0.014428 | 0.003616
17 | 0.99622 | -0.072038 | 0.022841 | 0.0057244
18 | 0.99731 | -0.051082 | 0 | 0
19 | 0.996 | -0.076295 | 0 | 0
20 | 1 | 0 | -0.32047 | -0.081938
21 | 0.99597 | -0.076599 | 0.023194 | 0.0058129
22 | 0.99717 | -0.053715 | 0.0035838 | 0.00089819
23 | 0.99427 | -0.10931 | 0.0003801 | 9.5263e-05
24 | 0.99487 | -0.098059 | 0.0057604 | 0.0014437
25 | 0.98795 | -0.22978 | 0 | 0
26 | 0.99715 | -0.054165 | 0.0021405 | 0.00053646
27 | 0.99413 | -0.11201 | 0.00052264 | 0.00013099
28 | 0.99349 | -0.12468 | 0.0012651 | 0.00031706
29 | 0.97891 | -0.40288 | 0.0024405 | 0.00061165
30 | 0.97863 | -0.40846 | 0.00026236 | 6.5753e-05
31 | 0.9785 | -0.41087 | 0.00061404 | 0.00015389
32 | 0.97789 | -0.42288 | 0.00015998 | 4.0094e-05
33 | 0.98561 | -0.27487 | 0.0040469 | 0.0010142
34 | 0.98409 | -0.30438 | 0.0068074 | 0.0017061
35 | 0.98241 | -0.33694 | 0 | 0
36 | 0.98247 | -0.33576 | 0 | 0
37 | 0.98241 | -0.33694 | 0.0021902 | 0.0005489
38 | 0.99119 | -0.16929 | 0.00045811 | 0.00011481
39 | 0.99111 | -0.17083 | 0.00042204 | 0.00010577
40 | 0.9912 | -0.16908 | 0.00034629 | 8.6787e-05
41 | 0.99093 | -0.17426 | 0 | 0
42 | 0.99303 | -0.13364 | 0.0046718 | 0.0011709
43 | 0.99086 | -0.1757 | 0.00050672 | 0.000127
44 | 0.99091 | -0.1747 | 0 | 0
45 | 0.97764 | -0.42777 | 0.001951 | 0.00048896
46 | 0.97773 | -0.42605 | 0 | 0
47 | 0.97751 | -0.43028 | 0.00018934 | 4.7453e-05
48 | 0.97787 | -0.42333 | 0.0016254 | 0.00040738
49 | 0.97744 | -0.43171 | 0.00029095 | 7.2919e-05
50 | 0.97489 | -0.48173 | 0.0021103 | 0.0005289
51 | 0.97578 | -0.46415 | 0.00038376 | 9.6179e-05
52 | 0.97592 | -0.46148 | 0.00042464 | 0.00010643
53 | 0.97595 | -0.46088 | 0 | 0
54 | 0.97546 | -0.47308 | 0.004082 | 0.0010231
55 | 0.97488 | -0.48449 | 0.017134 | 0.0042941
56 | 0.97896 | -0.40425 | 0 | 0
57 | 0.97485 | -0.48511 | 0.0047851 | 0.0011993
58 | 0.98136 | -0.35739 | 0.021101 | 0.0052884
59 | 0.97456 | -0.49076 | 0.0041897 | 0.00105
60 | 0.993 | -0.13407 | 0.00081926 | 0.00020532
61 | 0.9933 | -0.12834 | 0 | 0
62 | 0.97606 | -0.45877 | 0.00040693 | 0.00010199
63 | 0.97626 | -0.4549 | 0.00059838 | 0.00014997
64 | 0.97636 | -0.45292 | 0.0019293 | 0.00048352
65 | 0.97594 | -0.46101 | 0 | 0
66 | 0.97712 | -0.43796 | 0 | 0
67 | 0.97594 | -0.46118 | 0.0004247 | 0.00010644
68 | 0.9772 | -0.43638 | 0.00077216 | 0.00019352
69 | 0.97712 | -0.438 | 0.00015072 | 3.7773e-05
70 | 0.99125 | -0.16715 | 0.0018943 | 0.00047476
71 | 0.99084 | -0.17505 | 0.0041789 | 0.0010473
72 | 0.9902 | -0.18741 | 0.00081747 | 0.00020488
73 | 0.97354 | -0.51085 | 0.00024181 | 6.0603e-05
74 | 0.97354 | -0.51099 | 0.000361 | 9.0475e-05
75 | 0.97356 | -0.51049 | 0 | 0
76 | 0.97359 | -0.51 | 0.00043651 | 0.0001094
77 | 0.97367 | -0.5084 | 0 | 0
78 | 0.973 | -0.52161 | 0 | 0
79 | 0.97263 | -0.52889 | 0 | 0
80 | 0.97294 | -0.52281 | 0.0012586 | 0.00031543
81 | 0.99079 | -0.17698 | 0.0044278 | 0.0011097
82 | 0.9909 | -0.17482 | 0.00020967 | 5.2549e-05
83 | 0.97249 | -0.53166 | 0.00033837 | 8.4804e-05
84 | 0.97445 | -0.49409 | 0.0010622 | 0.0002662
85 | 0.97449 | -0.49333 | 0.00044976 | 0.00011272
86 | 0.97433 | -0.49648 | 0.00024217 | 6.0694e-05
87 | 0.97421 | -0.49894 | 0.00099597 | 0.00024961
88 | 0.97994 | -0.38623 | 0 | 0
89 | 0.97426 | -0.49791 | 0.0004989 | 0.00012504
90 | 0.97398 | -0.50337 | 0 | 0
91 | 0.97309 | -0.52102 | 0.00013929 | 3.491e-05
92 | 0.97381 | -0.50683 | 0.0033325 | 0.00083521
93 | 0.97374 | -0.5081 | 0 | 0
94 | 0.9738 | -0.50691 | 0.0011303 | 0.00028329
95 | 0.97361 | -0.51072 | 0.0009829 | 0.00024634
96 | 0.97301 | -0.52257 | 0 | 0
97 | 0.97297 | -0.52346 | 0.0020146 | 0.00050491
98 | 0.97299 | -0.52292 | 0.0018852 | 0.00047249
99 | 0.98274 | -0.33166 | 0.0002093 | 5.2455e-05
100 | 0.98294 | -0.32768 | 0.0015819 | 0.00039646
101 | 0.98165 | -0.35296 | 0.00063163 | 0.0001583
102 | 0.98376 | -0.31178 | 0.00055711 | 0.00013962
103 | 0.98155 | -0.35477 | 0 | 0
104 | 0.98142 | -0.3573 | 0.0021325 | 0.00053444
105 | 0.98095 | -0.36654 | 0.00065562 | 0.00016431
106 | 0.97356 | -0.5118 | 0.0010024 | 0.00025123
107 | 0.97355 | -0.51192 | 0.00031356 | 7.8587e-05
108 | 0.97224 | -0.53662 | 0.0027513 | 0.00068955
109 | 0.97217 | -0.53803 | 0.00054696 | 0.00013708
110 | 0.9723 | -0.53551 | 0 | 0
111 | 0.97199 | -0.54171 | 0 | 0
112 | 0.9724 | -0.53359 | 0 | 0
113 | 0.97194 | -0.54273 | 0 | 0
114 | 0.97247 | -0.53203 | 0.0020171 | 0.00050554
115 | 0.97163 | -0.5488 | 0.00064167 | 0.00016082
116 | 0.97169 | -0.54775 | 0 | 0
117 | 0.97176 | -0.54625 | 0.00081967 | 0.00020543
118 | 0.9715 | -0.55154 | 0.00074513 | 0.00018675
119 | 0.97249 | -0.53169 | 0 | 0
120 | 0.9908 | -0.17679 | 0.001833 | 0.00045939
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0030339 | -0.00076002 | 0.0030341 | 0.00075988 | 1.6502e-07 | -1.4529e-07 | 0.0046536 | 0.0046535 | 0.0046536 | 0.97009 | -0.57641 | 0.97015 | -0.57527 | 1.2785
1 | 0.0019327 | 0.00048404 | -0.0019326 | -0.00048436 | 1.0447e-07 | -3.2448e-07 | 0.0029645 | 0.0029646 | 0.0029646 | 0.97009 | -0.57641 | 0.97003 | -0.57755 | 0.81445
2 | -0.011395 | -0.0028553 | 0.011396 | 0.002856 | 1.2833e-06 | 6.8296e-07 | 0.017478 | 0.017478 | 0.017478 | 0.97015 | -0.57527 | 0.97027 | -0.5729 | 4.8015
3 | -0.011396 | -0.002856 | 0.011443 | 0.0028807 | 4.6404e-05 | 2.4672e-05 | 0.017478 | 0.017476 | 0.017478 | 0.97027 | -0.5729 | 0.97458 | -0.48775 | 4.8015
4 | -0.011443 | -0.0028807 | 0.011446 | 0.0028824 | 3.2928e-06 | 1.749e-06 | 0.017476 | 0.017476 | 0.017476 | 0.97458 | -0.48775 | 0.97489 | -0.48173 | 4.801
5 | -0.014881 | -0.0037296 | 0.014882 | 0.0037299 | 6.0727e-07 | 3.5028e-07 | 0.022827 | 0.022827 | 0.022827 | 0.97006 | -0.57688 | 0.9701 | -0.57602 | 6.2711
6 | -0.026621 | -0.006672 | 0.02667 | 0.0067025 | 4.9051e-05 | 3.0422e-05 | 0.040833 | 0.040833 | 0.040833 | 0.9701 | -0.57602 | 0.97205 | -0.53742 | 11.2179
7 | 0.019632 | 0.0049259 | -0.019616 | -0.0049161 | 1.6112e-05 | 9.7228e-06 | 0.030054 | 0.030054 | 0.030054 | 0.97205 | -0.53742 | 0.97118 | -0.55465 | 8.2567
8 | -0.046302 | -0.011628 | 0.046424 | 0.011706 | 0.00012186 | 7.7186e-05 | 0.070887 | 0.070887 | 0.070887 | 0.97205 | -0.53742 | 0.97485 | -0.48242 | 19.4745
9 | -0.093439 | -0.023489 | 0.093852 | 0.023752 | 0.00041274 | 0.00026347 | 0.14265 | 0.14265 | 0.14265 | 0.97485 | -0.48242 | 0.97955 | -0.39035 | 39.1901
10 | 0.026265 | 0.0066167 | -0.026263 | -0.0066159 | 1.5046e-06 | 8.3614e-07 | 0.03991 | 0.039911 | 0.039911 | 0.97955 | -0.39035 | 0.97949 | -0.39155 | 5.4822
11 | -0.12012 | -0.030369 | 0.12026 | 0.030459 | 0.00014204 | 9.0329e-05 | 0.18256 | 0.18256 | 0.18256 | 0.97955 | -0.39035 | 0.98082 | -0.36573 | 25.0772
12 | 0.12313 | 0.03118 | -0.12312 | -0.031176 | 5.3083e-06 | 3.3769e-06 | 0.1869 | 0.1869 | 0.1869 | 0.98086 | -0.36483 | 0.98082 | -0.36573 | 25.6736
13 | -0.12517 | -0.031691 | 0.12592 | 0.032172 | 0.00075605 | 0.00048103 | 0.19 | 0.19 | 0.19 | 0.98086 | -0.36483 | 0.98733 | -0.23985 | 26.0988
14 | -0.12592 | -0.032172 | 0.12616 | 0.032323 | 0.0002375 | 0.0001511 | 0.19 | 0.19 | 0.19 | 0.98733 | -0.23985 | 0.98937 | -0.20092 | 26.0987
15 | -0.12616 | -0.032323 | 0.12697 | 0.032839 | 0.00080971 | 0.00051512 | 0.19 | 0.19 | 0.19 | 0.98937 | -0.20092 | 0.99631 | -0.069402 | 26.0986
16 | 0.026263 | 0.0066159 | -0.026249 | -0.006608 | 1.4226e-05 | 7.9063e-06 | 0.039911 | 0.039911 | 0.039911 | 0.97949 | -0.39155 | 0.97891 | -0.40288 | 5.4823
17 | -0.1414 | -0.036455 | 0.14188 | 0.03676 | 0.0004797 | 0.00030551 | 0.21155 | 0.21154 | 0.21155 | 0.99631 | -0.069402 | 1 | 0 | 29.0584
18 | -0.071649 | -0.018085 | 0.071721 | 0.01813 | 7.1994e-05 | 4.5203e-05 | 0.10706 | 0.10706 | 0.10706 | 0.99622 | -0.072038 | 0.99731 | -0.051082 | 14.7066
19 | 0.048808 | 0.01236 | -0.048798 | -0.012354 | 9.9753e-06 | 6.1239e-06 | 0.072948 | 0.072948 | 0.072948 | 0.99622 | -0.072038 | 0.996 | -0.076295 | 10.0204
20 | -0.17651 | -0.0449 | 0.17694 | 0.045178 | 0.00043566 | 0.00027795 | 0.26359 | 0.26359 | 0.26359 | 0.99731 | -0.051082 | 1 | 0 | 36.2072
21 | 0.099061 | 0.025335 | -0.098939 | -0.025258 | 0.00012216 | 7.7408e-05 | 0.14798 | 0.14798 | 0.14798 | 0.99731 | -0.051082 | 0.99597 | -0.076599 | 20.3273
22 | 0.0057251 | 0.0014346 | -0.0057244 | -0.0014345 | 7.1783e-07 | 1.1713e-07 | 0.0085419 | 0.008542 | 0.008542 | 0.99731 | -0.051082 | 0.99717 | -0.053715 | 2.3467
23 | 0.028015 | 0.0071292 | -0.027971 | -0.0071042 | 4.4514e-05 | 2.4974e-05 | 0.041893 | 0.041894 | 0.041894 | 0.996 | -0.076295 | 0.99427 | -0.10931 | 5.7547
24 | 0.020783 | 0.0052249 | -0.020761 | -0.0052118 | 2.1577e-05 | 1.3034e-05 | 0.031056 | 0.031056 | 0.031056 | 0.996 | -0.076295 | 0.99487 | -0.098059 | 8.5318
25 | 0.075745 | 0.019445 | -0.075187 | -0.019093 | 0.00055868 | 0.00035156 | 0.11333 | 0.11333 | 0.11333 | 0.99597 | -0.076599 | 0.98795 | -0.22978 | 15.5677
26 | 0.0021405 | 0.00053633 | -0.0021405 | -0.00053646 | 4.5875e-08 | -1.2705e-07 | 0.0031941 | 0.0031942 | 0.0031942 | 0.99717 | -0.053715 | 0.99715 | -0.054165 | 0.87753
27 | 0.02759 | 0.007009 | -0.027587 | -0.007007 | 3.5904e-06 | 2.007e-06 | 0.041325 | 0.041325 | 0.041325 | 0.99427 | -0.10931 | 0.99413 | -0.11201 | 5.6765
28 | 0.015001 | 0.0037681 | -0.014982 | -0.0037573 | 1.9036e-05 | 1.0876e-05 | 0.02244 | 0.02244 | 0.02244 | 0.99487 | -0.098059 | 0.99349 | -0.12468 | 6.165
29 | 0.075187 | 0.019093 | -0.075024 | -0.018991 | 0.00016277 | 0.00010245 | 0.11333 | 0.11333 | 0.11333 | 0.98795 | -0.22978 | 0.98561 | -0.27487 | 15.5678
30 | 0.027064 | 0.006876 | -0.026993 | -0.0068361 | 7.1654e-05 | 3.9847e-05 | 0.040543 | 0.040545 | 0.040545 | 0.99413 | -0.11201 | 0.99125 | -0.16715 | 5.5694
31 | 0.013717 | 0.0034402 | -0.013715 | -0.0034389 | 2.3866e-06 | 1.3322e-06 | 0.020546 | 0.020546 | 0.020546 | 0.99349 | -0.12468 | 0.9933 | -0.12834 | 5.6444
32 | 0.023808 | 0.0059963 | -0.023802 | -0.0059929 | 6.3508e-06 | 3.4149e-06 | 0.036201 | 0.036201 | 0.036201 | 0.97891 | -0.40288 | 0.97863 | -0.40846 | 4.9727
33 | 0.02354 | 0.0059271 | -0.023537 | -0.0059257 | 2.7095e-06 | 1.4508e-06 | 0.035803 | 0.035803 | 0.035803 | 0.97863 | -0.40846 | 0.9785 | -0.41087 | 4.9179
34 | 0.022923 | 0.0057718 | -0.02291 | -0.0057648 | 1.315e-05 | 6.9677e-06 | 0.034869 | 0.034869 | 0.034869 | 0.9785 | -0.41087 | 0.97789 | -0.42288 | 4.7897
35 | 0.02275 | 0.0057247 | -0.022749 | -0.0057245 | 4.9865e-07 | 2.6348e-07 | 0.034626 | 0.034626 | 0.034626 | 0.97789 | -0.42288 | 0.97787 | -0.42333 | 4.7563
36 | 0.070977 | 0.017977 | -0.070877 | -0.017913 | 0.00010044 | 6.3988e-05 | 0.10722 | 0.10722 | 0.10722 | 0.98561 | -0.27487 | 0.98409 | -0.30438 | 29.4572
37 | 0.064069 | 0.016206 | -0.063973 | -0.016145 | 9.632e-05 | 6.1298e-05 | 0.096931 | 0.096931 | 0.096931 | 0.98409 | -0.30438 | 0.98247 | -0.33576 | 26.6294
38 | -0.0021902 | -0.0005489 | 0.0021903 | 0.00054861 | 1.2249e-07 | -2.9748e-07 | 0.0033173 | 0.0033172 | 0.0033173 | 0.98241 | -0.33694 | 0.98247 | -0.33576 | 0.91135
39 | 0.0021902 | 0.0005489 | -0.0021902 | -0.0005489 | 6.0129e-11 | -1.3954e-10 | 0.0033173 | 0.0033173 | 0.0033173 | 0.98241 | -0.33694 | 0.98241 | -0.33694 | 0.91135
40 | 0.061783 | 0.015597 | -0.061719 | -0.015556 | 6.3931e-05 | 4.067e-05 | 0.093614 | 0.093614 | 0.093614 | 0.98247 | -0.33576 | 0.98136 | -0.35739 | 25.7181
41 | 0.0074017 | 0.0018538 | -0.0074012 | -0.0018536 | 5.4512e-07 | 1.9713e-07 | 0.011111 | 0.011111 | 0.011111 | 0.99119 | -0.16929 | 0.99111 | -0.17083 | 3.0526
42 | -0.0078598 | -0.0019686 | 0.0078599 | 0.0019686 | 7.6913e-08 | 3.0236e-08 | 0.011799 | 0.011799 | 0.011799 | 0.99119 | -0.16929 | 0.9912 | -0.16908 | 3.2415
43 | 0.0069791 | 0.0017478 | -0.006978 | -0.0017474 | 1.1379e-06 | 3.7214e-07 | 0.010478 | 0.010478 | 0.010478 | 0.99111 | -0.17083 | 0.99093 | -0.17426 | 2.8785
44 | -0.0082062 | -0.0020554 | 0.0082201 | 0.0020611 | 1.3868e-05 | 5.7283e-06 | 0.012319 | 0.012318 | 0.012319 | 0.9912 | -0.16908 | 0.99303 | -0.13364 | 3.3843
45 | 0.00234 | 0.00058567 | -0.0023398 | -0.00058602 | 1.6093e-07 | -3.448e-07 | 0.0035135 | 0.0035137 | 0.0035137 | 0.99093 | -0.17426 | 0.99086 | -0.1757 | 0.96529
46 | 0.004638 | 0.0011618 | -0.0046379 | -0.0011618 | 9.7418e-08 | -6.6488e-09 | 0.0069644 | 0.0069644 | 0.0069644 | 0.99093 | -0.17426 | 0.99091 | -0.1747 | 1.9133
47 | -0.013711 | -0.0034369 | 0.013715 | 0.0034389 | 3.464e-06 | 1.9338e-06 | 0.020546 | 0.020546 | 0.020546 | 0.99303 | -0.13364 | 0.9933 | -0.12834 | 5.6445
48 | 0.00081927 | 0.00020495 | -0.00081926 | -0.00020532 | 1.6907e-08 | -3.7622e-07 | 0.0012275 | 0.0012277 | 0.0012277 | 0.99303 | -0.13364 | 0.993 | -0.13407 | 0.33727
49 | 0.0018331 | 0.00045902 | -0.001833 | -0.00045939 | 9.5203e-08 | -3.7058e-07 | 0.0027527 | 0.0027528 | 0.0027528 | 0.99086 | -0.1757 | 0.9908 | -0.17679 | 0.75627
50 | 0.00020967 | 5.2133e-05 | -0.00020967 | -5.2549e-05 | 1.2025e-09 | -4.161e-07 | 0.00031471 | 0.00031486 | 0.00031486 | 0.99091 | -0.1747 | 0.9909 | -0.17482 | 0.0865
51 | 0.0044283 | 0.0011096 | -0.0044278 | -0.0011097 | 4.8198e-07 | -6.591e-08 | 0.0066497 | 0.0066498 | 0.0066498 | 0.99091 | -0.1747 | 0.99079 | -0.17698 | 1.8269
52 | -0.001951 | -0.00048896 | 0.0019511 | 0.00048846 | 1.5905e-07 | -5.0143e-07 | 0.0029695 | 0.0029693 | 0.0029695 | 0.97764 | -0.42777 | 0.97773 | -0.42605 | 0.81579
53 | 0.01917 | 0.0048272 | -0.019166 | -0.0048254 | 3.8763e-06 | 1.8721e-06 | 0.029183 | 0.029184 | 0.029184 | 0.97773 | -0.42605 | 0.97751 | -0.43028 | 4.0087
54 | -0.021121 | -0.0053157 | 0.021124 | 0.0053171 | 2.7451e-06 | 1.4016e-06 | 0.032153 | 0.032152 | 0.032153 | 0.97773 | -0.42605 | 0.97787 | -0.42333 | 4.4166
55 | 0.018977 | 0.0047779 | -0.018976 | -0.0047773 | 1.2976e-06 | 6.2266e-07 | 0.028895 | 0.028895 | 0.028895 | 0.97751 | -0.43028 | 0.97744 | -0.43171 | 3.9692
56 | 0.018685 | 0.0047044 | -0.01868 | -0.0047024 | 4.1661e-06 | 1.9785e-06 | 0.028453 | 0.028453 | 0.028453 | 0.97744 | -0.43171 | 0.9772 | -0.43638 | 3.9083
57 | -0.013556 | -0.0034113 | 0.013568 | 0.0034178 | 1.1397e-05 | 6.4085e-06 | 0.020697 | 0.020696 | 0.020697 | 0.97489 | -0.48173 | 0.97578 | -0.46415 | 5.6859
58 | -0.013952 | -0.0035139 | 0.013953 | 0.0035145 | 1.7838e-06 | 6.1678e-07 | 0.021282 | 0.021281 | 0.021282 | 0.97578 | -0.46415 | 0.97592 | -0.46148 | 2.9233
59 | -0.014378 | -0.003621 | 0.014378 | 0.0036211 | 4.152e-07 | 1.5065e-07 | 0.021929 | 0.021929 | 0.021929 | 0.97592 | -0.46148 | 0.97595 | -0.46088 | 3.0122
60 | 0.00042471 | 0.00010595 | -0.0004247 | -0.00010617 | 2.7176e-09 | -2.1431e-07 | 0.00064737 | 0.00064745 | 0.00064745 | 0.97595 | -0.46088 | 0.97594 | -0.46101 | 0.17787
61 | -0.014803 | -0.0037271 | 0.014805 | 0.0037276 | 1.492e-06 | 5.6467e-07 | 0.022576 | 0.022576 | 0.022576 | 0.97595 | -0.46088 | 0.97606 | -0.45877 | 3.1011
62 | 0.036312 | 0.009103 | -0.036292 | -0.0090906 | 1.9729e-05 | 1.2413e-05 | 0.055393 | 0.055393 | 0.055393 | 0.97546 | -0.47308 | 0.97488 | -0.48449 | 15.2178
63 | -0.040394 | -0.010126 | 0.040527 | 0.01021 | 0.00013296 | 8.3927e-05 | 0.06162 | 0.061619 | 0.06162 | 0.97546 | -0.47308 | 0.97896 | -0.40425 | 16.9285
64 | 0.019158 | 0.0047965 | -0.019158 | -0.0047962 | 5.5767e-07 | 3.3522e-07 | 0.029241 | 0.029241 | 0.029241 | 0.97488 | -0.48449 | 0.97485 | -0.48511 | 8.0331
65 | -0.040527 | -0.01021 | 0.040618 | 0.010267 | 9.1044e-05 | 5.7462e-05 | 0.061619 | 0.061619 | 0.061619 | 0.97896 | -0.40425 | 0.98136 | -0.35739 | 16.9284
66 | 0.014373 | 0.0035969 | -0.014369 | -0.0035947 | 3.8637e-06 | 2.2059e-06 | 0.021937 | 0.021937 | 0.021937 | 0.97485 | -0.48511 | 0.97456 | -0.49076 | 6.0266
67 | 0.010179 | 0.0025447 | -0.01017 | -0.0025404 | 8.5349e-06 | 4.289e-06 | 0.01554 | 0.01554 | 0.01554 | 0.97456 | -0.49076 | 0.97367 | -0.5084 | 4.2692
68 | -0.015212 | -0.0038296 | 0.015214 | 0.0038307 | 2.8106e-06 | 1.1023e-06 | 0.023196 | 0.023196 | 0.023196 | 0.97606 | -0.45877 | 0.97626 | -0.4549 | 3.1863
69 | -0.015813 | -0.0039807 | 0.015814 | 0.0039813 | 1.4969e-06 | 6.1446e-07 | 0.024108 | 0.024108 | 0.024108 | 0.97626 | -0.4549 | 0.97636 | -0.45292 | 3.3116
70 | -0.017744 | -0.0044648 | 0.017756 | 0.0044707 | 1.2698e-05 | 5.8094e-06 | 0.027048 | 0.027048 | 0.027048 | 0.97636 | -0.45292 | 0.97712 | -0.43796 | 3.7154
71 | 0.0004247 | 0.00010617 | -0.0004247 | -0.00010644 | 3.4389e-09 | -2.7112e-07 | 0.00064745 | 0.00064754 | 0.00064754 | 0.97594 | -0.46101 | 0.97594 | -0.46118 | 0.1779
72 | 0.00015072 | 3.7585e-05 | -0.00015072 | -3.7773e-05 | 2.9646e-10 | -1.8784e-07 | 0.00022945 | 0.00022952 | 0.00022952 | 0.97712 | -0.43796 | 0.97712 | -0.438 | 0.063055
73 | -0.017907 | -0.0045082 | 0.017908 | 0.0045089 | 1.3511e-06 | 6.2206e-07 | 0.027277 | 0.027277 | 0.027277 | 0.97712 | -0.43796 | 0.9772 | -0.43638 | 3.7468
74 | 0.025098 | 0.0063614 | -0.025089 | -0.0063562 | 9.5274e-06 | 5.1763e-06 | 0.037701 | 0.037702 | 0.037702 | 0.99125 | -0.16715 | 0.99084 | -0.17505 | 5.1788
75 | 0.02091 | 0.0053089 | -0.020897 | -0.0053026 | 1.2426e-05 | 6.2251e-06 | 0.031426 | 0.031427 | 0.031427 | 0.99084 | -0.17505 | 0.9902 | -0.18741 | 4.3169
76 | 0.02008 | 0.0050978 | -0.01996 | -0.0050391 | 0.00011954 | 5.8641e-05 | 0.030198 | 0.030205 | 0.030205 | 0.9902 | -0.18741 | 0.98376 | -0.31178 | 4.149
77 | 0.000361 | 9.0223e-05 | -0.000361 | -9.0475e-05 | 2.326e-09 | -2.5188e-07 | 0.00055168 | 0.00055178 | 0.00055178 | 0.97354 | -0.51085 | 0.97354 | -0.51099 | 0.15159
78 | -0.00060281 | -0.00015083 | 0.00060282 | 0.00015043 | 1.043e-08 | -4.0087e-07 | 0.00092128 | 0.00092113 | 0.00092128 | 0.97354 | -0.51085 | 0.97356 | -0.51049 | 0.2531
79 | -0.00060282 | -0.00015043 | 0.00060284 | 0.00014989 | 1.3871e-08 | -5.3335e-07 | 0.00092113 | 0.00092094 | 0.00092113 | 0.97356 | -0.51049 | 0.97359 | -0.51 | 0.25306
80 | -0.0010393 | -0.00025929 | 0.0010394 | 0.00025831 | 7.8828e-08 | -9.8634e-07 | 0.0015881 | 0.0015877 | 0.0015881 | 0.97359 | -0.51 | 0.97367 | -0.5084 | 0.43629
81 | 0.009131 | 0.0022821 | -0.0091253 | -0.0022794 | 5.7307e-06 | 2.692e-06 | 0.013952 | 0.013953 | 0.013953 | 0.97367 | -0.5084 | 0.973 | -0.52161 | 3.8331
82 | 0.0078666 | 0.0019646 | -0.0078639 | -0.0019634 | 2.7206e-06 | 1.1186e-06 | 0.012028 | 0.012028 | 0.012028 | 0.973 | -0.52161 | 0.97263 | -0.52889 | 3.3045
83 | 0.0012586 | 0.00031483 | -0.0012586 | -0.00031543 | 7.1907e-08 | -5.9683e-07 | 0.0019246 | 0.0019249 | 0.0019249 | 0.973 | -0.52161 | 0.97294 | -0.52281 | 0.52881
84 | 0.0078639 | 0.0019634 | -0.0078629 | -0.001963 | 1.0328e-06 | 4.2476e-07 | 0.012028 | 0.012028 | 0.012028 | 0.97263 | -0.52889 | 0.97249 | -0.53166 | 3.3045
85 | 0.0075245 | 0.0018782 | -0.0075245 | -0.0018782 | 1.2437e-08 | 4.8541e-09 | 0.011511 | 0.011511 | 0.011511 | 0.97249 | -0.53166 | 0.97249 | -0.53169 | 3.1622
86 | -0.0058481 | -0.0014628 | 0.0058483 | 0.0014628 | 2.0961e-07 | 4.681e-08 | 0.0089292 | 0.0089291 | 0.0089292 | 0.97445 | -0.49409 | 0.97449 | -0.49333 | 2.4531
87 | 0.0047859 | 0.0011966 | -0.0047854 | -0.0011966 | 5.444e-07 | 9.7647e-09 | 0.0073072 | 0.0073073 | 0.0073073 | 0.97445 | -0.49409 | 0.97433 | -0.49648 | 2.0075
88 | 0.0077628 | 0.0019431 | -0.0077607 | -0.0019422 | 2.0726e-06 | 8.3647e-07 | 0.011853 | 0.011853 | 0.011853 | 0.97449 | -0.49333 | 0.97421 | -0.49894 | 3.2563
89 | -0.014061 | -0.0035186 | 0.014133 | 0.0035595 | 7.2017e-05 | 4.087e-05 | 0.021469 | 0.021467 | 0.021469 | 0.97449 | -0.49333 | 0.97994 | -0.38623 | 5.898
90 | 0.0045432 | 0.0011359 | -0.0045429 | -0.0011359 | 3.0966e-07 | -1.5484e-08 | 0.0069375 | 0.0069376 | 0.0069376 | 0.97433 | -0.49648 | 0.97426 | -0.49791 | 1.9059
91 | 0.0067648 | 0.0016926 | -0.0067633 | -0.0016921 | 1.4256e-06 | 4.6903e-07 | 0.010332 | 0.010332 | 0.010332 | 0.97421 | -0.49894 | 0.97398 | -0.50337 | 2.8384
92 | -0.014133 | -0.0035595 | 0.014146 | 0.003567 | 1.3324e-05 | 7.5547e-06 | 0.021467 | 0.021466 | 0.021467 | 0.97994 | -0.38623 | 0.98095 | -0.36654 | 5.8974
93 | 0.004044 | 0.0010109 | -0.0040396 | -0.0010119 | 4.4437e-06 | -1.0197e-06 | 0.0061756 | 0.006177 | 0.006177 | 0.97426 | -0.49791 | 0.97309 | -0.52102 | 1.697
94 | 0.0044636 | 0.0011184 | -0.0044629 | -0.0011185 | 7.3544e-07 | -5.4088e-08 | 0.0068192 | 0.0068194 | 0.0068194 | 0.97398 | -0.50337 | 0.97381 | -0.50683 | 1.8735
95 | 0.0022997 | 0.00057374 | -0.0022992 | -0.0005748 | 5.1642e-07 | -1.0581e-06 | 0.0035125 | 0.003513 | 0.003513 | 0.97398 | -0.50337 | 0.97374 | -0.5081 | 0.96511
96 | 0.0039003 | 0.00097697 | -0.0039 | -0.00097705 | 2.884e-07 | -8.4e-08 | 0.005964 | 0.0059641 | 0.0059641 | 0.97309 | -0.52102 | 0.97301 | -0.52257 | 1.6385
97 | 0.0011303 | 0.00028324 | -0.0011303 | -0.00028329 | 4.2602e-09 | -4.4651e-08 | 0.0017272 | 0.0017272 | 0.0017272 | 0.97381 | -0.50683 | 0.9738 | -0.50691 | 0.47451
98 | 0.0022992 | 0.0005748 | -0.0022989 | -0.00057538 | 2.8699e-07 | -5.8756e-07 | 0.003513 | 0.0035133 | 0.0035133 | 0.97374 | -0.5081 | 0.97361 | -0.51072 | 0.96519
99 | 0.001316 | 0.00032905 | -0.001316 | -0.00032955 | 6.7198e-08 | -5.0791e-07 | 0.0020111 | 0.0020113 | 0.0020113 | 0.97361 | -0.51072 | 0.97356 | -0.5118 | 0.55255
100 | 0.0020147 | 0.00050467 | -0.0020146 | -0.00050491 | 8.5648e-08 | -2.4401e-07 | 0.003081 | 0.0030811 | 0.0030811 | 0.97301 | -0.52257 | 0.97297 | -0.52346 | 0.84645
101 | 0.0018853 | 0.00047238 | -0.0018852 | -0.00047249 | 3.0947e-08 | -1.035e-07 | 0.0028831 | 0.0028831 | 0.0028831 | 0.97301 | -0.52257 | 0.97299 | -0.52292 | 0.79207
102 | -0.017803 | -0.0044922 | 0.017807 | 0.0044942 | 3.3955e-06 | 2.0153e-06 | 0.026968 | 0.026968 | 0.026968 | 0.98274 | -0.33166 | 0.98294 | -0.32768 | 7.4087
103 | 0.017594 | 0.0044397 | -0.017576 | -0.0044291 | 1.7928e-05 | 1.0622e-05 | 0.026651 | 0.026651 | 0.026651 | 0.98274 | -0.33166 | 0.98165 | -0.35296 | 7.3217
104 | -0.019388 | -0.0048906 | 0.019403 | 0.0048995 | 1.477e-05 | 8.8735e-06 | 0.029362 | 0.029362 | 0.029362 | 0.98294 | -0.32768 | 0.98376 | -0.31178 | 8.0665
105 | 0.016944 | 0.0042708 | -0.016943 | -0.0042699 | 1.4695e-06 | 8.6544e-07 | 0.025694 | 0.025694 | 0.025694 | 0.98165 | -0.35296 | 0.98155 | -0.35477 | 7.0587
106 | 0.0021327 | 0.00053378 | -0.0021325 | -0.00053444 | 2.5687e-07 | -6.6381e-07 | 0.0032329 | 0.0032332 | 0.0032332 | 0.98155 | -0.35477 | 0.98142 | -0.3573 | 0.88824
107 | 0.01481 | 0.0037361 | -0.014802 | -0.0037313 | 8.3375e-06 | 4.7793e-06 | 0.022461 | 0.022461 | 0.022461 | 0.98155 | -0.35477 | 0.98095 | -0.36654 | 6.1706
108 | 0.00031357 | 7.8328e-05 | -0.00031356 | -7.8587e-05 | 1.7954e-09 | -2.5808e-07 | 0.00047917 | 0.00047926 | 0.00047926 | 0.97356 | -0.5118 | 0.97355 | -0.51192 | 0.13167
109 | 0.0027547 | 0.00068287 | -0.0027546 | -0.0006831 | 1.8293e-07 | -2.2364e-07 | 0.0042134 | 0.0042135 | 0.0042135 | 0.97224 | -0.53662 | 0.97217 | -0.53803 | 1.1576
110 | -0.0055061 | -0.0013724 | 0.0055064 | 0.0013725 | 2.907e-07 | 5.0581e-08 | 0.0084243 | 0.0084243 | 0.0084243 | 0.97224 | -0.53662 | 0.9723 | -0.53551 | 2.3144
111 | 0.0022076 | 0.00054602 | -0.0022072 | -0.00054688 | 3.8334e-07 | -8.6618e-07 | 0.0033764 | 0.0033768 | 0.0033768 | 0.97217 | -0.53803 | 0.97199 | -0.54171 | 0.92768
112 | -0.0055064 | -0.0013725 | 0.0055069 | 0.0013726 | 5.0013e-07 | 8.6982e-08 | 0.0084243 | 0.0084242 | 0.0084243 | 0.9723 | -0.53551 | 0.9724 | -0.53359 | 2.3144
113 | 0.0022072 | 0.00054688 | -0.0022071 | -0.00054712 | 1.0714e-07 | -2.4196e-07 | 0.0033768 | 0.0033769 | 0.0033769 | 0.97199 | -0.54171 | 0.97194 | -0.54273 | 0.92771
114 | -0.0055069 | -0.0013726 | 0.0055073 | 0.0013726 | 4.0742e-07 | 7.082e-08 | 0.0084242 | 0.0084241 | 0.0084242 | 0.9724 | -0.53359 | 0.97247 | -0.53203 | 2.3143
115 | 0.0022071 | 0.00054712 | -0.0022067 | -0.00054795 | 3.6717e-07 | -8.2884e-07 | 0.0033769 | 0.0033772 | 0.0033772 | 0.97194 | -0.54273 | 0.97176 | -0.54625 | 0.92781
116 | -0.0075244 | -0.0018782 | 0.0075245 | 0.0018782 | 1.2139e-07 | 4.7375e-08 | 0.011511 | 0.011511 | 0.011511 | 0.97247 | -0.53203 | 0.97249 | -0.53169 | 3.1622
117 | -0.00064167 | -0.00016082 | 0.0006417 | 0.00015974 | 3.2054e-08 | -1.0763e-06 | 0.00098269 | 0.0009823 | 0.00098269 | 0.97163 | -0.5488 | 0.97169 | -0.54775 | 0.26997
118 | -0.001387 | -0.00034318 | 0.0013871 | 0.00034252 | 9.7795e-08 | -6.5469e-07 | 0.0021224 | 0.0021221 | 0.0021224 | 0.97169 | -0.54775 | 0.97176 | -0.54625 | 0.58307
119 | 0.00074526 | 0.00018344 | -0.00074513 | -0.00018675 | 1.3383e-07 | -3.3111e-06 | 0.0011401 | 0.0011413 | 0.0011413 | 0.97169 | -0.54775 | 0.9715 | -0.55154 | 0.31354

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32047 | 0.081938

## res_load
| p_mw | q_mvar
0 | 0.0011012 | 0.00027599
1 | 0.008361 | 0.0020955
2 | 0.0019326 | 0.00048436
3 | 0.014881 | 0.0037296
4 | 0.011739 | 0.0029421
5 | 0.019616 | 0.0049161
6 | 0.047016 | 0.011783
7 | 0.0020408 | 0.00051147
8 | 0.0028616 | 0.00071719
9 | 0.014428 | 0.003616
10 | 0.022841 | 0.0057244
11 | 0.023194 | 0.0058129
12 | 0.0035838 | 0.00089819
13 | 0.0003801 | 9.5263e-05
14 | 0.0057604 | 0.0014437
15 | 0.0021405 | 0.00053646
16 | 0.00052264 | 0.00013099
17 | 0.0012651 | 0.00031706
18 | 0.0024405 | 0.00061165
19 | 0.00026236 | 6.5753e-05
20 | 0.00061404 | 0.00015389
21 | 0.00015998 | 4.0094e-05
22 | 0.0040469 | 0.0010142
23 | 0.0068074 | 0.0017061
24 | 0.0021902 | 0.0005489
25 | 0.00045811 | 0.00011481
26 | 0.00042204 | 0.00010577
27 | 0.00034629 | 8.6787e-05
28 | 0.0046718 | 0.0011709
29 | 0.00050672 | 0.000127
30 | 0.001951 | 0.00048896
31 | 0.00018934 | 4.7453e-05
32 | 0.0016254 | 0.00040738
33 | 0.00029095 | 7.2919e-05
34 | 0.0021103 | 0.0005289
35 | 0.00038376 | 9.6179e-05
36 | 0.00042464 | 0.00010643
37 | 0.004082 | 0.0010231
38 | 0.017134 | 0.0042941
39 | 0.0047851 | 0.0011993
40 | 0.021101 | 0.0052884
41 | 0.0041897 | 0.00105
42 | 0.00081926 | 0.00020532
43 | 0.00040693 | 0.00010199
44 | 0.00059838 | 0.00014997
45 | 0.0019293 | 0.00048352
46 | 0.0004247 | 0.00010644
47 | 0.00077216 | 0.00019352
48 | 0.00015072 | 3.7773e-05
49 | 0.0018943 | 0.00047476
50 | 0.0041789 | 0.0010473
51 | 0.00081747 | 0.00020488
52 | 0.00024181 | 6.0603e-05
53 | 0.000361 | 9.0475e-05
54 | 0.00043651 | 0.0001094
55 | 0.0012586 | 0.00031543
56 | 0.0044278 | 0.0011097
57 | 0.00020967 | 5.2549e-05
58 | 0.00033837 | 8.4804e-05
59 | 0.0010622 | 0.0002662
60 | 0.00044976 | 0.00011272
61 | 0.00024217 | 6.0694e-05
62 | 0.00099597 | 0.00024961
63 | 0.0004989 | 0.00012504
64 | 0.00013929 | 3.491e-05
65 | 0.0033325 | 0.00083521
66 | 0.0011303 | 0.00028329
67 | 0.0009829 | 0.00024634
68 | 0.0020146 | 0.00050491
69 | 0.0018852 | 0.00047249
70 | 0.0002093 | 5.2455e-05
71 | 0.0015819 | 0.00039646
72 | 0.00063163 | 0.0001583
73 | 0.00055711 | 0.00013962
74 | 0.0021325 | 0.00053444
75 | 0.00065562 | 0.00016431
76 | 0.0010024 | 0.00025123
77 | 0.00031356 | 7.8587e-05
78 | 0.0027513 | 0.00068955
79 | 0.00054696 | 0.00013708
80 | 0.0020171 | 0.00050554
81 | 0.00064167 | 0.00016082
82 | 0.00081967 | 0.00020543
83 | 0.00074513 | 0.00018675
84 | 0.001833 | 0.00045939

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1