## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1062-2_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1062-2_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1062-2_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1062-2_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1062-2_0_7_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1062-2_0_7_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_1062-2_0_7_node_34 | 0.4 | n |  | TRUE
7 | bus_LV_1062-2_0_7_node_80 | 0.4 | n |  | TRUE
8 | bus_LV_1062-2_0_7_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_1062-2_0_7_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1062-2_0_7_node_83 | 0.4 | n |  | TRUE
11 | bus_LV_1062-2_0_7_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1062-2_0_7_node_71 | 0.4 | n |  | TRUE
13 | bus_LV_1062-2_0_7_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1062-2_0_7_node_68 | 0.4 | n |  | TRUE
15 | bus_LV_1062-2_0_7_node_69 | 0.4 | n |  | TRUE
16 | bus_LV_1062-2_0_7_node_66 | 0.4 | n |  | TRUE
17 | bus_LV_1062-2_0_7_node_70 | 0.4 | n |  | TRUE
18 | bus_LV_1062-2_0_7_node_67 | 0.4 | n |  | TRUE
19 | bus_LV_1062-2_0_7_node_165 | 0.4 | n |  | TRUE
20 | bus_LV_1062-2_0_7_node_261 | 0.4 | n |  | TRUE
21 | bus_LV_1062-2_0_7_node_260 | 0.4 | n |  | TRUE
22 | bus_LV_1062-2_0_7_node_8 | 0.4 | n |  | TRUE
23 | bus_LV_1062-2_0_7_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_1062-2_0_7_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_1062-2_0_7_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_1062-2_0_7_node_256 | 0.4 | n |  | TRUE
27 | bus_LV_1062-2_0_7_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_1062-2_0_7_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_1062-2_0_7_node_257 | 0.4 | n |  | TRUE
30 | bus_LV_1062-2_0_7_node_255 | 0.4 | n |  | TRUE
31 | bus_LV_1062-2_0_7_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_1062-2_0_7_node_45 | 0.4 | n |  | TRUE
33 | bus_LV_1062-2_0_7_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_1062-2_0_7_node_44 | 0.4 | n |  | TRUE
35 | bus_LV_1062-2_0_7_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_1062-2_0_7_node_13 | 0.4 | n |  | TRUE
37 | bus_LV_1062-2_0_7_node_16 | 0.4 | n |  | TRUE
38 | bus_LV_1062-2_0_7_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_1062-2_0_7_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_1062-2_0_7_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_1062-2_0_7_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_1062-2_0_7_node_78 | 0.4 | n |  | TRUE
43 | bus_LV_1062-2_0_7_node_76 | 0.4 | n |  | TRUE
44 | bus_LV_1062-2_0_7_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_1062-2_0_7_node_82 | 0.4 | n |  | TRUE
46 | bus_LV_1062-2_0_7_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_1062-2_0_7_node_21 | 0.4 | n |  | TRUE
48 | bus_LV_1062-2_0_7_node_22 | 0.4 | n |  | TRUE
49 | bus_LV_1062-2_0_7_node_23 | 0.4 | n |  | TRUE
50 | bus_LV_1062-2_0_7_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_1062-2_0_7_node_92 | 0.4 | n |  | TRUE
52 | bus_LV_1062-2_0_7_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_1062-2_0_7_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_1062-2_0_7_node_27 | 0.4 | n |  | TRUE
55 | bus_LV_1062-2_0_7_node_63 | 0.4 | n |  | TRUE
56 | bus_LV_1062-2_0_7_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_1062-2_0_7_node_262 | 0.4 | n |  | TRUE
58 | bus_LV_1062-2_0_7_node_65 | 0.4 | n |  | TRUE
59 | bus_LV_1062-2_0_7_node_61 | 0.4 | n |  | TRUE
60 | bus_LV_1062-2_0_7_node_28 | 0.4 | n |  | TRUE
61 | bus_LV_1062-2_0_7_node_31 | 0.4 | n |  | TRUE
62 | bus_LV_1062-2_0_7_node_79 | 0.4 | n |  | TRUE
63 | bus_LV_1062-2_0_7_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_1062-2_0_7_node_35 | 0.4 | n |  | TRUE
65 | bus_LV_1062-2_0_7_node_36 | 0.4 | n |  | TRUE
66 | bus_LV_1062-2_0_7_node_37 | 0.4 | n |  | TRUE
67 | bus_LV_1062-2_0_7_node_38 | 0.4 | n |  | TRUE
68 | bus_LV_1062-2_0_7_node_39 | 0.4 | n |  | TRUE
69 | bus_LV_1062-2_0_7_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_1062-2_0_7_node_81 | 0.4 | n |  | TRUE
71 | bus_LV_1062-2_0_7_node_263 | 0.4 | n |  | TRUE
72 | bus_LV_1062-2_0_7_node_62 | 0.4 | n |  | TRUE
73 | bus_LV_1062-2_0_7_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_1062-2_0_7_node_46 | 0.4 | n |  | TRUE
75 | bus_LV_1062-2_0_7_node_47 | 0.4 | n |  | TRUE
76 | bus_LV_1062-2_0_7_node_48 | 0.4 | n |  | TRUE
77 | bus_LV_1062-2_0_7_node_49 | 0.4 | n |  | TRUE
78 | bus_LV_1062-2_0_7_node_50 | 0.4 | n |  | TRUE
79 | bus_LV_1062-2_0_7_node_51 | 0.4 | n |  | TRUE
80 | bus_LV_1062-2_0_7_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_1062-2_0_7_node_55 | 0.4 | n |  | TRUE
82 | bus_LV_1062-2_0_7_node_53 | 0.4 | n |  | TRUE
83 | bus_LV_1062-2_0_7_node_93 | 0.4 | n |  | TRUE
84 | bus_LV_1062-2_0_7_node_94 | 0.4 | n |  | TRUE
85 | bus_LV_1062-2_0_7_node_54 | 0.4 | n |  | TRUE
86 | bus_LV_1062-2_0_7_node_100 | 0.4 | n |  | TRUE
87 | bus_LV_1062-2_0_7_node_101 | 0.4 | n |  | TRUE
88 | bus_LV_1062-2_0_7_node_95 | 0.4 | n |  | TRUE
89 | bus_LV_1062-2_0_7_node_56 | 0.4 | n |  | TRUE
90 | bus_LV_1062-2_0_7_node_57 | 0.4 | n |  | TRUE
91 | bus_LV_1062-2_0_7_node_59 | 0.4 | n |  | TRUE
92 | bus_LV_1062-2_0_7_node_60 | 0.4 | n |  | TRUE
93 | bus_LV_1062-2_0_7_node_109 | 0.4 | n |  | TRUE
94 | bus_LV_1062-2_0_7_node_107 | 0.4 | n |  | TRUE
95 | bus_LV_1062-2_0_7_node_114 | 0.4 | n |  | TRUE
96 | bus_LV_1062-2_0_7_node_108 | 0.4 | n |  | TRUE
97 | bus_LV_1062-2_0_7_node_161 | 0.4 | n |  | TRUE
98 | bus_LV_1062-2_0_7_node_162 | 0.4 | n |  | TRUE
99 | bus_LV_1062-2_0_7_node_118 | 0.4 | n |  | TRUE
100 | bus_LV_1062-2_0_7_node_123 | 0.4 | n |  | TRUE
101 | bus_LV_1062-2_0_7_node_116 | 0.4 | n |  | TRUE
102 | bus_LV_1062-2_0_7_node_72 | 0.4 | n |  | TRUE
103 | bus_LV_1062-2_0_7_node_73 | 0.4 | n |  | TRUE
104 | bus_LV_1062-2_0_7_node_74 | 0.4 | n |  | TRUE
105 | bus_LV_1062-2_0_7_node_75 | 0.4 | n |  | TRUE
106 | bus_LV_1062-2_0_7_node_77 | 0.4 | n |  | TRUE
107 | bus_LV_1062-2_0_7_node_84 | 0.4 | n |  | TRUE
108 | bus_LV_1062-2_0_7_node_85 | 0.4 | n |  | TRUE
109 | bus_LV_1062-2_0_7_node_86 | 0.4 | n |  | TRUE
110 | bus_LV_1062-2_0_7_node_87 | 0.4 | n |  | TRUE
111 | bus_LV_1062-2_0_7_node_264 | 0.4 | n |  | TRUE
112 | bus_LV_1062-2_0_7_node_266 | 0.4 | n |  | TRUE
113 | bus_LV_1062-2_0_7_node_265 | 0.4 | n |  | TRUE
114 | bus_LV_1062-2_0_7_node_110 | 0.4 | n |  | TRUE
115 | bus_LV_1062-2_0_7_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_1062-2_0_7_node_97 | 0.4 | n |  | TRUE
117 | bus_LV_1062-2_0_7_node_98 | 0.4 | n |  | TRUE
118 | bus_LV_1062-2_0_7_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_1062-2_0_7_node_121 | 0.4 | n |  | TRUE
120 | bus_LV_1062-2_0_7_node_102 | 0.4 | n |  | TRUE
121 | bus_LV_1062-2_0_7_node_103 | 0.4 | n |  | TRUE
122 | bus_LV_1062-2_0_7_node_112 | 0.4 | n |  | TRUE
123 | bus_LV_1062-2_0_7_node_113 | 0.4 | n |  | TRUE
124 | bus_LV_1062-2_0_7_node_106 | 0.4 | n |  | TRUE
125 | bus_LV_1062-2_0_7_node_111 | 0.4 | n |  | TRUE
126 | bus_LV_1062-2_0_7_node_198 | 0.4 | n |  | TRUE
127 | bus_LV_1062-2_0_7_node_193 | 0.4 | n |  | TRUE
128 | bus_LV_1062-2_0_7_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_1062-2_0_7_node_268 | 0.4 | n |  | TRUE
130 | bus_LV_1062-2_0_7_node_131 | 0.4 | n |  | TRUE
131 | bus_LV_1062-2_0_7_node_183 | 0.4 | n |  | TRUE
132 | bus_LV_1062-2_0_7_node_184 | 0.4 | n |  | TRUE
133 | bus_LV_1062-2_0_7_node_177 | 0.4 | n |  | TRUE
134 | bus_LV_1062-2_0_7_node_238 | 0.4 | n |  | TRUE
135 | bus_LV_1062-2_0_7_node_122 | 0.4 | n |  | TRUE
136 | bus_LV_1062-2_0_7_node_236 | 0.4 | n |  | TRUE
137 | bus_LV_1062-2_0_7_node_120 | 0.4 | n |  | TRUE
138 | bus_LV_1062-2_0_7_node_237 | 0.4 | n |  | TRUE
139 | bus_LV_1062-2_0_7_node_190 | 0.4 | n |  | TRUE
140 | bus_LV_1062-2_0_7_node_235 | 0.4 | n |  | TRUE
141 | bus_LV_1062-2_0_7_node_117 | 0.4 | n |  | TRUE
142 | bus_LV_1062-2_0_7_node_119 | 0.4 | n |  | TRUE
143 | bus_LV_1062-2_0_7_node_124 | 0.4 | n |  | TRUE
144 | bus_LV_1062-2_0_7_node_125 | 0.4 | n |  | TRUE
145 | bus_LV_1062-2_0_7_node_130 | 0.4 | n |  | TRUE
146 | bus_LV_1062-2_0_7_node_128 | 0.4 | n |  | TRUE
147 | bus_LV_1062-2_0_7_node_197 | 0.4 | n |  | TRUE
148 | bus_LV_1062-2_0_7_node_228 | 0.4 | n |  | TRUE
149 | bus_LV_1062-2_0_7_node_215 | 0.4 | n |  | TRUE
150 | bus_LV_1062-2_0_7_node_220 | 0.4 | n |  | TRUE
151 | bus_LV_1062-2_0_7_node_219 | 0.4 | n |  | TRUE
152 | bus_LV_1062-2_0_7_node_191 | 0.4 | n |  | TRUE
153 | bus_LV_1062-2_0_7_node_267 | 0.4 | n |  | TRUE
154 | bus_LV_1062-2_0_7_node_166 | 0.4 | n |  | TRUE
155 | bus_LV_1062-2_0_7_node_174 | 0.4 | n |  | TRUE
156 | bus_LV_1062-2_0_7_node_234 | 0.4 | n |  | TRUE
157 | bus_LV_1062-2_0_7_node_252 | 0.4 | n |  | TRUE
158 | bus_LV_1062-2_0_7_node_126 | 0.4 | n |  | TRUE
159 | bus_LV_1062-2_0_7_node_199 | 0.4 | n |  | TRUE
160 | bus_LV_1062-2_0_7_node_127 | 0.4 | n |  | TRUE
161 | bus_LV_1062-2_0_7_node_129 | 0.4 | n |  | TRUE
162 | bus_LV_1062-2_0_7_node_244 | 0.4 | n |  | TRUE
163 | bus_LV_1062-2_0_7_node_217 | 0.4 | n |  | TRUE
164 | bus_LV_1062-2_0_7_node_222 | 0.4 | n |  | TRUE
165 | bus_LV_1062-2_0_7_node_221 | 0.4 | n |  | TRUE
166 | bus_LV_1062-2_0_7_node_180 | 0.4 | n |  | TRUE
167 | bus_LV_1062-2_0_7_node_216 | 0.4 | n |  | TRUE
168 | bus_LV_1062-2_0_7_node_178 | 0.4 | n |  | TRUE
169 | bus_LV_1062-2_0_7_node_179 | 0.4 | n |  | TRUE
170 | bus_LV_1062-2_0_7_node_176 | 0.4 | n |  | TRUE
171 | bus_LV_1062-2_0_7_node_181 | 0.4 | n |  | TRUE
172 | bus_LV_1062-2_0_7_node_132 | 0.4 | n |  | TRUE
173 | bus_LV_1062-2_0_7_node_133 | 0.4 | n |  | TRUE
174 | bus_LV_1062-2_0_7_node_134 | 0.4 | n |  | TRUE
175 | bus_LV_1062-2_0_7_node_135 | 0.4 | n |  | TRUE
176 | bus_LV_1062-2_0_7_node_136 | 0.4 | n |  | TRUE
177 | bus_LV_1062-2_0_7_node_137 | 0.4 | n |  | TRUE
178 | bus_LV_1062-2_0_7_node_138 | 0.4 | n |  | TRUE
179 | bus_LV_1062-2_0_7_node_139 | 0.4 | n |  | TRUE
180 | bus_LV_1062-2_0_7_node_140 | 0.4 | n |  | TRUE
181 | bus_LV_1062-2_0_7_node_232 | 0.4 | n |  | TRUE
182 | bus_LV_1062-2_0_7_node_231 | 0.4 | n |  | TRUE
183 | bus_LV_1062-2_0_7_node_200 | 0.4 | n |  | TRUE
184 | bus_LV_1062-2_0_7_node_153 | 0.4 | n |  | TRUE
185 | bus_LV_1062-2_0_7_node_152 | 0.4 | n |  | TRUE
186 | bus_LV_1062-2_0_7_node_233 | 0.4 | n |  | TRUE
187 | bus_LV_1062-2_0_7_node_201 | 0.4 | n |  | TRUE
188 | bus_LV_1062-2_0_7_node_223 | 0.4 | n |  | TRUE
189 | bus_LV_1062-2_0_7_node_151 | 0.4 | n |  | TRUE
190 | bus_LV_1062-2_0_7_node_141 | 0.4 | n |  | TRUE
191 | bus_LV_1062-2_0_7_node_142 | 0.4 | n |  | TRUE
192 | bus_LV_1062-2_0_7_node_143 | 0.4 | n |  | TRUE
193 | bus_LV_1062-2_0_7_node_144 | 0.4 | n |  | TRUE
194 | bus_LV_1062-2_0_7_node_145 | 0.4 | n |  | TRUE
195 | bus_LV_1062-2_0_7_node_146 | 0.4 | n |  | TRUE
196 | bus_LV_1062-2_0_7_node_147 | 0.4 | n |  | TRUE
197 | bus_LV_1062-2_0_7_node_148 | 0.4 | n |  | TRUE
198 | bus_LV_1062-2_0_7_node_149 | 0.4 | n |  | TRUE
199 | bus_LV_1062-2_0_7_node_150 | 0.4 | n |  | TRUE
200 | bus_LV_1062-2_0_7_node_249 | 0.4 | n |  | TRUE
201 | bus_LV_1062-2_0_7_node_175 | 0.4 | n |  | TRUE
202 | bus_LV_1062-2_0_7_node_226 | 0.4 | n |  | TRUE
203 | bus_LV_1062-2_0_7_node_188 | 0.4 | n |  | TRUE
204 | bus_LV_1062-2_0_7_node_185 | 0.4 | n |  | TRUE
205 | bus_LV_1062-2_0_7_node_209 | 0.4 | n |  | TRUE
206 | bus_LV_1062-2_0_7_node_210 | 0.4 | n |  | TRUE
207 | bus_LV_1062-2_0_7_node_172 | 0.4 | n |  | TRUE
208 | bus_LV_1062-2_0_7_node_225 | 0.4 | n |  | TRUE
209 | bus_LV_1062-2_0_7_node_189 | 0.4 | n |  | TRUE
210 | bus_LV_1062-2_0_7_node_186 | 0.4 | n |  | TRUE
211 | bus_LV_1062-2_0_7_node_239 | 0.4 | n |  | TRUE
212 | bus_LV_1062-2_0_7_node_154 | 0.4 | n |  | TRUE
213 | bus_LV_1062-2_0_7_node_155 | 0.4 | n |  | TRUE
214 | bus_LV_1062-2_0_7_node_156 | 0.4 | n |  | TRUE
215 | bus_LV_1062-2_0_7_node_157 | 0.4 | n |  | TRUE
216 | bus_LV_1062-2_0_7_node_158 | 0.4 | n |  | TRUE
217 | bus_LV_1062-2_0_7_node_159 | 0.4 | n |  | TRUE
218 | bus_LV_1062-2_0_7_node_160 | 0.4 | n |  | TRUE
219 | bus_LV_1062-2_0_7_node_240 | 0.4 | n |  | TRUE
220 | bus_LV_1062-2_0_7_node_224 | 0.4 | n |  | TRUE
221 | bus_LV_1062-2_0_7_node_205 | 0.4 | n |  | TRUE
222 | bus_LV_1062-2_0_7_node_292 | 0.4 | n |  | TRUE
223 | bus_LV_1062-2_0_7_node_163 | 0.4 | n |  | TRUE
224 | bus_LV_1062-2_0_7_node_164 | 0.4 | n |  | TRUE
225 | bus_LV_1062-2_0_7_node_269 | 0.4 | n |  | TRUE
226 | bus_LV_1062-2_0_7_node_259 | 0.4 | n |  | TRUE
227 | bus_LV_1062-2_0_7_node_282 | 0.4 | n |  | TRUE
228 | bus_LV_1062-2_0_7_node_281 | 0.4 | n |  | TRUE
229 | bus_LV_1062-2_0_7_node_167 | 0.4 | n |  | TRUE
230 | bus_LV_1062-2_0_7_node_168 | 0.4 | n |  | TRUE
231 | bus_LV_1062-2_0_7_node_169 | 0.4 | n |  | TRUE
232 | bus_LV_1062-2_0_7_node_170 | 0.4 | n |  | TRUE
233 | bus_LV_1062-2_0_7_node_171 | 0.4 | n |  | TRUE
234 | bus_LV_1062-2_0_7_node_173 | 0.4 | n |  | TRUE
235 | bus_LV_1062-2_0_7_node_211 | 0.4 | n |  | TRUE
236 | bus_LV_1062-2_0_7_node_212 | 0.4 | n |  | TRUE
237 | bus_LV_1062-2_0_7_node_182 | 0.4 | n |  | TRUE
238 | bus_LV_1062-2_0_7_node_218 | 0.4 | n |  | TRUE
239 | bus_LV_1062-2_0_7_node_250 | 0.4 | n |  | TRUE
240 | bus_LV_1062-2_0_7_node_213 | 0.4 | n |  | TRUE
241 | bus_LV_1062-2_0_7_node_214 | 0.4 | n |  | TRUE
242 | bus_LV_1062-2_0_7_node_251 | 0.4 | n |  | TRUE
243 | bus_LV_1062-2_0_7_node_229 | 0.4 | n |  | TRUE
244 | bus_LV_1062-2_0_7_node_187 | 0.4 | n |  | TRUE
245 | bus_LV_1062-2_0_7_node_207 | 0.4 | n |  | TRUE
246 | bus_LV_1062-2_0_7_node_192 | 0.4 | n |  | TRUE
247 | bus_LV_1062-2_0_7_node_194 | 0.4 | n |  | TRUE
248 | bus_LV_1062-2_0_7_node_195 | 0.4 | n |  | TRUE
249 | bus_LV_1062-2_0_7_node_196 | 0.4 | n |  | TRUE
250 | bus_LV_1062-2_0_7_node_243 | 0.4 | n |  | TRUE
251 | bus_LV_1062-2_0_7_node_241 | 0.4 | n |  | TRUE
252 | bus_LV_1062-2_0_7_node_247 | 0.4 | n |  | TRUE
253 | bus_LV_1062-2_0_7_node_203 | 0.4 | n |  | TRUE
254 | bus_LV_1062-2_0_7_node_227 | 0.4 | n |  | TRUE
255 | bus_LV_1062-2_0_7_node_202 | 0.4 | n |  | TRUE
256 | bus_LV_1062-2_0_7_node_204 | 0.4 | n |  | TRUE
257 | bus_LV_1062-2_0_7_node_206 | 0.4 | n |  | TRUE
258 | bus_LV_1062-2_0_7_node_208 | 0.4 | n |  | TRUE
259 | bus_LV_1062-2_0_7_node_230 | 0.4 | n |  | TRUE
260 | bus_LV_1062-2_0_7_node_245 | 0.4 | n |  | TRUE
261 | bus_LV_1062-2_0_7_node_291 | 0.4 | n |  | TRUE
262 | bus_LV_1062-2_0_7_node_242 | 0.4 | n |  | TRUE
263 | bus_LV_1062-2_0_7_node_246 | 0.4 | n |  | TRUE
264 | bus_LV_1062-2_0_7_node_248 | 0.4 | n |  | TRUE
265 | bus_LV_1062-2_0_7_node_253 | 0.4 | n |  | TRUE
266 | bus_LV_1062-2_0_7_node_254 | 0.4 | n |  | TRUE
267 | bus_LV_1062-2_0_7_node_258 | 0.4 | n |  | TRUE
268 | bus_LV_1062-2_0_7_node_287 | 0.4 | n |  | TRUE
269 | bus_LV_1062-2_0_7_node_288 | 0.4 | n |  | TRUE
270 | bus_LV_1062-2_0_7_node_289 | 0.4 | n |  | TRUE
271 | bus_LV_1062-2_0_7_node_283 | 0.4 | n |  | TRUE
272 | bus_LV_1062-2_0_7_node_280 | 0.4 | n |  | TRUE
273 | bus_LV_1062-2_0_7_node_270 | 0.4 | n |  | TRUE
274 | bus_LV_1062-2_0_7_node_271 | 0.4 | n |  | TRUE
275 | bus_LV_1062-2_0_7_node_272 | 0.4 | n |  | TRUE
276 | bus_LV_1062-2_0_7_node_273 | 0.4 | n |  | TRUE
277 | bus_LV_1062-2_0_7_node_290 | 0.4 | n |  | TRUE
278 | bus_LV_1062-2_0_7_node_276 | 0.4 | n |  | TRUE
279 | bus_LV_1062-2_0_7_node_277 | 0.4 | n |  | TRUE
280 | bus_LV_1062-2_0_7_node_278 | 0.4 | n |  | TRUE
281 | bus_LV_1062-2_0_7_node_279 | 0.4 | n |  | TRUE
282 | bus_LV_1062-2_0_7_node_284 | 0.4 | n |  | TRUE
283 | bus_MV_2_0_node_297 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1062-2_0_7_load_0 | 0 | 0.00029899 | 7.4934e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1062-2_0_7_load_1 | 1 | 0.0020304 | 0.00050887 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1062-2_0_7_load_2 | 2 | 0.001812 | 0.00045413 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1062-2_0_7_load_7 | 4 | 0.00017035 | 4.2693e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1062-2_0_7_load_33 | 5 | 0.00035453 | 8.8853e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1062-2_0_7_load_34 | 6 | 0.00024601 | 6.1657e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1062-2_0_7_load_80 | 7 | 0.00058859 | 0.00014751 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1062-2_0_7_load_83 | 10 | 0.00012676 | 3.177e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1062-2_0_7_load_69 | 15 | 0.0004308 | 0.00010797 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1062-2_0_7_load_66 | 16 | 0.00029274 | 7.3366e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1062-2_0_7_load_67 | 18 | 0.0014218 | 0.00035635 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1062-2_0_7_load_261 | 20 | 0.00063552 | 0.00015928 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1062-2_0_7_load_260 | 21 | 0.00098188 | 0.00024608 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1062-2_0_7_load_8 | 22 | 0.0019957 | 0.00050016 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1062-2_0_7_load_9 | 23 | 0.0013033 | 0.00032664 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1062-2_0_7_load_11 | 25 | 0.00030018 | 7.5233e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1062-2_0_7_load_256 | 26 | 0.00091557 | 0.00022946 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1062-2_0_7_load_14 | 27 | 0.00015128 | 3.7915e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1062-2_0_7_load_255 | 30 | 0.00047129 | 0.00011812 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1062-2_0_7_load_15 | 31 | 5.1287e-05 | 1.2854e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1062-2_0_7_load_45 | 32 | 4.2747e-05 | 1.0714e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1062-2_0_7_load_26 | 33 | 9.7542e-05 | 2.4446e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1062-2_0_7_load_44 | 34 | 0.00019031 | 4.7697e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1062-2_0_7_load_24 | 35 | 0.00019048 | 4.7739e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1062-2_0_7_load_13 | 36 | 0.00052624 | 0.00013189 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1062-2_0_7_load_16 | 37 | 0.0006491 | 0.00016268 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1062-2_0_7_load_17 | 38 | 0.00021695 | 5.4374e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1062-2_0_7_load_20 | 41 | 0.00025356 | 6.3549e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1062-2_0_7_load_78 | 42 | 0.00010601 | 2.6567e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1062-2_0_7_load_76 | 43 | 0.00015341 | 3.8449e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1062-2_0_7_load_32 | 44 | 0.00036238 | 9.0821e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1062-2_0_7_load_82 | 45 | 0.00063556 | 0.00015929 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1062-2_0_7_load_21 | 47 | 0.00035124 | 8.8029e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1062-2_0_7_load_22 | 48 | 0.00023005 | 5.7657e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1062-2_0_7_load_25 | 50 | 0.00059667 | 0.00014954 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1062-2_0_7_load_92 | 51 | 6.5895e-05 | 1.6515e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1062-2_0_7_load_40 | 52 | 0.00014299 | 3.5836e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1062-2_0_7_load_42 | 53 | 0.00015776 | 3.9538e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1062-2_0_7_load_27 | 54 | 0.0004169 | 0.00010448 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1062-2_0_7_load_43 | 56 | 4.4139e-05 | 1.1062e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1062-2_0_7_load_262 | 57 | 8.2495e-05 | 2.0675e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1062-2_0_7_load_61 | 59 | 6.2132e-05 | 1.5572e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1062-2_0_7_load_28 | 60 | 0.00097255 | 0.00024375 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1062-2_0_7_load_31 | 61 | 0.00015169 | 3.8017e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1062-2_0_7_load_79 | 62 | 0.0025977 | 0.00065104 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1062-2_0_7_load_35 | 64 | 0.00011992 | 3.0054e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1062-2_0_7_load_36 | 65 | 0.00040402 | 0.00010126 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1062-2_0_7_load_39 | 68 | 0.00012284 | 3.0787e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1062-2_0_7_load_81 | 70 | 6.8969e-05 | 1.7285e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1062-2_0_7_load_62 | 72 | 0.00016483 | 4.1311e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1062-2_0_7_load_64 | 73 | 0.00011925 | 2.9888e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1062-2_0_7_load_46 | 74 | 0.00018659 | 4.6763e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1062-2_0_7_load_47 | 75 | 0.0002412 | 6.0449e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1062-2_0_7_load_48 | 76 | 0.0002683 | 6.7241e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1062-2_0_7_load_49 | 77 | 0.00035499 | 8.8968e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1062-2_0_7_load_55 | 81 | 0.00042179 | 0.00010571 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1062-2_0_7_load_53 | 82 | 0.00037347 | 9.36e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1062-2_0_7_load_93 | 83 | 0.0013163 | 0.0003299 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1062-2_0_7_load_94 | 84 | 0.00038631 | 9.6818e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1062-2_0_7_load_100 | 86 | 0.00073007 | 0.00018297 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1062-2_0_7_load_101 | 87 | 0.0071521 | 0.0017925 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1062-2_0_7_load_57 | 90 | 0.001329 | 0.00033307 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1062-2_0_7_load_60 | 92 | 0.0041485 | 0.0010397 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1062-2_0_7_load_109 | 93 | 0.0035145 | 0.00088081 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1062-2_0_7_load_107 | 94 | 0.0010791 | 0.00027044 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1062-2_0_7_load_114 | 95 | 0.00037203 | 9.324e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1062-2_0_7_load_108 | 96 | 0.00050385 | 0.00012628 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1062-2_0_7_load_161 | 97 | 0.0036133 | 0.00090559 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1062-2_0_7_load_123 | 100 | 0.0024261 | 0.00060805 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1062-2_0_7_load_116 | 101 | 0.00089681 | 0.00022476 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1062-2_0_7_load_72 | 102 | 5.7341e-05 | 1.4371e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1062-2_0_7_load_73 | 103 | 4.6747e-05 | 1.1716e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1062-2_0_7_load_74 | 104 | 0.00041294 | 0.00010349 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1062-2_0_7_load_75 | 105 | 7.095e-05 | 1.7782e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1062-2_0_7_load_77 | 106 | 0.00073462 | 0.00018411 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1062-2_0_7_load_84 | 107 | 0.0001385 | 3.4712e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1062-2_0_7_load_86 | 109 | 0.00017261 | 4.326e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1062-2_0_7_load_87 | 110 | 7.8531e-05 | 1.9682e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1062-2_0_7_load_264 | 111 | 0.00014945 | 3.7457e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1062-2_0_7_load_266 | 112 | 0.00015416 | 3.8637e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1062-2_0_7_load_265 | 113 | 7.8344e-05 | 1.9635e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1062-2_0_7_load_96 | 115 | 0.0066542 | 0.0016677 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1062-2_0_7_load_97 | 116 | 0.0013702 | 0.00034342 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1062-2_0_7_load_98 | 117 | 0.0023148 | 0.00058015 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1062-2_0_7_load_99 | 118 | 0.0017665 | 0.00044274 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1062-2_0_7_load_102 | 120 | 0.0040165 | 0.0010066 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1062-2_0_7_load_103 | 121 | 0.00088025 | 0.00022061 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1062-2_0_7_load_106 | 124 | 0.0062863 | 0.0015755 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1062-2_0_7_load_193 | 127 | 0.0013786 | 0.00034552 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1062-2_0_7_load_115 | 128 | 0.00065133 | 0.00016324 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1062-2_0_7_load_268 | 129 | 0.0005374 | 0.00013468 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1062-2_0_7_load_184 | 132 | 0.0022872 | 0.00057324 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1062-2_0_7_load_238 | 134 | 0.00089683 | 0.00022477 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1062-2_0_7_load_236 | 136 | 0.0012263 | 0.00030734 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1062-2_0_7_load_237 | 138 | 0.0012059 | 0.00030222 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1062-2_0_7_load_190 | 139 | 0.0035827 | 0.00089792 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1062-2_0_7_load_235 | 140 | 0.0027291 | 0.00068398 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1062-2_0_7_load_124 | 143 | 0.00077942 | 0.00019534 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1062-2_0_7_load_125 | 144 | 0.004601 | 0.0011531 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1062-2_0_7_load_130 | 145 | 0.0025246 | 0.00063272 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1062-2_0_7_load_128 | 146 | 0.0009099 | 0.00022804 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1062-2_0_7_load_228 | 148 | 0.0071698 | 0.0017969 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1062-2_0_7_load_215 | 149 | 0.0022034 | 0.00055222 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1062-2_0_7_load_220 | 150 | 0.0015045 | 0.00037706 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1062-2_0_7_load_219 | 151 | 0.0015045 | 0.00037706 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1062-2_0_7_load_191 | 152 | 0.00085372 | 0.00021396 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1062-2_0_7_load_267 | 153 | 0.00061047 | 0.000153 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1062-2_0_7_load_166 | 154 | 0.00077941 | 0.00019534 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1062-2_0_7_load_174 | 155 | 0.0021111 | 0.0005291 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1062-2_0_7_load_234 | 156 | 0.0012119 | 0.00030373 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1062-2_0_7_load_252 | 157 | 0.00089683 | 0.00022477 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1062-2_0_7_load_126 | 158 | 0.00094913 | 0.00023787 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1062-2_0_7_load_127 | 160 | 0.0049859 | 0.0012496 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1062-2_0_7_load_129 | 161 | 0.0014998 | 0.00037589 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1062-2_0_7_load_244 | 162 | 0.00044847 | 0.0001124 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1062-2_0_7_load_217 | 163 | 0.0021352 | 0.00053513 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_1062-2_0_7_load_222 | 164 | 0.0019514 | 0.00048907 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_1062-2_0_7_load_221 | 165 | 0.0050746 | 0.0012718 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_1062-2_0_7_load_216 | 167 | 0.0021108 | 0.00052902 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_1062-2_0_7_load_176 | 170 | 0.0070388 | 0.0017641 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_1062-2_0_7_load_132 | 172 | 0.0024572 | 0.00061583 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_1062-2_0_7_load_133 | 173 | 0.00038207 | 9.5755e-05 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_1062-2_0_7_load_135 | 175 | 0.0013517 | 0.00033878 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_1062-2_0_7_load_136 | 176 | 0.00063216 | 0.00015844 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_1062-2_0_7_load_137 | 177 | 0.0004794 | 0.00012015 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_1062-2_0_7_load_139 | 179 | 0.00093715 | 0.00023487 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_1062-2_0_7_load_232 | 181 | 0.00054122 | 0.00013564 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_1062-2_0_7_load_231 | 182 | 0.0015329 | 0.00038417 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_1062-2_0_7_load_200 | 183 | 0.00034124 | 8.5524e-05 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_1062-2_0_7_load_153 | 184 | 0.00036946 | 9.2596e-05 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_1062-2_0_7_load_152 | 185 | 0.00055405 | 0.00013886 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_1062-2_0_7_load_233 | 186 | 0.00030832 | 7.7273e-05 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_1062-2_0_7_load_223 | 188 | 0.00097109 | 0.00024338 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_1062-2_0_7_load_151 | 189 | 0.0020704 | 0.00051889 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_1062-2_0_7_load_141 | 190 | 0.0025321 | 0.00063462 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_1062-2_0_7_load_142 | 191 | 0.0021265 | 0.00053294 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_1062-2_0_7_load_144 | 193 | 0.0021249 | 0.00053255 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_1062-2_0_7_load_146 | 195 | 0.0025855 | 0.00064799 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_1062-2_0_7_load_147 | 196 | 0.0021264 | 0.00053293 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_1062-2_0_7_load_148 | 197 | 0.0051758 | 0.0012972 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_1062-2_0_7_load_149 | 198 | 0.0024714 | 0.0006194 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_1062-2_0_7_load_249 | 200 | 0.0030944 | 0.00077553 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_1062-2_0_7_load_226 | 202 | 0.0017691 | 0.00044337 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_1062-2_0_7_load_188 | 203 | 0.0021024 | 0.0005269 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_1062-2_0_7_load_185 | 204 | 0.0003089 | 7.7419e-05 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_1062-2_0_7_load_209 | 205 | 0.0026252 | 0.00065793 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_1062-2_0_7_load_210 | 206 | 0.0028565 | 0.00071591 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_1062-2_0_7_load_172 | 207 | 0.0026636 | 0.00066757 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_1062-2_0_7_load_225 | 208 | 0.0029348 | 0.00073553 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_1062-2_0_7_load_189 | 209 | 0.00029899 | 7.4934e-05 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_1062-2_0_7_load_186 | 210 | 0.0058902 | 0.0014762 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_1062-2_0_7_load_239 | 211 | 0.00028851 | 7.2307e-05 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_1062-2_0_7_load_154 | 212 | 0.0018176 | 0.00045554 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_1062-2_0_7_load_155 | 213 | 0.00055507 | 0.00013911 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_1062-2_0_7_load_156 | 214 | 0.0016906 | 0.00042371 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_1062-2_0_7_load_157 | 215 | 0.00031499 | 7.8943e-05 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_1062-2_0_7_load_158 | 216 | 0.00029497 | 7.3927e-05 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_1062-2_0_7_load_159 | 217 | 0.001423 | 0.00035664 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_1062-2_0_7_load_160 | 218 | 0.00029538 | 7.4029e-05 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_1062-2_0_7_load_240 | 219 | 0.00029714 | 7.447e-05 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_1062-2_0_7_load_224 | 220 | 0.0018121 | 0.00045416 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_1062-2_0_7_load_292 | 222 | 0.00029114 | 7.2966e-05 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_1062-2_0_7_load_163 | 223 | 0.00070773 | 0.00017737 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_1062-2_0_7_load_164 | 224 | 0.00067745 | 0.00016979 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_1062-2_0_7_load_259 | 226 | 0.0017248 | 0.00043226 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_1062-2_0_7_load_282 | 227 | 0.00065642 | 0.00016451 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_1062-2_0_7_load_281 | 228 | 0.00065221 | 0.00016346 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_1062-2_0_7_load_167 | 229 | 0.0028443 | 0.00071285 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_1062-2_0_7_load_168 | 230 | 0.0013778 | 0.00034532 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_1062-2_0_7_load_170 | 232 | 0.0021103 | 0.00052889 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_1062-2_0_7_load_171 | 233 | 0.0028585 | 0.0007164 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_1062-2_0_7_load_173 | 234 | 0.0018071 | 0.00045289 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_1062-2_0_7_load_211 | 235 | 0.0023797 | 0.00059641 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_1062-2_0_7_load_212 | 236 | 0.0053448 | 0.0013395 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_1062-2_0_7_load_182 | 237 | 0.043832 | 0.010985 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_1062-2_0_7_load_218 | 238 | 0.00070715 | 0.00017723 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_1062-2_0_7_load_250 | 239 | 0.0071382 | 0.001789 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_1062-2_0_7_load_213 | 240 | 0.0037171 | 0.0009316 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_1062-2_0_7_load_214 | 241 | 0.0019254 | 0.00048254 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_1062-2_0_7_load_251 | 242 | 0.066214 | 0.016595 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_1062-2_0_7_load_229 | 243 | 0.0019169 | 0.00048042 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_1062-2_0_7_load_187 | 244 | 0.00060062 | 0.00015053 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_1062-2_0_7_load_207 | 245 | 0.00050328 | 0.00012613 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_1062-2_0_7_load_192 | 246 | 0.0040524 | 0.0010156 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_1062-2_0_7_load_195 | 248 | 0.0042524 | 0.0010658 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_1062-2_0_7_load_196 | 249 | 0.00077582 | 0.00019444 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_1062-2_0_7_load_241 | 251 | 0.0028599 | 0.00071677 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_1062-2_0_7_load_247 | 252 | 0.0022978 | 0.00057588 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_1062-2_0_7_load_203 | 253 | 0.0019186 | 0.00048084 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_1062-2_0_7_load_227 | 254 | 0.0060356 | 0.0015127 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_1062-2_0_7_load_202 | 255 | 0.0014464 | 0.00036251 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_1062-2_0_7_load_204 | 256 | 0.002253 | 0.00056466 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_1062-2_0_7_load_206 | 257 | 0.002253 | 0.00056466 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_1062-2_0_7_load_208 | 258 | 0.0045946 | 0.0011515 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_1062-2_0_7_load_230 | 259 | 0.0015992 | 0.0004008 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_1062-2_0_7_load_245 | 260 | 0.001637 | 0.00041027 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_1062-2_0_7_load_291 | 261 | 0.00029098 | 7.2926e-05 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_1062-2_0_7_load_242 | 262 | 0.0041467 | 0.0010393 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_1062-2_0_7_load_246 | 263 | 0.0015805 | 0.00039612 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_1062-2_0_7_load_248 | 264 | 0.0020671 | 0.00051806 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_1062-2_0_7_load_253 | 265 | 0.0016997 | 0.00042599 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_1062-2_0_7_load_258 | 267 | 0.00091527 | 0.00022939 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_1062-2_0_7_load_287 | 268 | 0.001771 | 0.00044386 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_1062-2_0_7_load_288 | 269 | 0.00045107 | 0.00011305 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_1062-2_0_7_load_289 | 270 | 0.00050875 | 0.0001275 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_1062-2_0_7_load_283 | 271 | 0.00057502 | 0.00014411 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_1062-2_0_7_load_280 | 272 | 0.00068044 | 0.00017053 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_1062-2_0_7_load_270 | 273 | 0.001625 | 0.00040726 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_1062-2_0_7_load_271 | 274 | 0.00061628 | 0.00015446 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_1062-2_0_7_load_272 | 275 | 0.00063473 | 0.00015908 | 0 | 0 |  | 1 | TRUE | wye
210 | LV_1062-2_0_7_load_273 | 276 | 0.00086918 | 0.00021784 | 0 | 0 |  | 1 | TRUE | wye
211 | LV_1062-2_0_7_load_290 | 277 | 0.0010306 | 0.00025828 | 0 | 0 |  | 1 | TRUE | wye
212 | LV_1062-2_0_7_load_276 | 278 | 0.00048056 | 0.00012044 | 0 | 0 |  | 1 | TRUE | wye
213 | LV_1062-2_0_7_load_277 | 279 | 0.00082174 | 0.00020595 | 0 | 0 |  | 1 | TRUE | wye
214 | LV_1062-2_0_7_load_278 | 280 | 0.0009021 | 0.00022609 | 0 | 0 |  | 1 | TRUE | wye
215 | LV_1062-2_0_7_load_279 | 281 | 0.001349 | 0.00033808 | 0 | 0 |  | 1 | TRUE | wye
216 | LV_1062-2_0_7_load_284 | 282 | 0.00098521 | 0.00024692 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 130 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1062-2_0_7_line_0 |  | 0 | 1 | 0.034049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1062-2_0_7_line_1 |  | 0 | 2 | 0.042138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1062-2_0_7_line_2 |  | 1 | 3 | 0.050967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1062-2_0_7_line_3 |  | 2 | 4 | 0.20782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1062-2_0_7_line_4 |  | 3 | 9 | 0.082523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1062-2_0_7_line_5 |  | 5 | 6 | 0.14257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_1062-2_0_7_line_6 |  | 5 | 7 | 0.12799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1062-2_0_7_line_7 |  | 5 | 8 | 0.17225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1062-2_0_7_line_8 |  | 6 | 62 | 0.087799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1062-2_0_7_line_9 |  | 7 | 13 | 0.060757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1062-2_0_7_line_10 |  | 8 | 60 | 0.015394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1062-2_0_7_line_11 |  | 9 | 10 | 0.011326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1062-2_0_7_line_12 |  | 10 | 12 | 0.0082244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1062-2_0_7_line_13 |  | 11 | 12 | 0.028919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1062-2_0_7_line_14 |  | 11 | 13 | 0.0098922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1062-2_0_7_line_15 |  | 12 | 17 | 0.023778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1062-2_0_7_line_16 |  | 14 | 15 | 0.017483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1062-2_0_7_line_17 |  | 14 | 16 | 0.011032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1062-2_0_7_line_18 |  | 15 | 17 | 0.031748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1062-2_0_7_line_19 |  | 16 | 97 | 0.23057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1062-2_0_7_line_20 |  | 16 | 18 | 0.028908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1062-2_0_7_line_21 |  | 19 | 20 | 0.063729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1062-2_0_7_line_22 |  | 19 | 21 | 0.043226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1062-2_0_7_line_23 |  | 21 | 226 | 0.021017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1062-2_0_7_line_24 |  | 22 | 23 | 0.046572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1062-2_0_7_line_25 |  | 22 | 24 | 0.025388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1062-2_0_7_line_26 |  | 23 | 25 | 0.021213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1062-2_0_7_line_27 |  | 23 | 26 | 0.25532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_1062-2_0_7_line_28 |  | 24 | 27 | 0.23062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1062-2_0_7_line_29 |  | 25 | 28 | 0.12601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1062-2_0_7_line_30 |  | 26 | 29 | 0.12498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_1062-2_0_7_line_31 |  | 26 | 30 | 0.021008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_1062-2_0_7_line_32 |  | 27 | 31 | 0.013272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1062-2_0_7_line_33 |  | 28 | 36 | 0.10621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1062-2_0_7_line_34 |  | 29 | 153 | 0.03481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_1062-2_0_7_line_35 |  | 30 | 265 | 0.24008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1062-2_0_7_line_36 |  | 31 | 32 | 0.0018394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_1062-2_0_7_line_37 |  | 32 | 34 | 0.034108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1062-2_0_7_line_38 |  | 33 | 34 | 0.0068938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1062-2_0_7_line_39 |  | 33 | 35 | 0.16455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1062-2_0_7_line_40 |  | 35 | 48 | 0.0056561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1062-2_0_7_line_41 |  | 37 | 38 | 0.01669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1062-2_0_7_line_42 |  | 38 | 39 | 0.014426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1062-2_0_7_line_43 |  | 39 | 40 | 0.1529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1062-2_0_7_line_44 |  | 39 | 41 | 0.061853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1062-2_0_7_line_45 |  | 40 | 44 | 0.1109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1062-2_0_7_line_46 |  | 41 | 45 | 0.018437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1062-2_0_7_line_47 |  | 42 | 43 | 0.091937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1062-2_0_7_line_48 |  | 43 | 104 | 0.034632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1062-2_0_7_line_49 |  | 44 | 46 | 0.0030944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1062-2_0_7_line_50 |  | 46 | 61 | 0.011996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1062-2_0_7_line_51 |  | 46 | 60 | 0.040492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1062-2_0_7_line_52 |  | 47 | 48 | 0.018107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1062-2_0_7_line_53 |  | 47 | 49 | 0.010895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1062-2_0_7_line_54 |  | 49 | 50 | 0.080329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1062-2_0_7_line_55 |  | 50 | 54 | 0.023673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_1062-2_0_7_line_56 |  | 51 | 52 | 0.040819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1062-2_0_7_line_57 |  | 51 | 53 | 0.24006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1062-2_0_7_line_58 |  | 52 | 67 | 0.01938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1062-2_0_7_line_59 |  | 53 | 56 | 0.0049241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1062-2_0_7_line_60 |  | 54 | 55 | 0.015914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_1062-2_0_7_line_61 |  | 55 | 59 | 0.019622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_1062-2_0_7_line_62 |  | 56 | 57 | 0.02721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_1062-2_0_7_line_63 |  | 56 | 58 | 0.32348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_1062-2_0_7_line_64 |  | 57 | 71 | 0.22286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_1062-2_0_7_line_65 |  | 58 | 73 | 0.021968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_1062-2_0_7_line_66 |  | 59 | 72 | 0.010473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1062-2_0_7_line_67 |  | 62 | 63 | 0.047636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_1062-2_0_7_line_68 |  | 63 | 81 | 0.011353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1062-2_0_7_line_69 |  | 64 | 65 | 0.027444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1062-2_0_7_line_70 |  | 64 | 66 | 0.14717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1062-2_0_7_line_71 |  | 65 | 67 | 0.016525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1062-2_0_7_line_72 |  | 66 | 68 | 0.021777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1062-2_0_7_line_73 |  | 68 | 69 | 0.024092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1062-2_0_7_line_74 |  | 69 | 70 | 0.014602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1062-2_0_7_line_75 |  | 71 | 111 | 0.043361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_1062-2_0_7_line_76 |  | 72 | 73 | 0.024245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_1062-2_0_7_line_77 |  | 74 | 75 | 0.013034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_1062-2_0_7_line_78 |  | 74 | 76 | 0.0052251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_1062-2_0_7_line_79 |  | 75 | 77 | 0.0016476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_1062-2_0_7_line_80 |  | 76 | 78 | 0.018292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_1062-2_0_7_line_81 |  | 77 | 79 | 0.086666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_1062-2_0_7_line_82 |  | 78 | 80 | 0.004361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_1062-2_0_7_line_83 |  | 79 | 81 | 0.0058876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_1062-2_0_7_line_84 |  | 79 | 82 | 0.0093379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_1062-2_0_7_line_85 |  | 80 | 83 | 0.10465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_1062-2_0_7_line_86 |  | 80 | 84 | 0.048136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1062-2_0_7_line_87 |  | 82 | 85 | 0.14071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_1062-2_0_7_line_88 |  | 83 | 86 | 0.0048156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_1062-2_0_7_line_89 |  | 83 | 87 | 0.031082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1062-2_0_7_line_90 |  | 84 | 88 | 0.049137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1062-2_0_7_line_91 |  | 85 | 89 | 0.075483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_1062-2_0_7_line_92 |  | 85 | 90 | 0.11816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1062-2_0_7_line_93 |  | 86 | 114 | 0.03708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_1062-2_0_7_line_94 |  | 88 | 115 | 0.058796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1062-2_0_7_line_95 |  | 88 | 116 | 0.012786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1062-2_0_7_line_96 |  | 89 | 91 | 0.12358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_1062-2_0_7_line_97 |  | 89 | 92 | 0.12552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1062-2_0_7_line_98 |  | 91 | 93 | 0.073082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_1062-2_0_7_line_99 |  | 91 | 94 | 0.18432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1062-2_0_7_line_100 |  | 93 | 95 | 0.17218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_1062-2_0_7_line_101 |  | 94 | 96 | 0.0053909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1062-2_0_7_line_102 |  | 95 | 123 | 0.054468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_1062-2_0_7_line_103 |  | 97 | 98 | 0.036769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1062-2_0_7_line_104 |  | 98 | 223 | 0.043156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1062-2_0_7_line_105 |  | 98 | 224 | 0.021065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1062-2_0_7_line_106 |  | 99 | 100 | 0.18057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1062-2_0_7_line_107 |  | 99 | 101 | 0.029623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1062-2_0_7_line_108 |  | 101 | 141 | 0.1896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1062-2_0_7_line_109 |  | 102 | 103 | 0.0047506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1062-2_0_7_line_110 |  | 102 | 104 | 0.094656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1062-2_0_7_line_111 |  | 103 | 105 | 0.0027936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1062-2_0_7_line_112 |  | 105 | 106 | 0.044299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1062-2_0_7_line_113 |  | 106 | 107 | 0.0018954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1062-2_0_7_line_114 |  | 107 | 108 | 0.044593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1062-2_0_7_line_115 |  | 108 | 109 | 0.071272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1062-2_0_7_line_116 |  | 108 | 110 | 0.015104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1062-2_0_7_line_117 |  | 109 | 111 | 0.17908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_1062-2_0_7_line_118 |  | 111 | 112 | 0.041204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1062-2_0_7_line_119 |  | 112 | 113 | 0.0012116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1062-2_0_7_line_120 |  | 114 | 119 | 0.045769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_1062-2_0_7_line_121 |  | 115 | 117 | 0.01568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1062-2_0_7_line_122 |  | 116 | 118 | 0.052204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1062-2_0_7_line_123 |  | 119 | 134 | 0.013099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1062-2_0_7_line_124 |  | 119 | 135 | 0.029577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1062-2_0_7_line_125 |  | 119 | 136 | 0.013601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_1062-2_0_7_line_126 |  | 120 | 121 | 0.016184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1062-2_0_7_line_127 |  | 121 | 122 | 0.20041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1062-2_0_7_line_128 |  | 122 | 123 | 0.028884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1062-2_0_7_line_129 |  | 123 | 128 | 0.012341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_1062-2_0_7_line_130 |  | 124 | 125 | 0.049686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1062-2_0_7_line_131 |  | 125 | 126 | 0.024475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1062-2_0_7_line_132 |  | 125 | 127 | 0.019164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1062-2_0_7_line_133 |  | 126 | 150 | 0.01469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1062-2_0_7_line_134 |  | 126 | 151 | 0.022687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1062-2_0_7_line_135 |  | 126 | 147 | 0.0074087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1062-2_0_7_line_136 |  | 127 | 152 | 0.0031976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1062-2_0_7_line_137 |  | 128 | 129 | 0.25463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
138 | LV_1062-2_0_7_line_138 |  | 129 | 153 | 0.033036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_1062-2_0_7_line_139 |  | 130 | 131 | 0.028068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_1062-2_0_7_line_140 |  | 130 | 132 | 0.028695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1062-2_0_7_line_141 |  | 130 | 133 | 0.14249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
142 | LV_1062-2_0_7_line_142 |  | 131 | 164 | 0.019504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1062-2_0_7_line_143 |  | 131 | 165 | 0.019364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
144 | LV_1062-2_0_7_line_144 |  | 133 | 169 | 0.011465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1062-2_0_7_line_145 |  | 133 | 170 | 0.017391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_1062-2_0_7_line_146 |  | 134 | 157 | 0.0068592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1062-2_0_7_line_147 |  | 135 | 145 | 0.13368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_1062-2_0_7_line_148 |  | 135 | 146 | 0.0025239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_1062-2_0_7_line_149 |  | 136 | 156 | 0.04525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
150 | LV_1062-2_0_7_line_150 |  | 137 | 138 | 0.015641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_1062-2_0_7_line_151 |  | 137 | 139 | 0.04116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
152 | LV_1062-2_0_7_line_152 |  | 137 | 140 | 0.011306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
153 | LV_1062-2_0_7_line_153 |  | 139 | 155 | 0.044177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
154 | LV_1062-2_0_7_line_154 |  | 140 | 156 | 0.018503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
155 | LV_1062-2_0_7_line_155 |  | 141 | 142 | 0.004292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_1062-2_0_7_line_156 |  | 142 | 143 | 0.034372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_1062-2_0_7_line_157 |  | 142 | 144 | 0.048446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_1062-2_0_7_line_158 |  | 143 | 154 | 0.00021085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_1062-2_0_7_line_159 |  | 146 | 158 | 0.0053517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_1062-2_0_7_line_160 |  | 147 | 148 | 0.015991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_1062-2_0_7_line_161 |  | 147 | 149 | 0.026149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_1062-2_0_7_line_162 |  | 148 | 252 | 0.0052002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_1062-2_0_7_line_163 |  | 149 | 241 | 0.038305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_1062-2_0_7_line_164 |  | 151 | 238 | 0.028424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_1062-2_0_7_line_165 |  | 152 | 246 | 0.05456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_1062-2_0_7_line_166 |  | 154 | 159 | 0.020615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_1062-2_0_7_line_167 |  | 155 | 233 | 0.012849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
168 | LV_1062-2_0_7_line_168 |  | 157 | 220 | 0.0072781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_1062-2_0_7_line_169 |  | 158 | 160 | 0.025206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_1062-2_0_7_line_170 |  | 159 | 220 | 0.031665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_1062-2_0_7_line_171 |  | 159 | 221 | 0.024542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_1062-2_0_7_line_172 |  | 159 | 217 | 0.087894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_1062-2_0_7_line_173 |  | 160 | 161 | 0.040384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_1062-2_0_7_line_174 |  | 162 | 163 | 0.0061412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_1062-2_0_7_line_175 |  | 163 | 167 | 0.023361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_1062-2_0_7_line_176 |  | 164 | 243 | 0.0098377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_1062-2_0_7_line_177 |  | 165 | 234 | 0.012873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
178 | LV_1062-2_0_7_line_178 |  | 166 | 167 | 0.021837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_1062-2_0_7_line_179 |  | 166 | 168 | 0.012209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_1062-2_0_7_line_180 |  | 168 | 171 | 0.037307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_1062-2_0_7_line_181 |  | 168 | 170 | 0.032446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_1062-2_0_7_line_182 |  | 169 | 237 | 0.014562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_1062-2_0_7_line_183 |  | 171 | 238 | 0.062279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_1062-2_0_7_line_184 |  | 172 | 173 | 0.061973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_1062-2_0_7_line_185 |  | 172 | 174 | 0.02607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_1062-2_0_7_line_186 |  | 173 | 175 | 0.16068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_1062-2_0_7_line_187 |  | 174 | 176 | 0.022834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_1062-2_0_7_line_188 |  | 174 | 177 | 0.066576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_1062-2_0_7_line_189 |  | 175 | 178 | 0.011998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_1062-2_0_7_line_190 |  | 176 | 179 | 0.021414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_1062-2_0_7_line_191 |  | 177 | 180 | 0.033844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_1062-2_0_7_line_192 |  | 178 | 181 | 0.012709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_1062-2_0_7_line_193 |  | 178 | 182 | 0.035613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_1062-2_0_7_line_194 |  | 179 | 183 | 0.0072146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_1062-2_0_7_line_195 |  | 180 | 184 | 0.0099016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_1062-2_0_7_line_196 |  | 180 | 185 | 0.053752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_1062-2_0_7_line_197 |  | 181 | 186 | 0.0022818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_1062-2_0_7_line_198 |  | 183 | 187 | 0.002268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_1062-2_0_7_line_199 |  | 184 | 188 | 0.05662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_1062-2_0_7_line_200 |  | 185 | 189 | 0.021403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_1062-2_0_7_line_201 |  | 187 | 254 | 0.018922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_1062-2_0_7_line_202 |  | 188 | 211 | 0.013508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_1062-2_0_7_line_203 |  | 190 | 191 | 0.0033014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_1062-2_0_7_line_204 |  | 190 | 192 | 0.03434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_1062-2_0_7_line_205 |  | 191 | 193 | 0.00016883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_1062-2_0_7_line_206 |  | 192 | 194 | 0.007356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_1062-2_0_7_line_207 |  | 192 | 195 | 0.0050859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_1062-2_0_7_line_208 |  | 193 | 196 | 0.00016188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_1062-2_0_7_line_209 |  | 194 | 197 | 0.013969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_1062-2_0_7_line_210 |  | 194 | 198 | 0.011208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_1062-2_0_7_line_211 |  | 195 | 199 | 0.026808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_1062-2_0_7_line_212 |  | 196 | 200 | 0.0051775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_1062-2_0_7_line_213 |  | 197 | 201 | 0.015167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_1062-2_0_7_line_214 |  | 198 | 202 | 0.016528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_1062-2_0_7_line_215 |  | 199 | 203 | 0.015845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_1062-2_0_7_line_216 |  | 199 | 204 | 0.01897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_1062-2_0_7_line_217 |  | 201 | 205 | 0.018187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_1062-2_0_7_line_218 |  | 201 | 206 | 0.019347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_1062-2_0_7_line_219 |  | 201 | 207 | 0.021318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
220 | LV_1062-2_0_7_line_220 |  | 202 | 208 | 0.01103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_1062-2_0_7_line_221 |  | 203 | 209 | 0.0056305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_1062-2_0_7_line_222 |  | 204 | 210 | 0.0085563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_1062-2_0_7_line_223 |  | 205 | 235 | 0.0067824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_1062-2_0_7_line_224 |  | 206 | 236 | 0.006251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_1062-2_0_7_line_225 |  | 207 | 231 | 0.0086331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
226 | LV_1062-2_0_7_line_226 |  | 209 | 245 | 0.005068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_1062-2_0_7_line_227 |  | 210 | 244 | 0.013744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_1062-2_0_7_line_228 |  | 212 | 213 | 0.0032428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_1062-2_0_7_line_229 |  | 212 | 214 | 0.011363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_1062-2_0_7_line_230 |  | 213 | 215 | 0.020352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_1062-2_0_7_line_231 |  | 214 | 216 | 0.051923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_1062-2_0_7_line_232 |  | 215 | 217 | 0.012374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_1062-2_0_7_line_233 |  | 216 | 218 | 0.024222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_1062-2_0_7_line_234 |  | 218 | 219 | 0.025656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_1062-2_0_7_line_235 |  | 219 | 222 | 0.021437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_1062-2_0_7_line_236 |  | 221 | 253 | 0.012975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_1062-2_0_7_line_237 |  | 222 | 261 | 0.021848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_1062-2_0_7_line_238 |  | 223 | 225 | 0.005673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_1062-2_0_7_line_239 |  | 224 | 226 | 0.020184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_1062-2_0_7_line_240 |  | 225 | 227 | 0.02009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_1062-2_0_7_line_241 |  | 225 | 228 | 0.013251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_1062-2_0_7_line_242 |  | 227 | 271 | 0.0042977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_1062-2_0_7_line_243 |  | 228 | 272 | 0.076322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_1062-2_0_7_line_244 |  | 229 | 230 | 0.012702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
245 | LV_1062-2_0_7_line_245 |  | 229 | 231 | 0.0055025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
246 | LV_1062-2_0_7_line_246 |  | 230 | 232 | 0.013179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
247 | LV_1062-2_0_7_line_247 |  | 231 | 233 | 0.012869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
248 | LV_1062-2_0_7_line_248 |  | 232 | 234 | 0.036366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
249 | LV_1062-2_0_7_line_249 |  | 235 | 254 | 0.018543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
250 | LV_1062-2_0_7_line_250 |  | 237 | 239 | 0.007644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_1062-2_0_7_line_251 |  | 239 | 242 | 0.0090479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
252 | LV_1062-2_0_7_line_252 |  | 240 | 241 | 0.016481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_1062-2_0_7_line_253 |  | 243 | 259 | 0.014844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_1062-2_0_7_line_254 |  | 246 | 247 | 0.0018103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
255 | LV_1062-2_0_7_line_255 |  | 247 | 248 | 0.056565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_1062-2_0_7_line_256 |  | 247 | 249 | 0.027855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_1062-2_0_7_line_257 |  | 249 | 250 | 0.066175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_1062-2_0_7_line_258 |  | 250 | 251 | 0.15238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
259 | LV_1062-2_0_7_line_259 |  | 251 | 262 | 0.043122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
260 | LV_1062-2_0_7_line_260 |  | 252 | 260 | 0.059276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
261 | LV_1062-2_0_7_line_261 |  | 253 | 255 | 0.0023407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_1062-2_0_7_line_262 |  | 255 | 256 | 0.029619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
263 | LV_1062-2_0_7_line_263 |  | 256 | 257 | 0.0073394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
264 | LV_1062-2_0_7_line_264 |  | 257 | 258 | 0.007901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
265 | LV_1062-2_0_7_line_265 |  | 260 | 263 | 0.0098508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
266 | LV_1062-2_0_7_line_266 |  | 263 | 264 | 0.024106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
267 | LV_1062-2_0_7_line_267 |  | 265 | 266 | 0.052228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
268 | LV_1062-2_0_7_line_268 |  | 266 | 267 | 0.21203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
269 | LV_1062-2_0_7_line_269 |  | 267 | 268 | 0.1042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
270 | LV_1062-2_0_7_line_270 |  | 268 | 269 | 0.026598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
271 | LV_1062-2_0_7_line_271 |  | 268 | 270 | 0.1937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
272 | LV_1062-2_0_7_line_272 |  | 270 | 277 | 0.040804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
273 | LV_1062-2_0_7_line_273 |  | 271 | 282 | 0.014649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
274 | LV_1062-2_0_7_line_274 |  | 272 | 281 | 0.049345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
275 | LV_1062-2_0_7_line_275 |  | 273 | 274 | 0.20607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
276 | LV_1062-2_0_7_line_276 |  | 274 | 275 | 0.019719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
277 | LV_1062-2_0_7_line_277 |  | 275 | 276 | 0.035266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
278 | LV_1062-2_0_7_line_278 |  | 275 | 277 | 0.20264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
279 | LV_1062-2_0_7_line_279 |  | 278 | 279 | 0.017363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
280 | LV_1062-2_0_7_line_280 |  | 279 | 280 | 0.018131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
281 | LV_1062-2_0_7_line_281 |  | 280 | 281 | 5.5012e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1062-2_0_7_trafo_131 | 0.63 MVA 20/0.4 kV | 283 | 130 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2654976.1502 | 1209999.7889 | 2654978.0537 | 1209985.3979 | 2654981.4602 | 1209966.1646
1 | 2655017.2674 | 1210009.0065 | 2654989.227 | 1210002.6555 | 2654976.1502 | 1209999.7889
2 | 2654993.1135 | 1209916.6068 | 2654985.2135 | 1209944.9731 | 2654981.4602 | 1209966.1646
3 | 2655017.2674 | 1210009.0065 | 2655225.0879 | 1210007.9757
4 | 2654917.614 | 1209907.8288 | 2654918.5992 | 1209911.44 | 2654918.8706 | 1209914.1663 | 2654941.1939 | 1209907.5233 | 2654966.0024 | 1209910.8092 | 2654993.1135 | 1209916.6068
5 | 2654841.3323 | 1210091.0234 | 2654832.785 | 1210084.6654 | 2654814.4533 | 1210076.3477 | 2654801.9096 | 1210074.1979 | 2654786.0752 | 1210073.6745 | 2654772.4526 | 1210071.4815 | 2654752.8556 | 1210069.3449 | 2654746.334 | 1210066.917 | 2654741.3922 | 1210062.936 | 2654716.1919 | 1210036.6704
6 | 2654841.3323 | 1210091.0234 | 2654845.227 | 1209963.0962
7 | 2654841.3323 | 1210091.0234 | 2654858.6717 | 1210262.398
8 | 2654716.1919 | 1210036.6704 | 2654709.8932 | 1210030.1055 | 2654698.439 | 1210016.8815 | 2654684.5111 | 1210004.8579 | 2654670.0592 | 1209992.785 | 2654658.4144 | 1209987.075 | 2654647.8615 | 1209983.9486
9 | 2654873.8498 | 1209909.4718 | 2654845.227 | 1209963.0962
10 | 2654858.6717 | 1210262.398 | 2654868.0991 | 1210266.1869 | 2654872.7197 | 1210268.6458
11 | 2654917.614 | 1209907.8288 | 2654911.8583 | 1209908.0537 | 2654906.3065 | 1209907.6616
12 | 2654898.1025 | 1209907.0822 | 2654906.3065 | 1209907.6616
13 | 2654898.1025 | 1209907.0822 | 2654896.4064 | 1209912.9923 | 2654894.35 | 1209915.108 | 2654888.6537 | 1209913.8327 | 2654881.2974 | 1209910.4075 | 2654878.8081 | 1209905.048
14 | 2654873.8498 | 1209909.4718 | 2654876.1968 | 1209911.2944 | 2654878.1145 | 1209908.566 | 2654878.8081 | 1209905.048
15 | 2654880.6694 | 1209891.9129 | 2654887.3806 | 1209901.0245 | 2654893.0178 | 1209905.4234 | 2654898.1025 | 1209907.0822
16 | 2654925.581 | 1209882.8872 | 2654908.1413 | 1209881.6503
17 | 2654925.581 | 1209882.8872 | 2654926.2737 | 1209871.877
18 | 2654880.6694 | 1209891.9129 | 2654885.7247 | 1209885.2109 | 2654896.0414 | 1209880.7921 | 2654908.1413 | 1209881.6503
19 | 2655020.6258 | 1209661.4973 | 2654926.2737 | 1209871.877
20 | 2654926.2737 | 1209871.877 | 2654926.4624 | 1209868.8759 | 2654925.7063 | 1209864.3218 | 2654922.3404 | 1209860.8888 | 2654918.446 | 1209858.7183 | 2654906.5531 | 1209856.9894
21 | 2655162.776 | 1209664.8221 | 2655160.441 | 1209601.1357
22 | 2655162.776 | 1209664.8221 | 2655155.9486 | 1209665.0147 | 2655119.6026 | 1209663.1039
23 | 2655098.5932 | 1209662.5948 | 2655116.6937 | 1209662.951 | 2655119.6026 | 1209663.1039
24 | 2653761.4136 | 1210647.2047 | 2653750.7984 | 1210642.1347 | 2653737.9855 | 1210638.7507 | 2653724.8924 | 1210638.6328 | 2653717.6645 | 1210643.0345
25 | 2653783.1859 | 1210660.0815 | 2653782.02 | 1210659.593 | 2653770.609 | 1210651.5965 | 2653761.4136 | 1210647.2047
26 | 2653701.0049 | 1210655.7614 | 2653705.3912 | 1210650.5088 | 2653717.6645 | 1210643.0345
27 | 2653717.6645 | 1210643.0345 | 2653717.8637 | 1210387.7156
28 | 2653783.1859 | 1210660.0815 | 2653966.3353 | 1210519.94
29 | 2653605.7163 | 1210732.3504 | 2653643.4286 | 1210714.2118 | 2653665.0549 | 1210702.6104 | 2653670.4647 | 1210698.501 | 2653675.0779 | 1210694.2511 | 2653678.2092 | 1210689.9989 | 2653681.6278 | 1210684.2262 | 2653691.3938 | 1210667.2706 | 2653701.0049 | 1210655.7614
30 | 2653748.7054 | 1210316.0109 | 2653759.9908 | 1210343.0842 | 2653760.2584 | 1210358.9293 | 2653764.9463 | 1210378.472 | 2653764.8814 | 1210381.451 | 2653762.133 | 1210387.0518 | 2653759.457 | 1210390.5187 | 2653755.5786 | 1210394.1526 | 2653752.4852 | 1210395.8702 | 2653750.423 | 1210396.9967 | 2653747.3411 | 1210397.4359 | 2653743.0733 | 1210397.0639 | 2653735.3253 | 1210394.0924 | 2653727.3391 | 1210388.873 | 2653721.5839 | 1210387.4092 | 2653717.8637 | 1210387.7156
31 | 2653697.5778 | 1210389.1841 | 2653698.2397 | 1210389.6227 | 2653703.8669 | 1210390.9519 | 2653707.4595 | 1210390.3505 | 2653710.4572 | 1210389.1435 | 2653715.9862 | 1210387.8702 | 2653717.8637 | 1210387.7156
32 | 2653966.3353 | 1210519.94 | 2653972.4079 | 1210518.2161 | 2653979.2905 | 1210517.1876
33 | 2653605.7163 | 1210732.3504 | 2653603.4952 | 1210734.265 | 2653600.4122 | 1210735.6937 | 2653597.8588 | 1210738.2278 | 2653596.8738 | 1210741.2763 | 2653597.3611 | 1210750.4862 | 2653597.9306 | 1210760.6863 | 2653598.9925 | 1210768.5227 | 2653600.2779 | 1210775.1715 | 2653600.9785 | 1210781.7706 | 2653600.0681 | 1210788.3664 | 2653587.4384 | 1210810.2994 | 2653577.7797 | 1210818.7399 | 2653574.6958 | 1210821.9697 | 2653572.663 | 1210824.2606
34 | 2653748.7054 | 1210316.0109 | 2653757.9134 | 1210310.4683 | 2653765.3756 | 1210307.2225 | 2653777.0297 | 1210303.4919 | 2653780.6017 | 1210302.5719
35 | 2653462.2732 | 1210341.5592 | 2653697.5778 | 1210389.1841
36 | 2653981.1133 | 1210516.9527 | 2653980.7562 | 1210516.9686 | 2653979.2905 | 1210517.1876
37 | 2653981.1133 | 1210516.9527 | 2654015.1873 | 1210515.4367
38 | 2654022.0743 | 1210515.1303 | 2654015.1873 | 1210515.4367
39 | 2654022.0743 | 1210515.1303 | 2654072.941 | 1210512.8671 | 2654155.4336 | 1210500.6855 | 2654172.2368 | 1210501.5273 | 2654185.2053 | 1210505.0032
40 | 2654190.6686 | 1210506.4674 | 2654185.2053 | 1210505.0032
41 | 2655150.7579 | 1210368.5353 | 2655155.2861 | 1210367.2825 | 2655160.0634 | 1210362.6906 | 2655158.7367 | 1210357.4919
42 | 2655136.8545 | 1210372.3819 | 2655150.7579 | 1210368.5353
43 | 2654985.0705 | 1210361.2864 | 2654996.9361 | 1210363.5415 | 2655013.7524 | 1210366.2981 | 2655036.172 | 1210368.8174 | 2655053.4192 | 1210371.8115 | 2655066.8732 | 1210374.893 | 2655088.451 | 1210377.2157 | 2655136.8545 | 1210372.3819
44 | 2655136.8545 | 1210372.3819 | 2655141.6522 | 1210377.9184 | 2655151.6094 | 1210379.4335 | 2655184.2234 | 1210376.7111 | 2655195.2709 | 1210372.7755
45 | 2654985.0705 | 1210361.2864 | 2654979.0821 | 1210352.1703 | 2654960.6529 | 1210342.1724 | 2654932.2839 | 1210324.6231 | 2654923.1791 | 1210319.6585 | 2654906.9948 | 1210316.7635 | 2654900.5559 | 1210311.9792 | 2654894.9547 | 1210302.7099
46 | 2655195.2709 | 1210372.7755 | 2655201.197 | 1210370.6644 | 2655213.3186 | 1210369.8872
47 | 2655101.2833 | 1210701.7119 | 2655071.1769 | 1210697.3918 | 2655042.0024 | 1210699.0014 | 2655013.2277 | 1210705.062 | 2655010.3764 | 1210705.576
48 | 2654976.2934 | 1210711.7197 | 2655010.3764 | 1210705.576
49 | 2654893.3543 | 1210300.0614 | 2654894.9547 | 1210302.7099
50 | 2654893.3543 | 1210300.0614 | 2654882.6223 | 1210294.7005
51 | 2654893.3543 | 1210300.0614 | 2654889.9713 | 1210284.4655 | 2654888.6257 | 1210279.5502 | 2654882.2572 | 1210273.7215 | 2654872.7197 | 1210268.6458
52 | 2654190.6686 | 1210506.4674 | 2654193.5328 | 1210507.2351 | 2654204.5631 | 1210510.2593 | 2654208.2198 | 1210510.8539
53 | 2654218.9739 | 1210512.6027 | 2654208.2198 | 1210510.8539
54 | 2654218.9739 | 1210512.6027 | 2654223.965 | 1210511.981 | 2654232.4182 | 1210505.0536 | 2654257.7413 | 1210503.3271 | 2654292.4168 | 1210508.6122 | 2654296.2564 | 1210509.3622
55 | 2654319.4835 | 1210513.9304 | 2654318.5669 | 1210513.7198 | 2654296.2564 | 1210509.3622
56 | 2654225.9389 | 1210876.7409 | 2654214.3203 | 1210876.655 | 2654188.8397 | 1210890.9154
57 | 2654225.9389 | 1210876.7409 | 2654463.7087 | 1210843.6462
58 | 2654172.3252 | 1210901.0438 | 2654183.6301 | 1210893.831 | 2654188.8397 | 1210890.9154
59 | 2654466.0479 | 1210839.3132 | 2654466.0479 | 1210839.3132 | 2654463.7087 | 1210843.6462
60 | 2654334.9937 | 1210517.4938 | 2654319.4835 | 1210513.9304
61 | 2654334.9937 | 1210517.4938 | 2654354.5577 | 1210519.0006
62 | 2654491.1374 | 1210849.8444 | 2654466.0479 | 1210839.3132
63 | 2654466.0479 | 1210839.3132 | 2654411.101 | 1210520.5333
64 | 2654703.2333 | 1210915.5276 | 2654689.37 | 1210914.9335 | 2654658.1734 | 1210907.6212 | 2654621.8698 | 1210893.6917 | 2654568.1863 | 1210877.2686 | 2654533.2516 | 1210867.3435 | 2654501.4091 | 1210854.1559 | 2654491.1374 | 1210849.8444
65 | 2654411.101 | 1210520.5333 | 2654389.2071 | 1210518.7327
66 | 2654354.5577 | 1210519.0006 | 2654364.9998 | 1210519.8049
67 | 2654611.2219 | 1209958.9486 | 2654619.0131 | 1209973.8287 | 2654628.0784 | 1209979.037 | 2654647.378 | 1209983.8053 | 2654647.8615 | 1209983.9486
68 | 2654611.2219 | 1209958.9486 | 2654600.3367 | 1209962.1727
69 | 2654163.1306 | 1210887.3135 | 2654156.4376 | 1210877.3188 | 2654152.4378 | 1210875.9261 | 2654147.1192 | 1210877.4899 | 2654142.2641 | 1210880.3525
70 | 2654020.2679 | 1210848.4455 | 2654035.6118 | 1210843.3369 | 2654049.9727 | 1210842.711 | 2654063.013 | 1210848.6104 | 2654071.2396 | 1210858.224 | 2654078.6927 | 1210869.3314 | 2654088.4055 | 1210880.9708 | 2654100.4131 | 1210890.1184 | 2654112.2079 | 1210894.2389 | 2654121.5474 | 1210892.567 | 2654142.2641 | 1210880.3525
71 | 2654172.3252 | 1210901.0438 | 2654163.1306 | 1210887.3135
72 | 2654020.2679 | 1210848.4455 | 2654006.8267 | 1210857.4515 | 2654001.246 | 1210857.889
73 | 2653980.9044 | 1210849.1454 | 2653983.3456 | 1210853.9815 | 2653988.3973 | 1210856.7177 | 2653999.5794 | 1210858.0196 | 2654001.246 | 1210857.889
74 | 2653980.9044 | 1210849.1454 | 2653966.3386 | 1210850.172
75 | 2654703.2333 | 1210915.5276 | 2654733.7484 | 1210921.7332 | 2654745.0703 | 1210926.3342
76 | 2654364.9998 | 1210519.8049 | 2654366.7539 | 1210519.94 | 2654389.2071 | 1210518.7327 | 2654389.2071 | 1210518.7327
77 | 2654563.9969 | 1209867.2865 | 2654567.4437 | 1209879.8566
78 | 2654563.9969 | 1209867.2865 | 2654562.6151 | 1209862.2474
79 | 2654567.8794 | 1209881.4456 | 2654567.4437 | 1209879.8566
80 | 2654559.8955 | 1209844.2444 | 2654560.6772 | 1209855.1803 | 2654562.6151 | 1209862.2474
81 | 2654594.6916 | 1209963.8448 | 2654592.9202 | 1209958.0807 | 2654587.9283 | 1209942.9483 | 2654585.8389 | 1209936.2141 | 2654570.2097 | 1209889.9437 | 2654567.8794 | 1209881.4456
82 | 2654559.791 | 1209839.8853 | 2654559.8955 | 1209844.2444
83 | 2654594.6916 | 1209963.8448 | 2654600.3367 | 1209962.1727
84 | 2654594.6916 | 1209963.8448 | 2654585.6277 | 1209966.0902
85 | 2654559.791 | 1209839.8853 | 2654559.8363 | 1209833.2707 | 2654558.2397 | 1209785.9391 | 2654557.3725 | 1209771.8784 | 2654555.6087 | 1209735.3517
86 | 2654559.791 | 1209839.8853 | 2654517.3509 | 1209862.5984
87 | 2654449.9449 | 1210003.2352 | 2654524.7071 | 1209981.1822 | 2654585.6277 | 1209966.0902
88 | 2654555.6087 | 1209735.3517 | 2654555.478 | 1209730.5378
89 | 2654555.6087 | 1209735.3517 | 2654586.687 | 1209734.8802
90 | 2654473.2874 | 1209884.0328 | 2654483.197 | 1209880.8769 | 2654517.3509 | 1209862.5984
91 | 2654408.8264 | 1210065.7419 | 2654410.629 | 1210059.7659 | 2654426.9526 | 1210034.1661 | 2654448.1367 | 1210008.9888 | 2654449.9449 | 1210003.2352
92 | 2654449.9449 | 1210003.2352 | 2654386.0125 | 1210027.1222 | 2654337.7177 | 1210039.7212
93 | 2654554.4714 | 1209693.4719 | 2654555.478 | 1209730.5378
94 | 2654473.2874 | 1209884.0328 | 2654454.2939 | 1209828.3886
95 | 2654473.2874 | 1209884.0328 | 2654461.2877 | 1209888.4482
96 | 2654408.8264 | 1210065.7419 | 2654407.1569 | 1210071.2966 | 2654400.9728 | 1210092.6863 | 2654394.7516 | 1210097.2991 | 2654339.3621 | 1210118.7963 | 2654329.424 | 1210120.9516 | 2654311.103 | 1210118.917
97 | 2654408.8264 | 1210065.7419 | 2654419.2151 | 1210065.8589 | 2654445.4379 | 1210063.1964 | 2654460.243 | 1210064.9213 | 2654463.3712 | 1210069.4303 | 2654463.3158 | 1210075.5001 | 2654458.5053 | 1210081.2596 | 2654428.3574 | 1210107.6226 | 2654426.7261 | 1210113.1444 | 2654428.7762 | 1210121.9029
98 | 2654311.103 | 1210118.917 | 2654281.5698 | 1210116.2246 | 2654275.7459 | 1210118.9622 | 2654267.0726 | 1210125.7874 | 2654262.5524 | 1210128.9148 | 2654252.2455 | 1210130.6889 | 2654242.2756 | 1210129.9286
99 | 2654311.103 | 1210118.917 | 2654312.0294 | 1210125.685 | 2654319.6403 | 1210132.8697 | 2654340.908 | 1210151.0073 | 2654351.4654 | 1210154.272 | 2654376.2474 | 1210163.7256 | 2654414.7272 | 1210180.4306 | 2654440.8869 | 1210184.6271 | 2654455.1718 | 1210185.0243 | 2654459.69 | 1210182.9532 | 2654471.7414 | 1210176.2362
100 | 2654242.2756 | 1210129.9286 | 2654070.097 | 1210130.6474
101 | 2654476.4502 | 1210173.6116 | 2654471.7414 | 1210176.2362
102 | 2654070.097 | 1210130.6474 | 2654062.038 | 1210132.6201 | 2654019.4013 | 1210129.9992 | 2654018.0056 | 1210128.8526 | 2654017.5882 | 1210127.1033
103 | 2655057.3674 | 1209661.4249 | 2655047.7122 | 1209660.8244 | 2655020.6258 | 1209661.4973
104 | 2655057.3674 | 1209661.4249 | 2655057.3429 | 1209659.9571 | 2655057.2816 | 1209655.8986 | 2655059.9519 | 1209650.6979 | 2655069.2245 | 1209639.221 | 2655070.5962 | 1209633.0745 | 2655070.9836 | 1209622.3506
105 | 2655057.3674 | 1209661.4249 | 2655065.6096 | 1209661.9457 | 2655078.4134 | 1209662.1976
106 | 2654655.9092 | 1209766.0428 | 2654798.5448 | 1209687.4814 | 2654801.2642 | 1209685.1939 | 2654803.5351 | 1209682.9023 | 2654805.8101 | 1209680.166 | 2654806.7396 | 1209678.2734 | 2654807.3678 | 1209676.0778 | 2654807.5658 | 1209672.7221
107 | 2654807.5658 | 1209672.7221 | 2654777.9581 | 1209673.6652
108 | 2654588.459 | 1209679.73 | 2654732.5154 | 1209675.1128 | 2654777.9581 | 1209673.6652
109 | 2654883.5577 | 1210713.9654 | 2654879.0468 | 1210712.4755
110 | 2654883.5577 | 1210713.9654 | 2654897.7106 | 1210718.6399 | 2654913.055 | 1210721.8385 | 2654929.9652 | 1210720.0708 | 2654976.2934 | 1210711.7197
111 | 2654879.0468 | 1210712.4755 | 2654876.3941 | 1210711.5993
112 | 2654876.3941 | 1210711.5993 | 2654834.3303 | 1210697.7061
113 | 2654832.5305 | 1210697.1117 | 2654834.3303 | 1210697.7061
114 | 2654788.9709 | 1210691.8805 | 2654791.48 | 1210692.5706 | 2654810.8892 | 1210690.9367 | 2654826.2105 | 1210695.0243 | 2654832.5305 | 1210697.1117
115 | 2654788.9709 | 1210691.8805 | 2654788.0751 | 1210699.2211 | 2654783.9618 | 1210725.0876 | 2654782.9501 | 1210735.9515 | 2654787.2403 | 1210745.441 | 2654799.8691 | 1210755.842
116 | 2654788.9709 | 1210691.8805 | 2654781.9667 | 1210689.9373 | 2654775.7023 | 1210685.2309
117 | 2654799.8691 | 1210755.842 | 2654745.0703 | 1210926.3342
118 | 2654782.9138 | 1210942.6155 | 2654762.3822 | 1210933.3694 | 2654745.0703 | 1210926.3342
119 | 2654782.9138 | 1210942.6155 | 2654784.0185 | 1210943.113
120 | 2654521.8021 | 1209677.7531 | 2654541.4869 | 1209677.088 | 2654541.6307 | 1209681.3141 | 2654541.7809 | 1209685.6736 | 2654544.8527 | 1209685.5571 | 2654547.4689 | 1209686.2259 | 2654549.3279 | 1209687.4102 | 2654551.6901 | 1209691.7455 | 2654551.7794 | 1209693.6141 | 2654554.4714 | 1209693.4719
121 | 2654449.2286 | 1209813.5492 | 2654454.2939 | 1209828.3886
122 | 2654461.2877 | 1209888.4482 | 2654434.3403 | 1209898.3639 | 2654413.804 | 1209909.7686
123 | 2654521.8021 | 1209677.7531 | 2654522.082 | 1209676.2325 | 2654522.506 | 1209673.9239 | 2654528.9353 | 1209667.3351
124 | 2654499.9772 | 1209687.215 | 2654500.2831 | 1209682.8485 | 2654520.9789 | 1209682.1704 | 2654521.8021 | 1209677.7531
125 | 2654521.8021 | 1209677.7531 | 2654508.2111 | 1209678.2668
126 | 2654196.6761 | 1209973.6995 | 2654181.3781 | 1209968.419
127 | 2654181.3781 | 1209968.419 | 2654035.3315 | 1210105.6623
128 | 2654035.3315 | 1210105.6623 | 2654033.9969 | 1210111.1979 | 2654032.265 | 1210114.4508 | 2654018.5087 | 1210125.3328 | 2654017.5882 | 1210127.1033
129 | 2654005.5025 | 1210129.7622 | 2654017.5882 | 1210127.1033
130 | 2653971.5933 | 1209702.5353 | 2653974.873 | 1209750.8603 | 2653974.8338 | 1209752.1097
131 | 2653971.5933 | 1209702.5353 | 2653977.492 | 1209702.4886 | 2653993.1372 | 1209702.1965 | 2653996.0643 | 1209702.1118
132 | 2653971.5933 | 1209702.5353 | 2653968.2017 | 1209683.6737
133 | 2653995.6043 | 1209687.4323 | 2653996.0643 | 1209702.1118
134 | 2653996.0643 | 1209702.1118 | 2654018.7425 | 1209701.4668
135 | 2653993.7279 | 1209706.6378 | 2653993.1372 | 1209702.1965 | 2653996.0643 | 1209702.1118
136 | 2653968.2017 | 1209683.6737 | 2653967.7868 | 1209681.3661 | 2653967.6007 | 1209680.5336
137 | 2654005.5025 | 1210129.7622 | 2653812.9886 | 1210296.4228
138 | 2653780.6017 | 1210302.5719 | 2653791.252 | 1210299.829 | 2653801.2661 | 1210297.6179 | 2653812.9886 | 1210296.4228
139 | 2654338.3263 | 1209685.0514 | 2654338.2756 | 1209678.925 | 2654346.2603 | 1209658.4856
140 | 2654338.3263 | 1209685.0514 | 2654367.0043 | 1209684.0598
141 | 2654195.5244 | 1209690.5455 | 2654338.3263 | 1209685.0514
142 | 2654346.2603 | 1209658.4856 | 2654365.6878 | 1209656.7559
143 | 2654346.2603 | 1209658.4856 | 2654355.0566 | 1209641.2349
144 | 2654195.5244 | 1209690.5455 | 2654195.0964 | 1209679.0904
145 | 2654195.5244 | 1209690.5455 | 2654178.1408 | 1209691.0552
146 | 2654528.9353 | 1209667.3351 | 2654533.7257 | 1209662.4258
147 | 2654499.9772 | 1209687.215 | 2654366.4035 | 1209692.595
148 | 2654499.9772 | 1209687.215 | 2654499.8204 | 1209689.3926 | 2654499.5449 | 1209689.5929
149 | 2654462.9937 | 1209679.9762 | 2654508.2111 | 1209678.2668
150 | 2654433.206 | 1209681.1022 | 2654417.5832 | 1209681.8563
151 | 2654433.206 | 1209681.1022 | 2654432.9739 | 1209679.0544 | 2654418.5225 | 1209642.7235
152 | 2654433.206 | 1209681.1022 | 2654444.5038 | 1209680.6751
153 | 2654403.341 | 1209601.2442 | 2654413.7511 | 1209630.7283 | 2654418.5225 | 1209642.7235
154 | 2654462.9937 | 1209679.9762 | 2654444.5038 | 1209680.6751
155 | 2654587.6843 | 1209675.5093 | 2654588.459 | 1209679.73
156 | 2654587.6843 | 1209675.5093 | 2654586.8877 | 1209671.1994 | 2654569.7835 | 1209646.5662
157 | 2654587.6843 | 1209675.5093 | 2654636.1009 | 1209673.8258
158 | 2654569.6633 | 1209646.393 | 2654569.7835 | 1209646.5662
159 | 2654499.5449 | 1209689.5929 | 2654495.2154 | 1209692.7388
160 | 2653993.7279 | 1209706.6378 | 2653995.7497 | 1209721.754 | 2653996.1067 | 1209722.4028
161 | 2653993.7279 | 1209706.6378 | 2654019.8455 | 1209705.357
162 | 2653996.1067 | 1209722.4028 | 2653998.6135 | 1209726.9589
163 | 2654058.105 | 1209703.4806 | 2654019.8455 | 1209705.357
164 | 2654018.7425 | 1209701.4668 | 2654026.6047 | 1209701.2432 | 2654047.1279 | 1209700.0319
165 | 2653951.313 | 1209628.5957 | 2653962.8411 | 1209659.2416 | 2653967.6007 | 1209680.5336
166 | 2654555.893 | 1209631.1034 | 2654567.4498 | 1209643.2051 | 2654569.6633 | 1209646.393
167 | 2654403.341 | 1209601.2442 | 2654402.5552 | 1209599.0185 | 2654399.1642 | 1209589.0926
168 | 2654538.8086 | 1209657.2167 | 2654533.7257 | 1209662.4258
169 | 2654478.3579 | 1209711.1908 | 2654480.6263 | 1209707.0835 | 2654492.0234 | 1209695.0581 | 2654495.2154 | 1209692.7388
170 | 2654555.893 | 1209631.1034 | 2654550.5939 | 1209636.2247 | 2654542.4091 | 1209653.5269 | 2654538.8086 | 1209657.2167
171 | 2654555.893 | 1209631.1034 | 2654544.3335 | 1209618.457 | 2654539.85 | 1209612.5236
172 | 2654555.893 | 1209631.1034 | 2654594.3955 | 1209601.6268 | 2654597.7537 | 1209595.9652 | 2654597.8813 | 1209582.0136 | 2654598.6323 | 1209574.7051 | 2654601.1933 | 1209570.6149 | 2654607.3845 | 1209568.063
173 | 2654466.529 | 1209749.3022 | 2654467.7499 | 1209736.2945 | 2654474.3275 | 1209718.4884 | 2654478.3579 | 1209711.1908
174 | 2654197.0062 | 1209699.418 | 2654190.87 | 1209699.6652
175 | 2654167.5511 | 1209700.9069 | 2654171.7427 | 1209700.4356 | 2654190.87 | 1209699.6652
176 | 2654365.6878 | 1209656.7559 | 2654375.4867 | 1209655.8835
177 | 2654355.0566 | 1209641.2349 | 2654357.0719 | 1209637.2825 | 2654358.4166 | 1209629.8459 | 2654358.4097 | 1209628.9666
178 | 2654145.8506 | 1209703.3469 | 2654167.5511 | 1209700.9069
179 | 2654145.7485 | 1209691.1387 | 2654145.8034 | 1209697.6542 | 2654145.8506 | 1209703.3469
180 | 2654109.3436 | 1209697.4902 | 2654122.0022 | 1209692.9467 | 2654128.3666 | 1209691.8371 | 2654139.7044 | 1209691.2951 | 2654145.7485 | 1209691.1387
181 | 2654145.7485 | 1209691.1387 | 2654151.5113 | 1209691.8358 | 2654178.1408 | 1209691.0552
182 | 2654195.0964 | 1209679.0904 | 2654194.8147 | 1209671.6056 | 2654197.1935 | 1209664.9455
183 | 2654109.3436 | 1209697.4902 | 2654080.3335 | 1209698.0722 | 2654047.1279 | 1209700.0319
184 | 2654317.4973 | 1209434.8355 | 2654332.666 | 1209437.6975 | 2654378.4133 | 1209446.2306
185 | 2654404.0414 | 1209451.0109 | 2654378.4133 | 1209446.2306
186 | 2654218.7766 | 1209309.0183 | 2654258.876 | 1209366.3841 | 2654309.0131 | 1209429.1328 | 2654311.3764 | 1209431.7113 | 2654317.4973 | 1209434.8355 | 2654317.4973 | 1209434.8355
187 | 2654404.0414 | 1209451.0109 | 2654413.8086 | 1209471.6507
188 | 2654404.0414 | 1209451.0109 | 2654419.7047 | 1209386.3041
189 | 2654211.9025 | 1209299.1843 | 2654218.7766 | 1209309.0183
190 | 2654422.9684 | 1209491.0071 | 2654413.8086 | 1209471.6507
191 | 2654435.6962 | 1209356.4766 | 2654419.7047 | 1209386.3041
192 | 2654211.9025 | 1209299.1843 | 2654207.7554 | 1209293.8101 | 2654204.3392 | 1209288.9745
193 | 2654211.9025 | 1209299.1843 | 2654201.3519 | 1209305.8702 | 2654196.1127 | 1209313.605 | 2654190.0258 | 1209325.9682
194 | 2654422.9684 | 1209491.0071 | 2654422.9684 | 1209491.0071 | 2654425.1147 | 1209497.8951
195 | 2654435.6962 | 1209356.4766 | 2654440.2212 | 1209347.6695
196 | 2654435.6962 | 1209356.4766 | 2654485.6876 | 1209376.2276
197 | 2654203.0226 | 1209287.1109 | 2654204.3392 | 1209288.9745
198 | 2654425.7895 | 1209500.0604 | 2654425.1147 | 1209497.8951
199 | 2654440.2212 | 1209347.6695 | 2654448.9604 | 1209330.66 | 2654451.7058 | 1209326.3492 | 2654454.6451 | 1209322.4514 | 2654473.094 | 1209302.0518
200 | 2654505.5933 | 1209384.0921 | 2654485.6876 | 1209376.2276
201 | 2654425.7895 | 1209500.0604 | 2654423.3098 | 1209510.2439 | 2654422.8472 | 1209518.6727
202 | 2654482.9937 | 1209292.9592 | 2654482.9937 | 1209292.9592 | 2654480.2257 | 1209294.7461 | 2654475.5469 | 1209299.3395 | 2654473.094 | 1209302.0518
203 | 2654476.9938 | 1209589.2627 | 2654475.7979 | 1209586.1856
204 | 2654456.239 | 1209558.4172 | 2654459.2985 | 1209564.6599 | 2654473.8482 | 1209581.1691 | 2654475.7979 | 1209586.1856
205 | 2654477.055 | 1209589.4201 | 2654476.9938 | 1209589.2627
206 | 2654449.3538 | 1209555.775 | 2654456.239 | 1209558.4172
207 | 2654456.239 | 1209558.4172 | 2654461.3155 | 1209558.7282
208 | 2654477.1137 | 1209589.571 | 2654477.055 | 1209589.4201
209 | 2654449.3538 | 1209555.775 | 2654443.8782 | 1209556.0919 | 2654435.6626 | 1209558.2105
210 | 2654449.3538 | 1209555.775 | 2654446.9532 | 1209544.8273
211 | 2654488.1197 | 1209559.0417 | 2654462.6355 | 1209558.8091 | 2654461.3155 | 1209558.7282
212 | 2654477.1137 | 1209589.571 | 2654478.9893 | 1209594.3968
213 | 2654420.9756 | 1209561.9978 | 2654435.6626 | 1209558.2105
214 | 2654441.8494 | 1209529.1824 | 2654445.3037 | 1209537.3049 | 2654446.9532 | 1209544.8273
215 | 2654488.1197 | 1209559.0417 | 2654498.9275 | 1209559.1404 | 2654503.7799 | 1209560.4914
216 | 2654488.1197 | 1209559.0417 | 2654487.361 | 1209540.0873
217 | 2654420.9756 | 1209561.9978 | 2654420.1573 | 1209557.5432 | 2654421.0673 | 1209551.1032 | 2654421.4594 | 1209543.9598
218 | 2654420.9756 | 1209561.9978 | 2654422.0522 | 1209565.6319 | 2654425.8457 | 1209580.7195
219 | 2654420.9756 | 1209561.9978 | 2654402.4899 | 1209572.6147
220 | 2654437.5328 | 1209519.0325 | 2654441.8494 | 1209529.1824
221 | 2654509.0316 | 1209562.3262 | 2654508.3819 | 1209561.7727 | 2654503.7799 | 1209560.4914
222 | 2654487.7987 | 1209531.6634 | 2654487.0985 | 1209533.5284 | 2654487.361 | 1209540.0873
223 | 2654421.8311 | 1209537.1876 | 2654421.4594 | 1209543.9598
224 | 2654427.37 | 1209586.7819 | 2654425.8457 | 1209580.7195
225 | 2654395.0037 | 1209576.9144 | 2654402.4899 | 1209572.6147
226 | 2654509.0316 | 1209562.3262 | 2654512.8897 | 1209565.6125
227 | 2654496.2889 | 1209520.9715 | 2654488.3839 | 1209530.1047 | 2654487.7987 | 1209531.6634
228 | 2654635.9282 | 1209584.3421 | 2654633.8523 | 1209581.8508
229 | 2654643.3187 | 1209592.9692 | 2654643.3187 | 1209592.9692 | 2654641.3692 | 1209590.8723 | 2654635.9282 | 1209584.3421
230 | 2654619.5154 | 1209567.9391 | 2654623.904 | 1209569.9112 | 2654633.8523 | 1209581.8508
231 | 2654643.3187 | 1209592.9692 | 2654646.5174 | 1209593.1096 | 2654650.2078 | 1209591.02 | 2654653.4336 | 1209588.2145 | 2654665.0799 | 1209569.7879 | 2654672.8742 | 1209559.4754 | 2654677.4249 | 1209556.4219
232 | 2654619.5154 | 1209567.9391 | 2654618.1963 | 1209567.3463 | 2654608.7926 | 1209567.4826 | 2654607.3845 | 1209568.063
233 | 2654698.1404 | 1209543.9965 | 2654695.2623 | 1209545.0497 | 2654682.7632 | 1209552.8398 | 2654677.4249 | 1209556.4219
234 | 2654722.9666 | 1209538.1141 | 2654708.8072 | 1209540.093 | 2654698.1404 | 1209543.9965
235 | 2654744.2973 | 1209537.1881 | 2654739.6225 | 1209536.7179 | 2654730.9776 | 1209536.9944 | 2654722.9666 | 1209538.1141
236 | 2654539.85 | 1209612.5236 | 2654529.4231 | 1209620.2456
237 | 2654766.0019 | 1209539.6776 | 2654752.5173 | 1209538.0147 | 2654744.2973 | 1209537.1881
238 | 2655071.1884 | 1209616.6813 | 2655070.9836 | 1209622.3506
239 | 2655098.5932 | 1209662.5948 | 2655078.4134 | 1209662.1976
240 | 2655071.1884 | 1209616.6813 | 2655091.263 | 1209615.9054
241 | 2655071.1884 | 1209616.6813 | 2655070.7082 | 1209603.4387
242 | 2655095.5575 | 1209615.7394 | 2655091.263 | 1209615.9054
243 | 2655074.0156 | 1209527.4197 | 2655069.3586 | 1209566.2233 | 2655070.7082 | 1209603.4387
244 | 2654379.8307 | 1209586.9728 | 2654390.4173 | 1209579.9547
245 | 2654395.0037 | 1209576.9144 | 2654390.4173 | 1209579.9547
246 | 2654370.5551 | 1209596.2828 | 2654378.4933 | 1209587.8594 | 2654379.8307 | 1209586.9728
247 | 2654395.0037 | 1209576.9144 | 2654399.1642 | 1209589.0926
248 | 2654370.5551 | 1209596.2828 | 2654365.4148 | 1209601.7374 | 2654359.8624 | 1209611.3147 | 2654358.332 | 1209619.1166 | 2654358.4097 | 1209628.9666
249 | 2654422.8472 | 1209518.6727 | 2654421.8311 | 1209537.1876
250 | 2654203.8927 | 1209661.2642 | 2654197.1935 | 1209664.9455
251 | 2654211.8222 | 1209656.9069 | 2654203.8927 | 1209661.2642
252 | 2654058.105 | 1209703.4806 | 2654074.5666 | 1209702.6733
253 | 2654375.4867 | 1209655.8835 | 2654375.4867 | 1209655.8835 | 2654378.5817 | 1209656.5676 | 2654379.9834 | 1209668.1573
254 | 2653950.6756 | 1209626.9013 | 2653951.313 | 1209628.5957
255 | 2653950.6756 | 1209626.9013 | 2653980.7838 | 1209604.1155 | 2653997.4202 | 1209595.1162
256 | 2653950.6756 | 1209626.9013 | 2653941.1892 | 1209605.0916 | 2653938.9755 | 1209601.6749
257 | 2653899.4271 | 1209548.97 | 2653901.3988 | 1209553.6795 | 2653907.1684 | 1209561.2139 | 2653929.2774 | 1209586.7064 | 2653938.9755 | 1209601.6749
258 | 2653899.4271 | 1209548.97 | 2653902.477 | 1209529.4082 | 2653906.0815 | 1209514.9322 | 2653919.6804 | 1209480.3789 | 2653954.8258 | 1209407.9257
259 | 2653970.0467 | 1209367.6227 | 2653958.3615 | 1209400.6366 | 2653954.8258 | 1209407.9257
260 | 2654028.2568 | 1209765.2699 | 2654010.3873 | 1209765.6013 | 2654007.727 | 1209763.0757 | 2654004.8904 | 1209740.57 | 2654003.1453 | 1209735.1955 | 2653998.6135 | 1209726.9589
261 | 2654527.542 | 1209621.6387 | 2654529.4231 | 1209620.2456
262 | 2654503.7398 | 1209639.2664 | 2654527.542 | 1209621.6387
263 | 2654503.7398 | 1209639.2664 | 2654497.8418 | 1209643.6344
264 | 2654491.4924 | 1209648.3367 | 2654497.8418 | 1209643.6344
265 | 2654028.2568 | 1209765.2699 | 2654038.1059 | 1209765.0873
266 | 2654051.1405 | 1209752.4067 | 2654051.2388 | 1209761.6909 | 2654049.0588 | 1209764.8842 | 2654038.1059 | 1209765.0873
267 | 2653412.8765 | 1210336.1421 | 2653417.9607 | 1210340.4123 | 2653423.6824 | 1210338.8403 | 2653441.646 | 1210335.7549 | 2653462.2732 | 1210341.5592
268 | 2653381.2314 | 1210545.7946 | 2653412.8765 | 1210336.1421
269 | 2653406.1062 | 1210646.9833 | 2653381.2314 | 1210545.7946
270 | 2653413.9869 | 1210667.9602 | 2653415.6807 | 1210661.2714 | 2653415.552 | 1210652.7318 | 2653408.2567 | 1210647.5968 | 2653406.1062 | 1210646.9833
271 | 2653406.1062 | 1210646.9833 | 2653223.9933 | 1210712.9801
272 | 2653223.9933 | 1210712.9801 | 2653222.6115 | 1210711.6657 | 2653217.8311 | 1210709.1438 | 2653210.6034 | 1210708.3567 | 2653203.784 | 1210708.6405 | 2653188.8046 | 1210712.1313 | 2653185.2033 | 1210713.9078
273 | 2655110.1953 | 1209615.1737 | 2655095.5575 | 1209615.7394
274 | 2655074.0156 | 1209527.4197 | 2655076.2919 | 1209508.4529 | 2655082.5561 | 1209499.3052 | 2655090.2605 | 1209493.8731 | 2655099.832 | 1209492.1332
275 | 2653027.7188 | 1210961.7696 | 2653028.9708 | 1210961.8132 | 2653056.4564 | 1210965.3151 | 2653100.0309 | 1210970.3722 | 2653130.3664 | 1210974.7003 | 2653139.946 | 1210974.1853 | 2653149.3575 | 1210971.2117 | 2653157.9475 | 1210966.6188 | 2653167.8092 | 1210959.18 | 2653173.1702 | 1210951.1118 | 2653184.1371 | 1210933.9216 | 2653189.8882 | 1210927.28 | 2653197.4862 | 1210921.4553 | 2653205.8868 | 1210917.6613 | 2653209.121 | 1210916.6377
276 | 2653228.2367 | 1210911.9258 | 2653217.1275 | 1210914.1038 | 2653209.121 | 1210916.6377
277 | 2653228.2367 | 1210911.9258 | 2653231.0129 | 1210911.3815 | 2653240.1881 | 1210911.0632 | 2653247.0909 | 1210914.171 | 2653252.7521 | 1210919.3024 | 2653255.5269 | 1210926.8538
278 | 2653228.2367 | 1210911.9258 | 2653185.2033 | 1210713.9078
279 | 2655122.5205 | 1209469.9344 | 2655117.8965 | 1209473.4938 | 2655116.2264 | 1209478.1923 | 2655114.7847 | 1209484.5731
280 | 2655099.8861 | 1209492.1233 | 2655110.2242 | 1209490.2441 | 2655114.261 | 1209486.8905 | 2655114.7847 | 1209484.5731
281 | 2655099.832 | 1209492.1332 | 2655099.8861 | 1209492.1233

## bus_geodata
| x | y | coords
0 | 2654976.1502 | 1209999.7889
1 | 2654981.4602 | 1209966.1646
2 | 2655017.2674 | 1210009.0065
3 | 2654993.1135 | 1209916.6068
4 | 2655225.0879 | 1210007.9757
5 | 2654841.3323 | 1210091.0234
6 | 2654716.1919 | 1210036.6704
7 | 2654845.227 | 1209963.0962
8 | 2654858.6717 | 1210262.398
9 | 2654917.614 | 1209907.8288
10 | 2654906.3065 | 1209907.6616
11 | 2654878.8081 | 1209905.048
12 | 2654898.1025 | 1209907.0822
13 | 2654873.8498 | 1209909.4718
14 | 2654925.581 | 1209882.8872
15 | 2654908.1413 | 1209881.6503
16 | 2654926.2737 | 1209871.877
17 | 2654880.6694 | 1209891.9129
18 | 2654906.5531 | 1209856.9894
19 | 2655162.776 | 1209664.8221
20 | 2655160.441 | 1209601.1357
21 | 2655119.6026 | 1209663.1039
22 | 2653761.4136 | 1210647.2047
23 | 2653717.6645 | 1210643.0345
24 | 2653783.1859 | 1210660.0815
25 | 2653701.0049 | 1210655.7614
26 | 2653717.8637 | 1210387.7156
27 | 2653966.3353 | 1210519.94
28 | 2653605.7163 | 1210732.3504
29 | 2653748.7054 | 1210316.0109
30 | 2653697.5778 | 1210389.1841
31 | 2653979.2905 | 1210517.1876
32 | 2653981.1133 | 1210516.9527
33 | 2654022.0743 | 1210515.1303
34 | 2654015.1873 | 1210515.4367
35 | 2654185.2053 | 1210505.0032
36 | 2653572.663 | 1210824.2606
37 | 2655158.7367 | 1210357.4919
38 | 2655150.7579 | 1210368.5353
39 | 2655136.8545 | 1210372.3819
40 | 2654985.0705 | 1210361.2864
41 | 2655195.2709 | 1210372.7755
42 | 2655101.2833 | 1210701.7119
43 | 2655010.3764 | 1210705.576
44 | 2654894.9547 | 1210302.7099
45 | 2655213.3186 | 1210369.8872
46 | 2654893.3543 | 1210300.0614
47 | 2654208.2198 | 1210510.8539
48 | 2654190.6686 | 1210506.4674
49 | 2654218.9739 | 1210512.6027
50 | 2654296.2564 | 1210509.3622
51 | 2654225.9389 | 1210876.7409
52 | 2654188.8397 | 1210890.9154
53 | 2654463.7087 | 1210843.6462
54 | 2654319.4835 | 1210513.9304
55 | 2654334.9937 | 1210517.4938
56 | 2654466.0479 | 1210839.3132
57 | 2654491.1374 | 1210849.8444
58 | 2654411.101 | 1210520.5333
59 | 2654354.5577 | 1210519.0006
60 | 2654872.7197 | 1210268.6458
61 | 2654882.6223 | 1210294.7005
62 | 2654647.8615 | 1209983.9486
63 | 2654611.2219 | 1209958.9486
64 | 2654142.2641 | 1210880.3525
65 | 2654163.1306 | 1210887.3135
66 | 2654020.2679 | 1210848.4455
67 | 2654172.3252 | 1210901.0438
68 | 2654001.246 | 1210857.889
69 | 2653980.9044 | 1210849.1454
70 | 2653966.3386 | 1210850.172
71 | 2654703.2333 | 1210915.5276
72 | 2654364.9998 | 1210519.8049
73 | 2654389.2071 | 1210518.7327
74 | 2654563.9969 | 1209867.2865
75 | 2654567.4437 | 1209879.8566
76 | 2654562.6151 | 1209862.2474
77 | 2654567.8794 | 1209881.4456
78 | 2654559.8955 | 1209844.2444
79 | 2654594.6916 | 1209963.8448
80 | 2654559.791 | 1209839.8853
81 | 2654600.3367 | 1209962.1727
82 | 2654585.6277 | 1209966.0902
83 | 2654555.6087 | 1209735.3517
84 | 2654517.3509 | 1209862.5984
85 | 2654449.9449 | 1210003.2352
86 | 2654555.478 | 1209730.5378
87 | 2654586.687 | 1209734.8802
88 | 2654473.2874 | 1209884.0328
89 | 2654408.8264 | 1210065.7419
90 | 2654337.7177 | 1210039.7212
91 | 2654311.103 | 1210118.917
92 | 2654428.7762 | 1210121.9029
93 | 2654242.2756 | 1210129.9286
94 | 2654471.7414 | 1210176.2362
95 | 2654070.097 | 1210130.6474
96 | 2654476.4502 | 1210173.6116
97 | 2655020.6258 | 1209661.4973
98 | 2655057.3674 | 1209661.4249
99 | 2654807.5658 | 1209672.7221
100 | 2654655.9092 | 1209766.0428
101 | 2654777.9581 | 1209673.6652
102 | 2654883.5577 | 1210713.9654
103 | 2654879.0468 | 1210712.4755
104 | 2654976.2934 | 1210711.7197
105 | 2654876.3941 | 1210711.5993
106 | 2654834.3303 | 1210697.7061
107 | 2654832.5305 | 1210697.1117
108 | 2654788.9709 | 1210691.8805
109 | 2654799.8691 | 1210755.842
110 | 2654775.7023 | 1210685.2309
111 | 2654745.0703 | 1210926.3342
112 | 2654782.9138 | 1210942.6155
113 | 2654784.0185 | 1210943.113
114 | 2654554.4714 | 1209693.4719
115 | 2654454.2939 | 1209828.3886
116 | 2654461.2877 | 1209888.4482
117 | 2654449.2286 | 1209813.5492
118 | 2654413.804 | 1209909.7686
119 | 2654521.8021 | 1209677.7531
120 | 2654196.6761 | 1209973.6995
121 | 2654181.3781 | 1209968.419
122 | 2654035.3315 | 1210105.6623
123 | 2654017.5882 | 1210127.1033
124 | 2653974.8338 | 1209752.1097
125 | 2653971.5933 | 1209702.5353
126 | 2653996.0643 | 1209702.1118
127 | 2653968.2017 | 1209683.6737
128 | 2654005.5025 | 1210129.7622
129 | 2653812.9886 | 1210296.4228
130 | 2654338.3263 | 1209685.0514
131 | 2654346.2603 | 1209658.4856
132 | 2654367.0043 | 1209684.0598
133 | 2654195.5244 | 1209690.5455
134 | 2654528.9353 | 1209667.3351
135 | 2654499.9772 | 1209687.215
136 | 2654508.2111 | 1209678.2668
137 | 2654433.206 | 1209681.1022
138 | 2654417.5832 | 1209681.8563
139 | 2654418.5225 | 1209642.7235
140 | 2654444.5038 | 1209680.6751
141 | 2654588.459 | 1209679.73
142 | 2654587.6843 | 1209675.5093
143 | 2654569.7835 | 1209646.5662
144 | 2654636.1009 | 1209673.8258
145 | 2654366.4035 | 1209692.595
146 | 2654499.5449 | 1209689.5929
147 | 2653993.7279 | 1209706.6378
148 | 2653996.1067 | 1209722.4028
149 | 2654019.8455 | 1209705.357
150 | 2653995.6043 | 1209687.4323
151 | 2654018.7425 | 1209701.4668
152 | 2653967.6007 | 1209680.5336
153 | 2653780.6017 | 1210302.5719
154 | 2654569.6633 | 1209646.393
155 | 2654403.341 | 1209601.2442
156 | 2654462.9937 | 1209679.9762
157 | 2654533.7257 | 1209662.4258
158 | 2654495.2154 | 1209692.7388
159 | 2654555.893 | 1209631.1034
160 | 2654478.3579 | 1209711.1908
161 | 2654466.529 | 1209749.3022
162 | 2654197.0062 | 1209699.418
163 | 2654190.87 | 1209699.6652
164 | 2654365.6878 | 1209656.7559
165 | 2654355.0566 | 1209641.2349
166 | 2654145.8506 | 1209703.3469
167 | 2654167.5511 | 1209700.9069
168 | 2654145.7485 | 1209691.1387
169 | 2654195.0964 | 1209679.0904
170 | 2654178.1408 | 1209691.0552
171 | 2654109.3436 | 1209697.4902
172 | 2654378.4133 | 1209446.2306
173 | 2654317.4973 | 1209434.8355
174 | 2654404.0414 | 1209451.0109
175 | 2654218.7766 | 1209309.0183
176 | 2654413.8086 | 1209471.6507
177 | 2654419.7047 | 1209386.3041
178 | 2654211.9025 | 1209299.1843
179 | 2654422.9684 | 1209491.0071
180 | 2654435.6962 | 1209356.4766
181 | 2654204.3392 | 1209288.9745
182 | 2654190.0258 | 1209325.9682
183 | 2654425.1147 | 1209497.8951
184 | 2654440.2212 | 1209347.6695
185 | 2654485.6876 | 1209376.2276
186 | 2654203.0226 | 1209287.1109
187 | 2654425.7895 | 1209500.0604
188 | 2654473.094 | 1209302.0518
189 | 2654505.5933 | 1209384.0921
190 | 2654475.7979 | 1209586.1856
191 | 2654476.9938 | 1209589.2627
192 | 2654456.239 | 1209558.4172
193 | 2654477.055 | 1209589.4201
194 | 2654449.3538 | 1209555.775
195 | 2654461.3155 | 1209558.7282
196 | 2654477.1137 | 1209589.571
197 | 2654435.6626 | 1209558.2105
198 | 2654446.9532 | 1209544.8273
199 | 2654488.1197 | 1209559.0417
200 | 2654478.9893 | 1209594.3968
201 | 2654420.9756 | 1209561.9978
202 | 2654441.8494 | 1209529.1824
203 | 2654503.7799 | 1209560.4914
204 | 2654487.361 | 1209540.0873
205 | 2654421.4594 | 1209543.9598
206 | 2654425.8457 | 1209580.7195
207 | 2654402.4899 | 1209572.6147
208 | 2654437.5328 | 1209519.0325
209 | 2654509.0316 | 1209562.3262
210 | 2654487.7987 | 1209531.6634
211 | 2654482.9937 | 1209292.9592
212 | 2654635.9282 | 1209584.3421
213 | 2654633.8523 | 1209581.8508
214 | 2654643.3187 | 1209592.9692
215 | 2654619.5154 | 1209567.9391
216 | 2654677.4249 | 1209556.4219
217 | 2654607.3845 | 1209568.063
218 | 2654698.1404 | 1209543.9965
219 | 2654722.9666 | 1209538.1141
220 | 2654538.8086 | 1209657.2167
221 | 2654539.85 | 1209612.5236
222 | 2654744.2973 | 1209537.1881
223 | 2655070.9836 | 1209622.3506
224 | 2655078.4134 | 1209662.1976
225 | 2655071.1884 | 1209616.6813
226 | 2655098.5932 | 1209662.5948
227 | 2655091.263 | 1209615.9054
228 | 2655070.7082 | 1209603.4387
229 | 2654390.4173 | 1209579.9547
230 | 2654379.8307 | 1209586.9728
231 | 2654395.0037 | 1209576.9144
232 | 2654370.5551 | 1209596.2828
233 | 2654399.1642 | 1209589.0926
234 | 2654358.4097 | 1209628.9666
235 | 2654421.8311 | 1209537.1876
236 | 2654427.37 | 1209586.7819
237 | 2654197.1935 | 1209664.9455
238 | 2654047.1279 | 1209700.0319
239 | 2654203.8927 | 1209661.2642
240 | 2654074.5666 | 1209702.6733
241 | 2654058.105 | 1209703.4806
242 | 2654211.8222 | 1209656.9069
243 | 2654375.4867 | 1209655.8835
244 | 2654496.2889 | 1209520.9715
245 | 2654512.8897 | 1209565.6125
246 | 2653951.313 | 1209628.5957
247 | 2653950.6756 | 1209626.9013
248 | 2653997.4202 | 1209595.1162
249 | 2653938.9755 | 1209601.6749
250 | 2653899.4271 | 1209548.97
251 | 2653954.8258 | 1209407.9257
252 | 2653998.6135 | 1209726.9589
253 | 2654529.4231 | 1209620.2456
254 | 2654422.8472 | 1209518.6727
255 | 2654527.542 | 1209621.6387
256 | 2654503.7398 | 1209639.2664
257 | 2654497.8418 | 1209643.6344
258 | 2654491.4924 | 1209648.3367
259 | 2654379.9834 | 1209668.1573
260 | 2654028.2568 | 1209765.2699
261 | 2654766.0019 | 1209539.6776
262 | 2653970.0467 | 1209367.6227
263 | 2654038.1059 | 1209765.0873
264 | 2654051.1405 | 1209752.4067
265 | 2653462.2732 | 1210341.5592
266 | 2653412.8765 | 1210336.1421
267 | 2653381.2314 | 1210545.7946
268 | 2653406.1062 | 1210646.9833
269 | 2653413.9869 | 1210667.9602
270 | 2653223.9933 | 1210712.9801
271 | 2655095.5575 | 1209615.7394
272 | 2655074.0156 | 1209527.4197
273 | 2653027.7188 | 1210961.7696
274 | 2653209.121 | 1210916.6377
275 | 2653228.2367 | 1210911.9258
276 | 2653255.5269 | 1210926.8538
277 | 2653185.2033 | 1210713.9078
278 | 2655122.5205 | 1209469.9344
279 | 2655114.7847 | 1209484.5731
280 | 2655099.8861 | 1209492.1233
281 | 2655099.832 | 1209492.1332
282 | 2655110.1953 | 1209615.1737
283 | 2654338.3637 | 1209689.2876

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97676 | -0.45023 | 0.00029899 | 7.4934e-05
1 | 0.97683 | -0.4488 | 0.0020304 | 0.00050887
2 | 0.97668 | -0.45176 | 0.001812 | 0.00045413
3 | 0.97703 | -0.44478 | 0 | 0
4 | 0.97665 | -0.45242 | 0.00017035 | 4.2693e-05
5 | 0.97878 | -0.41057 | 0.00035453 | 8.8853e-05
6 | 0.97965 | -0.39353 | 0.00024601 | 6.1657e-05
7 | 0.9781 | -0.42378 | 0.00058859 | 0.00014751
8 | 0.97826 | -0.42079 | 0 | 0
9 | 0.97736 | -0.43827 | 0 | 0
10 | 0.97741 | -0.43738 | 0.00012676 | 3.177e-05
11 | 0.97774 | -0.43089 | 0 | 0
12 | 0.97744 | -0.43671 | 0 | 0
13 | 0.97779 | -0.42989 | 0 | 0
14 | 0.97625 | -0.46006 | 0 | 0
15 | 0.97653 | -0.45457 | 0.0004308 | 0.00010797
16 | 0.97608 | -0.46353 | 0.00029274 | 7.3366e-05
17 | 0.97705 | -0.44435 | 0 | 0
18 | 0.97604 | -0.46428 | 0.0014218 | 0.00035635
19 | 0.97215 | -0.54094 | 0 | 0
20 | 0.97211 | -0.54169 | 0.00063552 | 0.00015928
21 | 0.97218 | -0.54043 | 0.00098188 | 0.00024608
22 | 0.97241 | -0.53846 | 0.0019957 | 0.00050016
23 | 0.9725 | -0.53665 | 0.0013033 | 0.00032664
24 | 0.97238 | -0.53921 | 0 | 0
25 | 0.97249 | -0.53697 | 0.00030018 | 7.5233e-05
26 | 0.97312 | -0.52418 | 0.00091557 | 0.00022946
27 | 0.97204 | -0.54604 | 0.00015128 | 3.7915e-05
28 | 0.97242 | -0.53821 | 0 | 0
29 | 0.97375 | -0.5114 | 0 | 0
30 | 0.97306 | -0.52522 | 0.00047129 | 0.00011812
31 | 0.97203 | -0.54643 | 5.1287e-05 | 1.2854e-05
32 | 0.97202 | -0.54648 | 4.2747e-05 | 1.0714e-05
33 | 0.97197 | -0.54764 | 9.7542e-05 | 2.4446e-05
34 | 0.97198 | -0.54745 | 0.00019031 | 4.7697e-05
35 | 0.97175 | -0.55209 | 0.00019048 | 4.7739e-05
36 | 0.97237 | -0.53924 | 0.00052624 | 0.00013189
37 | 0.97767 | -0.43241 | 0.0006491 | 0.00016268
38 | 0.97768 | -0.43221 | 0.00021695 | 5.4374e-05
39 | 0.97769 | -0.43199 | 0 | 0
40 | 0.97794 | -0.42708 | 0 | 0
41 | 0.97764 | -0.43299 | 0.00025356 | 6.3549e-05
42 | 0.97066 | -0.57413 | 0.00010601 | 2.6567e-05
43 | 0.97067 | -0.57395 | 0.00015341 | 3.8449e-05
44 | 0.97812 | -0.42351 | 0.00036238 | 9.0821e-05
45 | 0.97763 | -0.4332 | 0.00063556 | 0.00015929
46 | 0.97813 | -0.42339 | 0 | 0
47 | 0.97172 | -0.55269 | 0.00035124 | 8.8029e-05
48 | 0.97174 | -0.55224 | 0.00023005 | 5.7657e-05
49 | 0.97171 | -0.55295 | 0 | 0
50 | 0.97162 | -0.55482 | 0.00059667 | 0.00014954
51 | 0.97103 | -0.56671 | 6.5895e-05 | 1.6515e-05
52 | 0.971 | -0.56737 | 0.00014299 | 3.5836e-05
53 | 0.97124 | -0.56255 | 0.00015776 | 3.9538e-05
54 | 0.97159 | -0.55531 | 0.0004169 | 0.00010448
55 | 0.97158 | -0.55561 | 0 | 0
56 | 0.97124 | -0.56245 | 4.4139e-05 | 1.1062e-05
57 | 0.97123 | -0.56277 | 8.2495e-05 | 2.0675e-05
58 | 0.97151 | -0.55697 | 0 | 0
59 | 0.97156 | -0.55598 | 6.2132e-05 | 1.5572e-05
60 | 0.97821 | -0.42171 | 0.00097255 | 0.00024375
61 | 0.97813 | -0.42342 | 0.00015169 | 3.8017e-05
62 | 0.98019 | -0.38294 | 0.0025977 | 0.00065104
63 | 0.98051 | -0.37664 | 0 | 0
64 | 0.97097 | -0.56801 | 0.00011992 | 3.0054e-05
65 | 0.97098 | -0.56785 | 0.00040402 | 0.00010126
66 | 0.97094 | -0.56855 | 0 | 0
67 | 0.97099 | -0.56763 | 0 | 0
68 | 0.97094 | -0.56862 | 0.00012284 | 3.0787e-05
69 | 0.97094 | -0.56865 | 0 | 0
70 | 0.97094 | -0.56867 | 6.8969e-05 | 1.7285e-05
71 | 0.97111 | -0.56524 | 0 | 0
72 | 0.97155 | -0.55617 | 0.00016483 | 4.1311e-05
73 | 0.97153 | -0.5566 | 0.00011925 | 2.9888e-05
74 | 0.98226 | -0.34221 | 0.00018659 | 4.6763e-05
75 | 0.98205 | -0.34637 | 0.0002412 | 6.0449e-05
76 | 0.98234 | -0.34054 | 0.0002683 | 6.7241e-05
77 | 0.98202 | -0.34689 | 0.00035499 | 8.8968e-05
78 | 0.98264 | -0.33467 | 0 | 0
79 | 0.98062 | -0.37435 | 0 | 0
80 | 0.98272 | -0.33327 | 0 | 0
81 | 0.98058 | -0.37514 | 0.00042179 | 0.00010571
82 | 0.98054 | -0.37606 | 0.00037347 | 9.36e-05
83 | 0.98473 | -0.29388 | 0.0013163 | 0.0003299
84 | 0.98216 | -0.34413 | 0.00038631 | 9.6818e-05
85 | 0.97925 | -0.40162 | 0 | 0
86 | 0.98483 | -0.29189 | 0.00073007 | 0.00018297
87 | 0.98452 | -0.29788 | 0.0071521 | 0.0017925
88 | 0.98161 | -0.35489 | 0 | 0
89 | 0.97858 | -0.4149 | 0 | 0
90 | 0.9791 | -0.40448 | 0.001329 | 0.00033307
91 | 0.9776 | -0.43433 | 0 | 0
92 | 0.97809 | -0.42439 | 0.0041485 | 0.0010397
93 | 0.97705 | -0.44531 | 0.0035145 | 0.00088081
94 | 0.97733 | -0.43966 | 0.0010791 | 0.00027044
95 | 0.97589 | -0.46843 | 0.00037203 | 9.324e-05
96 | 0.97733 | -0.43971 | 0.00050385 | 0.00012628
97 | 0.97276 | -0.52897 | 0.0036133 | 0.00090559
98 | 0.97235 | -0.53699 | 0 | 0
99 | 0.98385 | -0.31111 | 0 | 0
100 | 0.98345 | -0.31901 | 0.0024261 | 0.00060805
101 | 0.98392 | -0.30981 | 0.00089681 | 0.00022476
102 | 0.97074 | -0.57259 | 5.7341e-05 | 1.4371e-05
103 | 0.97074 | -0.57253 | 4.6747e-05 | 1.1716e-05
104 | 0.97068 | -0.57378 | 0.00041294 | 0.00010349
105 | 0.97074 | -0.57249 | 7.095e-05 | 1.7782e-05
106 | 0.97078 | -0.57179 | 0.00073462 | 0.00018411
107 | 0.97078 | -0.57173 | 0.0001385 | 3.4712e-05
108 | 0.97085 | -0.57031 | 0 | 0
109 | 0.97097 | -0.56792 | 0.00017261 | 4.326e-05
110 | 0.97085 | -0.57033 | 7.8531e-05 | 1.9682e-05
111 | 0.97108 | -0.56572 | 0.00014945 | 3.7457e-05
112 | 0.97107 | -0.5659 | 0.00015416 | 3.8637e-05
113 | 0.97107 | -0.5659 | 7.8344e-05 | 1.9635e-05
114 | 0.98562 | -0.27644 | 0 | 0
115 | 0.98112 | -0.36444 | 0.0066542 | 0.0016677
116 | 0.98157 | -0.35562 | 0.0013702 | 0.00034342
117 | 0.98109 | -0.3651 | 0.0023148 | 0.00058015
118 | 0.98149 | -0.35729 | 0.0017665 | 0.00044274
119 | 0.9866 | -0.25741 | 0 | 0
120 | 0.97443 | -0.49746 | 0.0040165 | 0.0010066
121 | 0.97449 | -0.49626 | 0.00088025 | 0.00022061
122 | 0.9754 | -0.47825 | 0 | 0
123 | 0.97553 | -0.47566 | 0 | 0
124 | 0.97758 | -0.43205 | 0.0062863 | 0.0015755
125 | 0.97787 | -0.42635 | 0 | 0
126 | 0.97843 | -0.41537 | 0 | 0
127 | 0.97754 | -0.43276 | 0.0013786 | 0.00034552
128 | 0.97546 | -0.47702 | 0.00065133 | 0.00016324
129 | 0.9741 | -0.50437 | 0.0005374 | 0.00013468
130 | 1 | 0 | -0.43127 | -0.1098
131 | 0.99844 | -0.029643 | 0 | 0
132 | 0.99994 | -0.0011443 | 0.0022872 | 0.00057324
133 | 0.98817 | -0.22604 | 0 | 0
134 | 0.98621 | -0.26512 | 0.00089683 | 0.00022477
135 | 0.98631 | -0.26317 | 0 | 0
136 | 0.98703 | -0.2491 | 0.0012263 | 0.00030734
137 | 0.98942 | -0.20266 | 0 | 0
138 | 0.98941 | -0.20299 | 0.0012059 | 0.00030222
139 | 0.99078 | -0.17651 | 0.0035827 | 0.00089792
140 | 0.98906 | -0.20979 | 0.0027291 | 0.00068398
141 | 0.9845 | -0.29844 | 0 | 0
142 | 0.98451 | -0.29818 | 0 | 0
143 | 0.98476 | -0.29328 | 0.00077942 | 0.00019534
144 | 0.98431 | -0.30219 | 0.004601 | 0.0011531
145 | 0.986 | -0.26922 | 0.0025246 | 0.00063272
146 | 0.98629 | -0.26355 | 0.0009099 | 0.00022804
147 | 0.97827 | -0.41842 | 0 | 0
148 | 0.97805 | -0.42272 | 0.0071698 | 0.0017969
149 | 0.97808 | -0.42216 | 0.0022034 | 0.00055222
150 | 0.97841 | -0.41578 | 0.0015045 | 0.00037706
151 | 0.97945 | -0.39527 | 0.0015045 | 0.00037706
152 | 0.97749 | -0.43375 | 0.00085372 | 0.00021396
153 | 0.97393 | -0.50784 | 0.00061047 | 0.000153
154 | 0.98476 | -0.29324 | 0.00077941 | 0.00019534
155 | 0.99227 | -0.14782 | 0.0021111 | 0.0005291
156 | 0.98846 | -0.22125 | 0.0012119 | 0.00030373
157 | 0.986 | -0.26905 | 0.00089683 | 0.00022477
158 | 0.98625 | -0.26426 | 0.00094913 | 0.00023787
159 | 0.98494 | -0.28972 | 0 | 0
160 | 0.9861 | -0.26719 | 0.0049859 | 0.0012496
161 | 0.98604 | -0.26828 | 0.0014998 | 0.00037589
162 | 0.98528 | -0.28187 | 0.00044847 | 0.0001124
163 | 0.98528 | -0.28182 | 0.0021352 | 0.00053513
164 | 0.99834 | -0.031508 | 0.0019514 | 0.00048907
165 | 0.99739 | -0.049683 | 0.0050746 | 0.0012718
166 | 0.98543 | -0.2789 | 0 | 0
167 | 0.98533 | -0.28074 | 0.0021108 | 0.00052902
168 | 0.98548 | -0.27787 | 0 | 0
169 | 0.98693 | -0.25005 | 0 | 0
170 | 0.98716 | -0.24552 | 0.0070388 | 0.0017641
171 | 0.98372 | -0.31204 | 0 | 0
172 | 0.99046 | -0.18301 | 0.0024572 | 0.00061583
173 | 0.99023 | -0.18755 | 0.00038207 | 9.5755e-05
174 | 0.99062 | -0.17996 | 0 | 0
175 | 0.98968 | -0.19824 | 0.0013517 | 0.00033878
176 | 0.99085 | -0.17537 | 0.00063216 | 0.00015844
177 | 0.99033 | -0.18557 | 0.0004794 | 0.00012015
178 | 0.98965 | -0.19875 | 0 | 0
179 | 0.99109 | -0.17082 | 0.00093715 | 0.00023487
180 | 0.9902 | -0.18813 | 0 | 0
181 | 0.98964 | -0.19894 | 0.00054122 | 0.00013564
182 | 0.9896 | -0.19972 | 0.0015329 | 0.00038417
183 | 0.99117 | -0.16917 | 0.00034124 | 8.5524e-05
184 | 0.99018 | -0.18842 | 0.00036946 | 9.2596e-05
185 | 0.99007 | -0.19064 | 0.00055405 | 0.00013886
186 | 0.98964 | -0.19895 | 0.00030832 | 7.7273e-05
187 | 0.9912 | -0.16864 | 0 | 0
188 | 0.99012 | -0.18969 | 0.00097109 | 0.00024338
189 | 0.99003 | -0.19143 | 0.0020704 | 0.00051889
190 | 0.99084 | -0.17557 | 0.0025321 | 0.00063462
191 | 0.99081 | -0.17612 | 0.0021265 | 0.00053294
192 | 0.99122 | -0.16825 | 0 | 0
193 | 0.99081 | -0.17614 | 0.0021249 | 0.00053255
194 | 0.99138 | -0.16508 | 0 | 0
195 | 0.99116 | -0.16936 | 0.0025855 | 0.00064799
196 | 0.99081 | -0.17616 | 0.0021264 | 0.00053293
197 | 0.99179 | -0.15729 | 0.0051758 | 0.0012972
198 | 0.99131 | -0.16651 | 0.0024714 | 0.0006194
199 | 0.99092 | -0.17398 | 0 | 0
200 | 0.9908 | -0.17644 | 0.0030944 | 0.00077553
201 | 0.99229 | -0.14744 | 0 | 0
202 | 0.99124 | -0.16789 | 0.0017691 | 0.00044337
203 | 0.99088 | -0.1748 | 0.0021024 | 0.0005269
204 | 0.99081 | -0.17627 | 0.0003089 | 7.7419e-05
205 | 0.99189 | -0.15526 | 0.0026252 | 0.00065793
206 | 0.99215 | -0.15025 | 0.0028565 | 0.00071591
207 | 0.99297 | -0.13441 | 0.0026636 | 0.00066757
208 | 0.99121 | -0.16846 | 0.0029348 | 0.00073553
209 | 0.99088 | -0.17488 | 0.00029899 | 7.4934e-05
210 | 0.99076 | -0.17725 | 0.0058902 | 0.0014762
211 | 0.99011 | -0.18976 | 0.00028851 | 7.2307e-05
212 | 0.98417 | -0.30485 | 0.0018176 | 0.00045554
213 | 0.98418 | -0.30456 | 0.00055507 | 0.00013911
214 | 0.98414 | -0.30549 | 0.0016906 | 0.00042371
215 | 0.98429 | -0.30253 | 0.00031499 | 7.8943e-05
216 | 0.98407 | -0.30687 | 0.00029497 | 7.3927e-05
217 | 0.98436 | -0.30123 | 0.001423 | 0.00035664
218 | 0.98404 | -0.30738 | 0.00029538 | 7.4029e-05
219 | 0.98402 | -0.30779 | 0.00029714 | 7.447e-05
220 | 0.9858 | -0.2731 | 0.0018121 | 0.00045416
221 | 0.98466 | -0.29522 | 0 | 0
222 | 0.98401 | -0.30802 | 0.00029114 | 7.2966e-05
223 | 0.97204 | -0.54321 | 0.00070773 | 0.00017737
224 | 0.97227 | -0.53856 | 0.00067745 | 0.00016979
225 | 0.972 | -0.54396 | 0 | 0
226 | 0.97221 | -0.5398 | 0.0017248 | 0.00043226
227 | 0.97196 | -0.54478 | 0.00065642 | 0.00016451
228 | 0.97194 | -0.54515 | 0.00065221 | 0.00016346
229 | 0.99344 | -0.12533 | 0.0028443 | 0.00071285
230 | 0.9941 | -0.11265 | 0.0013778 | 0.00034532
231 | 0.99316 | -0.13075 | 0 | 0
232 | 0.99479 | -0.099442 | 0.0021103 | 0.00052889
233 | 0.99271 | -0.13937 | 0.0028585 | 0.0007164
234 | 0.9967 | -0.062742 | 0.0018071 | 0.00045289
235 | 0.99176 | -0.15786 | 0.0023797 | 0.00059641
236 | 0.99212 | -0.15084 | 0.0053448 | 0.0013395
237 | 0.98536 | -0.28064 | 0.043832 | 0.010985
238 | 0.98078 | -0.36936 | 0.00070715 | 0.00017723
239 | 0.98484 | -0.29071 | 0.0071382 | 0.001789
240 | 0.97782 | -0.42722 | 0.0037171 | 0.0009316
241 | 0.97788 | -0.4261 | 0.0019254 | 0.00048254
242 | 0.98429 | -0.30148 | 0.066214 | 0.016595
243 | 0.99831 | -0.032113 | 0.0019169 | 0.00048042
244 | 0.99075 | -0.1774 | 0.00060062 | 0.00015053
245 | 0.99088 | -0.17492 | 0.00050328 | 0.00012613
246 | 0.97667 | -0.44978 | 0.0040524 | 0.0010156
247 | 0.97665 | -0.45018 | 0 | 0
248 | 0.97643 | -0.45458 | 0.0042524 | 0.0010658
249 | 0.97645 | -0.45415 | 0.00077582 | 0.00019444
250 | 0.97602 | -0.46264 | 0 | 0
251 | 0.97503 | -0.4822 | 0.0028599 | 0.00071677
252 | 0.97802 | -0.42344 | 0.0022978 | 0.00057588
253 | 0.98451 | -0.29813 | 0.0019186 | 0.00048084
254 | 0.99143 | -0.1642 | 0.0060356 | 0.0015127
255 | 0.98449 | -0.29858 | 0.0014464 | 0.00036251
256 | 0.98424 | -0.30343 | 0.002253 | 0.00056466
257 | 0.9842 | -0.30433 | 0.002253 | 0.00056466
258 | 0.98416 | -0.30498 | 0.0045946 | 0.0011515
259 | 0.99829 | -0.032528 | 0.0015992 | 0.0004008
260 | 0.97772 | -0.42915 | 0.001637 | 0.00041027
261 | 0.984 | -0.30813 | 0.00029098 | 7.2926e-05
262 | 0.97486 | -0.48548 | 0.0041467 | 0.0010393
263 | 0.97769 | -0.42981 | 0.0015805 | 0.00039612
264 | 0.97765 | -0.43072 | 0.0020671 | 0.00051806
265 | 0.9725 | -0.53651 | 0.0016997 | 0.00042599
266 | 0.9724 | -0.53855 | 0 | 0
267 | 0.97198 | -0.54684 | 0.00091527 | 0.00022939
268 | 0.9718 | -0.55046 | 0.001771 | 0.00044386
269 | 0.97179 | -0.55069 | 0.00045107 | 0.00011305
270 | 0.97132 | -0.55995 | 0.00050875 | 0.0001275
271 | 0.97195 | -0.5449 | 0.00057502 | 0.00014411
272 | 0.97164 | -0.55112 | 0.00068044 | 0.00017053
273 | 0.97007 | -0.58468 | 0.001625 | 0.00040726
274 | 0.97039 | -0.57847 | 0.00061628 | 0.00015446
275 | 0.97043 | -0.57765 | 0.00063473 | 0.00015908
276 | 0.9704 | -0.57821 | 0.00086918 | 0.00021784
277 | 0.97114 | -0.56357 | 0.0010306 | 0.00025828
278 | 0.97144 | -0.55496 | 0.00048056 | 0.00012044
279 | 0.97145 | -0.5548 | 0.00082174 | 0.00020595
280 | 0.97147 | -0.55437 | 0.0009021 | 0.00022609
281 | 0.97147 | -0.55436 | 0.001349 | 0.00033808
282 | 0.97194 | -0.54517 | 0.00098521 | 0.00024692
283 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0022815 | -0.00056872 | 0.0022816 | 0.0005684 | 1.5414e-07 | -3.2756e-07 | 0.0034746 | 0.0034744 | 0.0034746 | 0.97676 | -0.45023 | 0.97683 | -0.4488 | 0.95455
1 | 0.0019825 | 0.00049379 | -0.0019824 | -0.00049423 | 1.4404e-07 | -4.3519e-07 | 0.0030191 | 0.0030193 | 0.0030193 | 0.97676 | -0.45023 | 0.97668 | -0.45176 | 0.82947
2 | -0.004312 | -0.0010773 | 0.0043129 | 0.0010772 | 8.2431e-07 | -1.106e-07 | 0.0065674 | 0.0065671 | 0.0065674 | 0.97683 | -0.4488 | 0.97703 | -0.44478 | 1.8042
3 | 0.00017035 | 4.0095e-05 | -0.00017035 | -4.2693e-05 | 5.231e-09 | -2.5974e-06 | 0.00025863 | 0.00025954 | 0.00025954 | 0.97668 | -0.45176 | 0.97665 | -0.45242 | 0.071302
4 | -0.0043129 | -0.0010772 | 0.0043142 | 0.001077 | 1.3345e-06 | -1.7973e-07 | 0.0065671 | 0.0065668 | 0.0065671 | 0.97703 | -0.44478 | 0.97736 | -0.43827 | 1.8042
5 | -0.026326 | -0.0066084 | 0.026348 | 0.0066149 | 2.1413e-05 | 6.5304e-06 | 0.040027 | 0.040024 | 0.040027 | 0.97878 | -0.41057 | 0.97965 | -0.39353 | 2.7491
6 | 0.022727 | 0.0057131 | -0.022713 | -0.0057104 | 1.433e-05 | 2.7416e-06 | 0.034558 | 0.03456 | 0.03456 | 0.97878 | -0.41057 | 0.9781 | -0.42378 | 2.3736
7 | 0.0032445 | 0.00080642 | -0.0032429 | -0.00080758 | 1.5703e-06 | -1.1588e-06 | 0.0049301 | 0.0049309 | 0.0049309 | 0.97878 | -0.41057 | 0.97826 | -0.42079 | 1.3546
8 | -0.026594 | -0.0066766 | 0.026607 | 0.0066807 | 1.3433e-05 | 4.1728e-06 | 0.040398 | 0.040397 | 0.040398 | 0.97965 | -0.39353 | 0.98019 | -0.38294 | 2.7746
9 | 0.022124 | 0.0055628 | -0.022118 | -0.0055618 | 6.4556e-06 | 1.0823e-06 | 0.033665 | 0.033666 | 0.033666 | 0.9781 | -0.42378 | 0.97779 | -0.42989 | 2.3122
10 | 0.0032429 | 0.00080758 | -0.0032428 | -0.00080768 | 1.4036e-07 | -1.0344e-07 | 0.0049309 | 0.004931 | 0.004931 | 0.97826 | -0.42079 | 0.97821 | -0.42171 | 1.3547
11 | -0.0043142 | -0.001077 | 0.0043144 | 0.001077 | 1.8315e-07 | -2.4728e-08 | 0.0065668 | 0.0065667 | 0.0065668 | 0.97736 | -0.43827 | 0.97741 | -0.43738 | 1.8041
12 | -0.0044412 | -0.0011087 | 0.0044413 | 0.0011087 | 1.4093e-07 | -1.289e-08 | 0.0067597 | 0.0067597 | 0.0067597 | 0.97741 | -0.43738 | 0.97744 | -0.43671 | 1.8571
13 | 0.022117 | 0.0055616 | -0.022111 | -0.0055584 | 6.1457e-06 | 3.2081e-06 | 0.033666 | 0.033666 | 0.033666 | 0.97774 | -0.43089 | 0.97744 | -0.43671 | 4.6245
14 | -0.022117 | -0.0055616 | 0.022118 | 0.0055618 | 1.0511e-06 | 1.7642e-07 | 0.033666 | 0.033666 | 0.033666 | 0.97774 | -0.43089 | 0.97779 | -0.42989 | 2.3122
15 | 0.017669 | 0.0044497 | -0.017663 | -0.0044458 | 6.4555e-06 | 3.8336e-06 | 0.026907 | 0.026907 | 0.026907 | 0.97744 | -0.43671 | 0.97705 | -0.44435 | 7.392
16 | -0.017219 | -0.0043301 | 0.017223 | 0.0043327 | 4.5179e-06 | 2.6728e-06 | 0.026251 | 0.026251 | 0.026251 | 0.97625 | -0.46006 | 0.97653 | -0.45457 | 7.2117
17 | 0.017219 | 0.0043301 | -0.017216 | -0.0043284 | 2.8508e-06 | 1.6866e-06 | 0.026251 | 0.026251 | 0.026251 | 0.97625 | -0.46006 | 0.97608 | -0.46353 | 7.2117
18 | -0.017654 | -0.0044407 | 0.017663 | 0.0044458 | 8.6194e-06 | 5.119e-06 | 0.026907 | 0.026907 | 0.026907 | 0.97653 | -0.45457 | 0.97705 | -0.44435 | 7.392
19 | 0.015501 | 0.003899 | -0.015453 | -0.003871 | 4.8309e-05 | 2.8046e-05 | 0.023637 | 0.023638 | 0.023638 | 0.97608 | -0.46353 | 0.97276 | -0.52897 | 6.4939
20 | 0.0014219 | 0.00035602 | -0.0014218 | -0.00035635 | 5.0934e-08 | -3.2871e-07 | 0.0021675 | 0.0021677 | 0.0021677 | 0.97608 | -0.46353 | 0.97604 | -0.46428 | 0.59551
21 | 0.00063554 | 0.0001585 | -0.00063552 | -0.00015928 | 2.2609e-08 | -7.7566e-07 | 0.0009725 | 0.00097279 | 0.00097279 | 0.97215 | -0.54094 | 0.97211 | -0.54169 | 0.26725
22 | -0.00063554 | -0.0001585 | 0.00063555 | 0.00015797 | 1.5328e-08 | -5.2616e-07 | 0.0009725 | 0.00097231 | 0.0009725 | 0.97215 | -0.54094 | 0.97218 | -0.54043 | 0.26717
23 | -0.0016174 | -0.00040406 | 0.0016175 | 0.00040383 | 4.8283e-08 | -2.297e-07 | 0.0024752 | 0.0024751 | 0.0024752 | 0.97218 | -0.54043 | 0.97221 | -0.5398 | 0.67999
24 | -0.0082299 | -0.0019806 | 0.0082306 | 0.0019787 | 6.8924e-07 | -1.8701e-06 | 0.012565 | 0.012564 | 0.012565 | 0.97241 | -0.53846 | 0.9725 | -0.53665 | 0.86295
25 | 0.0062343 | 0.0014804 | -0.006234 | -0.0014816 | 2.1532e-07 | -1.122e-06 | 0.009511 | 0.0095114 | 0.0095114 | 0.97241 | -0.53846 | 0.97238 | -0.53921 | 0.65326
26 | 0.00082649 | 0.00020402 | -0.00082648 | -0.00020428 | 1.27e-08 | -2.5508e-07 | 0.0012635 | 0.0012636 | 0.0012636 | 0.9725 | -0.53665 | 0.97249 | -0.53697 | 0.34714
27 | -0.01036 | -0.0025094 | 0.010366 | 0.0025005 | 5.9899e-06 | -8.8461e-06 | 0.015821 | 0.015817 | 0.015821 | 0.9725 | -0.53665 | 0.97312 | -0.52418 | 1.0866
28 | 0.006234 | 0.0014816 | -0.0062321 | -0.0014918 | 1.9567e-06 | -1.0186e-05 | 0.0095114 | 0.0095154 | 0.0095154 | 0.97238 | -0.53921 | 0.97204 | -0.54604 | 0.65353
29 | 0.00052629 | 0.00012904 | -0.00052626 | -0.00013059 | 3.0586e-08 | -1.5437e-06 | 0.00080427 | 0.00080483 | 0.00080483 | 0.97249 | -0.53697 | 0.97242 | -0.53821 | 0.22111
30 | -0.021892 | -0.0053535 | 0.021906 | 0.0053557 | 1.3093e-05 | 2.1645e-06 | 0.033429 | 0.033427 | 0.033429 | 0.97312 | -0.52418 | 0.97375 | -0.5114 | 2.2959
31 | 0.01061 | 0.0026235 | -0.01061 | -0.0026242 | 5.1765e-07 | -7.126e-07 | 0.016212 | 0.016212 | 0.016212 | 0.97312 | -0.52418 | 0.97306 | -0.52522 | 1.1135
32 | 0.0060808 | 0.0014538 | -0.0060807 | -0.0014544 | 1.0724e-07 | -5.8942e-07 | 0.0092838 | 0.009284 | 0.009284 | 0.97204 | -0.54604 | 0.97203 | -0.54643 | 0.63764
33 | 0.00052626 | 0.00013059 | -0.00052624 | -0.00013189 | 2.5814e-08 | -1.301e-06 | 0.00080483 | 0.0008053 | 0.0008053 | 0.97242 | -0.53821 | 0.97237 | -0.53924 | 0.22124
34 | -0.021906 | -0.0053557 | 0.021909 | 0.0053563 | 3.6463e-06 | 6.0122e-07 | 0.033427 | 0.033426 | 0.033427 | 0.97375 | -0.5114 | 0.97393 | -0.50784 | 2.2958
35 | 0.010139 | 0.0025061 | -0.010133 | -0.0025146 | 5.403e-06 | -8.4641e-06 | 0.015492 | 0.015496 | 0.015496 | 0.97306 | -0.52522 | 0.9725 | -0.53651 | 1.0643
36 | 0.0060294 | 0.0014416 | -0.0060294 | -0.0014417 | 1.4613e-08 | -8.1846e-08 | 0.0092055 | 0.0092055 | 0.0092055 | 0.97203 | -0.54643 | 0.97202 | -0.54648 | 0.63225
37 | 0.0059867 | 0.0014309 | -0.0059864 | -0.0014325 | 2.6715e-07 | -1.5201e-06 | 0.0091401 | 0.0091407 | 0.0091407 | 0.97202 | -0.54648 | 0.97198 | -0.54745 | 0.62779
38 | -0.005796 | -0.0013851 | 0.0057961 | 0.0013848 | 5.0613e-08 | -3.0938e-07 | 0.0088495 | 0.0088494 | 0.0088495 | 0.97197 | -0.54764 | 0.97198 | -0.54745 | 0.60779
39 | 0.0056985 | 0.0013606 | -0.0056973 | -0.001368 | 1.1681e-06 | -7.4086e-06 | 0.0087001 | 0.008703 | 0.008703 | 0.97197 | -0.54764 | 0.97175 | -0.55209 | 0.59773
40 | 0.0055068 | 0.0013203 | -0.0055068 | -0.0013206 | 3.7516e-08 | -2.5627e-07 | 0.0084113 | 0.0084114 | 0.0084114 | 0.97175 | -0.55209 | 0.97174 | -0.55224 | 0.57771
41 | -0.0006491 | -0.00016268 | 0.00064911 | 0.00016247 | 6.1081e-09 | -2.0538e-07 | 0.00098793 | 0.00098786 | 0.00098793 | 0.97767 | -0.43241 | 0.97768 | -0.43221 | 0.27141
42 | -0.00086606 | -0.00021685 | 0.00086607 | 0.00021667 | 9.3975e-09 | -1.7489e-07 | 0.0013181 | 0.001318 | 0.0013181 | 0.97768 | -0.43221 | 0.97769 | -0.43199 | 0.3621
43 | -0.0017552 | -0.00043853 | 0.0017556 | 0.00043688 | 4.0892e-07 | -1.6562e-06 | 0.0026709 | 0.0026702 | 0.0026709 | 0.97769 | -0.43199 | 0.97794 | -0.42708 | 0.73377
44 | 0.00088917 | 0.00022186 | -0.00088913 | -0.00022261 | 4.2465e-08 | -7.4845e-07 | 0.0013529 | 0.0013532 | 0.0013532 | 0.97769 | -0.43199 | 0.97764 | -0.43299 | 0.37176
45 | -0.0017556 | -0.00043688 | 0.0017559 | 0.00043567 | 2.9646e-07 | -1.2019e-06 | 0.0026702 | 0.0026697 | 0.0026702 | 0.97794 | -0.42708 | 0.97812 | -0.42351 | 0.73358
46 | 0.00063557 | 0.00015906 | -0.00063556 | -0.00015929 | 6.4695e-09 | -2.2705e-07 | 0.00096728 | 0.00096736 | 0.00096736 | 0.97764 | -0.43299 | 0.97763 | -0.4332 | 0.26576
47 | -0.00010601 | -2.6567e-05 | 0.00010601 | 2.5432e-05 | 9.0817e-10 | -1.1358e-06 | 0.00016251 | 0.0001621 | 0.00016251 | 0.97066 | -0.57413 | 0.97067 | -0.57395 | 0.044644
48 | -0.00025942 | -6.388e-05 | 0.00025942 | 6.3453e-05 | 2.0489e-09 | -4.2678e-07 | 0.00039727 | 0.00039712 | 0.00039727 | 0.97067 | -0.57395 | 0.97068 | -0.57378 | 0.10914
49 | -0.0021183 | -0.0005265 | 0.0021183 | 0.00052646 | 1.2039e-08 | -3.1135e-08 | 0.003221 | 0.003221 | 0.003221 | 0.97812 | -0.42351 | 0.97813 | -0.42339 | 0.8849
50 | 0.00015169 | 3.7867e-05 | -0.00015169 | -3.8017e-05 | 2.3952e-10 | -1.5042e-07 | 0.00023071 | 0.00023076 | 0.00023076 | 0.97813 | -0.42339 | 0.97813 | -0.42342 | 0.063397
51 | -0.00227 | -0.00056433 | 0.0022702 | 0.00056394 | 1.8091e-07 | -3.9251e-07 | 0.0034517 | 0.0034515 | 0.0034517 | 0.97813 | -0.42339 | 0.97821 | -0.42171 | 0.94828
52 | -0.0052766 | -0.0012637 | 0.0052767 | 0.0012629 | 1.1026e-07 | -8.267e-07 | 0.0080595 | 0.0080591 | 0.0080595 | 0.97172 | -0.55269 | 0.97174 | -0.55224 | 0.55353
53 | 0.0049254 | 0.0011757 | -0.0049253 | -0.0011762 | 5.7789e-08 | -5.0288e-07 | 0.0075216 | 0.0075218 | 0.0075218 | 0.97172 | -0.55269 | 0.97171 | -0.55295 | 0.51661
54 | 0.0049253 | 0.0011762 | -0.0049249 | -0.0011799 | 4.2615e-07 | -3.7072e-06 | 0.0075218 | 0.0075232 | 0.0075232 | 0.97171 | -0.55295 | 0.97162 | -0.55482 | 0.5167
55 | 0.0043282 | 0.0010304 | -0.0043281 | -0.0010315 | 9.6956e-08 | -1.1107e-06 | 0.0066095 | 0.0066099 | 0.0066099 | 0.97162 | -0.55482 | 0.97159 | -0.55531 | 0.45397
56 | 0.00085879 | 0.0002114 | -0.00085876 | -0.00021188 | 2.6458e-08 | -4.8799e-07 | 0.0013146 | 0.0013148 | 0.0013148 | 0.97103 | -0.56671 | 0.971 | -0.56737 | 0.36121
57 | -0.00092469 | -0.00022791 | 0.00092487 | 0.00022506 | 1.8027e-07 | -2.8549e-06 | 0.0014156 | 0.0014146 | 0.0014156 | 0.97103 | -0.56671 | 0.97124 | -0.56255 | 0.38891
58 | 0.00071578 | 0.00017605 | -0.00071577 | -0.00017628 | 8.7257e-09 | -2.3413e-07 | 0.0010957 | 0.0010958 | 0.0010958 | 0.971 | -0.56737 | 0.97099 | -0.56763 | 0.30104
59 | -0.0010826 | -0.00026459 | 0.0010826 | 0.00026454 | 5.0654e-09 | -5.7697e-08 | 0.0016563 | 0.0016562 | 0.0016563 | 0.97124 | -0.56255 | 0.97124 | -0.56245 | 0.45502
60 | 0.0039112 | 0.00092699 | -0.0039112 | -0.00092775 | 5.3203e-08 | -7.543e-07 | 0.0059714 | 0.0059717 | 0.0059717 | 0.97159 | -0.55531 | 0.97158 | -0.55561 | 0.41014
61 | 0.0039112 | 0.00092775 | -0.0039111 | -0.00092868 | 6.5604e-08 | -9.3e-07 | 0.0059717 | 0.005972 | 0.005972 | 0.97158 | -0.55561 | 0.97156 | -0.55598 | 0.41017
62 | 0.0024371 | 0.00058445 | -0.002437 | -0.00058577 | 3.539e-08 | -1.3243e-06 | 0.0037244 | 0.0037249 | 0.0037249 | 0.97124 | -0.56245 | 0.97123 | -0.56277 | 0.25583
63 | -0.0035638 | -0.00086005 | 0.0035647 | 0.00084461 | 8.9929e-07 | -1.5442e-05 | 0.0054483 | 0.0054428 | 0.0054483 | 0.97124 | -0.56245 | 0.97151 | -0.55697 | 0.3742
64 | 0.0023545 | 0.0005651 | -0.0023543 | -0.00057596 | 2.7085e-07 | -1.0857e-05 | 0.0035985 | 0.0036024 | 0.0036024 | 0.97123 | -0.56277 | 0.97111 | -0.56524 | 0.24742
65 | -0.0035647 | -0.00084461 | 0.0035648 | 0.00084356 | 6.1005e-08 | -1.049e-06 | 0.0054428 | 0.0054424 | 0.0054428 | 0.97151 | -0.55697 | 0.97153 | -0.5566 | 0.37382
66 | 0.003849 | 0.0009131 | -0.003849 | -0.0009136 | 3.3912e-08 | -4.9707e-07 | 0.0058769 | 0.005877 | 0.005877 | 0.97156 | -0.55598 | 0.97155 | -0.55617 | 0.40364
67 | -0.029205 | -0.0073318 | 0.029214 | 0.007335 | 8.7799e-06 | 3.2166e-06 | 0.04434 | 0.044339 | 0.04434 | 0.98019 | -0.38294 | 0.98051 | -0.37664 | 3.0453
68 | -0.029214 | -0.007335 | 0.029216 | 0.0073358 | 2.0924e-06 | 7.6633e-07 | 0.044339 | 0.044339 | 0.044339 | 0.98051 | -0.37664 | 0.98058 | -0.37514 | 3.0453
69 | -0.00031173 | -7.5562e-05 | 0.00031174 | 7.5224e-05 | 2.3393e-09 | -3.3795e-07 | 0.00047682 | 0.0004767 | 0.00047682 | 0.97097 | -0.56801 | 0.97098 | -0.56785 | 0.131
70 | 0.00019182 | 4.5508e-05 | -0.00019181 | -4.7325e-05 | 4.7501e-09 | -1.8173e-06 | 0.00029306 | 0.00029369 | 0.00029369 | 0.97097 | -0.56801 | 0.97094 | -0.56855 | 0.080685
71 | -0.00071576 | -0.00017648 | 0.00071577 | 0.00017628 | 7.4411e-09 | -1.9963e-07 | 0.0010959 | 0.0010958 | 0.0010959 | 0.97098 | -0.56785 | 0.97099 | -0.56763 | 0.30106
72 | 0.00019181 | 4.7325e-05 | -0.00019181 | -4.7594e-05 | 7.0464e-10 | -2.6889e-07 | 0.00029369 | 0.00029379 | 0.00029379 | 0.97094 | -0.56855 | 0.97094 | -0.56862 | 0.080712
73 | 6.8969e-05 | 1.6807e-05 | -6.8969e-05 | -1.7105e-05 | 1.0071e-10 | -2.979e-07 | 0.00010553 | 0.00010563 | 0.00010563 | 0.97094 | -0.56862 | 0.97094 | -0.56865 | 0.02902
74 | 6.8969e-05 | 1.7105e-05 | -6.8969e-05 | -1.7285e-05 | 6.1138e-11 | -1.8055e-07 | 0.00010563 | 0.0001057 | 0.0001057 | 0.97094 | -0.56865 | 0.97094 | -0.56867 | 0.029038
75 | 0.0023543 | 0.00057596 | -0.0023542 | -0.00057807 | 5.2765e-08 | -2.112e-06 | 0.0036024 | 0.0036032 | 0.0036032 | 0.97111 | -0.56524 | 0.97108 | -0.56572 | 0.24747
76 | 0.0036841 | 0.00087229 | -0.0036841 | -0.00087345 | 7.1913e-08 | -1.1549e-06 | 0.0056246 | 0.005625 | 0.005625 | 0.97155 | -0.55617 | 0.97153 | -0.5566 | 0.38633
77 | 0.070474 | 0.017602 | -0.07046 | -0.017594 | 1.3922e-05 | 8.2502e-06 | 0.10674 | 0.10674 | 0.10674 | 0.98226 | -0.34221 | 0.98205 | -0.34637 | 7.331
78 | -0.07066 | -0.017649 | 0.070666 | 0.017652 | 5.6105e-06 | 3.3262e-06 | 0.10702 | 0.10702 | 0.10702 | 0.98226 | -0.34221 | 0.98234 | -0.34054 | 7.3504
79 | 0.070219 | 0.017534 | -0.070217 | -0.017533 | 1.7478e-06 | 1.0352e-06 | 0.10637 | 0.10637 | 0.10637 | 0.98205 | -0.34637 | 0.98202 | -0.34689 | 7.3059
80 | -0.070934 | -0.01772 | 0.070954 | 0.017731 | 1.9791e-05 | 1.1739e-05 | 0.10743 | 0.10743 | 0.10743 | 0.98234 | -0.34054 | 0.98264 | -0.33467 | 7.3783
81 | 0.069862 | 0.017444 | -0.069771 | -0.01739 | 9.101e-05 | 5.3867e-05 | 0.10584 | 0.10584 | 0.10584 | 0.98202 | -0.34689 | 0.98062 | -0.37435 | 7.269
82 | -0.070954 | -0.017731 | 0.070959 | 0.017734 | 4.7183e-06 | 2.7987e-06 | 0.10743 | 0.10743 | 0.10743 | 0.98264 | -0.33467 | 0.98272 | -0.33327 | 7.3783
83 | 0.029639 | 0.0074419 | -0.029637 | -0.0074415 | 1.1167e-06 | 4.1758e-07 | 0.044979 | 0.044979 | 0.044979 | 0.98062 | -0.37435 | 0.98058 | -0.37514 | 3.0892
84 | 0.040132 | 0.009948 | -0.040129 | -0.0099463 | 3.2424e-06 | 1.6039e-06 | 0.060858 | 0.060858 | 0.060858 | 0.98062 | -0.37435 | 0.98054 | -0.37606 | 4.1798
85 | -0.083468 | -0.020873 | 0.083625 | 0.020968 | 0.00015667 | 9.4956e-05 | 0.12637 | 0.12637 | 0.12637 | 0.98272 | -0.33327 | 0.98473 | -0.29388 | 8.6793
86 | 0.012509 | 0.0031388 | -0.012503 | -0.0031352 | 6.4772e-06 | 3.5359e-06 | 0.018943 | 0.018943 | 0.018943 | 0.98272 | -0.33327 | 0.98216 | -0.34413 | 5.2041
87 | 0.039756 | 0.0098527 | -0.039708 | -0.0098291 | 4.7954e-05 | 2.3601e-05 | 0.060292 | 0.060294 | 0.060294 | 0.98054 | -0.37606 | 0.97925 | -0.40162 | 4.1411
88 | -0.092094 | -0.023091 | 0.092103 | 0.023096 | 8.7437e-06 | 5.3509e-06 | 0.13917 | 0.13917 | 0.13917 | 0.98473 | -0.29388 | 0.98483 | -0.29189 | 9.5581
89 | 0.0071534 | 0.001793 | -0.0071521 | -0.0017925 | 1.3619e-06 | 4.7631e-07 | 0.01081 | 0.01081 | 0.01081 | 0.98473 | -0.29388 | 0.98452 | -0.29788 | 2.9697
90 | 0.012116 | 0.0030384 | -0.01211 | -0.0030351 | 6.2099e-06 | 3.3528e-06 | 0.018358 | 0.018358 | 0.018358 | 0.98216 | -0.34413 | 0.98161 | -0.35489 | 5.0434
91 | 0.038379 | 0.0094974 | -0.038355 | -0.0094859 | 2.4032e-05 | 1.1585e-05 | 0.058275 | 0.058276 | 0.058276 | 0.97925 | -0.40162 | 0.97858 | -0.4149 | 4.0025
92 | 0.0013291 | 0.0003317 | -0.001329 | -0.00033307 | 1.807e-07 | -1.3706e-06 | 0.0020192 | 0.0020197 | 0.0020197 | 0.97925 | -0.40162 | 0.9791 | -0.40448 | 0.55487
93 | -0.092833 | -0.023279 | 0.092902 | 0.023321 | 6.8396e-05 | 4.1885e-05 | 0.14027 | 0.14027 | 0.14027 | 0.98483 | -0.29189 | 0.98562 | -0.27644 | 9.6339
94 | 0.0089732 | 0.0022496 | -0.0089691 | -0.0022477 | 4.0798e-06 | 1.8682e-06 | 0.013603 | 0.013603 | 0.013603 | 0.98161 | -0.35489 | 0.98112 | -0.36444 | 3.7371
95 | 0.003137 | 0.00078549 | -0.0031369 | -0.00078558 | 1.0842e-07 | -9.2239e-08 | 0.0047552 | 0.0047552 | 0.0047552 | 0.98161 | -0.35489 | 0.98157 | -0.35562 | 1.3064
96 | 0.034204 | 0.0084465 | -0.034173 | -0.0084327 | 3.1289e-05 | 1.382e-05 | 0.051966 | 0.051968 | 0.051968 | 0.97858 | -0.4149 | 0.9776 | -0.43433 | 3.5692
97 | 0.0041504 | 0.0010393 | -0.0041485 | -0.0010397 | 1.8747e-06 | -3.7631e-07 | 0.0063107 | 0.0063113 | 0.0063113 | 0.97858 | -0.4149 | 0.97809 | -0.42439 | 1.7339
98 | 0.03259 | 0.0080381 | -0.032573 | -0.008031 | 1.6828e-05 | 7.1067e-06 | 0.049559 | 0.04956 | 0.04956 | 0.9776 | -0.43433 | 0.97705 | -0.44531 | 3.4038
99 | 0.0015833 | 0.0003946 | -0.0015829 | -0.00039665 | 4.0134e-07 | -2.0536e-06 | 0.0024092 | 0.00241 | 0.00241 | 0.9776 | -0.43433 | 0.97733 | -0.43966 | 0.6621
100 | 0.029058 | 0.0071502 | -0.029027 | -0.0071386 | 3.1548e-05 | 1.1576e-05 | 0.044208 | 0.044211 | 0.044211 | 0.97705 | -0.44531 | 0.97589 | -0.46843 | 3.0364
101 | 0.00050385 | 0.00012621 | -0.00050385 | -0.00012628 | 1.1896e-09 | -6.6792e-08 | 0.0007671 | 0.00076713 | 0.00076713 | 0.97733 | -0.43966 | 0.97733 | -0.43971 | 0.21075
102 | 0.028655 | 0.0070454 | -0.028645 | -0.0070419 | 9.7266e-06 | 3.5038e-06 | 0.043643 | 0.043644 | 0.043644 | 0.97589 | -0.46843 | 0.97553 | -0.47566 | 2.9976
103 | 0.01184 | 0.0029654 | -0.011835 | -0.0029629 | 4.5225e-06 | 2.4381e-06 | 0.018111 | 0.018111 | 0.018111 | 0.97276 | -0.52897 | 0.97235 | -0.53699 | 4.9755
104 | 0.0078151 | 0.0019572 | -0.0078128 | -0.0019563 | 2.3147e-06 | 9.4625e-07 | 0.011959 | 0.011959 | 0.011959 | 0.97235 | -0.53699 | 0.97204 | -0.54321 | 3.2855
105 | 0.0040202 | 0.0010057 | -0.0040199 | -0.0010058 | 2.9893e-07 | -6.9951e-08 | 0.0061515 | 0.0061516 | 0.0061516 | 0.97235 | -0.53699 | 0.97227 | -0.53856 | 1.69
106 | 0.002427 | 0.00060634 | -0.0024261 | -0.00060805 | 9.1225e-07 | -1.7082e-06 | 0.0036701 | 0.0036709 | 0.0036709 | 0.98385 | -0.31111 | 0.98345 | -0.31901 | 1.0085
107 | -0.002427 | -0.00060634 | 0.0024272 | 0.00060606 | 1.4962e-07 | -2.8045e-07 | 0.0036701 | 0.0036699 | 0.0036701 | 0.98385 | -0.31111 | 0.98392 | -0.30981 | 1.0083
108 | -0.003324 | -0.00083082 | 0.0033258 | 0.00082956 | 1.7958e-06 | -1.2601e-06 | 0.0050262 | 0.0050254 | 0.0050262 | 0.98392 | -0.30981 | 0.9845 | -0.29844 | 1.3808
109 | -0.00072974 | -0.00018017 | 0.00072974 | 0.00018011 | 2.2251e-09 | -5.7307e-08 | 0.0011176 | 0.0011176 | 0.0011176 | 0.97074 | -0.57259 | 0.97074 | -0.57253 | 0.30704
110 | 0.00067239 | 0.0001658 | -0.00067236 | -0.00016694 | 3.7652e-08 | -1.146e-06 | 0.0010297 | 0.0010301 | 0.0010301 | 0.97074 | -0.57259 | 0.97068 | -0.57378 | 0.283
111 | -0.00077648 | -0.00019183 | 0.00077649 | 0.00019179 | 1.4816e-09 | -3.3589e-08 | 0.0011892 | 0.0011892 | 0.0011892 | 0.97074 | -0.57253 | 0.97074 | -0.57249 | 0.32672
112 | -0.00084744 | -0.00020958 | 0.00084746 | 0.00020905 | 2.7983e-08 | -5.2977e-07 | 0.001298 | 0.0012978 | 0.001298 | 0.97074 | -0.57249 | 0.97078 | -0.57179 | 0.35659
113 | -0.0015821 | -0.00039316 | 0.0015821 | 0.00039314 | 4.1757e-09 | -2.0762e-08 | 0.0024238 | 0.0024238 | 0.0024238 | 0.97078 | -0.57179 | 0.97078 | -0.57173 | 0.66589
114 | -0.0017206 | -0.00042785 | 0.0017207 | 0.00042738 | 1.162e-07 | -4.7702e-07 | 0.0026361 | 0.0026359 | 0.0026361 | 0.97078 | -0.57173 | 0.97085 | -0.57031 | 0.72421
115 | -0.0017992 | -0.00044687 | 0.0017994 | 0.00044612 | 2.0301e-07 | -7.5151e-07 | 0.0027562 | 0.0027559 | 0.0027562 | 0.97085 | -0.57031 | 0.97097 | -0.56792 | 0.7572
116 | 7.8531e-05 | 1.9495e-05 | -7.8531e-05 | -1.9682e-05 | 8.2006e-11 | -1.8672e-07 | 0.0001203 | 0.00012036 | 0.00012036 | 0.97085 | -0.57031 | 0.97085 | -0.57033 | 0.033067
117 | -0.0019721 | -0.00048938 | 0.0019723 | 0.00048286 | 2.0406e-07 | -6.5152e-06 | 0.0030204 | 0.0030181 | 0.0030204 | 0.97097 | -0.56792 | 0.97108 | -0.56572 | 0.2766
118 | 0.00023251 | 5.7748e-05 | -0.00023251 | -5.8256e-05 | 1.9603e-09 | -5.085e-07 | 0.00035609 | 0.00035627 | 0.00035627 | 0.97108 | -0.56572 | 0.97107 | -0.5659 | 0.097877
119 | 7.8344e-05 | 1.962e-05 | -7.8344e-05 | -1.9635e-05 | 6.5461e-12 | -1.4985e-08 | 0.00012004 | 0.00012005 | 0.00012005 | 0.97107 | -0.5659 | 0.97107 | -0.5659 | 0.032981
120 | -0.092902 | -0.023321 | 0.092986 | 0.023373 | 8.4423e-05 | 5.1695e-05 | 0.14027 | 0.14027 | 0.14027 | 0.98562 | -0.27644 | 0.9866 | -0.25741 | 9.6339
121 | 0.0023149 | 0.00058 | -0.0023148 | -0.00058015 | 7.2479e-08 | -1.5163e-07 | 0.0035108 | 0.0035109 | 0.0035109 | 0.98112 | -0.36444 | 0.98109 | -0.3651 | 0.96454
122 | 0.0017667 | 0.00044217 | -0.0017665 | -0.00044274 | 1.4041e-07 | -5.6996e-07 | 0.002678 | 0.0026782 | 0.0026782 | 0.98157 | -0.35562 | 0.98149 | -0.35729 | 0.73578
123 | 0.032893 | 0.0082581 | -0.03288 | -0.0082505 | 1.2092e-05 | 7.5716e-06 | 0.049614 | 0.049614 | 0.049614 | 0.9866 | -0.25741 | 0.98621 | -0.26512 | 13.6303
124 | 0.010874 | 0.0027244 | -0.010871 | -0.0027228 | 2.9835e-06 | 1.5318e-06 | 0.016401 | 0.016401 | 0.016401 | 0.9866 | -0.25741 | 0.98631 | -0.26317 | 4.5057
125 | -0.13675 | -0.034355 | 0.13681 | 0.034389 | 5.4258e-05 | 3.403e-05 | 0.20628 | 0.20628 | 0.20628 | 0.9866 | -0.25741 | 0.98703 | -0.2491 | 14.1678
126 | -0.0040165 | -0.0010066 | 0.0040168 | 0.0010066 | 2.2831e-07 | -5.5491e-08 | 0.0061335 | 0.0061335 | 0.0061335 | 0.97443 | -0.49746 | 0.97449 | -0.49626 | 1.685
127 | -0.004897 | -0.0012272 | 0.0049012 | 0.0012274 | 4.2017e-06 | 1.8995e-07 | 0.0074776 | 0.0074767 | 0.0074776 | 0.97449 | -0.49626 | 0.9754 | -0.47825 | 2.0543
128 | -0.0049012 | -0.0012274 | 0.0049018 | 0.0012274 | 6.0548e-07 | 2.6937e-08 | 0.0074767 | 0.0074766 | 0.0074767 | 0.9754 | -0.47825 | 0.97553 | -0.47566 | 2.054
129 | 0.023743 | 0.0058145 | -0.023742 | -0.0058141 | 1.5135e-06 | 3.5234e-07 | 0.036168 | 0.036168 | 0.036168 | 0.97553 | -0.47566 | 0.97546 | -0.47702 | 2.4841
130 | -0.0062863 | -0.0015755 | 0.006288 | 0.001576 | 1.7059e-06 | 4.6868e-07 | 0.0095687 | 0.0095685 | 0.0095687 | 0.97758 | -0.43205 | 0.97787 | -0.42635 | 2.6288
131 | -0.024639 | -0.006182 | 0.024652 | 0.00619 | 1.2904e-05 | 7.9512e-06 | 0.037496 | 0.037495 | 0.037496 | 0.97787 | -0.42635 | 0.97843 | -0.41537 | 10.301
132 | 0.018351 | 0.0046061 | -0.018345 | -0.0046027 | 5.605e-06 | 3.3468e-06 | 0.027927 | 0.027927 | 0.027927 | 0.97787 | -0.42635 | 0.97754 | -0.43276 | 7.6723
133 | 0.0015045 | 0.00037689 | -0.0015045 | -0.00037706 | 2.884e-08 | -1.6604e-07 | 0.002288 | 0.0022881 | 0.0022881 | 0.97843 | -0.41537 | 0.97841 | -0.41578 | 0.6286
134 | -0.048765 | -0.012235 | 0.048812 | 0.012265 | 4.6801e-05 | 2.9667e-05 | 0.074168 | 0.074168 | 0.074168 | 0.97843 | -0.41537 | 0.97945 | -0.39527 | 20.3759
135 | 0.022609 | 0.005668 | -0.022606 | -0.005666 | 3.2848e-06 | 2.0093e-06 | 0.034385 | 0.034385 | 0.034385 | 0.97843 | -0.41537 | 0.97827 | -0.41842 | 9.4464
136 | 0.016967 | 0.0042572 | -0.016966 | -0.0042567 | 7.9994e-07 | 4.7188e-07 | 0.025829 | 0.025829 | 0.025829 | 0.97754 | -0.43276 | 0.97749 | -0.43375 | 7.0958
137 | 0.02309 | 0.0056509 | -0.023061 | -0.0056447 | 2.9539e-05 | 6.208e-06 | 0.035175 | 0.035179 | 0.035179 | 0.97546 | -0.47702 | 0.9741 | -0.50437 | 2.4161
138 | 0.022523 | 0.00551 | -0.02252 | -0.0055093 | 3.6562e-06 | 6.9524e-07 | 0.034358 | 0.034359 | 0.034359 | 0.9741 | -0.50437 | 0.97393 | -0.50784 | 2.3598
139 | 0.24461 | 0.06232 | -0.24426 | -0.062098 | 0.00034929 | 0.00022208 | 0.36434 | 0.36434 | 0.36434 | 1 | 0 | 0.99844 | -0.029643 | 25.0231
140 | 0.0022874 | 0.00057294 | -0.0022872 | -0.00057324 | 1.2466e-07 | -2.9666e-07 | 0.0034035 | 0.0034037 | 0.0034037 | 1 | 0 | 0.99994 | -0.0011443 | 0.93507
141 | 0.18273 | 0.046907 | -0.18075 | -0.045643 | 0.001981 | 0.0012642 | 0.2723 | 0.2723 | 0.2723 | 1 | 0 | 0.98817 | -0.22604 | 37.4042
142 | 0.0054681 | 0.0013701 | -0.0054676 | -0.00137 | 4.8574e-07 | 5.5812e-08 | 0.0081493 | 0.0081493 | 0.0081493 | 0.99844 | -0.029643 | 0.99834 | -0.031508 | 2.2388
143 | 0.23879 | 0.060728 | -0.23856 | -0.060581 | 0.00023032 | 0.00014639 | 0.35619 | 0.35619 | 0.35619 | 0.99844 | -0.029643 | 0.99739 | -0.049683 | 24.4635
144 | 0.11756 | 0.029609 | -0.11742 | -0.029523 | 0.00013481 | 8.6134e-05 | 0.17708 | 0.17708 | 0.17708 | 0.98817 | -0.22604 | 0.98693 | -0.25005 | 48.6476
145 | 0.063191 | 0.016034 | -0.063132 | -0.015996 | 5.9138e-05 | 3.7625e-05 | 0.095226 | 0.095226 | 0.095226 | 0.98817 | -0.22604 | 0.98716 | -0.24552 | 26.1609
146 | 0.031984 | 0.0080257 | -0.031978 | -0.008022 | 5.991e-06 | 3.7468e-06 | 0.048261 | 0.048261 | 0.048261 | 0.98621 | -0.26512 | 0.986 | -0.26905 | 13.2586
147 | 0.0025253 | 0.00063148 | -0.0025246 | -0.00063272 | 7.2758e-07 | -1.2399e-06 | 0.0038094 | 0.00381 | 0.00381 | 0.98631 | -0.26317 | 0.986 | -0.26922 | 1.0467
148 | 0.0083461 | 0.0020913 | -0.008346 | -0.0020913 | 1.5006e-07 | 6.3827e-08 | 0.012591 | 0.012591 | 0.012591 | 0.98631 | -0.26317 | 0.98629 | -0.26355 | 3.4592
149 | -0.13803 | -0.034697 | 0.13822 | 0.034812 | 0.00018376 | 0.00011529 | 0.20813 | 0.20813 | 0.20813 | 0.98703 | -0.2491 | 0.98846 | -0.22125 | 14.2948
150 | 0.0012059 | 0.00030203 | -0.0012059 | -0.00030222 | 1.9291e-08 | -1.8853e-07 | 0.0018135 | 0.0018136 | 0.0018136 | 0.98942 | -0.20266 | 0.98941 | -0.20299 | 0.49823
151 | -0.14349 | -0.03618 | 0.14367 | 0.036293 | 0.00017983 | 0.00011297 | 0.21587 | 0.21587 | 0.21587 | 0.98942 | -0.20266 | 0.99078 | -0.17651 | 14.8265
152 | 0.14228 | 0.035878 | -0.14223 | -0.035848 | 4.8568e-05 | 3.0503e-05 | 0.21406 | 0.21406 | 0.21406 | 0.98942 | -0.20266 | 0.98906 | -0.20979 | 14.702
153 | -0.14725 | -0.037191 | 0.14745 | 0.037318 | 0.00020275 | 0.00012748 | 0.22125 | 0.22125 | 0.22125 | 0.99078 | -0.17651 | 0.99227 | -0.14782 | 15.196
154 | 0.13951 | 0.035164 | -0.13943 | -0.035116 | 7.6466e-05 | 4.7989e-05 | 0.20995 | 0.20996 | 0.20996 | 0.98906 | -0.20979 | 0.98846 | -0.22125 | 14.42
155 | -0.0033258 | -0.00082956 | 0.0033258 | 0.00082953 | 4.0647e-08 | -2.8563e-08 | 0.0050254 | 0.0050253 | 0.0050254 | 0.9845 | -0.29844 | 0.98451 | -0.29818 | 1.3806
156 | -0.0079277 | -0.0019826 | 0.0079295 | 0.0019833 | 1.8501e-06 | 7.4686e-07 | 0.011981 | 0.01198 | 0.011981 | 0.98451 | -0.29818 | 0.98476 | -0.29328 | 3.2914
157 | 0.0046019 | 0.0011531 | -0.004601 | -0.0011531 | 8.7888e-07 | -5.3427e-08 | 0.0069553 | 0.0069555 | 0.0069555 | 0.98451 | -0.29818 | 0.98431 | -0.30219 | 1.9108
158 | -0.008709 | -0.0021787 | 0.008709 | 0.0021787 | 1.369e-08 | 6.0794e-09 | 0.013158 | 0.013158 | 0.013158 | 0.98476 | -0.29328 | 0.98476 | -0.29324 | 3.6149
159 | 0.0074361 | 0.0018632 | -0.0074358 | -0.0018631 | 2.5259e-07 | 9.3361e-08 | 0.011219 | 0.011219 | 0.011219 | 0.98629 | -0.26355 | 0.98625 | -0.26426 | 3.0821
160 | 0.014757 | 0.003699 | -0.014754 | -0.0036972 | 3.0215e-06 | 1.733e-06 | 0.022447 | 0.022447 | 0.022447 | 0.97827 | -0.41842 | 0.97805 | -0.42272 | 6.1667
161 | 0.0078485 | 0.001967 | -0.0078471 | -0.0019665 | 1.3975e-06 | 5.6618e-07 | 0.011938 | 0.011938 | 0.011938 | 0.97827 | -0.41842 | 0.97808 | -0.42216 | 3.2797
162 | 0.0075843 | 0.0019003 | -0.007584 | -0.0019002 | 2.5963e-07 | 1.0091e-07 | 0.011539 | 0.011539 | 0.011539 | 0.97805 | -0.42272 | 0.97802 | -0.42344 | 3.17
163 | 0.0056437 | 0.0014143 | -0.0056427 | -0.0014141 | 1.059e-06 | 1.971e-07 | 0.0085861 | 0.0085863 | 0.0085863 | 0.97808 | -0.42216 | 0.97788 | -0.4261 | 2.3589
164 | -0.050317 | -0.012642 | 0.050379 | 0.012681 | 6.2305e-05 | 3.9517e-05 | 0.076454 | 0.076454 | 0.076454 | 0.97945 | -0.39527 | 0.98078 | -0.36936 | 21.0038
165 | 0.016112 | 0.0040428 | -0.0161 | -0.0040356 | 1.231e-05 | 7.1953e-06 | 0.024529 | 0.024529 | 0.024529 | 0.97749 | -0.43375 | 0.97667 | -0.44978 | 6.7388
166 | -0.0094884 | -0.002374 | 0.00949 | 0.0023748 | 1.5887e-06 | 7.5448e-07 | 0.014336 | 0.014336 | 0.014336 | 0.98476 | -0.29324 | 0.98494 | -0.28972 | 3.9384
167 | -0.14957 | -0.037848 | 0.14963 | 0.037886 | 6.067e-05 | 3.8165e-05 | 0.22442 | 0.22442 | 0.22442 | 0.99227 | -0.14782 | 0.99271 | -0.13937 | 15.4134
168 | 0.031081 | 0.0077972 | -0.031075 | -0.0077935 | 6.0054e-06 | 3.7506e-06 | 0.046908 | 0.046908 | 0.046908 | 0.986 | -0.26905 | 0.9858 | -0.2731 | 12.8868
169 | 0.0064867 | 0.0016253 | -0.0064858 | -0.001625 | 9.0535e-07 | 2.5782e-07 | 0.0097867 | 0.0097869 | 0.0097869 | 0.98625 | -0.26426 | 0.9861 | -0.26719 | 2.6887
170 | -0.029239 | -0.0073249 | 0.029263 | 0.0073393 | 2.317e-05 | 1.4425e-05 | 0.044173 | 0.044173 | 0.044173 | 0.98494 | -0.28972 | 0.9858 | -0.2731 | 12.1354
171 | 0.012473 | 0.0031281 | -0.01247 | -0.0031263 | 3.2684e-06 | 1.7795e-06 | 0.018845 | 0.018845 | 0.018845 | 0.98494 | -0.28972 | 0.98466 | -0.29522 | 5.1772
172 | 0.0072761 | 0.001822 | -0.0072721 | -0.0018206 | 3.9825e-06 | 1.4308e-06 | 0.010992 | 0.010992 | 0.010992 | 0.98494 | -0.28972 | 0.98436 | -0.30123 | 3.0199
173 | 0.0014999 | 0.00037542 | -0.0014998 | -0.00037589 | 7.7571e-08 | -4.655e-07 | 0.0022632 | 0.0022633 | 0.0022633 | 0.9861 | -0.26719 | 0.98604 | -0.26828 | 0.6218
174 | -0.00044847 | -0.0001124 | 0.00044847 | 0.00011232 | 1.0564e-09 | -7.7537e-08 | 0.00067731 | 0.00067728 | 0.00067731 | 0.98528 | -0.28187 | 0.98528 | -0.28182 | 0.18607
175 | -0.0025837 | -0.00064746 | 0.0025838 | 0.00064724 | 1.3338e-07 | -2.1218e-07 | 0.003902 | 0.0039019 | 0.003902 | 0.98528 | -0.28182 | 0.98533 | -0.28074 | 1.072
176 | 0.0035162 | 0.00088098 | -0.0035161 | -0.00088105 | 1.0133e-07 | -6.3783e-08 | 0.0052408 | 0.0052409 | 0.0052409 | 0.99834 | -0.031508 | 0.99831 | -0.032113 | 1.4398
177 | 0.23348 | 0.059309 | -0.23334 | -0.059216 | 0.00014667 | 9.3199e-05 | 0.34862 | 0.34862 | 0.34862 | 0.99739 | -0.049683 | 0.9967 | -0.062742 | 23.9435
178 | 0.0046951 | 0.0011762 | -0.0046946 | -0.0011763 | 4.1159e-07 | -1.4759e-08 | 0.0070895 | 0.0070896 | 0.0070896 | 0.98543 | -0.2789 | 0.98533 | -0.28074 | 1.9477
179 | -0.0046951 | -0.0011762 | 0.0046953 | 0.0011762 | 2.301e-07 | -8.2778e-09 | 0.0070895 | 0.0070894 | 0.0070895 | 0.98543 | -0.2789 | 0.98548 | -0.27787 | 1.9477
180 | 0.051311 | 0.013001 | -0.051226 | -0.012947 | 8.4084e-05 | 5.334e-05 | 0.077526 | 0.077526 | 0.077526 | 0.98548 | -0.27787 | 0.98372 | -0.31204 | 21.2985
181 | -0.056006 | -0.014177 | 0.056093 | 0.014232 | 8.7114e-05 | 5.5339e-05 | 0.084616 | 0.084616 | 0.084616 | 0.98548 | -0.27787 | 0.98716 | -0.24552 | 23.2461
182 | 0.11742 | 0.029523 | -0.11725 | -0.029413 | 0.00017123 | 0.0001094 | 0.17708 | 0.17708 | 0.17708 | 0.98693 | -0.25005 | 0.98536 | -0.28064 | 48.6477
183 | 0.051226 | 0.012947 | -0.051086 | -0.012858 | 0.00014037 | 8.9049e-05 | 0.077526 | 0.077527 | 0.077527 | 0.98372 | -0.31204 | 0.98078 | -0.36936 | 21.2986
184 | 0.0041191 | 0.0010298 | -0.0041183 | -0.0010301 | 8.8978e-07 | -2.2795e-07 | 0.0061875 | 0.0061878 | 0.0061878 | 0.99046 | -0.18301 | 0.99023 | -0.18755 | 1.6999
185 | -0.0065763 | -0.0016457 | 0.0065773 | 0.0016459 | 9.5411e-07 | 2.7505e-07 | 0.009879 | 0.0098789 | 0.009879 | 0.99046 | -0.18301 | 0.99062 | -0.17996 | 2.714
186 | 0.0037362 | 0.0009343 | -0.0037343 | -0.00093515 | 1.8991e-06 | -8.5046e-07 | 0.0056136 | 0.0056144 | 0.0056144 | 0.99023 | -0.18755 | 0.98968 | -0.19824 | 1.5424
187 | -0.011312 | -0.0028303 | 0.011315 | 0.0028316 | 2.472e-06 | 1.288e-06 | 0.016991 | 0.016991 | 0.016991 | 0.99062 | -0.17996 | 0.99085 | -0.17537 | 4.6678
188 | 0.0047352 | 0.0011844 | -0.0047339 | -0.0011844 | 1.2628e-06 | -4.8657e-08 | 0.0071119 | 0.0071123 | 0.0071123 | 0.99062 | -0.17996 | 0.99033 | -0.18557 | 1.9539
189 | 0.0023826 | 0.00059637 | -0.0023825 | -0.00059649 | 5.7731e-08 | -1.1723e-07 | 0.003582 | 0.003582 | 0.003582 | 0.98968 | -0.19824 | 0.98965 | -0.19875 | 0.98408
190 | -0.011947 | -0.00299 | 0.01195 | 0.0029914 | 2.5845e-06 | 1.3782e-06 | 0.01794 | 0.01794 | 0.01794 | 0.99085 | -0.17537 | 0.99109 | -0.17082 | 4.9286
191 | 0.0042545 | 0.0010642 | -0.004254 | -0.0010644 | 5.1854e-07 | -1.0354e-07 | 0.0063919 | 0.0063921 | 0.0063921 | 0.99033 | -0.18557 | 0.9902 | -0.18813 | 1.7561
192 | 0.00084956 | 0.00021273 | -0.00084955 | -0.00021289 | 7.7758e-09 | -1.5832e-07 | 0.0012773 | 0.0012774 | 0.0012774 | 0.98965 | -0.19875 | 0.98964 | -0.19894 | 0.35092
193 | 0.0015329 | 0.00038376 | -0.0015329 | -0.00038417 | 7.0944e-08 | -4.1217e-07 | 0.0023047 | 0.0023049 | 0.0023049 | 0.98965 | -0.19875 | 0.9896 | -0.19972 | 0.63321
194 | -0.012887 | -0.0032263 | 0.012888 | 0.0032268 | 1.0127e-06 | 5.5514e-07 | 0.019347 | 0.019347 | 0.019347 | 0.99109 | -0.17082 | 0.99117 | -0.16917 | 5.3151
195 | 0.0016292 | 0.00040732 | -0.0016291 | -0.00040743 | 2.225e-08 | -1.1313e-07 | 0.0024479 | 0.0024479 | 0.0024479 | 0.9902 | -0.18813 | 0.99018 | -0.18842 | 0.6725
196 | 0.0026249 | 0.00065704 | -0.0026245 | -0.00065753 | 3.136e-07 | -4.9064e-07 | 0.0039442 | 0.0039445 | 0.0039445 | 0.9902 | -0.18813 | 0.99007 | -0.19064 | 1.0836
197 | 0.00030832 | 7.7244e-05 | -0.00030832 | -7.7273e-05 | 1.8392e-10 | -2.9201e-08 | 0.00046358 | 0.00046359 | 0.00046359 | 0.98964 | -0.19894 | 0.98964 | -0.19895 | 0.12736
198 | -0.013229 | -0.0033123 | 0.013229 | 0.0033125 | 3.3543e-07 | 1.8545e-07 | 0.019859 | 0.019859 | 0.019859 | 0.99117 | -0.16917 | 0.9912 | -0.16864 | 5.4559
199 | 0.0012597 | 0.00031483 | -0.0012596 | -0.00031551 | 7.6072e-08 | -6.7957e-07 | 0.0018927 | 0.001893 | 0.001893 | 0.99018 | -0.18842 | 0.99012 | -0.18969 | 0.52004
200 | 0.0020705 | 0.00051867 | -0.0020704 | -0.00051889 | 7.7719e-08 | -2.2549e-07 | 0.0031117 | 0.0031118 | 0.0031118 | 0.99007 | -0.19064 | 0.99003 | -0.19143 | 0.8549
201 | -0.013229 | -0.0033125 | 0.013232 | 0.0033141 | 2.7986e-06 | 1.5471e-06 | 0.019859 | 0.019859 | 0.019859 | 0.9912 | -0.16864 | 0.99143 | -0.1642 | 5.4559
202 | 0.00028851 | 7.2134e-05 | -0.00028851 | -7.2307e-05 | 9.5221e-10 | -1.7312e-07 | 0.00043353 | 0.00043359 | 0.00043359 | 0.99012 | -0.18969 | 0.99011 | -0.18976 | 0.11912
203 | 0.0094725 | 0.002374 | -0.0094723 | -0.0023739 | 2.5053e-07 | 1.1782e-07 | 0.014226 | 0.014226 | 0.014226 | 0.99084 | -0.17557 | 0.99081 | -0.17612 | 3.9081
204 | -0.012005 | -0.0030087 | 0.012009 | 0.0030109 | 4.1853e-06 | 2.2361e-06 | 0.018028 | 0.018028 | 0.018028 | 0.99084 | -0.17557 | 0.99122 | -0.16825 | 4.9528
205 | 0.0073458 | 0.001841 | -0.0073458 | -0.001841 | 7.7059e-09 | 2.7574e-09 | 0.011032 | 0.011032 | 0.011032 | 0.99081 | -0.17612 | 0.99081 | -0.17614 | 3.0308
206 | -0.024303 | -0.0060923 | 0.024306 | 0.0060945 | 3.6717e-06 | 2.2551e-06 | 0.036484 | 0.036484 | 0.036484 | 0.99122 | -0.16825 | 0.99138 | -0.16508 | 10.023
207 | 0.012294 | 0.0030814 | -0.012293 | -0.003081 | 6.4962e-07 | 3.502e-07 | 0.018456 | 0.018456 | 0.018456 | 0.99122 | -0.16825 | 0.99116 | -0.16936 | 5.0702
208 | 0.0052209 | 0.0013084 | -0.0052209 | -0.0013084 | 3.732e-09 | 3.0421e-10 | 0.0078408 | 0.0078408 | 0.0078408 | 0.99081 | -0.17614 | 0.99081 | -0.17616 | 2.1541
209 | -0.031483 | -0.0078929 | 0.031494 | 0.0079002 | 1.1697e-05 | 7.3061e-06 | 0.047255 | 0.047255 | 0.047255 | 0.99138 | -0.16508 | 0.99179 | -0.15729 | 12.982
210 | 0.0071762 | 0.0017984 | -0.0071757 | -0.0017982 | 4.8761e-07 | 1.6756e-07 | 0.010771 | 0.010771 | 0.010771 | 0.99138 | -0.16508 | 0.99131 | -0.16651 | 2.9591
211 | 0.0097077 | 0.002433 | -0.0097056 | -0.002432 | 2.1353e-06 | 1.0212e-06 | 0.014574 | 0.014574 | 0.014574 | 0.99116 | -0.16936 | 0.99092 | -0.17398 | 4.0039
212 | 0.0030945 | 0.00077549 | -0.0030944 | -0.00077553 | 4.1932e-08 | -3.9845e-08 | 0.0046473 | 0.0046473 | 0.0046473 | 0.99081 | -0.17616 | 0.9908 | -0.17644 | 1.2767
213 | -0.03667 | -0.0091974 | 0.036687 | 0.0092082 | 1.7218e-05 | 1.0824e-05 | 0.05502 | 0.05502 | 0.05502 | 0.99179 | -0.15729 | 0.99229 | -0.14744 | 15.1154
214 | 0.0047043 | 0.0011788 | -0.0047039 | -0.0011788 | 3.0904e-07 | -1.5277e-08 | 0.0070613 | 0.0070614 | 0.0070614 | 0.99131 | -0.16651 | 0.99124 | -0.16789 | 1.9399
215 | 0.0029048 | 0.00072771 | -0.0029046 | -0.00072784 | 1.1305e-07 | -1.3176e-07 | 0.0043618 | 0.0043619 | 0.0043619 | 0.99092 | -0.17398 | 0.99088 | -0.1748 | 1.1983
216 | 0.0068008 | 0.0017043 | -0.0068001 | -0.0017041 | 7.419e-07 | 2.3047e-07 | 0.010212 | 0.010212 | 0.010212 | 0.99092 | -0.17398 | 0.99081 | -0.17627 | 2.8056
217 | 0.02429 | 0.0060918 | -0.024281 | -0.0060862 | 9.0497e-06 | 5.557e-06 | 0.036427 | 0.036427 | 0.036427 | 0.99229 | -0.14744 | 0.99189 | -0.15526 | 10.0073
218 | 0.0082026 | 0.0020559 | -0.0082015 | -0.0020555 | 1.0977e-06 | 4.5266e-07 | 0.0123 | 0.012301 | 0.012301 | 0.99229 | -0.14744 | 0.99215 | -0.15025 | 3.3793
219 | -0.06918 | -0.017356 | 0.069223 | 0.017383 | 4.3022e-05 | 2.6983e-05 | 0.10375 | 0.10375 | 0.10375 | 0.99229 | -0.14744 | 0.99297 | -0.13441 | 14.251
220 | 0.0029349 | 0.00073544 | -0.0029348 | -0.00073553 | 8.0285e-08 | -9.079e-08 | 0.0044057 | 0.0044058 | 0.0044058 | 0.99124 | -0.16789 | 0.99121 | -0.16846 | 1.2104
221 | 0.00080228 | 0.00020093 | -0.00080227 | -0.000201 | 3.0647e-09 | -7.0566e-08 | 0.0012047 | 0.0012048 | 0.0012048 | 0.99088 | -0.1748 | 0.99088 | -0.17488 | 0.33098
222 | 0.0064912 | 0.0016267 | -0.0064909 | -0.0016266 | 3.0493e-07 | 8.4961e-08 | 0.0097485 | 0.0097486 | 0.0097486 | 0.99081 | -0.17627 | 0.99076 | -0.17725 | 2.6782
223 | 0.021656 | 0.0054283 | -0.021653 | -0.0054266 | 2.6845e-06 | 1.6306e-06 | 0.032488 | 0.032488 | 0.032488 | 0.99189 | -0.15526 | 0.99176 | -0.15786 | 8.9254
224 | 0.005345 | 0.0013396 | -0.0053448 | -0.0013395 | 1.5064e-07 | 1.5685e-08 | 0.0080164 | 0.0080164 | 0.0080164 | 0.99215 | -0.15025 | 0.99212 | -0.15084 | 2.2023
225 | -0.071887 | -0.01805 | 0.071899 | 0.018058 | 1.2526e-05 | 7.6817e-06 | 0.10774 | 0.10774 | 0.10774 | 0.99297 | -0.13441 | 0.99316 | -0.13075 | 9.8662
226 | 0.00050328 | 0.00012607 | -0.00050328 | -0.00012613 | 1.0856e-09 | -6.4586e-08 | 0.00075576 | 0.00075579 | 0.00075579 | 0.99088 | -0.17488 | 0.99088 | -0.17492 | 0.20763
227 | 0.00060062 | 0.00015035 | -0.00060062 | -0.00015053 | 4.1937e-09 | -1.7431e-07 | 0.00090201 | 0.00090207 | 0.00090207 | 0.99076 | -0.17725 | 0.99075 | -0.1774 | 0.24782
228 | -0.0049781 | -0.0012457 | 0.0049782 | 0.0012457 | 6.8877e-08 | 2.8738e-09 | 0.007526 | 0.0075259 | 0.007526 | 0.98417 | -0.30485 | 0.98418 | -0.30456 | 2.0676
229 | 0.0031605 | 0.0007902 | -0.0031604 | -0.00079028 | 9.7272e-08 | -8.2133e-08 | 0.0047778 | 0.0047779 | 0.0047779 | 0.98417 | -0.30485 | 0.98414 | -0.30549 | 1.3126
230 | -0.0055332 | -0.0013849 | 0.0055338 | 0.0013849 | 5.3406e-07 | 8.3142e-08 | 0.0083652 | 0.0083651 | 0.0083652 | 0.98418 | -0.30456 | 0.98429 | -0.30253 | 2.2981
231 | 0.0014698 | 0.00036657 | -0.0014697 | -0.00036717 | 9.6114e-08 | -5.982e-07 | 0.0022216 | 0.0022219 | 0.0022219 | 0.98414 | -0.30549 | 0.98407 | -0.30687 | 0.6104
232 | -0.0058488 | -0.0014639 | 0.0058491 | 0.001464 | 3.6271e-07 | 7.485e-08 | 0.0088413 | 0.0088412 | 0.0088413 | 0.98429 | -0.30253 | 0.98436 | -0.30123 | 2.4289
233 | 0.0011747 | 0.00029324 | -0.0011747 | -0.00029353 | 2.8646e-08 | -2.8938e-07 | 0.0017758 | 0.0017759 | 0.0017759 | 0.98407 | -0.30687 | 0.98404 | -0.30738 | 0.4879
234 | 0.00087928 | 0.0002195 | -0.00087926 | -0.00021982 | 1.7002e-08 | -3.1504e-07 | 0.0013293 | 0.0013294 | 0.0013294 | 0.98404 | -0.30738 | 0.98402 | -0.30779 | 0.36522
235 | 0.00058212 | 0.00014535 | -0.00058212 | -0.00014562 | 6.227e-09 | -2.6833e-07 | 0.00088008 | 0.00088018 | 0.00088018 | 0.98402 | -0.30779 | 0.98401 | -0.30802 | 0.24181
236 | 0.01247 | 0.0031263 | -0.012468 | -0.0031254 | 1.728e-06 | 9.4089e-07 | 0.018845 | 0.018845 | 0.018845 | 0.98466 | -0.29522 | 0.98451 | -0.29813 | 5.1773
237 | 0.00029098 | 7.265e-05 | -0.00029098 | -7.2926e-05 | 1.586e-09 | -2.7652e-07 | 0.00043992 | 0.00044002 | 0.00044002 | 0.98401 | -0.30802 | 0.984 | -0.30813 | 0.12088
238 | 0.0071051 | 0.0017789 | -0.0071048 | -0.0017788 | 2.5164e-07 | 9.0732e-08 | 0.010876 | 0.010876 | 0.010876 | 0.97204 | -0.54321 | 0.972 | -0.54396 | 2.9879
239 | 0.0033424 | 0.00083597 | -0.0033422 | -0.00083609 | 1.9802e-07 | -1.2357e-07 | 0.0051148 | 0.0051149 | 0.0051149 | 0.97227 | -0.53856 | 0.97221 | -0.5398 | 1.4052
240 | 0.0022168 | 0.00055513 | -0.0022167 | -0.00055533 | 8.6755e-08 | -1.9347e-07 | 0.0033935 | 0.0033935 | 0.0033935 | 0.972 | -0.54396 | 0.97196 | -0.54478 | 0.93229
241 | 0.0048881 | 0.0012237 | -0.0048878 | -0.0012237 | 2.7822e-07 | 1.3825e-08 | 0.0074826 | 0.0074826 | 0.0074826 | 0.972 | -0.54396 | 0.97194 | -0.54515 | 2.0557
242 | 0.0015603 | 0.00039081 | -0.0015603 | -0.00039086 | 9.1952e-09 | -4.738e-08 | 0.0023886 | 0.0023886 | 0.0023886 | 0.97196 | -0.54478 | 0.97195 | -0.5449 | 0.65621
243 | 0.0042356 | 0.0010602 | -0.0042344 | -0.0010604 | 1.2034e-06 | -1.7542e-07 | 0.0064841 | 0.0064844 | 0.0064844 | 0.97194 | -0.54515 | 0.97164 | -0.55112 | 1.7814
244 | -0.22735 | -0.05745 | 0.22749 | 0.057538 | 0.00013822 | 8.7804e-05 | 0.3407 | 0.3407 | 0.3407 | 0.99344 | -0.12533 | 0.9941 | -0.11265 | 23.3998
245 | 0.22451 | 0.056737 | -0.22445 | -0.0567 | 5.8392e-05 | 3.7086e-05 | 0.33644 | 0.33644 | 0.33644 | 0.99344 | -0.12533 | 0.99316 | -0.13075 | 23.1073
246 | -0.22887 | -0.057883 | 0.22901 | 0.057975 | 0.00014516 | 9.2218e-05 | 0.34276 | 0.34276 | 0.34276 | 0.9941 | -0.11265 | 0.99479 | -0.099442 | 23.5415
247 | 0.15255 | 0.038642 | -0.15248 | -0.038602 | 6.3106e-05 | 3.9722e-05 | 0.2287 | 0.2287 | 0.2287 | 0.99316 | -0.13075 | 0.99271 | -0.13937 | 15.7077
248 | -0.23112 | -0.058504 | 0.23153 | 0.058763 | 0.00040796 | 0.00025921 | 0.34592 | 0.34592 | 0.34592 | 0.99479 | -0.099442 | 0.9967 | -0.062742 | 23.7583
249 | 0.019274 | 0.0048302 | -0.019268 | -0.0048267 | 5.8149e-06 | 3.4823e-06 | 0.028918 | 0.028918 | 0.028918 | 0.99176 | -0.15786 | 0.99143 | -0.1642 | 7.9445
250 | 0.073422 | 0.018428 | -0.073386 | -0.018405 | 3.5245e-05 | 2.246e-05 | 0.11089 | 0.11089 | 0.11089 | 0.98536 | -0.28064 | 0.98484 | -0.29071 | 30.463
251 | 0.066248 | 0.016616 | -0.066214 | -0.016595 | 3.3998e-05 | 2.1643e-05 | 0.1001 | 0.1001 | 0.1001 | 0.98484 | -0.29071 | 0.98429 | -0.30148 | 27.5001
252 | -0.0037171 | -0.0009316 | 0.0037173 | 0.00093152 | 1.9776e-07 | -8.0188e-08 | 0.0056566 | 0.0056565 | 0.0056566 | 0.97782 | -0.42722 | 0.97788 | -0.4261 | 1.554
253 | 0.0015993 | 0.00040063 | -0.0015992 | -0.0004008 | 3.1629e-08 | -1.7384e-07 | 0.0023837 | 0.0023837 | 0.0023837 | 0.99831 | -0.032113 | 0.99829 | -0.032528 | 0.65488
254 | 0.012048 | 0.00302 | -0.012047 | -0.0030198 | 2.2872e-07 | 1.2373e-07 | 0.018355 | 0.018355 | 0.018355 | 0.97667 | -0.44978 | 0.97665 | -0.45018 | 5.0426
255 | 0.0042533 | 0.0010656 | -0.0042524 | -0.0010658 | 8.9078e-07 | -1.3759e-07 | 0.0064802 | 0.0064804 | 0.0064804 | 0.97665 | -0.45018 | 0.97643 | -0.45458 | 1.7803
256 | 0.0077939 | 0.0019542 | -0.0077925 | -0.0019536 | 1.473e-06 | 5.9423e-07 | 0.011875 | 0.011875 | 0.011875 | 0.97665 | -0.45018 | 0.97645 | -0.45415 | 3.2624
257 | 0.0070167 | 0.0017592 | -0.0070138 | -0.0017582 | 2.8375e-06 | 9.8858e-07 | 0.010693 | 0.010693 | 0.010693 | 0.97645 | -0.45415 | 0.97602 | -0.46264 | 2.9377
258 | 0.0070138 | 0.0017582 | -0.0070073 | -0.0017559 | 6.5342e-06 | 2.2795e-06 | 0.010693 | 0.010694 | 0.010694 | 0.97602 | -0.46264 | 0.97503 | -0.4822 | 2.9379
259 | 0.0041473 | 0.0010391 | -0.0041467 | -0.0010393 | 6.4782e-07 | -1.2314e-07 | 0.0063293 | 0.0063295 | 0.0063295 | 0.97503 | -0.4822 | 0.97486 | -0.48548 | 1.7389
260 | 0.0052863 | 0.0013243 | -0.0052848 | -0.0013242 | 1.4379e-06 | 1.7663e-07 | 0.0080427 | 0.0080429 | 0.0080429 | 0.97802 | -0.42344 | 0.97772 | -0.42915 | 2.2096
261 | 0.01055 | 0.0026445 | -0.01055 | -0.0026444 | 2.2318e-07 | 1.1307e-07 | 0.015945 | 0.015945 | 0.015945 | 0.98451 | -0.29813 | 0.98449 | -0.29858 | 4.3806
262 | 0.0091032 | 0.0022819 | -0.0091011 | -0.0022809 | 2.1028e-06 | 9.6925e-07 | 0.013759 | 0.013759 | 0.013759 | 0.98449 | -0.29858 | 0.98424 | -0.30343 | 3.78
263 | 0.0068481 | 0.0017163 | -0.0068478 | -0.0017162 | 2.9501e-07 | 9.5535e-08 | 0.010353 | 0.010353 | 0.010353 | 0.98424 | -0.30343 | 0.9842 | -0.30433 | 2.8443
264 | 0.0045948 | 0.0011515 | -0.0045946 | -0.0011515 | 1.4299e-07 | -8.8907e-09 | 0.0069469 | 0.0069469 | 0.0069469 | 0.9842 | -0.30433 | 0.98416 | -0.30498 | 1.9085
265 | 0.0036478 | 0.00091388 | -0.0036477 | -0.00091393 | 1.1385e-07 | -5.0674e-08 | 0.0055515 | 0.0055516 | 0.0055516 | 0.97772 | -0.42915 | 0.97769 | -0.42981 | 1.5252
266 | 0.0020672 | 0.00051781 | -0.0020671 | -0.00051806 | 8.9475e-08 | -2.4502e-07 | 0.0031461 | 0.0031462 | 0.0031462 | 0.97769 | -0.42981 | 0.97765 | -0.43072 | 0.86433
267 | 0.0084336 | 0.0020886 | -0.0084328 | -0.0020906 | 8.1426e-07 | -2.0707e-06 | 0.012895 | 0.012896 | 0.012896 | 0.9725 | -0.53651 | 0.9724 | -0.53855 | 0.88572
268 | 0.0084328 | 0.0020906 | -0.0084294 | -0.002099 | 3.3068e-06 | -8.3999e-06 | 0.012896 | 0.0129 | 0.0129 | 0.9724 | -0.53855 | 0.97198 | -0.54684 | 0.88598
269 | 0.0075142 | 0.0018697 | -0.0075129 | -0.001874 | 1.2918e-06 | -4.3383e-06 | 0.011499 | 0.011501 | 0.011501 | 0.97198 | -0.54684 | 0.9718 | -0.55046 | 0.78987
270 | 0.00045108 | 0.00011272 | -0.00045107 | -0.00011305 | 4.7575e-09 | -3.2649e-07 | 0.00069057 | 0.00069069 | 0.00069069 | 0.9718 | -0.55046 | 0.97179 | -0.55069 | 0.18975
271 | 0.0052908 | 0.0013174 | -0.0052884 | -0.0013207 | 2.3823e-06 | -3.2728e-06 | 0.0080982 | 0.0080999 | 0.0080999 | 0.9718 | -0.55046 | 0.97132 | -0.55995 | 1.1126
272 | 0.0047797 | 0.0011932 | -0.0047788 | -0.0011932 | 8.2003e-07 | 1.986e-08 | 0.0073205 | 0.0073207 | 0.0073207 | 0.97132 | -0.55995 | 0.97114 | -0.56357 | 2.0112
273 | 0.00098523 | 0.00024674 | -0.00098521 | -0.00024692 | 1.2497e-08 | -1.7355e-07 | 0.0015083 | 0.0015083 | 0.0015083 | 0.97195 | -0.5449 | 0.97194 | -0.54517 | 0.41438
274 | 0.0035539 | 0.00088987 | -0.0035534 | -0.00089013 | 5.4811e-07 | -2.6027e-07 | 0.0054424 | 0.0054426 | 0.0054426 | 0.97164 | -0.55112 | 0.97147 | -0.55436 | 1.4952
275 | -0.001625 | -0.00040726 | 0.0016255 | 0.00040503 | 4.7996e-07 | -2.2378e-06 | 0.0024926 | 0.0024917 | 0.0024926 | 0.97007 | -0.58468 | 0.97039 | -0.57847 | 0.68478
276 | -0.0022418 | -0.00055948 | 0.0022418 | 0.00055929 | 8.7334e-08 | -1.8772e-07 | 0.0034367 | 0.0034366 | 0.0034367 | 0.97039 | -0.57847 | 0.97043 | -0.57765 | 0.94415
277 | 0.0008692 | 0.00021742 | -0.00086918 | -0.00021784 | 2.3489e-08 | -4.2066e-07 | 0.0013326 | 0.0013328 | 0.0013328 | 0.97043 | -0.57765 | 0.9704 | -0.57821 | 0.36615
278 | -0.0037458 | -0.00093579 | 0.0037483 | 0.00093489 | 2.5055e-06 | -9.0188e-07 | 0.0057426 | 0.0057417 | 0.0057426 | 0.97043 | -0.57765 | 0.97114 | -0.56357 | 1.5776
279 | -0.00048056 | -0.00012044 | 0.00048056 | 0.00012023 | 3.5278e-09 | -2.1271e-07 | 0.0007361 | 0.00073603 | 0.0007361 | 0.97144 | -0.55496 | 0.97145 | -0.5548 | 0.20223
280 | -0.0013023 | -0.00032617 | 0.0013023 | 0.00032597 | 2.7053e-08 | -2.0717e-07 | 0.0019947 | 0.0019946 | 0.0019947 | 0.97145 | -0.5548 | 0.97147 | -0.55437 | 0.548
281 | -0.0022044 | -0.00055205 | 0.0022044 | 0.00055205 | 2.3568e-10 | -5.2809e-10 | 0.0033764 | 0.0033764 | 0.0033764 | 0.97147 | -0.55437 | 0.97147 | -0.55436 | 0.92758

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43127 | 0.1098

## res_load
| p_mw | q_mvar
0 | 0.00029899 | 7.4934e-05
1 | 0.0020304 | 0.00050887
2 | 0.001812 | 0.00045413
3 | 0.00017035 | 4.2693e-05
4 | 0.00035453 | 8.8853e-05
5 | 0.00024601 | 6.1657e-05
6 | 0.00058859 | 0.00014751
7 | 0.00012676 | 3.177e-05
8 | 0.0004308 | 0.00010797
9 | 0.00029274 | 7.3366e-05
10 | 0.0014218 | 0.00035635
11 | 0.00063552 | 0.00015928
12 | 0.00098188 | 0.00024608
13 | 0.0019957 | 0.00050016
14 | 0.0013033 | 0.00032664
15 | 0.00030018 | 7.5233e-05
16 | 0.00091557 | 0.00022946
17 | 0.00015128 | 3.7915e-05
18 | 0.00047129 | 0.00011812
19 | 5.1287e-05 | 1.2854e-05
20 | 4.2747e-05 | 1.0714e-05
21 | 9.7542e-05 | 2.4446e-05
22 | 0.00019031 | 4.7697e-05
23 | 0.00019048 | 4.7739e-05
24 | 0.00052624 | 0.00013189
25 | 0.0006491 | 0.00016268
26 | 0.00021695 | 5.4374e-05
27 | 0.00025356 | 6.3549e-05
28 | 0.00010601 | 2.6567e-05
29 | 0.00015341 | 3.8449e-05
30 | 0.00036238 | 9.0821e-05
31 | 0.00063556 | 0.00015929
32 | 0.00035124 | 8.8029e-05
33 | 0.00023005 | 5.7657e-05
34 | 0.00059667 | 0.00014954
35 | 6.5895e-05 | 1.6515e-05
36 | 0.00014299 | 3.5836e-05
37 | 0.00015776 | 3.9538e-05
38 | 0.0004169 | 0.00010448
39 | 4.4139e-05 | 1.1062e-05
40 | 8.2495e-05 | 2.0675e-05
41 | 6.2132e-05 | 1.5572e-05
42 | 0.00097255 | 0.00024375
43 | 0.00015169 | 3.8017e-05
44 | 0.0025977 | 0.00065104
45 | 0.00011992 | 3.0054e-05
46 | 0.00040402 | 0.00010126
47 | 0.00012284 | 3.0787e-05
48 | 6.8969e-05 | 1.7285e-05
49 | 0.00016483 | 4.1311e-05
50 | 0.00011925 | 2.9888e-05
51 | 0.00018659 | 4.6763e-05
52 | 0.0002412 | 6.0449e-05
53 | 0.0002683 | 6.7241e-05
54 | 0.00035499 | 8.8968e-05
55 | 0.00042179 | 0.00010571
56 | 0.00037347 | 9.36e-05
57 | 0.0013163 | 0.0003299
58 | 0.00038631 | 9.6818e-05
59 | 0.00073007 | 0.00018297
60 | 0.0071521 | 0.0017925
61 | 0.001329 | 0.00033307
62 | 0.0041485 | 0.0010397
63 | 0.0035145 | 0.00088081
64 | 0.0010791 | 0.00027044
65 | 0.00037203 | 9.324e-05
66 | 0.00050385 | 0.00012628
67 | 0.0036133 | 0.00090559
68 | 0.0024261 | 0.00060805
69 | 0.00089681 | 0.00022476
70 | 5.7341e-05 | 1.4371e-05
71 | 4.6747e-05 | 1.1716e-05
72 | 0.00041294 | 0.00010349
73 | 7.095e-05 | 1.7782e-05
74 | 0.00073462 | 0.00018411
75 | 0.0001385 | 3.4712e-05
76 | 0.00017261 | 4.326e-05
77 | 7.8531e-05 | 1.9682e-05
78 | 0.00014945 | 3.7457e-05
79 | 0.00015416 | 3.8637e-05
80 | 7.8344e-05 | 1.9635e-05
81 | 0.0066542 | 0.0016677
82 | 0.0013702 | 0.00034342
83 | 0.0023148 | 0.00058015
84 | 0.0017665 | 0.00044274
85 | 0.0040165 | 0.0010066
86 | 0.00088025 | 0.00022061
87 | 0.0062863 | 0.0015755
88 | 0.0013786 | 0.00034552
89 | 0.00065133 | 0.00016324
90 | 0.0005374 | 0.00013468
91 | 0.0022872 | 0.00057324
92 | 0.00089683 | 0.00022477
93 | 0.0012263 | 0.00030734
94 | 0.0012059 | 0.00030222
95 | 0.0035827 | 0.00089792
96 | 0.0027291 | 0.00068398
97 | 0.00077942 | 0.00019534
98 | 0.004601 | 0.0011531
99 | 0.0025246 | 0.00063272
100 | 0.0009099 | 0.00022804
101 | 0.0071698 | 0.0017969
102 | 0.0022034 | 0.00055222
103 | 0.0015045 | 0.00037706
104 | 0.0015045 | 0.00037706
105 | 0.00085372 | 0.00021396
106 | 0.00061047 | 0.000153
107 | 0.00077941 | 0.00019534
108 | 0.0021111 | 0.0005291
109 | 0.0012119 | 0.00030373
110 | 0.00089683 | 0.00022477
111 | 0.00094913 | 0.00023787
112 | 0.0049859 | 0.0012496
113 | 0.0014998 | 0.00037589
114 | 0.00044847 | 0.0001124
115 | 0.0021352 | 0.00053513
116 | 0.0019514 | 0.00048907
117 | 0.0050746 | 0.0012718
118 | 0.0021108 | 0.00052902
119 | 0.0070388 | 0.0017641
120 | 0.0024572 | 0.00061583
121 | 0.00038207 | 9.5755e-05
122 | 0.0013517 | 0.00033878
123 | 0.00063216 | 0.00015844
124 | 0.0004794 | 0.00012015
125 | 0.00093715 | 0.00023487
126 | 0.00054122 | 0.00013564
127 | 0.0015329 | 0.00038417
128 | 0.00034124 | 8.5524e-05
129 | 0.00036946 | 9.2596e-05
130 | 0.00055405 | 0.00013886
131 | 0.00030832 | 7.7273e-05
132 | 0.00097109 | 0.00024338
133 | 0.0020704 | 0.00051889
134 | 0.0025321 | 0.00063462
135 | 0.0021265 | 0.00053294
136 | 0.0021249 | 0.00053255
137 | 0.0025855 | 0.00064799
138 | 0.0021264 | 0.00053293
139 | 0.0051758 | 0.0012972
140 | 0.0024714 | 0.0006194
141 | 0.0030944 | 0.00077553
142 | 0.0017691 | 0.00044337
143 | 0.0021024 | 0.0005269
144 | 0.0003089 | 7.7419e-05
145 | 0.0026252 | 0.00065793
146 | 0.0028565 | 0.00071591
147 | 0.0026636 | 0.00066757
148 | 0.0029348 | 0.00073553
149 | 0.00029899 | 7.4934e-05
150 | 0.0058902 | 0.0014762
151 | 0.00028851 | 7.2307e-05
152 | 0.0018176 | 0.00045554
153 | 0.00055507 | 0.00013911
154 | 0.0016906 | 0.00042371
155 | 0.00031499 | 7.8943e-05
156 | 0.00029497 | 7.3927e-05
157 | 0.001423 | 0.00035664
158 | 0.00029538 | 7.4029e-05
159 | 0.00029714 | 7.447e-05
160 | 0.0018121 | 0.00045416
161 | 0.00029114 | 7.2966e-05
162 | 0.00070773 | 0.00017737
163 | 0.00067745 | 0.00016979
164 | 0.0017248 | 0.00043226
165 | 0.00065642 | 0.00016451
166 | 0.00065221 | 0.00016346
167 | 0.0028443 | 0.00071285
168 | 0.0013778 | 0.00034532
169 | 0.0021103 | 0.00052889
170 | 0.0028585 | 0.0007164
171 | 0.0018071 | 0.00045289
172 | 0.0023797 | 0.00059641
173 | 0.0053448 | 0.0013395
174 | 0.043832 | 0.010985
175 | 0.00070715 | 0.00017723
176 | 0.0071382 | 0.001789
177 | 0.0037171 | 0.0009316
178 | 0.0019254 | 0.00048254
179 | 0.066214 | 0.016595
180 | 0.0019169 | 0.00048042
181 | 0.00060062 | 0.00015053
182 | 0.00050328 | 0.00012613
183 | 0.0040524 | 0.0010156
184 | 0.0042524 | 0.0010658
185 | 0.00077582 | 0.00019444
186 | 0.0028599 | 0.00071677
187 | 0.0022978 | 0.00057588
188 | 0.0019186 | 0.00048084
189 | 0.0060356 | 0.0015127
190 | 0.0014464 | 0.00036251
191 | 0.002253 | 0.00056466
192 | 0.002253 | 0.00056466
193 | 0.0045946 | 0.0011515
194 | 0.0015992 | 0.0004008
195 | 0.001637 | 0.00041027
196 | 0.00029098 | 7.2926e-05
197 | 0.0041467 | 0.0010393
198 | 0.0015805 | 0.00039612
199 | 0.0020671 | 0.00051806
200 | 0.0016997 | 0.00042599
201 | 0.00091527 | 0.00022939
202 | 0.001771 | 0.00044386
203 | 0.00045107 | 0.00011305
204 | 0.00050875 | 0.0001275
205 | 0.00057502 | 0.00014411
206 | 0.00068044 | 0.00017053
207 | 0.001625 | 0.00040726
208 | 0.00061628 | 0.00015446
209 | 0.00063473 | 0.00015908
210 | 0.00086918 | 0.00021784
211 | 0.0010306 | 0.00025828
212 | 0.00048056 | 0.00012044
213 | 0.00082174 | 0.00020595
214 | 0.0009021 | 0.00022609
215 | 0.001349 | 0.00033808
216 | 0.00098521 | 0.00024692

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1