## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1062-3_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1062-3_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1062-3_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1062-3_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1062-3_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1062-3_0_6_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1062-3_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1062-3_0_6_node_239 | 0.4 | n |  | TRUE
8 | bus_LV_1062-3_0_6_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1062-3_0_6_node_41 | 0.4 | n |  | TRUE
10 | bus_LV_1062-3_0_6_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_1062-3_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1062-3_0_6_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1062-3_0_6_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_1062-3_0_6_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_1062-3_0_6_node_167 | 0.4 | n |  | TRUE
16 | bus_LV_1062-3_0_6_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1062-3_0_6_node_38 | 0.4 | n |  | TRUE
18 | bus_LV_1062-3_0_6_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1062-3_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1062-3_0_6_node_222 | 0.4 | n |  | TRUE
21 | bus_LV_1062-3_0_6_node_237 | 0.4 | n |  | TRUE
22 | bus_LV_1062-3_0_6_node_243 | 0.4 | n |  | TRUE
23 | bus_LV_1062-3_0_6_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1062-3_0_6_node_100 | 0.4 | n |  | TRUE
25 | bus_LV_1062-3_0_6_node_75 | 0.4 | n |  | TRUE
26 | bus_LV_1062-3_0_6_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1062-3_0_6_node_229 | 0.4 | n |  | TRUE
28 | bus_LV_1062-3_0_6_node_221 | 0.4 | n |  | TRUE
29 | bus_LV_1062-3_0_6_node_168 | 0.4 | n |  | TRUE
30 | bus_LV_1062-3_0_6_node_238 | 0.4 | n |  | TRUE
31 | bus_LV_1062-3_0_6_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1062-3_0_6_node_245 | 0.4 | n |  | TRUE
33 | bus_LV_1062-3_0_6_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_1062-3_0_6_node_71 | 0.4 | n |  | TRUE
35 | bus_LV_1062-3_0_6_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_1062-3_0_6_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_1062-3_0_6_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_1062-3_0_6_node_16 | 0.4 | n |  | TRUE
39 | bus_LV_1062-3_0_6_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_1062-3_0_6_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_1062-3_0_6_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1062-3_0_6_node_55 | 0.4 | n |  | TRUE
43 | bus_LV_1062-3_0_6_node_58 | 0.4 | n |  | TRUE
44 | bus_LV_1062-3_0_6_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_1062-3_0_6_node_72 | 0.4 | n |  | TRUE
46 | bus_LV_1062-3_0_6_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_1062-3_0_6_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_1062-3_0_6_node_67 | 0.4 | n |  | TRUE
49 | bus_LV_1062-3_0_6_node_240 | 0.4 | n |  | TRUE
50 | bus_LV_1062-3_0_6_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_1062-3_0_6_node_161 | 0.4 | n |  | TRUE
52 | bus_LV_1062-3_0_6_node_29 | 0.4 | n |  | TRUE
53 | bus_LV_1062-3_0_6_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_1062-3_0_6_node_62 | 0.4 | n |  | TRUE
55 | bus_LV_1062-3_0_6_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_1062-3_0_6_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_1062-3_0_6_node_155 | 0.4 | n |  | TRUE
58 | bus_LV_1062-3_0_6_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_1062-3_0_6_node_162 | 0.4 | n |  | TRUE
60 | bus_LV_1062-3_0_6_node_182 | 0.4 | n |  | TRUE
61 | bus_LV_1062-3_0_6_node_57 | 0.4 | n |  | TRUE
62 | bus_LV_1062-3_0_6_node_244 | 0.4 | n |  | TRUE
63 | bus_LV_1062-3_0_6_node_76 | 0.4 | n |  | TRUE
64 | bus_LV_1062-3_0_6_node_74 | 0.4 | n |  | TRUE
65 | bus_LV_1062-3_0_6_node_25 | 0.4 | n |  | TRUE
66 | bus_LV_1062-3_0_6_node_40 | 0.4 | n |  | TRUE
67 | bus_LV_1062-3_0_6_node_214 | 0.4 | n |  | TRUE
68 | bus_LV_1062-3_0_6_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_1062-3_0_6_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_1062-3_0_6_node_56 | 0.4 | n |  | TRUE
71 | bus_LV_1062-3_0_6_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_1062-3_0_6_node_241 | 0.4 | n |  | TRUE
73 | bus_LV_1062-3_0_6_node_42 | 0.4 | n |  | TRUE
74 | bus_LV_1062-3_0_6_node_43 | 0.4 | n |  | TRUE
75 | bus_LV_1062-3_0_6_node_160 | 0.4 | n |  | TRUE
76 | bus_LV_1062-3_0_6_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_1062-3_0_6_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_1062-3_0_6_node_158 | 0.4 | n |  | TRUE
79 | bus_LV_1062-3_0_6_node_157 | 0.4 | n |  | TRUE
80 | bus_LV_1062-3_0_6_node_156 | 0.4 | n |  | TRUE
81 | bus_LV_1062-3_0_6_node_223 | 0.4 | n |  | TRUE
82 | bus_LV_1062-3_0_6_node_159 | 0.4 | n |  | TRUE
83 | bus_LV_1062-3_0_6_node_154 | 0.4 | n |  | TRUE
84 | bus_LV_1062-3_0_6_node_165 | 0.4 | n |  | TRUE
85 | bus_LV_1062-3_0_6_node_173 | 0.4 | n |  | TRUE
86 | bus_LV_1062-3_0_6_node_180 | 0.4 | n |  | TRUE
87 | bus_LV_1062-3_0_6_node_215 | 0.4 | n |  | TRUE
88 | bus_LV_1062-3_0_6_node_65 | 0.4 | n |  | TRUE
89 | bus_LV_1062-3_0_6_node_66 | 0.4 | n |  | TRUE
90 | bus_LV_1062-3_0_6_node_63 | 0.4 | n |  | TRUE
91 | bus_LV_1062-3_0_6_node_61 | 0.4 | n |  | TRUE
92 | bus_LV_1062-3_0_6_node_69 | 0.4 | n |  | TRUE
93 | bus_LV_1062-3_0_6_node_70 | 0.4 | n |  | TRUE
94 | bus_LV_1062-3_0_6_node_201 | 0.4 | n |  | TRUE
95 | bus_LV_1062-3_0_6_node_202 | 0.4 | n |  | TRUE
96 | bus_LV_1062-3_0_6_node_73 | 0.4 | n |  | TRUE
97 | bus_LV_1062-3_0_6_node_99 | 0.4 | n |  | TRUE
98 | bus_LV_1062-3_0_6_node_195 | 0.4 | n |  | TRUE
99 | bus_LV_1062-3_0_6_node_191 | 0.4 | n |  | TRUE
100 | bus_LV_1062-3_0_6_node_224 | 0.4 | n |  | TRUE
101 | bus_LV_1062-3_0_6_node_212 | 0.4 | n |  | TRUE
102 | bus_LV_1062-3_0_6_node_163 | 0.4 | n |  | TRUE
103 | bus_LV_1062-3_0_6_node_164 | 0.4 | n |  | TRUE
104 | bus_LV_1062-3_0_6_node_166 | 0.4 | n |  | TRUE
105 | bus_LV_1062-3_0_6_node_169 | 0.4 | n |  | TRUE
106 | bus_LV_1062-3_0_6_node_170 | 0.4 | n |  | TRUE
107 | bus_LV_1062-3_0_6_node_171 | 0.4 | n |  | TRUE
108 | bus_LV_1062-3_0_6_node_172 | 0.4 | n |  | TRUE
109 | bus_LV_1062-3_0_6_node_179 | 0.4 | n |  | TRUE
110 | bus_LV_1062-3_0_6_node_181 | 0.4 | n |  | TRUE
111 | bus_LV_1062-3_0_6_node_183 | 0.4 | n |  | TRUE
112 | bus_LV_1062-3_0_6_node_185 | 0.4 | n |  | TRUE
113 | bus_LV_1062-3_0_6_node_186 | 0.4 | n |  | TRUE
114 | bus_LV_1062-3_0_6_node_187 | 0.4 | n |  | TRUE
115 | bus_LV_1062-3_0_6_node_188 | 0.4 | n |  | TRUE
116 | bus_LV_1062-3_0_6_node_189 | 0.4 | n |  | TRUE
117 | bus_LV_1062-3_0_6_node_193 | 0.4 | n |  | TRUE
118 | bus_LV_1062-3_0_6_node_194 | 0.4 | n |  | TRUE
119 | bus_LV_1062-3_0_6_node_192 | 0.4 | n |  | TRUE
120 | bus_LV_1062-3_0_6_node_234 | 0.4 | n |  | TRUE
121 | bus_LV_1062-3_0_6_node_196 | 0.4 | n |  | TRUE
122 | bus_LV_1062-3_0_6_node_233 | 0.4 | n |  | TRUE
123 | bus_LV_1062-3_0_6_node_203 | 0.4 | n |  | TRUE
124 | bus_LV_1062-3_0_6_node_204 | 0.4 | n |  | TRUE
125 | bus_LV_1062-3_0_6_node_205 | 0.4 | n |  | TRUE
126 | bus_LV_1062-3_0_6_node_206 | 0.4 | n |  | TRUE
127 | bus_LV_1062-3_0_6_node_207 | 0.4 | n |  | TRUE
128 | bus_LV_1062-3_0_6_node_208 | 0.4 | n |  | TRUE
129 | bus_LV_1062-3_0_6_node_209 | 0.4 | n |  | TRUE
130 | bus_LV_1062-3_0_6_node_210 | 0.4 | n |  | TRUE
131 | bus_LV_1062-3_0_6_node_211 | 0.4 | n |  | TRUE
132 | bus_LV_1062-3_0_6_node_213 | 0.4 | n |  | TRUE
133 | bus_LV_1062-3_0_6_node_218 | 0.4 | n |  | TRUE
134 | bus_LV_1062-3_0_6_node_236 | 0.4 | n |  | TRUE
135 | bus_LV_1062-3_0_6_node_230 | 0.4 | n |  | TRUE
136 | bus_LV_1062-3_0_6_node_219 | 0.4 | n |  | TRUE
137 | bus_LV_1062-3_0_6_node_216 | 0.4 | n |  | TRUE
138 | bus_LV_1062-3_0_6_node_217 | 0.4 | n |  | TRUE
139 | bus_LV_1062-3_0_6_node_242 | 0.4 | n |  | TRUE
140 | bus_LV_1062-3_0_6_node_220 | 0.4 | n |  | TRUE
141 | bus_LV_1062-3_0_6_node_225 | 0.4 | n |  | TRUE
142 | bus_LV_1062-3_0_6_node_235 | 0.4 | n |  | TRUE
143 | bus_MV_2_0_node_27 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1062-3_0_6_load_0 | 0 | 0.00016463 | 4.1261e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1062-3_0_6_load_1 | 1 | 0.00025427 | 6.3726e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1062-3_0_6_load_4 | 3 | 0.000119 | 2.9825e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1062-3_0_6_load_239 | 7 | 0.00045612 | 0.00011431 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1062-3_0_6_load_41 | 9 | 0.0040556 | 0.0010164 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1062-3_0_6_load_9 | 11 | 0.00020875 | 5.2319e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1062-3_0_6_load_167 | 15 | 0.0079434 | 0.0019908 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1062-3_0_6_load_38 | 17 | 0.0018842 | 0.00047222 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1062-3_0_6_load_222 | 20 | 0.0018814 | 0.00047153 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1062-3_0_6_load_237 | 21 | 0.00022237 | 5.5731e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1062-3_0_6_load_243 | 22 | 0.0012034 | 0.0003016 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1062-3_0_6_load_100 | 24 | 0.00038872 | 9.7423e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1062-3_0_6_load_229 | 27 | 0.00044439 | 0.00011137 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1062-3_0_6_load_221 | 28 | 0.00058212 | 0.00014589 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1062-3_0_6_load_168 | 29 | 0.00029899 | 7.4933e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1062-3_0_6_load_238 | 30 | 8.543e-05 | 2.1411e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1062-3_0_6_load_245 | 32 | 0.0049759 | 0.0012471 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1062-3_0_6_load_71 | 34 | 0.003103 | 0.00077769 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1062-3_0_6_load_16 | 38 | 0.0044937 | 0.0011262 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1062-3_0_6_load_37 | 41 | 0.01058 | 0.0026515 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1062-3_0_6_load_55 | 42 | 0.0041994 | 0.0010525 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1062-3_0_6_load_58 | 43 | 0.0033914 | 0.00084997 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1062-3_0_6_load_72 | 45 | 0.0073211 | 0.0018348 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1062-3_0_6_load_67 | 48 | 0.0054458 | 0.0013648 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1062-3_0_6_load_240 | 49 | 0.0074371 | 0.0018639 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1062-3_0_6_load_161 | 51 | 0.0045885 | 0.00115 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1062-3_0_6_load_62 | 54 | 0.00055438 | 0.00013894 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1062-3_0_6_load_59 | 56 | 0.0044684 | 0.0011199 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1062-3_0_6_load_155 | 57 | 0.012041 | 0.0030178 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1062-3_0_6_load_162 | 59 | 0.021118 | 0.0052927 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1062-3_0_6_load_57 | 61 | 0.0061582 | 0.0015434 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1062-3_0_6_load_244 | 62 | 0.0027643 | 0.0006928 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1062-3_0_6_load_76 | 63 | 0.00061666 | 0.00015455 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1062-3_0_6_load_74 | 64 | 0.0002422 | 6.0701e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1062-3_0_6_load_214 | 67 | 0.0030369 | 0.00076111 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1062-3_0_6_load_53 | 68 | 0.0030759 | 0.00077089 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1062-3_0_6_load_54 | 69 | 0.0031225 | 0.00078257 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1062-3_0_6_load_56 | 70 | 0.006099 | 0.0015285 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1062-3_0_6_load_68 | 71 | 0.0023349 | 0.00058518 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1062-3_0_6_load_241 | 72 | 0.014624 | 0.0036651 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1062-3_0_6_load_42 | 73 | 0.0028143 | 0.00070533 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1062-3_0_6_load_43 | 74 | 0.00094096 | 0.00023583 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1062-3_0_6_load_64 | 76 | 0.00055441 | 0.00013895 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1062-3_0_6_load_60 | 77 | 0.0016918 | 0.000424 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1062-3_0_6_load_158 | 78 | 0.0077897 | 0.0019523 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1062-3_0_6_load_159 | 82 | 0.010571 | 0.0026492 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1062-3_0_6_load_154 | 83 | 0.0080875 | 0.0020269 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1062-3_0_6_load_165 | 84 | 0.0010344 | 0.00025925 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1062-3_0_6_load_173 | 85 | 0.03262 | 0.0081754 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1062-3_0_6_load_215 | 87 | 0.006766 | 0.0016957 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1062-3_0_6_load_66 | 89 | 0.0010557 | 0.00026458 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1062-3_0_6_load_63 | 90 | 0.0070008 | 0.0017546 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1062-3_0_6_load_61 | 91 | 0.004234 | 0.0010611 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1062-3_0_6_load_69 | 92 | 0.020388 | 0.0051098 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1062-3_0_6_load_201 | 94 | 0.0038134 | 0.00095573 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1062-3_0_6_load_202 | 95 | 0.0021217 | 0.00053175 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1062-3_0_6_load_73 | 96 | 0.00067284 | 0.00016863 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1062-3_0_6_load_99 | 97 | 0.00037581 | 9.4187e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1062-3_0_6_load_195 | 98 | 0.0019287 | 0.00048338 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1062-3_0_6_load_191 | 99 | 0.006123 | 0.0015346 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1062-3_0_6_load_224 | 100 | 0.0028033 | 0.00070258 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1062-3_0_6_load_212 | 101 | 0.00359 | 0.00089974 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1062-3_0_6_load_163 | 102 | 0.0050055 | 0.0012545 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1062-3_0_6_load_164 | 103 | 0.0019006 | 0.00047633 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1062-3_0_6_load_166 | 104 | 0.0050392 | 0.0012629 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1062-3_0_6_load_169 | 105 | 0.0081854 | 0.0020514 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1062-3_0_6_load_172 | 108 | 0.00095718 | 0.00023989 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1062-3_0_6_load_179 | 109 | 0.025556 | 0.006405 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1062-3_0_6_load_181 | 110 | 0.037626 | 0.00943 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1062-3_0_6_load_183 | 111 | 0.010739 | 0.0026916 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1062-3_0_6_load_185 | 112 | 0.0032933 | 0.00082538 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1062-3_0_6_load_193 | 117 | 0.0047217 | 0.0011834 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1062-3_0_6_load_194 | 118 | 0.0046111 | 0.0011557 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1062-3_0_6_load_192 | 119 | 0.0030002 | 0.00075193 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1062-3_0_6_load_234 | 120 | 0.0034151 | 0.00085589 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1062-3_0_6_load_196 | 121 | 0.0027127 | 0.00067987 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1062-3_0_6_load_233 | 122 | 0.0042382 | 0.0010622 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1062-3_0_6_load_203 | 123 | 0.0027778 | 0.00069617 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1062-3_0_6_load_206 | 126 | 0.0026873 | 0.0006735 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1062-3_0_6_load_207 | 127 | 0.0086948 | 0.0021791 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1062-3_0_6_load_208 | 128 | 0.0043541 | 0.0010912 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1062-3_0_6_load_209 | 129 | 0.0032243 | 0.0008081 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1062-3_0_6_load_210 | 130 | 0.0057448 | 0.0014398 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1062-3_0_6_load_211 | 131 | 0.010055 | 0.0025199 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1062-3_0_6_load_213 | 132 | 0.0034085 | 0.00085424 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1062-3_0_6_load_218 | 133 | 0.0082189 | 0.0020598 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1062-3_0_6_load_236 | 134 | 0.016583 | 0.0041562 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1062-3_0_6_load_230 | 135 | 0.0026598 | 0.00066661 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1062-3_0_6_load_219 | 136 | 0.0040764 | 0.0010216 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1062-3_0_6_load_216 | 137 | 0.0043493 | 0.00109 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1062-3_0_6_load_217 | 138 | 0.005531 | 0.0013862 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1062-3_0_6_load_242 | 139 | 0.0066523 | 0.0016672 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1062-3_0_6_load_220 | 140 | 0.0037614 | 0.00094269 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1062-3_0_6_load_225 | 141 | 0.0028017 | 0.00070217 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1062-3_0_6_load_235 | 142 | 0.0056979 | 0.001428 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1062-3_0_6_line_0 |  | 0 | 1 | 0.018647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1062-3_0_6_line_1 |  | 0 | 2 | 0.027763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1062-3_0_6_line_2 |  | 2 | 3 | 0.018769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1062-3_0_6_line_3 |  | 3 | 4 | 0.032254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1062-3_0_6_line_4 |  | 4 | 5 | 0.29181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1062-3_0_6_line_5 |  | 5 | 11 | 0.060981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1062-3_0_6_line_6 |  | 5 | 6 | 0.31582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1062-3_0_6_line_7 |  | 6 | 7 | 0.036227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1062-3_0_6_line_8 |  | 7 | 12 | 0.029303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1062-3_0_6_line_9 |  | 8 | 9 | 0.068878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1062-3_0_6_line_10 |  | 8 | 10 | 0.03996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1062-3_0_6_line_11 |  | 10 | 17 | 0.16808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1062-3_0_6_line_12 |  | 11 | 18 | 0.063826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1062-3_0_6_line_13 |  | 12 | 16 | 0.092158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1062-3_0_6_line_14 |  | 12 | 21 | 0.037395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1062-3_0_6_line_15 |  | 13 | 14 | 0.036547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1062-3_0_6_line_16 |  | 13 | 15 | 0.12107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1062-3_0_6_line_17 |  | 13 | 16 | 0.28887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1062-3_0_6_line_18 |  | 14 | 34 | 0.017647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1062-3_0_6_line_19 |  | 14 | 31 | 0.053087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1062-3_0_6_line_20 |  | 15 | 84 | 0.010903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1062-3_0_6_line_21 |  | 16 | 22 | 0.029975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1062-3_0_6_line_22 |  | 17 | 65 | 0.11323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1062-3_0_6_line_23 |  | 18 | 19 | 0.018224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1062-3_0_6_line_24 |  | 19 | 20 | 0.070566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1062-3_0_6_line_25 |  | 20 | 26 | 0.02096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1062-3_0_6_line_26 |  | 21 | 30 | 0.01129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1062-3_0_6_line_27 |  | 22 | 62 | 0.018088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1062-3_0_6_line_28 |  | 23 | 24 | 0.068735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1062-3_0_6_line_29 |  | 23 | 25 | 0.3189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1062-3_0_6_line_30 |  | 24 | 27 | 0.023166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1062-3_0_6_line_31 |  | 25 | 63 | 0.0652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1062-3_0_6_line_32 |  | 25 | 64 | 0.020627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1062-3_0_6_line_33 |  | 26 | 27 | 0.01664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1062-3_0_6_line_34 |  | 28 | 29 | 0.013761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1062-3_0_6_line_35 |  | 29 | 104 | 0.052097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1062-3_0_6_line_36 |  | 31 | 32 | 0.004843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1062-3_0_6_line_37 |  | 31 | 33 | 0.043525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1062-3_0_6_line_38 |  | 33 | 57 | 0.011783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1062-3_0_6_line_39 |  | 33 | 52 | 0.010699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1062-3_0_6_line_40 |  | 34 | 47 | 0.030914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_1062-3_0_6_line_41 |  | 35 | 36 | 0.004389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1062-3_0_6_line_42 |  | 35 | 37 | 0.0087789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1062-3_0_6_line_43 |  | 35 | 38 | 0.037047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1062-3_0_6_line_44 |  | 36 | 41 | 0.016723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1062-3_0_6_line_45 |  | 37 | 42 | 0.015805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1062-3_0_6_line_46 |  | 37 | 43 | 0.017102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1062-3_0_6_line_47 |  | 38 | 39 | 0.0053323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1062-3_0_6_line_48 |  | 39 | 40 | 0.070121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1062-3_0_6_line_49 |  | 40 | 49 | 0.027964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1062-3_0_6_line_50 |  | 41 | 67 | 0.0013299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1062-3_0_6_line_51 |  | 42 | 69 | 0.015115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1062-3_0_6_line_52 |  | 43 | 70 | 0.026891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1062-3_0_6_line_53 |  | 44 | 45 | 0.016716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1062-3_0_6_line_54 |  | 44 | 46 | 0.015585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1062-3_0_6_line_55 |  | 46 | 47 | 0.027945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1062-3_0_6_line_56 |  | 46 | 48 | 0.010724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1062-3_0_6_line_57 |  | 47 | 55 | 0.0085803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1062-3_0_6_line_58 |  | 48 | 71 | 0.019073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1062-3_0_6_line_59 |  | 49 | 72 | 0.024406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1062-3_0_6_line_60 |  | 50 | 51 | 0.025241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_1062-3_0_6_line_61 |  | 50 | 52 | 0.013847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_1062-3_0_6_line_62 |  | 51 | 75 | 0.022742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_1062-3_0_6_line_63 |  | 53 | 54 | 0.035575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1062-3_0_6_line_64 |  | 53 | 55 | 0.025029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1062-3_0_6_line_65 |  | 53 | 56 | 0.021563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1062-3_0_6_line_66 |  | 54 | 76 | 7.2944e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1062-3_0_6_line_67 |  | 55 | 61 | 0.0076771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1062-3_0_6_line_68 |  | 56 | 77 | 0.013391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1062-3_0_6_line_69 |  | 57 | 83 | 0.011275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1062-3_0_6_line_70 |  | 58 | 59 | 0.024167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1062-3_0_6_line_71 |  | 58 | 60 | 0.019678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1062-3_0_6_line_72 |  | 59 | 75 | 0.016938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1062-3_0_6_line_73 |  | 60 | 85 | 0.044045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1062-3_0_6_line_74 |  | 60 | 86 | 0.024088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1062-3_0_6_line_75 |  | 61 | 70 | 0.027645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1062-3_0_6_line_76 |  | 63 | 97 | 0.032453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1062-3_0_6_line_77 |  | 64 | 96 | 0.0043289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1062-3_0_6_line_78 |  | 65 | 66 | 0.097815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1062-3_0_6_line_79 |  | 66 | 73 | 0.021103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1062-3_0_6_line_80 |  | 66 | 74 | 0.047452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1062-3_0_6_line_81 |  | 67 | 87 | 0.03052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1062-3_0_6_line_82 |  | 68 | 69 | 0.023394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1062-3_0_6_line_83 |  | 71 | 92 | 0.010069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1062-3_0_6_line_84 |  | 73 | 88 | 0.022323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1062-3_0_6_line_85 |  | 75 | 82 | 0.015429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_1062-3_0_6_line_86 |  | 77 | 91 | 0.0071432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1062-3_0_6_line_87 |  | 78 | 79 | 0.01495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1062-3_0_6_line_88 |  | 79 | 82 | 0.012284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1062-3_0_6_line_89 |  | 79 | 80 | 0.10123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1062-3_0_6_line_90 |  | 80 | 81 | 0.014641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1062-3_0_6_line_91 |  | 81 | 100 | 0.016586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1062-3_0_6_line_92 |  | 81 | 101 | 0.02144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1062-3_0_6_line_93 |  | 84 | 102 | 0.03327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1062-3_0_6_line_94 |  | 85 | 107 | 0.031567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1062-3_0_6_line_95 |  | 86 | 111 | 0.022914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1062-3_0_6_line_96 |  | 86 | 109 | 0.013208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1062-3_0_6_line_97 |  | 87 | 137 | 0.013147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1062-3_0_6_line_98 |  | 88 | 89 | 0.030952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1062-3_0_6_line_99 |  | 88 | 90 | 0.0081359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1062-3_0_6_line_100 |  | 90 | 91 | 0.005083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1062-3_0_6_line_101 |  | 92 | 93 | 0.037782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1062-3_0_6_line_102 |  | 93 | 94 | 0.033407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1062-3_0_6_line_103 |  | 93 | 95 | 0.017247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1062-3_0_6_line_104 |  | 98 | 99 | 0.0033805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1062-3_0_6_line_105 |  | 99 | 114 | 0.013137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1062-3_0_6_line_106 |  | 100 | 141 | 0.0073499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1062-3_0_6_line_107 |  | 101 | 128 | 0.0062055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1062-3_0_6_line_108 |  | 102 | 103 | 0.10774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1062-3_0_6_line_109 |  | 103 | 104 | 0.021566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1062-3_0_6_line_110 |  | 105 | 106 | 0.065996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1062-3_0_6_line_111 |  | 106 | 107 | 0.047712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1062-3_0_6_line_112 |  | 106 | 108 | 0.087663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1062-3_0_6_line_113 |  | 109 | 110 | 0.028931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1062-3_0_6_line_114 |  | 112 | 113 | 0.016125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1062-3_0_6_line_115 |  | 112 | 114 | 0.036142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1062-3_0_6_line_116 |  | 113 | 115 | 0.003285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1062-3_0_6_line_117 |  | 113 | 116 | 0.10278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1062-3_0_6_line_118 |  | 114 | 117 | 0.020092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1062-3_0_6_line_119 |  | 115 | 118 | 0.037961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1062-3_0_6_line_120 |  | 115 | 119 | 0.015438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1062-3_0_6_line_121 |  | 116 | 120 | 0.037342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1062-3_0_6_line_122 |  | 117 | 121 | 0.0032267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1062-3_0_6_line_123 |  | 120 | 122 | 0.003142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1062-3_0_6_line_124 |  | 122 | 142 | 0.017022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1062-3_0_6_line_125 |  | 123 | 124 | 0.02411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1062-3_0_6_line_126 |  | 123 | 125 | 0.013093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1062-3_0_6_line_127 |  | 124 | 126 | 0.034793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1062-3_0_6_line_128 |  | 124 | 127 | 0.014496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1062-3_0_6_line_129 |  | 125 | 128 | 0.024953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1062-3_0_6_line_130 |  | 125 | 129 | 0.014908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1062-3_0_6_line_131 |  | 126 | 130 | 0.0043992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1062-3_0_6_line_132 |  | 127 | 131 | 0.011777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1062-3_0_6_line_133 |  | 129 | 132 | 0.0057876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1062-3_0_6_line_134 |  | 130 | 133 | 0.017013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1062-3_0_6_line_135 |  | 131 | 134 | 0.017478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1062-3_0_6_line_136 |  | 132 | 135 | 0.017072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1062-3_0_6_line_137 |  | 133 | 136 | 6.1881e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1062-3_0_6_line_138 |  | 136 | 140 | 0.00038849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1062-3_0_6_line_139 |  | 137 | 138 | 0.0076231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1062-3_0_6_line_140 |  | 138 | 139 | 0.020274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1062-3_0_6_line_141 |  | 141 | 142 | 0.0037311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1062-3_0_6_trafo_161 | 0.63 MVA 20/0.4 kV | 143 | 51 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32
0 | 2655223.3314 | 1209924.9683 | 2655239.6128 | 1209933.3814 | 2655239.8062 | 1209933.1256
1 | 2655198.6666 | 1209912.2234 | 2655223.3314 | 1209924.9683
2 | 2655198.6666 | 1209912.2234 | 2655200.8368 | 1209898.6464 | 2655200.9671 | 1209896.0572 | 2655200.2513 | 1209893.7381
3 | 2655207.4776 | 1209870.1242 | 2655203.868 | 1209872.5145 | 2655199.8352 | 1209875.4567 | 2655196.2642 | 1209878.6033 | 2655194.5257 | 1209880.8442 | 2655193.7396 | 1209882.8381 | 2655193.6597 | 1209884.9052 | 2655194.3492 | 1209886.7794 | 2655195.4078 | 1209888.19 | 2655200.2513 | 1209893.7381
4 | 2655191.5952 | 1209773.6644 | 2655184.4949 | 1209772.1534 | 2655172.2231 | 1209768.4822 | 2655163.7076 | 1209766.3022 | 2655153.0535 | 1209764.4138 | 2655143.8595 | 1209763.2726 | 2655130.1534 | 1209762.6568 | 2655115.7549 | 1209762.9351 | 2655106.2604 | 1209763.0587 | 2655099.9224 | 1209763.7673 | 2655096.2965 | 1209764.6232 | 2655093.0896 | 1209766.2057 | 2655091.4448 | 1209768.1805 | 2655090.4326 | 1209770.7839 | 2655089.2489 | 1209784.5589 | 2655154.3075 | 1209811.2977 | 2655218.2735 | 1209841.885 | 2655210.403 | 1209868.5726 | 2655207.4776 | 1209870.1242
5 | 2655191.5952 | 1209773.6644 | 2655191.4194 | 1209758.9762 | 2655190.9918 | 1209748.5105 | 2655190.8656 | 1209745.7188 | 2655189.889 | 1209741.1848 | 2655188.4772 | 1209737.6919 | 2655186.2364 | 1209735.0696 | 2655183.0465 | 1209732.3385 | 2655178.536 | 1209729.3951 | 2655171.774 | 1209726.6309 | 2655167.6997 | 1209725.3283
6 | 2655191.5952 | 1209773.6644 | 2655198.9473 | 1209774.2549 | 2655204.6825 | 1209772.1623 | 2655213.1331 | 1209765.7477 | 2655219.0752 | 1209761.8225 | 2655223.4239 | 1209760.0728 | 2655228.7897 | 1209759.2887 | 2655262.102 | 1209758.6854 | 2655302.326 | 1209758.6245 | 2655353.2271 | 1209761.2423 | 2655382.7391 | 1209763.9064 | 2655422.5568 | 1209767.4892 | 2655439.4651 | 1209769.5029 | 2655495.501 | 1209779.8186 | 2655501.6889 | 1209781.3548
7 | 2655501.6889 | 1209781.3548 | 2655503.3079 | 1209777.2674 | 2655501.9846 | 1209772.4522 | 2655501.6796 | 1209770.9152 | 2655496.2644 | 1209768.0186 | 2655499.5388 | 1209749.172
8 | 2655496.5724 | 1209720.193 | 2655500.2236 | 1209745.2308 | 2655499.5388 | 1209749.172
9 | 2655664.3331 | 1210055.6104 | 2655660.7015 | 1210066.8721 | 2655671.7091 | 1210122.8415
10 | 2655705.7151 | 1210143.7823 | 2655698.76 | 1210138.1696 | 2655692.7688 | 1210134.3337 | 2655671.7091 | 1210122.8415
11 | 2655705.7151 | 1210143.7823 | 2655778.166 | 1210029.4684 | 2655792.9325 | 1210012.5296 | 2655801.3031 | 1210006.582
12 | 2655149.6723 | 1209668.9035 | 2655150.3904 | 1209678.3824 | 2655156.4997 | 1209717.2175 | 2655157.4338 | 1209720.5948 | 2655159.0755 | 1209722.2554 | 2655161.3537 | 1209723.2993 | 2655167.6997 | 1209725.3283
13 | 2655566.1861 | 1209706.5991 | 2655494.8003 | 1209699.8867 | 2655495.3799 | 1209715.2012 | 2655496.5724 | 1209720.193
14 | 2655496.5724 | 1209720.193 | 2655471.0034 | 1209723.4351 | 2655462.3842 | 1209728.3246 | 2655461.5817 | 1209729.8362
15 | 2655842.0969 | 1209723.7726 | 2655857.2113 | 1209724.9814 | 2655859.8263 | 1209724.9503 | 2655862.1359 | 1209723.4376 | 2655869.5592 | 1209724.5411 | 2655877.9692 | 1209725.7983
16 | 2655842.0969 | 1209723.7726 | 2655831.3085 | 1209723.2491 | 2655816.4999 | 1209723.4775 | 2655802.6132 | 1209722.6583 | 2655721.3839 | 1209715.4902
17 | 2655566.1861 | 1209706.5991 | 2655731.7413 | 1209720.3727 | 2655823.4276 | 1209728.0005 | 2655846.3154 | 1209730.2604 | 2655842.0969 | 1209723.7726
18 | 2655877.9692 | 1209725.7983 | 2655878.8483 | 1209726.885 | 2655881.8265 | 1209728.6472 | 2655887.2494 | 1209729.8987 | 2655894.4382 | 1209730.6063
19 | 2655877.9692 | 1209725.7983 | 2655876.2186 | 1209723.614 | 2655874.5735 | 1209719.0959 | 2655873.8572 | 1209708.7386 | 2655874.1092 | 1209698.8795 | 2655874.8358 | 1209696.7739 | 2655876.102 | 1209695.485 | 2655878.3907 | 1209694.5837 | 2655880.078 | 1209694.5995 | 2655882.0064 | 1209691.5824 | 2655884.1979 | 1209684.0206 | 2655883.7866 | 1209678.4356
20 | 2655710.523 | 1209714.5318 | 2655721.3839 | 1209715.4902
21 | 2655566.1861 | 1209706.5991 | 2655565.0327 | 1209723.5318 | 2655562.6204 | 1209736.309
22 | 2655887.6027 | 1209935.6136 | 2655880.8958 | 1209938.3858 | 2655851.8148 | 1209964.496 | 2655828.0381 | 1209988.2766 | 2655813.0802 | 1210002.9122 | 2655801.3031 | 1210006.582
23 | 2655149.6723 | 1209668.9035 | 2655162.8359 | 1209669.8479 | 2655162.776 | 1209664.8221
24 | 2655162.776 | 1209664.8221 | 2655160.2507 | 1209595.9467 | 2655160.2427 | 1209594.3027
25 | 2655160.1404 | 1209573.3433 | 2655160.2427 | 1209594.3027
26 | 2655456.288 | 1209739.8081 | 2655461.5817 | 1209729.8362
27 | 2655549.419 | 1209744.9215 | 2655561.6027 | 1209741.6996 | 2655562.6204 | 1209736.309
28 | 2655233.0429 | 1209504.2651 | 2655226.004 | 1209512.5049 | 2655220.8099 | 1209519.3498 | 2655201.1152 | 1209551.4201 | 2655194.5312 | 1209561.0557
29 | 2655233.0429 | 1209504.2651 | 2655243.3933 | 1209499.5914 | 2655263.726 | 1209488.9622 | 2655273.6045 | 1209484.362 | 2655282.8468 | 1209481.9795 | 2655290.6982 | 1209481.2184 | 2655296.4188 | 1209481.5494 | 2655301.6828 | 1209482.7544 | 2655315.0247 | 1209486.6581 | 2655319.3357 | 1209487.354 | 2655322.7535 | 1209486.8298 | 2655325.7624 | 1209485.3123 | 2655327.9798 | 1209483.0871 | 2655329.7373 | 1209479.6236 | 2655329.9157 | 1209476.7791 | 2655328.8855 | 1209473.1229 | 2655301.943 | 1209416.1394 | 2655301.2773 | 1209411.6861 | 2655301.6902 | 1209408.1434 | 2655303.1146 | 1209406.1888 | 2655305.7536 | 1209405.2237 | 2655309.3826 | 1209405.691 | 2655321.2948 | 1209408.0472 | 2655330.3036 | 1209408.72 | 2655338.4022 | 1209409.1842 | 2655344.0614 | 1209408.7697 | 2655348.208 | 1209407.5296 | 2655351.9388 | 1209405.2184 | 2655354.8677 | 1209402.4995 | 2655361.1943 | 1209389.9618 | 2655367.3074 | 1209373.3975 | 2655382.3763 | 1209330.4673 | 2655383.4934 | 1209328.8656
30 | 2655194.5312 | 1209561.0557 | 2655188.8329 | 1209569.395 | 2655187.0836 | 1209571.1466 | 2655184.9687 | 1209572.1721 | 2655182.2965 | 1209572.6254 | 2655179.5204 | 1209572.811 | 2655176.7743 | 1209572.8864
31 | 2655383.4934 | 1209328.8656 | 2655368.5883 | 1209309.0823 | 2655362.991 | 1209301.1812 | 2655358.3932 | 1209297.7921 | 2655349.5257 | 1209293.3295 | 2655344.6956 | 1209290.4052 | 2655337.8947 | 1209287.685 | 2655336.0133 | 1209286.6703
32 | 2655383.4934 | 1209328.8656 | 2655386.2588 | 1209324.9334 | 2655399.1383 | 1209315.7468
33 | 2655160.1404 | 1209573.3433 | 2655176.7743 | 1209572.8864
34 | 2655496.6843 | 1209695.6615 | 2655482.976 | 1209694.4518
35 | 2655496.6843 | 1209695.6615 | 2655548.5793 | 1209700.241
36 | 2655883.7866 | 1209678.4356 | 2655883.4289 | 1209673.6072
37 | 2655883.7866 | 1209678.4356 | 2655900.5918 | 1209675.2355 | 2655905.8147 | 1209674.3061 | 2655905.8572 | 1209673.8284 | 2655906.0206 | 1209671.8065 | 2655910.594 | 1209666.3794 | 2655913.2624 | 1209663.0802 | 2655920.5089 | 1209663.5929
38 | 2655920.5089 | 1209663.5929 | 2655925.4616 | 1209663.9283 | 2655932.2558 | 1209664.513
39 | 2655920.5089 | 1209663.5929 | 2655921.4753 | 1209652.94
40 | 2655925.2035 | 1209733.6342 | 2655894.4382 | 1209730.6063
41 | 2655999.8058 | 1209740.1151 | 2656004.1876 | 1209740.5342
42 | 2656003.5353 | 1209749.2889 | 2656003.8743 | 1209744.756 | 2656004.1876 | 1209740.5342
43 | 2656004.1876 | 1209740.5342 | 2656041.0865 | 1209743.845
44 | 2655999.8058 | 1209740.1151 | 2656003.7398 | 1209723.8612
45 | 2656003.5353 | 1209749.2889 | 2656011.798 | 1209750.0335 | 2656019.0669 | 1209751.9178
46 | 2656003.5353 | 1209749.2889 | 2655986.5022 | 1209747.758
47 | 2656046.3975 | 1209744.3215 | 2656041.0865 | 1209743.845
48 | 2656046.3975 | 1209744.3215 | 2656094.6905 | 1209748.6554 | 2656097.5675 | 1209727.2141
49 | 2656097.5675 | 1209727.2141 | 2656100.5368 | 1209699.4081
50 | 2656003.7398 | 1209723.8612 | 2656004.0527 | 1209722.5686
51 | 2656019.0669 | 1209751.9178 | 2656020.9651 | 1209752.4098 | 2656027.2492 | 1209755.0259 | 2656030.6935 | 1209758.149 | 2656031.871 | 1209759.3728
52 | 2655959.7187 | 1209745.3506 | 2655986.5022 | 1209747.758
53 | 2655968.6984 | 1209737.3773 | 2655971.4233 | 1209720.8845
54 | 2655968.6984 | 1209737.3773 | 2655953.1296 | 1209735.9972
55 | 2655925.2035 | 1209733.6342 | 2655953.1296 | 1209735.9972
56 | 2655953.1296 | 1209735.9972 | 2655954.2024 | 1209725.327
57 | 2655924.538 | 1209742.1886 | 2655924.8663 | 1209737.978 | 2655925.2035 | 1209733.6342
58 | 2655954.2024 | 1209725.327 | 2655956.1102 | 1209706.3501
59 | 2656100.5368 | 1209699.4081 | 2656102.7018 | 1209679.1337 | 2656103.423 | 1209675.1825 | 2656103.423 | 1209675.1825
60 | 2655907.6373 | 1209651.7653 | 2655906.0576 | 1209651.6282 | 2655906.2537 | 1209649.362 | 2655898.3005 | 1209641.5273 | 2655899.443 | 1209636.4016 | 2655899.9076 | 1209631.4586
61 | 2655921.4753 | 1209652.94 | 2655907.6373 | 1209651.7653
62 | 2655901.0922 | 1209608.8451 | 2655901.6803 | 1209612.5972 | 2655899.9076 | 1209631.4586
63 | 2655899.5371 | 1209739.942 | 2655864.0794 | 1209737.0497
64 | 2655924.538 | 1209742.1886 | 2655899.5371 | 1209739.942
65 | 2655899.5371 | 1209739.942 | 2655898.7693 | 1209761.491
66 | 2655864.0067 | 1209737.0438 | 2655864.0794 | 1209737.0497
67 | 2655924.538 | 1209742.1886 | 2655932.1843 | 1209742.8758
68 | 2655898.7693 | 1209761.491 | 2655898.2925 | 1209774.874
69 | 2655942.681 | 1209661.9552 | 2655942.681 | 1209661.9552 | 2655940.5274 | 1209663.0356 | 2655939.524 | 1209663.8601 | 2655937.9108 | 1209664.8566 | 2655936.4817 | 1209664.8766 | 2655932.2558 | 1209664.513
70 | 2655860.582 | 1209615.8145 | 2655884.399 | 1209611.717
71 | 2655860.582 | 1209615.8145 | 2655856.9854 | 1209596.4693
72 | 2655901.0922 | 1209608.8451 | 2655884.399 | 1209611.717
73 | 2655856.9854 | 1209596.4693 | 2655842.6735 | 1209596.3798 | 2655821.7844 | 1209589.2246 | 2655814.2899 | 1209587.6773
74 | 2655854.7471 | 1209572.4896 | 2655856.9854 | 1209596.4693
75 | 2655959.7187 | 1209745.3506 | 2655932.1843 | 1209742.8758
76 | 2655323.4666 | 1209259.0565 | 2655323.3831 | 1209268.0611 | 2655324.9487 | 1209273.8346 | 2655327.6717 | 1209279.3964 | 2655331.7909 | 1209284.3931 | 2655336.0133 | 1209286.6703
77 | 2655402.6626 | 1209313.233 | 2655399.1383 | 1209315.7468
78 | 2655894.1168 | 1209838.2165 | 2655895.1998 | 1209852.424 | 2655894.2791 | 1209868.7585 | 2655887.6027 | 1209935.6136
79 | 2655894.1168 | 1209838.2165 | 2655896.2256 | 1209832.9776 | 2655896.7746 | 1209817.5319
80 | 2655894.1168 | 1209838.2165 | 2655891.2425 | 1209841.5916 | 2655886.4941 | 1209841.3693 | 2655849.0997 | 1209833.2526
81 | 2656011.2322 | 1209692.9053 | 2656004.0527 | 1209722.5686
82 | 2656040.6397 | 1209780.4092 | 2656040.4585 | 1209776.9852 | 2656038.4977 | 1209769.6736 | 2656035.1949 | 1209762.8274 | 2656031.871 | 1209759.3728
83 | 2655957.1174 | 1209696.3314 | 2655956.1102 | 1209706.3501
84 | 2655897.5674 | 1209795.2232 | 2655896.7746 | 1209817.5319
85 | 2655901.0922 | 1209608.8451 | 2655916.2959 | 1209606.2208
86 | 2655898.0381 | 1209782.0126 | 2655898.2925 | 1209774.874
87 | 2655928.4012 | 1209604.1313 | 2655929.1255 | 1209607.9515 | 2655931.723 | 1209618.7045
88 | 2655928.4012 | 1209604.1313 | 2655916.2959 | 1209606.2208
89 | 2656017.3535 | 1209567.9548 | 2656014.8964 | 1209569.7773 | 2656010.1568 | 1209571.8341 | 2656004.8196 | 1209572.7846 | 2655987.5724 | 1209572.0112 | 2655979.1224 | 1209575.0005 | 2655963.1754 | 1209588.7814 | 2655952.2572 | 1209591.5474 | 2655945.2245 | 1209596.5956 | 2655943.0948 | 1209601.612 | 2655928.4012 | 1209604.1313
90 | 2656024.0961 | 1209554.9548 | 2656020.3312 | 1209562.4906 | 2656017.8022 | 1209567.1141 | 2656017.3535 | 1209567.9548
91 | 2656024.0961 | 1209554.9548 | 2656026.5421 | 1209555.9228 | 2656028.8263 | 1209556.3222 | 2656030.7106 | 1209556.4066 | 2656032.8735 | 1209555.96 | 2656034.9861 | 1209555.2016 | 2656038.014 | 1209553.2955 | 2656039.2953 | 1209552.1489
92 | 2656024.0961 | 1209554.9548 | 2656022.146 | 1209553.7802 | 2656019.4902 | 1209551.6763 | 2656013.1935 | 1209546.3251 | 2656007.8135 | 1209541.0829
93 | 2655710.523 | 1209714.5318 | 2655677.3813 | 1209711.6072
94 | 2655783.3745 | 1209581.2942 | 2655814.2899 | 1209587.6773
95 | 2655854.7471 | 1209572.4896 | 2655862.7071 | 1209562.5693 | 2655866.7018 | 1209553.19
96 | 2655854.7471 | 1209572.4896 | 2655841.8291 | 1209569.7385
97 | 2656013.1827 | 1209679.904 | 2656011.2322 | 1209692.9053 | 2656011.2322 | 1209692.9053
98 | 2655897.5674 | 1209795.2232 | 2655866.5254 | 1209795.2771
99 | 2655897.5674 | 1209795.2232 | 2655897.8571 | 1209787.0925
100 | 2655898.0381 | 1209782.0126 | 2655897.8571 | 1209787.0925
101 | 2655962.5173 | 1209658.9393 | 2655957.2791 | 1209694.7226 | 2655957.1174 | 1209696.3314
102 | 2655962.5173 | 1209658.9393 | 2655965.482 | 1209638.655 | 2655967.0835 | 1209634.8455 | 2655968.4743 | 1209634.0581 | 2655971.4499 | 1209633.6635 | 2655975.5836 | 1209634.2452
103 | 2655962.5173 | 1209658.9393 | 2655974.5504 | 1209660.4752 | 2655979.486 | 1209661.8223
104 | 2656112.0391 | 1209612.5206 | 2656108.9369 | 1209611.1776
105 | 2656124.5911 | 1209616.2463 | 2656115.8845 | 1209614.1855 | 2656112.0391 | 1209612.5206
106 | 2656039.2953 | 1209552.1489 | 2656041.9234 | 1209549.7968 | 2656044.6335 | 1209547.1005
107 | 2656003.3691 | 1209536.7522 | 2656007.8135 | 1209541.0829
108 | 2655570.0614 | 1209702.1367 | 2655677.3813 | 1209711.6072
109 | 2655570.0614 | 1209702.1367 | 2655548.5793 | 1209700.241
110 | 2655736.5131 | 1209571.6397 | 2655743.5889 | 1209529.414 | 2655748.5698 | 1209525.1135 | 2655765.1379 | 1209526.1604
111 | 2655736.5131 | 1209571.6397 | 2655783.3745 | 1209581.2942
112 | 2655736.5131 | 1209571.6397 | 2655722.0465 | 1209658.1006
113 | 2655813.5327 | 1209563.7101 | 2655820.0035 | 1209565.0936 | 2655822.4765 | 1209565.617 | 2655841.8291 | 1209569.7385
114 | 2656138.1695 | 1209565.8439 | 2656134.4417 | 1209581.5324
115 | 2656124.5911 | 1209616.2463 | 2656124.7058 | 1209614.5575 | 2656132.1861 | 1209591.0249 | 2656134.4417 | 1209581.5324
116 | 2656138.1695 | 1209565.8439 | 2656141.354 | 1209566.6855
117 | 2656086.6511 | 1209502.5887 | 2656105.5781 | 1209513.0839 | 2656120.8652 | 1209521.0323 | 2656131.7798 | 1209525.949 | 2656147.6965 | 1209532.4136 | 2656138.1695 | 1209565.8439
118 | 2656124.5911 | 1209616.2463 | 2656125.987 | 1209618.1495 | 2656130.1191 | 1209620.0673 | 2656142.8544 | 1209623.4476
119 | 2656178.1423 | 1209576.4596 | 2656141.354 | 1209566.6855
120 | 2656141.354 | 1209566.6855 | 2656137.8334 | 1209581.7171
121 | 2656086.6511 | 1209502.5887 | 2656080.3933 | 1209508.4667 | 2656060.7606 | 1209529.4786
122 | 2656145.9732 | 1209624.2754 | 2656142.8544 | 1209623.4476
123 | 2656058.6155 | 1209531.7745 | 2656060.7606 | 1209529.4786
124 | 2656058.6155 | 1209531.7745 | 2656051.7454 | 1209539.1271 | 2656047.2063 | 1209544.4018
125 | 2655960.8422 | 1209491.4904 | 2655973.9087 | 1209506.8776 | 2655976.5806 | 1209509.7506
126 | 2655985.4975 | 1209519.3382 | 2655976.5806 | 1209509.7506
127 | 2655960.8422 | 1209491.4904 | 2655955.0359 | 1209498.6847 | 2655943.7043 | 1209516.3335 | 2655941.543 | 1209520.3656
128 | 2655960.8422 | 1209491.4904 | 2655957.3216 | 1209486.7657 | 2655951.8455 | 1209480.1298
129 | 2655985.4975 | 1209519.3382 | 2656003.3691 | 1209536.7522
130 | 2655985.4975 | 1209519.3382 | 2655996.5759 | 1209509.3618
131 | 2655939.4647 | 1209524.2429 | 2655939.4647 | 1209524.2429 | 2655941.543 | 1209520.3656
132 | 2655951.8455 | 1209480.1298 | 2655944.3493 | 1209471.0459 | 2655944.3493 | 1209471.0459
133 | 2655996.5759 | 1209509.3618 | 2656000.8767 | 1209505.4888
134 | 2655955.1905 | 1209530.6086 | 2655944.9334 | 1209527.1181 | 2655939.4647 | 1209524.2429
135 | 2655927.1027 | 1209469.3722 | 2655941.9041 | 1209469.989 | 2655944.3493 | 1209471.0459
136 | 2656013.563 | 1209494.0645 | 2656000.8767 | 1209505.4888
137 | 2655955.2491 | 1209530.6286 | 2655955.1905 | 1209530.6086
138 | 2655955.6168 | 1209530.7537 | 2655955.2491 | 1209530.6286
139 | 2656013.1827 | 1209679.904 | 2656014.3137 | 1209672.3652
140 | 2656017.3216 | 1209652.316 | 2656014.3137 | 1209672.3652
141 | 2656047.2063 | 1209544.4018 | 2656046.3736 | 1209545.3693 | 2656044.6335 | 1209547.1005

## bus_geodata
| x | y | coords
0 | 2655223.3314 | 1209924.9683
1 | 2655239.8062 | 1209933.1256
2 | 2655198.6666 | 1209912.2234
3 | 2655200.2513 | 1209893.7381
4 | 2655207.4776 | 1209870.1242
5 | 2655191.5952 | 1209773.6644
6 | 2655501.6889 | 1209781.3548
7 | 2655499.5388 | 1209749.172
8 | 2655671.7091 | 1210122.8415
9 | 2655664.3331 | 1210055.6104
10 | 2655705.7151 | 1210143.7823
11 | 2655167.6997 | 1209725.3283
12 | 2655496.5724 | 1209720.193
13 | 2655842.0969 | 1209723.7726
14 | 2655877.9692 | 1209725.7983
15 | 2655721.3839 | 1209715.4902
16 | 2655566.1861 | 1209706.5991
17 | 2655801.3031 | 1210006.582
18 | 2655149.6723 | 1209668.9035
19 | 2655162.776 | 1209664.8221
20 | 2655160.2427 | 1209594.3027
21 | 2655461.5817 | 1209729.8362
22 | 2655562.6204 | 1209736.309
23 | 2655233.0429 | 1209504.2651
24 | 2655194.5312 | 1209561.0557
25 | 2655383.4934 | 1209328.8656
26 | 2655160.1404 | 1209573.3433
27 | 2655176.7743 | 1209572.8864
28 | 2655482.976 | 1209694.4518
29 | 2655496.6843 | 1209695.6615
30 | 2655456.288 | 1209739.8081
31 | 2655883.7866 | 1209678.4356
32 | 2655883.4289 | 1209673.6072
33 | 2655920.5089 | 1209663.5929
34 | 2655894.4382 | 1209730.6063
35 | 2656004.1876 | 1209740.5342
36 | 2655999.8058 | 1209740.1151
37 | 2656003.5353 | 1209749.2889
38 | 2656041.0865 | 1209743.845
39 | 2656046.3975 | 1209744.3215
40 | 2656097.5676 | 1209727.2141
41 | 2656003.7398 | 1209723.8612
42 | 2656019.0669 | 1209751.9178
43 | 2655986.5022 | 1209747.758
44 | 2655968.6984 | 1209737.3773
45 | 2655971.4233 | 1209720.8845
46 | 2655953.1296 | 1209735.9972
47 | 2655925.2035 | 1209733.6342
48 | 2655954.2024 | 1209725.327
49 | 2656100.5368 | 1209699.4081
50 | 2655907.6373 | 1209651.7653
51 | 2655899.9076 | 1209631.4586
52 | 2655921.4753 | 1209652.94
53 | 2655899.5371 | 1209739.942
54 | 2655864.0794 | 1209737.0497
55 | 2655924.538 | 1209742.1886
56 | 2655898.7693 | 1209761.491
57 | 2655932.2558 | 1209664.513
58 | 2655860.582 | 1209615.8145
59 | 2655884.399 | 1209611.717
60 | 2655856.9854 | 1209596.4693
61 | 2655932.1843 | 1209742.8758
62 | 2655549.419 | 1209744.9215
63 | 2655336.0133 | 1209286.6703
64 | 2655399.1383 | 1209315.7468
65 | 2655887.6027 | 1209935.6136
66 | 2655894.1168 | 1209838.2165
67 | 2656004.0527 | 1209722.5686
68 | 2656040.6397 | 1209780.4092
69 | 2656031.871 | 1209759.3728
70 | 2655959.7187 | 1209745.3506
71 | 2655956.1102 | 1209706.3501
72 | 2656103.423 | 1209675.1825
73 | 2655896.7746 | 1209817.5319
74 | 2655849.0997 | 1209833.2527
75 | 2655901.0922 | 1209608.8451
76 | 2655864.0067 | 1209737.0438
77 | 2655898.2925 | 1209774.874
78 | 2655931.723 | 1209618.7045
79 | 2655928.4012 | 1209604.1313
80 | 2656017.3535 | 1209567.9548
81 | 2656024.0961 | 1209554.9548
82 | 2655916.2959 | 1209606.2208
83 | 2655942.681 | 1209661.9552
84 | 2655710.523 | 1209714.5318
85 | 2655814.2899 | 1209587.6773
86 | 2655854.7471 | 1209572.4896
87 | 2656011.2322 | 1209692.9053
88 | 2655897.5674 | 1209795.2232
89 | 2655866.5254 | 1209795.2771
90 | 2655897.8571 | 1209787.0925
91 | 2655898.0381 | 1209782.0126
92 | 2655957.1174 | 1209696.3314
93 | 2655962.5173 | 1209658.9393
94 | 2655975.5835 | 1209634.2452
95 | 2655979.486 | 1209661.8223
96 | 2655402.6626 | 1209313.233
97 | 2655323.4666 | 1209259.0565
98 | 2656108.9369 | 1209611.1776
99 | 2656112.0391 | 1209612.5206
100 | 2656039.2953 | 1209552.1489
101 | 2656007.8135 | 1209541.0829
102 | 2655677.3813 | 1209711.6072
103 | 2655570.0614 | 1209702.1367
104 | 2655548.5793 | 1209700.241
105 | 2655765.1379 | 1209526.1604
106 | 2655736.5131 | 1209571.6397
107 | 2655783.3745 | 1209581.2942
108 | 2655722.0465 | 1209658.1006
109 | 2655841.8291 | 1209569.7385
110 | 2655813.5327 | 1209563.7101
111 | 2655866.7018 | 1209553.19
112 | 2656134.4417 | 1209581.5324
113 | 2656138.1695 | 1209565.8439
114 | 2656124.5911 | 1209616.2463
115 | 2656141.354 | 1209566.6855
116 | 2656086.6511 | 1209502.5887
117 | 2656142.8544 | 1209623.4476
118 | 2656178.1423 | 1209576.4596
119 | 2656137.8334 | 1209581.7171
120 | 2656060.7606 | 1209529.4786
121 | 2656145.9732 | 1209624.2754
122 | 2656058.6155 | 1209531.7745
123 | 2655976.5806 | 1209509.7506
124 | 2655960.8422 | 1209491.4904
125 | 2655985.4975 | 1209519.3382
126 | 2655941.543 | 1209520.3656
127 | 2655951.8455 | 1209480.1298
128 | 2656003.3691 | 1209536.7522
129 | 2655996.5759 | 1209509.3618
130 | 2655939.4647 | 1209524.2429
131 | 2655944.3493 | 1209471.0459
132 | 2656000.8767 | 1209505.4888
133 | 2655955.1905 | 1209530.6086
134 | 2655927.1027 | 1209469.3722
135 | 2656013.563 | 1209494.0645
136 | 2655955.2491 | 1209530.6286
137 | 2656013.1827 | 1209679.904
138 | 2656014.3137 | 1209672.3652
139 | 2656017.3216 | 1209652.316
140 | 2655955.6168 | 1209530.7537
141 | 2656044.6335 | 1209547.1005
142 | 2656047.2063 | 1209544.4018
143 | 2655901.0922 | 1209608.8451

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98441 | -0.30047 | 0.00016463 | 4.1261e-05
1 | 0.9844 | -0.30055 | 0.00025427 | 6.3726e-05
2 | 0.98442 | -0.30026 | 0 | 0
3 | 0.98443 | -0.30012 | 0.000119 | 2.9825e-05
4 | 0.98444 | -0.2998 | 0 | 0
5 | 0.98459 | -0.29694 | 0 | 0
6 | 0.98615 | -0.26626 | 0 | 0
7 | 0.98633 | -0.26274 | 0.00045612 | 0.00011431
8 | 0.98254 | -0.33588 | 0 | 0
9 | 0.98228 | -0.34093 | 0.0040556 | 0.0010164
10 | 0.98269 | -0.33296 | 0 | 0
11 | 0.98431 | -0.30226 | 0.00020875 | 5.2319e-05
12 | 0.98648 | -0.25965 | 0 | 0
13 | 0.98969 | -0.19707 | 0 | 0
14 | 0.99076 | -0.17629 | 0 | 0
15 | 0.98726 | -0.24418 | 0.0079434 | 0.0019908
16 | 0.987 | -0.24945 | 0 | 0
17 | 0.98332 | -0.32064 | 0.0018842 | 0.00047222
18 | 0.98404 | -0.3076 | 0 | 0
19 | 0.98397 | -0.30912 | 0 | 0
20 | 0.98366 | -0.31502 | 0.0018814 | 0.00047153
21 | 0.98647 | -0.25986 | 0.00022237 | 5.5731e-05
22 | 0.98689 | -0.25158 | 0.0012034 | 0.0003016
23 | 0.9834 | -0.32024 | 0 | 0
24 | 0.98352 | -0.31785 | 0.00038872 | 9.7423e-05
25 | 0.98284 | -0.33126 | 0 | 0
26 | 0.98361 | -0.31606 | 0 | 0
27 | 0.98357 | -0.31689 | 0.00044439 | 0.00011137
28 | 0.98579 | -0.27289 | 0.00058212 | 0.00014589
29 | 0.98579 | -0.27274 | 0.00029899 | 7.4933e-05
30 | 0.98647 | -0.25988 | 8.543e-05 | 2.1411e-05
31 | 0.99395 | -0.11512 | 0 | 0
32 | 0.99392 | -0.11554 | 0.0049759 | 0.0012471
33 | 0.99663 | -0.06398 | 0 | 0
34 | 0.98987 | -0.19337 | 0.003103 | 0.00077769
35 | 0.98026 | -0.37994 | 0 | 0
36 | 0.98011 | -0.38288 | 0 | 0
37 | 0.98077 | -0.36984 | 0 | 0
38 | 0.97934 | -0.39781 | 0.0044937 | 0.0011262
39 | 0.97923 | -0.39995 | 0 | 0
40 | 0.9778 | -0.42811 | 0 | 0
41 | 0.97953 | -0.39409 | 0.01058 | 0.0026515
42 | 0.98062 | -0.37282 | 0.0041994 | 0.0010525
43 | 0.98194 | -0.34698 | 0.0033914 | 0.00084997
44 | 0.98641 | -0.26029 | 0 | 0
45 | 0.9863 | -0.26248 | 0.0073211 | 0.0018348
46 | 0.98652 | -0.25824 | 0 | 0
47 | 0.98758 | -0.23753 | 0 | 0
48 | 0.98618 | -0.26479 | 0.0054458 | 0.0013648
49 | 0.97723 | -0.43936 | 0.0074371 | 0.0018639
50 | 0.99829 | -0.032383 | 0 | 0
51 | 1 | 0 | -0.50957 | -0.13006
52 | 0.99735 | -0.050195 | 0 | 0
53 | 0.98597 | -0.26889 | 0 | 0
54 | 0.98593 | -0.2696 | 0.00055438 | 0.00013894
55 | 0.98664 | -0.25576 | 0 | 0
56 | 0.98541 | -0.27979 | 0.0044684 | 0.0011199
57 | 0.99641 | -0.068143 | 0.012041 | 0.0030178
58 | 0.99335 | -0.12702 | 0 | 0
59 | 0.99592 | -0.077757 | 0.021118 | 0.0052927
60 | 0.99126 | -0.16732 | 0 | 0
61 | 0.986 | -0.26808 | 0.0061582 | 0.0015434
62 | 0.98685 | -0.25247 | 0.0027643 | 0.0006928
63 | 0.98278 | -0.33243 | 0.00061666 | 0.00015455
64 | 0.98282 | -0.3316 | 0.0002422 | 6.0701e-05
65 | 0.98394 | -0.3085 | 0 | 0
66 | 0.98447 | -0.29802 | 0 | 0
67 | 0.9795 | -0.39473 | 0.0030369 | 0.00076111
68 | 0.98047 | -0.37582 | 0.0030759 | 0.00077089
69 | 0.98053 | -0.37452 | 0.0031225 | 0.00078257
70 | 0.98387 | -0.30949 | 0.006099 | 0.0015285
71 | 0.98568 | -0.2746 | 0.0023349 | 0.00058518
72 | 0.9769 | -0.44588 | 0.014624 | 0.0036651
73 | 0.98461 | -0.29541 | 0.0028143 | 0.00070533
74 | 0.98443 | -0.29883 | 0.00094096 | 0.00023583
75 | 0.99804 | -0.03712 | 0 | 0
76 | 0.98593 | -0.2696 | 0.00055441 | 0.00013895
77 | 0.98511 | -0.28549 | 0.0016918 | 0.000424
78 | 0.99539 | -0.087257 | 0.0077897 | 0.0019523
79 | 0.9955 | -0.085209 | 0 | 0
80 | 0.98372 | -0.31079 | 0 | 0
81 | 0.98202 | -0.34386 | 0 | 0
82 | 0.99701 | -0.056519 | 0.010571 | 0.0026492
83 | 0.99633 | -0.069744 | 0.0080875 | 0.0020269
84 | 0.98712 | -0.24689 | 0.0010344 | 0.00025925
85 | 0.98958 | -0.20001 | 0.03262 | 0.0081754
86 | 0.98963 | -0.19895 | 0 | 0
87 | 0.97884 | -0.40766 | 0.006766 | 0.0016957
88 | 0.98481 | -0.29151 | 0 | 0
89 | 0.98478 | -0.2921 | 0.0010557 | 0.00026458
90 | 0.98489 | -0.28993 | 0.0070008 | 0.0017546
91 | 0.98497 | -0.28831 | 0.004234 | 0.0010611
92 | 0.98543 | -0.27935 | 0.020388 | 0.0051098
93 | 0.98523 | -0.28338 | 0 | 0
94 | 0.98511 | -0.28567 | 0.0038134 | 0.00095573
95 | 0.98519 | -0.28404 | 0.0021217 | 0.00053175
96 | 0.98282 | -0.33165 | 0.00067284 | 0.00016863
97 | 0.98277 | -0.33265 | 0.00037581 | 9.4187e-05
98 | 0.97593 | -0.46317 | 0.0019287 | 0.00048338
99 | 0.97593 | -0.46305 | 0.006123 | 0.0015346
100 | 0.98132 | -0.35746 | 0.0028033 | 0.00070258
101 | 0.98043 | -0.37485 | 0.00359 | 0.00089974
102 | 0.98673 | -0.25453 | 0.0050055 | 0.0012545
103 | 0.98595 | -0.26963 | 0.0019006 | 0.00047633
104 | 0.98584 | -0.27192 | 0.0050392 | 0.0012629
105 | 0.98842 | -0.22256 | 0.0081854 | 0.0020514
106 | 0.98891 | -0.21293 | 0 | 0
107 | 0.98931 | -0.20515 | 0 | 0
108 | 0.98884 | -0.21442 | 0.00095718 | 0.00023989
109 | 0.98886 | -0.21382 | 0.025556 | 0.006405
110 | 0.98786 | -0.23324 | 0.037626 | 0.00943
111 | 0.9894 | -0.20334 | 0.010739 | 0.0026916
112 | 0.97655 | -0.45088 | 0.0032933 | 0.00082538
113 | 0.97683 | -0.44535 | 0 | 0
114 | 0.97603 | -0.46112 | 0 | 0
115 | 0.97681 | -0.4458 | 0 | 0
116 | 0.97935 | -0.39592 | 0 | 0
117 | 0.97589 | -0.46385 | 0.0047217 | 0.0011834
118 | 0.97665 | -0.449 | 0.0046111 | 0.0011557
119 | 0.97677 | -0.44665 | 0.0030002 | 0.00075193
120 | 0.98027 | -0.37802 | 0.0034151 | 0.00085589
121 | 0.97588 | -0.46401 | 0.0027127 | 0.00067987
122 | 0.98035 | -0.37632 | 0.0042382 | 0.0010622
123 | 0.97756 | -0.43098 | 0.0027778 | 0.00069617
124 | 0.97622 | -0.45733 | 0 | 0
125 | 0.97832 | -0.41605 | 0 | 0
126 | 0.97542 | -0.47292 | 0.0026873 | 0.0006735
127 | 0.97574 | -0.4667 | 0.0086948 | 0.0021791
128 | 0.97999 | -0.38343 | 0.0043541 | 0.0010912
129 | 0.97819 | -0.41857 | 0.0032243 | 0.0008081
130 | 0.97534 | -0.47468 | 0.0057448 | 0.0014398
131 | 0.97545 | -0.47244 | 0.010055 | 0.0025199
132 | 0.97816 | -0.41921 | 0.0034085 | 0.00085424
133 | 0.97508 | -0.47969 | 0.0082189 | 0.0020598
134 | 0.97518 | -0.47776 | 0.016583 | 0.0041562
135 | 0.97812 | -0.42004 | 0.0026598 | 0.00066661
136 | 0.97508 | -0.4797 | 0.0040764 | 0.0010216
137 | 0.97864 | -0.41161 | 0.0043493 | 0.00109
138 | 0.97856 | -0.4133 | 0.005531 | 0.0013862
139 | 0.97843 | -0.41576 | 0.0066523 | 0.0016672
140 | 0.97508 | -0.47972 | 0.0037614 | 0.00094269
141 | 0.98103 | -0.36313 | 0.0028017 | 0.00070217
142 | 0.98089 | -0.36581 | 0.0056979 | 0.001428
143 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00025427 | 6.349e-05 | -0.00025427 | -6.3726e-05 | 1.0328e-09 | -2.3641e-07 | 0.00038427 | 0.00038435 | 0.00038435 | 0.98441 | -0.30047 | 0.9844 | -0.30055 | 0.10559
1 | -0.0004189 | -0.00010475 | 0.00041891 | 0.0001044 | 4.1724e-09 | -3.5029e-07 | 0.00063312 | 0.000633 | 0.00063312 | 0.98441 | -0.30047 | 0.98442 | -0.30026 | 0.17394
2 | -0.00041891 | -0.0001044 | 0.00041891 | 0.00010416 | 2.8198e-09 | -2.3682e-07 | 0.000633 | 0.00063291 | 0.000633 | 0.98442 | -0.30026 | 0.98443 | -0.30012 | 0.1739
3 | -0.00053791 | -0.00013399 | 0.00053792 | 0.00013358 | 7.9892e-09 | -4.0497e-07 | 0.00081279 | 0.00081265 | 0.00081279 | 0.98443 | -0.30012 | 0.98444 | -0.2998 | 0.22329
4 | -0.00053792 | -0.00013358 | 0.00053799 | 0.00012992 | 7.2149e-08 | -3.6645e-06 | 0.00081265 | 0.00081135 | 0.00081265 | 0.98444 | -0.2998 | 0.98459 | -0.29694 | 0.22326
5 | 0.0048365 | 0.0012044 | -0.0048352 | -0.0012044 | 1.2209e-06 | 6.0327e-09 | 0.0073066 | 0.0073069 | 0.0073069 | 0.98459 | -0.29694 | 0.98431 | -0.30226 | 2.0074
6 | -0.0053745 | -0.0013343 | 0.0053823 | 0.0013353 | 7.8036e-06 | 9.7132e-07 | 0.008118 | 0.0081166 | 0.008118 | 0.98459 | -0.29694 | 0.98615 | -0.26626 | 2.2302
7 | -0.0053823 | -0.0013353 | 0.0053832 | 0.0013354 | 8.9496e-07 | 1.1049e-07 | 0.0081166 | 0.0081164 | 0.0081166 | 0.98615 | -0.26626 | 0.98633 | -0.26274 | 2.2298
8 | -0.0058393 | -0.0014497 | 0.0058401 | 0.0014499 | 8.5182e-07 | 1.7111e-07 | 0.0088045 | 0.0088044 | 0.0088045 | 0.98633 | -0.26274 | 0.98648 | -0.25965 | 2.4188
9 | 0.0040566 | 0.0010162 | -0.0040556 | -0.0010164 | 9.7488e-07 | -2.4819e-07 | 0.0061434 | 0.0061437 | 0.0061437 | 0.98254 | -0.33588 | 0.98228 | -0.34093 | 1.6878
10 | -0.0040566 | -0.0010162 | 0.0040572 | 0.001016 | 5.6554e-07 | -1.4423e-07 | 0.0061434 | 0.0061432 | 0.0061434 | 0.98254 | -0.33588 | 0.98269 | -0.33296 | 1.6877
11 | -0.0040572 | -0.001016 | 0.0040596 | 0.0010154 | 2.3784e-06 | -6.0858e-07 | 0.0061432 | 0.0061425 | 0.0061432 | 0.98269 | -0.33296 | 0.98332 | -0.32064 | 1.6877
12 | 0.0046265 | 0.0011521 | -0.0046253 | -0.0011521 | 1.17e-06 | -6.2297e-08 | 0.0069913 | 0.0069916 | 0.0069916 | 0.98431 | -0.30226 | 0.98404 | -0.3076 | 1.9208
13 | -0.0061479 | -0.0015264 | 0.0061509 | 0.0015271 | 2.9687e-06 | 7.2274e-07 | 0.0092685 | 0.009268 | 0.0092685 | 0.98648 | -0.25965 | 0.987 | -0.24945 | 2.5463
14 | 0.0003078 | 7.6522e-05 | -0.0003078 | -7.6998e-05 | 3.0211e-09 | -4.7548e-07 | 0.00046407 | 0.00046424 | 0.00046424 | 0.98648 | -0.25965 | 0.98647 | -0.25986 | 0.12754
15 | -0.03201 | -0.0080333 | 0.032042 | 0.0080531 | 3.1751e-05 | 1.985e-05 | 0.048132 | 0.048132 | 0.048132 | 0.98969 | -0.19707 | 0.99076 | -0.17629 | 13.2231
16 | 0.021866 | 0.0054996 | -0.021817 | -0.0054698 | 4.9092e-05 | 2.9867e-05 | 0.032883 | 0.032884 | 0.032884 | 0.98969 | -0.19707 | 0.98726 | -0.24418 | 9.034
17 | 0.010144 | 0.0025336 | -0.010119 | -0.0025212 | 2.5192e-05 | 1.2421e-05 | 0.015249 | 0.01525 | 0.01525 | 0.98969 | -0.19707 | 0.987 | -0.24945 | 4.1897
18 | 0.1646 | 0.041741 | -0.16447 | -0.041655 | 0.000135 | 8.572e-05 | 0.24739 | 0.24739 | 0.24739 | 0.99076 | -0.17629 | 0.98987 | -0.19337 | 22.6545
19 | -0.19664 | -0.049794 | 0.19722 | 0.050163 | 0.00057952 | 0.00036883 | 0.29552 | 0.29552 | 0.29552 | 0.99076 | -0.17629 | 0.99395 | -0.11512 | 27.0621
20 | 0.013874 | 0.003479 | -0.013872 | -0.003478 | 1.7879e-06 | 1.0048e-06 | 0.020911 | 0.020911 | 0.020911 | 0.98726 | -0.24418 | 0.98712 | -0.24689 | 5.7448
21 | 0.0039682 | 0.00099412 | -0.0039678 | -0.00099424 | 4.0229e-07 | -1.2558e-07 | 0.0059824 | 0.0059825 | 0.0059825 | 0.987 | -0.24945 | 0.98689 | -0.25158 | 1.6435
22 | -0.0059438 | -0.0014877 | 0.0059472 | 0.0014884 | 3.4344e-06 | 7.6076e-07 | 0.0089937 | 0.0089932 | 0.0089937 | 0.98332 | -0.32064 | 0.98394 | -0.3085 | 2.4708
23 | 0.0046253 | 0.0011521 | -0.004625 | -0.0011521 | 3.3406e-07 | -1.7693e-08 | 0.0069916 | 0.0069917 | 0.0069917 | 0.98404 | -0.3076 | 0.98397 | -0.30912 | 1.9208
24 | 0.004625 | 0.0011521 | -0.0046237 | -0.0011522 | 1.2936e-06 | -6.8121e-08 | 0.0069917 | 0.006992 | 0.006992 | 0.98397 | -0.30912 | 0.98366 | -0.31502 | 1.9209
25 | 0.0027423 | 0.00068067 | -0.0027421 | -0.00068085 | 1.351e-07 | -1.7958e-07 | 0.0041459 | 0.004146 | 0.004146 | 0.98366 | -0.31502 | 0.98361 | -0.31606 | 1.139
26 | 8.543e-05 | 2.1267e-05 | -8.543e-05 | -2.1411e-05 | 7.0269e-11 | -1.4409e-07 | 0.00012881 | 0.00012886 | 0.00012886 | 0.98647 | -0.25986 | 0.98647 | -0.25988 | 0.035402
27 | 0.0027644 | 0.00069264 | -0.0027643 | -0.0006928 | 1.1784e-07 | -1.557e-07 | 0.0041681 | 0.0041682 | 0.0041682 | 0.98689 | -0.25158 | 0.98685 | -0.25247 | 1.1451
28 | -0.0019086 | -0.00047316 | 0.0019088 | 0.00047242 | 2.1468e-07 | -7.3478e-07 | 0.0028861 | 0.0028858 | 0.0028861 | 0.9834 | -0.32024 | 0.98352 | -0.31785 | 0.79288
29 | 0.0019086 | 0.00047316 | -0.0019076 | -0.00047656 | 9.9662e-07 | -3.4059e-06 | 0.0028861 | 0.0028875 | 0.0028875 | 0.9834 | -0.32024 | 0.98284 | -0.33126 | 0.79328
30 | -0.0022975 | -0.00056984 | 0.0022976 | 0.00056962 | 1.0483e-07 | -2.2691e-07 | 0.0034739 | 0.0034738 | 0.0034739 | 0.98352 | -0.31785 | 0.98357 | -0.31689 | 0.95437
31 | 0.00099253 | 0.00024754 | -0.00099247 | -0.00024833 | 5.5189e-08 | -7.9091e-07 | 0.0015023 | 0.0015025 | 0.0015025 | 0.98284 | -0.33126 | 0.98278 | -0.33243 | 0.41279
32 | 0.00091505 | 0.00022902 | -0.00091504 | -0.00022928 | 1.4845e-08 | -2.519e-07 | 0.0013853 | 0.0013854 | 0.0013854 | 0.98284 | -0.33126 | 0.98282 | -0.3316 | 0.3806
33 | 0.0027421 | 0.00068085 | -0.002742 | -0.00068099 | 1.0727e-07 | -1.4255e-07 | 0.004146 | 0.0041461 | 0.0041461 | 0.98361 | -0.31606 | 0.98357 | -0.31689 | 1.139
34 | -0.00058212 | -0.00014589 | 0.00058212 | 0.00014572 | 3.9842e-09 | -1.729e-07 | 0.00087869 | 0.00087863 | 0.00087869 | 0.98579 | -0.27289 | 0.98579 | -0.27274 | 0.2414
35 | -0.00088111 | -0.00022065 | 0.00088114 | 0.00022001 | 3.4548e-08 | -6.4211e-07 | 0.0013299 | 0.0013297 | 0.0013299 | 0.98579 | -0.27274 | 0.98584 | -0.27192 | 0.36537
36 | 0.004976 | 0.0012471 | -0.0049759 | -0.0012471 | 1.0078e-07 | 1.7334e-09 | 0.0074494 | 0.0074494 | 0.0074494 | 0.99395 | -0.11512 | 0.99392 | -0.11554 | 2.0465
37 | -0.2022 | -0.05141 | 0.2027 | 0.051728 | 0.00049939 | 0.00031791 | 0.30297 | 0.30297 | 0.30297 | 0.99395 | -0.11512 | 0.99663 | -0.06398 | 27.7443
38 | 0.020133 | 0.0050474 | -0.020129 | -0.005045 | 3.993e-06 | 2.402e-06 | 0.030061 | 0.030061 | 0.030061 | 0.99663 | -0.06398 | 0.99641 | -0.068143 | 8.2585
39 | -0.22283 | -0.056775 | 0.22298 | 0.05687 | 0.00014832 | 9.4509e-05 | 0.33303 | 0.33303 | 0.33303 | 0.99663 | -0.06398 | 0.99735 | -0.050195 | 30.497
40 | 0.16136 | 0.040878 | -0.16102 | -0.04066 | 0.00034149 | 0.00021776 | 0.24272 | 0.24272 | 0.24272 | 0.98987 | -0.19337 | 0.98758 | -0.23753 | 33.341
41 | 0.03696 | 0.0092794 | -0.036955 | -0.0092761 | 5.1819e-06 | 3.2611e-06 | 0.056111 | 0.056111 | 0.056111 | 0.98026 | -0.37994 | 0.98011 | -0.38288 | 15.4151
42 | -0.063586 | -0.015978 | 0.063617 | 0.015998 | 3.0681e-05 | 1.9525e-05 | 0.096538 | 0.096538 | 0.096538 | 0.98026 | -0.37994 | 0.98077 | -0.36984 | 26.5214
43 | 0.026626 | 0.0066987 | -0.026603 | -0.0066846 | 2.2705e-05 | 1.4065e-05 | 0.040427 | 0.040427 | 0.040427 | 0.98026 | -0.37994 | 0.97934 | -0.39781 | 11.1064
44 | 0.036955 | 0.0092761 | -0.036935 | -0.0092637 | 1.9744e-05 | 1.2426e-05 | 0.056111 | 0.056111 | 0.056111 | 0.98011 | -0.38288 | 0.97953 | -0.39409 | 15.4151
45 | 0.0104 | 0.0026066 | -0.010398 | -0.0026059 | 1.4756e-06 | 7.4498e-07 | 0.015779 | 0.015779 | 0.015779 | 0.98077 | -0.36984 | 0.98062 | -0.37282 | 4.3348
46 | -0.074017 | -0.018604 | 0.074098 | 0.018656 | 8.0902e-05 | 5.1561e-05 | 0.11232 | 0.11232 | 0.11232 | 0.98077 | -0.36984 | 0.98194 | -0.34698 | 30.8562
47 | 0.022109 | 0.0055584 | -0.022107 | -0.005557 | 2.2574e-06 | 1.3777e-06 | 0.033599 | 0.033599 | 0.033599 | 0.97934 | -0.39781 | 0.97923 | -0.39995 | 9.2306
48 | 0.022107 | 0.005557 | -0.022078 | -0.0055389 | 2.9685e-05 | 1.8118e-05 | 0.033599 | 0.0336 | 0.0336 | 0.97923 | -0.39995 | 0.9778 | -0.42811 | 9.2307
49 | 0.022078 | 0.0055389 | -0.022066 | -0.0055317 | 1.1839e-05 | 7.2262e-06 | 0.0336 | 0.0336 | 0.0336 | 0.9778 | -0.42811 | 0.97723 | -0.43936 | 9.2307
50 | 0.026356 | 0.0066122 | -0.026355 | -0.0066117 | 7.9953e-07 | 4.9496e-07 | 0.040039 | 0.040039 | 0.040039 | 0.97953 | -0.39409 | 0.9795 | -0.39473 | 10.9998
51 | 0.0061991 | 0.0015534 | -0.0061986 | -0.0015533 | 5.0155e-07 | 1.3032e-07 | 0.0094066 | 0.0094066 | 0.0094066 | 0.98062 | -0.37282 | 0.98053 | -0.37452 | 2.5842
52 | -0.077489 | -0.019506 | 0.077628 | 0.019594 | 0.00013912 | 8.8697e-05 | 0.11746 | 0.11746 | 0.11746 | 0.98194 | -0.34698 | 0.98387 | -0.30949 | 32.2681
53 | 0.0073219 | 0.0018351 | -0.0073211 | -0.0018348 | 7.6475e-07 | 2.7608e-07 | 0.011045 | 0.011045 | 0.011045 | 0.98641 | -0.26029 | 0.9863 | -0.26248 | 3.0344
54 | -0.0073219 | -0.0018351 | 0.0073226 | 0.0018354 | 7.1298e-07 | 2.5734e-07 | 0.011045 | 0.011045 | 0.011045 | 0.98641 | -0.26029 | 0.98652 | -0.25824 | 3.0344
55 | -0.041458 | -0.010401 | 0.041499 | 0.010427 | 4.0984e-05 | 2.5873e-05 | 0.062538 | 0.062537 | 0.062538 | 0.98652 | -0.25824 | 0.98758 | -0.23753 | 17.1806
56 | 0.034136 | 0.0085659 | -0.034125 | -0.0085592 | 1.0663e-05 | 6.6874e-06 | 0.051492 | 0.051493 | 0.051493 | 0.98652 | -0.25824 | 0.98618 | -0.26479 | 14.1463
57 | 0.11952 | 0.030233 | -0.11942 | -0.030166 | 0.00010447 | 6.6748e-05 | 0.18019 | 0.18019 | 0.18019 | 0.98758 | -0.23753 | 0.98664 | -0.25576 | 49.5015
58 | 0.028679 | 0.0071944 | -0.028666 | -0.007186 | 1.3395e-05 | 8.3293e-06 | 0.043276 | 0.043276 | 0.043276 | 0.98618 | -0.26479 | 0.98568 | -0.2746 | 11.8889
59 | 0.014629 | 0.0036677 | -0.014624 | -0.0036651 | 4.5413e-06 | 2.6008e-06 | 0.022275 | 0.022275 | 0.022275 | 0.97723 | -0.43936 | 0.9769 | -0.44588 | 6.1196
60 | -0.22317 | -0.056992 | 0.22352 | 0.057215 | 0.00034992 | 0.00022296 | 0.33303 | 0.33303 | 0.33303 | 0.99829 | -0.032383 | 1 | 0 | 30.497
61 | 0.22317 | 0.056992 | -0.22298 | -0.05687 | 0.00019197 | 0.00012232 | 0.33303 | 0.33303 | 0.33303 | 0.99829 | -0.032383 | 0.99735 | -0.050195 | 30.497
62 | 0.2844 | 0.07284 | -0.28389 | -0.072515 | 0.00051046 | 0.0003258 | 0.42375 | 0.42375 | 0.42375 | 1 | 0 | 0.99804 | -0.03712 | 38.8046
63 | 0.0011088 | 0.00027746 | -0.0011088 | -0.00027789 | 3.7356e-08 | -4.2979e-07 | 0.0016733 | 0.0016734 | 0.0016734 | 0.98597 | -0.26889 | 0.98593 | -0.2696 | 0.45974
64 | -0.029294 | -0.0073481 | 0.029312 | 0.0073595 | 1.8347e-05 | 1.1423e-05 | 0.044212 | 0.044212 | 0.044212 | 0.98597 | -0.26889 | 0.98664 | -0.25576 | 12.1463
65 | 0.028185 | 0.0070707 | -0.02817 | -0.0070616 | 1.4632e-05 | 9.0898e-06 | 0.042539 | 0.042539 | 0.042539 | 0.98597 | -0.26889 | 0.98541 | -0.27979 | 11.6866
66 | 0.00055441 | 0.00013895 | -0.00055441 | -0.00013895 | 1.8367e-11 | -9.1673e-10 | 0.00083675 | 0.00083675 | 0.00083675 | 0.98593 | -0.2696 | 0.98593 | -0.2696 | 0.22988
67 | 0.090105 | 0.022807 | -0.090052 | -0.022773 | 5.3228e-05 | 3.3968e-05 | 0.13597 | 0.13597 | 0.13597 | 0.98664 | -0.25576 | 0.986 | -0.26808 | 37.3553
68 | 0.023702 | 0.0059417 | -0.023695 | -0.0059377 | 6.4332e-06 | 3.9467e-06 | 0.035792 | 0.035792 | 0.035792 | 0.98541 | -0.27979 | 0.98511 | -0.28549 | 9.8329
69 | 0.0080881 | 0.0020272 | -0.0080875 | -0.0020269 | 6.1686e-07 | 2.4794e-07 | 0.012079 | 0.012079 | 0.012079 | 0.99641 | -0.068143 | 0.99633 | -0.069744 | 3.3183
70 | -0.11618 | -0.029303 | 0.11645 | 0.029479 | 0.00027468 | 0.00017548 | 0.1741 | 0.1741 | 0.1741 | 0.99335 | -0.12702 | 0.99592 | -0.077757 | 47.8285
71 | 0.11618 | 0.029303 | -0.11595 | -0.02916 | 0.00022366 | 0.00014289 | 0.1741 | 0.1741 | 0.1741 | 0.99335 | -0.12702 | 0.99126 | -0.16732 | 47.8285
72 | -0.13757 | -0.034771 | 0.13784 | 0.034943 | 0.00026863 | 0.0001717 | 0.20565 | 0.20565 | 0.20565 | 0.99592 | -0.077757 | 0.99804 | -0.03712 | 56.4969
73 | 0.041837 | 0.010511 | -0.041772 | -0.01047 | 6.5166e-05 | 4.1139e-05 | 0.062812 | 0.062812 | 0.062812 | 0.99126 | -0.16732 | 0.98958 | -0.20001 | 17.2561
74 | 0.074116 | 0.018649 | -0.074004 | -0.018578 | 0.00011186 | 7.1284e-05 | 0.11128 | 0.11128 | 0.11128 | 0.99126 | -0.16732 | 0.98963 | -0.19895 | 30.5724
75 | 0.083894 | 0.021229 | -0.083727 | -0.021123 | 0.00016637 | 0.00010612 | 0.12668 | 0.12668 | 0.12668 | 0.986 | -0.26808 | 0.98387 | -0.30949 | 34.8021
76 | 0.00037582 | 9.3779e-05 | -0.00037581 | -9.4187e-05 | 3.9393e-09 | -4.0869e-07 | 0.00056887 | 0.00056902 | 0.00056902 | 0.98278 | -0.33243 | 0.98277 | -0.33265 | 0.15632
77 | 0.00067284 | 0.00016858 | -0.00067284 | -0.00016863 | 1.6846e-09 | -5.378e-08 | 0.0010187 | 0.0010187 | 0.0010187 | 0.98282 | -0.3316 | 0.98282 | -0.33165 | 0.27986
78 | -0.0059472 | -0.0014884 | 0.0059502 | 0.0014891 | 2.9665e-06 | 6.5553e-07 | 0.0089932 | 0.0089928 | 0.0089932 | 0.98394 | -0.3085 | 0.98447 | -0.29802 | 2.4707
79 | -0.0068912 | -0.0017243 | 0.006892 | 0.0017246 | 8.5838e-07 | 2.81e-07 | 0.010415 | 0.010415 | 0.010415 | 0.98447 | -0.29802 | 0.98461 | -0.29541 | 2.8612
80 | 0.000941 | 0.00023525 | -0.00094096 | -0.00023583 | 3.5992e-08 | -5.8029e-07 | 0.0014221 | 0.0014223 | 0.0014223 | 0.98447 | -0.29802 | 0.98443 | -0.29883 | 0.39075
81 | 0.023318 | 0.0058506 | -0.023303 | -0.0058418 | 1.4363e-05 | 8.8086e-06 | 0.035426 | 0.035426 | 0.035426 | 0.9795 | -0.39473 | 0.97884 | -0.40766 | 9.7324
82 | -0.0030759 | -0.00077089 | 0.0030761 | 0.00077072 | 1.9117e-07 | -1.7271e-07 | 0.0046682 | 0.0046681 | 0.0046682 | 0.98047 | -0.37582 | 0.98053 | -0.37452 | 1.2825
83 | 0.026331 | 0.0066009 | -0.026325 | -0.0065972 | 5.9665e-06 | 3.6903e-06 | 0.039751 | 0.039751 | 0.039751 | 0.98568 | -0.2746 | 0.98543 | -0.27935 | 10.9206
84 | -0.0097063 | -0.0024299 | 0.0097081 | 0.0024308 | 1.801e-06 | 8.6868e-07 | 0.014668 | 0.014668 | 0.014668 | 0.98461 | -0.29541 | 0.98481 | -0.29151 | 4.0297
85 | 0.14605 | 0.037571 | -0.14591 | -0.037484 | 0.0001376 | 8.7664e-05 | 0.2181 | 0.2181 | 0.2181 | 0.99804 | -0.03712 | 0.99701 | -0.056519 | 29.9586
86 | 0.022004 | 0.0055137 | -0.022001 | -0.0055119 | 2.959e-06 | 1.8028e-06 | 0.033236 | 0.033236 | 0.033236 | 0.98511 | -0.28549 | 0.98497 | -0.28831 | 9.1309
87 | -0.0077897 | -0.0019523 | 0.0077905 | 0.0019526 | 7.6025e-07 | 2.922e-07 | 0.011645 | 0.011645 | 0.011645 | 0.99539 | -0.087257 | 0.9955 | -0.085209 | 3.1991
88 | -0.13515 | -0.034714 | 0.13534 | 0.034835 | 0.00018857 | 0.00012052 | 0.20232 | 0.20232 | 0.20232 | 0.9955 | -0.085209 | 0.99701 | -0.056519 | 55.5832
89 | 0.12736 | 0.032761 | -0.12598 | -0.031879 | 0.0013802 | 0.00088202 | 0.19068 | 0.19068 | 0.19068 | 0.9955 | -0.085209 | 0.98372 | -0.31079 | 52.3842
90 | 0.12598 | 0.031879 | -0.12578 | -0.031752 | 0.00019962 | 0.00012757 | 0.19068 | 0.19068 | 0.19068 | 0.98372 | -0.31079 | 0.98202 | -0.34386 | 52.3842
91 | 0.045513 | 0.011467 | -0.045483 | -0.011448 | 2.96e-05 | 1.8735e-05 | 0.068986 | 0.068986 | 0.068986 | 0.98202 | -0.34386 | 0.98132 | -0.35746 | 18.9522
92 | 0.080272 | 0.020285 | -0.080153 | -0.020209 | 0.00011906 | 7.593e-05 | 0.12169 | 0.12169 | 0.12169 | 0.98202 | -0.34386 | 0.98043 | -0.37485 | 33.4321
93 | 0.012837 | 0.0032187 | -0.012833 | -0.0032161 | 4.6724e-06 | 2.5652e-06 | 0.019352 | 0.019352 | 0.019352 | 0.98712 | -0.24689 | 0.98673 | -0.25453 | 5.3165
94 | 0.009152 | 0.0022944 | -0.0091497 | -0.0022934 | 2.242e-06 | 1.0294e-06 | 0.013762 | 0.013762 | 0.013762 | 0.98958 | -0.20001 | 0.98931 | -0.20515 | 3.7808
95 | 0.010742 | 0.0026927 | -0.010739 | -0.0026916 | 2.2416e-06 | 1.1403e-06 | 0.016151 | 0.016152 | 0.016152 | 0.98963 | -0.19895 | 0.9894 | -0.20334 | 4.4373
96 | 0.063262 | 0.015885 | -0.063217 | -0.015857 | 4.4824e-05 | 2.8518e-05 | 0.095132 | 0.095132 | 0.095132 | 0.98963 | -0.19895 | 0.98886 | -0.21382 | 26.1352
97 | 0.016537 | 0.0041461 | -0.016534 | -0.0041442 | 3.116e-06 | 1.829e-06 | 0.02514 | 0.02514 | 0.02514 | 0.97884 | -0.40766 | 0.97864 | -0.41161 | 6.9067
98 | 0.0010557 | 0.0002642 | -0.0010557 | -0.00026458 | 2.9531e-08 | -3.7491e-07 | 0.001595 | 0.0015951 | 0.0015951 | 0.98481 | -0.29151 | 0.98478 | -0.2921 | 0.43822
99 | -0.010764 | -0.002695 | 0.010765 | 0.0026954 | 8.0692e-07 | 4.129e-07 | 0.016263 | 0.016263 | 0.016263 | 0.98481 | -0.29151 | 0.98489 | -0.28993 | 4.4678
100 | -0.017765 | -0.00445 | 0.017767 | 0.0044508 | 1.3732e-06 | 8.1413e-07 | 0.02684 | 0.02684 | 0.02684 | 0.98489 | -0.28993 | 0.98497 | -0.28831 | 7.3736
101 | 0.0059367 | 0.0014874 | -0.0059356 | -0.0014871 | 1.1386e-06 | 2.4745e-07 | 0.0089644 | 0.0089645 | 0.0089645 | 0.98543 | -0.27935 | 0.98523 | -0.28338 | 2.4628
102 | 0.0038138 | 0.00095557 | -0.0038134 | -0.00095573 | 4.1564e-07 | -1.5935e-07 | 0.00576 | 0.0057602 | 0.0057602 | 0.98523 | -0.28338 | 0.98511 | -0.28567 | 1.5825
103 | 0.0021218 | 0.00053157 | -0.0021217 | -0.00053175 | 6.6416e-08 | -1.7712e-07 | 0.0032045 | 0.0032046 | 0.0032046 | 0.98523 | -0.28338 | 0.98519 | -0.28404 | 0.88038
104 | -0.0019287 | -0.00048338 | 0.0019287 | 0.00048335 | 1.0963e-08 | -3.5224e-08 | 0.0029408 | 0.0029407 | 0.0029408 | 0.97593 | -0.46317 | 0.97593 | -0.46305 | 0.8079
105 | -0.0080517 | -0.0020179 | 0.0080524 | 0.0020182 | 7.4249e-07 | 3.1102e-07 | 0.012277 | 0.012276 | 0.012277 | 0.97593 | -0.46305 | 0.97603 | -0.46112 | 3.3727
106 | 0.04268 | 0.010746 | -0.042669 | -0.010738 | 1.155e-05 | 7.2994e-06 | 0.064735 | 0.064735 | 0.064735 | 0.98132 | -0.35746 | 0.98103 | -0.36313 | 17.7844
107 | 0.076563 | 0.019309 | -0.076531 | -0.019289 | 3.1445e-05 | 2.0046e-05 | 0.11624 | 0.11624 | 0.11624 | 0.98043 | -0.37485 | 0.97999 | -0.38343 | 31.9352
108 | 0.0078272 | 0.0019616 | -0.0078216 | -0.0019594 | 5.6292e-06 | 2.2276e-06 | 0.011804 | 0.011804 | 0.011804 | 0.98673 | -0.25453 | 0.98595 | -0.26963 | 3.2429
109 | 0.005921 | 0.0014831 | -0.0059204 | -0.001483 | 6.4574e-07 | 1.3828e-07 | 0.0089358 | 0.0089359 | 0.0089359 | 0.98595 | -0.26963 | 0.98584 | -0.27192 | 2.4549
110 | -0.0081854 | -0.0020514 | 0.0081891 | 0.002053 | 3.7579e-06 | 1.5588e-06 | 0.012323 | 0.012322 | 0.012323 | 0.98842 | -0.22256 | 0.98891 | -0.21293 | 3.3853
111 | -0.0091464 | -0.0022918 | 0.0091497 | 0.0022934 | 3.3887e-06 | 1.5564e-06 | 0.013762 | 0.013762 | 0.013762 | 0.98891 | -0.21293 | 0.98931 | -0.20515 | 3.7809
112 | 0.00095725 | 0.00023881 | -0.00095718 | -0.00023989 | 6.8183e-08 | -1.081e-06 | 0.00144 | 0.0014404 | 0.0014404 | 0.98891 | -0.21293 | 0.98884 | -0.21442 | 0.39571
113 | 0.037661 | 0.0094519 | -0.037626 | -0.00943 | 3.485e-05 | 2.1933e-05 | 0.056676 | 0.056676 | 0.056676 | 0.98886 | -0.21382 | 0.98786 | -0.23324 | 15.5704
114 | -0.018789 | -0.0047116 | 0.018794 | 0.0047145 | 4.9566e-06 | 2.9704e-06 | 0.02863 | 0.02863 | 0.02863 | 0.97655 | -0.45088 | 0.97683 | -0.44535 | 7.8654
115 | 0.015495 | 0.0038862 | -0.015488 | -0.0038818 | 7.5564e-06 | 4.3842e-06 | 0.023612 | 0.023612 | 0.023612 | 0.97655 | -0.45088 | 0.97603 | -0.46112 | 6.4869
116 | 0.0076124 | 0.0019075 | -0.0076122 | -0.0019074 | 1.6564e-07 | 6.4889e-08 | 0.011596 | 0.011596 | 0.011596 | 0.97683 | -0.44535 | 0.97681 | -0.4458 | 3.1857
117 | -0.026406 | -0.006622 | 0.026468 | 0.0066607 | 6.2368e-05 | 3.8626e-05 | 0.040226 | 0.040225 | 0.040226 | 0.97683 | -0.44535 | 0.97935 | -0.39592 | 11.0511
118 | 0.0074354 | 0.0018636 | -0.0074344 | -0.0018632 | 9.6817e-07 | 3.6856e-07 | 0.011336 | 0.011336 | 0.011336 | 0.97603 | -0.46112 | 0.97589 | -0.46385 | 3.1142
119 | 0.0046118 | 0.0011556 | -0.0046111 | -0.0011557 | 7.0261e-07 | -2.544e-08 | 0.0070253 | 0.0070255 | 0.0070255 | 0.97681 | -0.4458 | 0.97665 | -0.449 | 1.9301
120 | 0.0030003 | 0.00075181 | -0.0030002 | -0.00075193 | 1.2094e-07 | -1.1585e-07 | 0.0045705 | 0.0045706 | 0.0045706 | 0.97681 | -0.4458 | 0.97677 | -0.44665 | 1.2557
121 | -0.026468 | -0.0066607 | 0.026491 | 0.0066747 | 2.2658e-05 | 1.4031e-05 | 0.040225 | 0.040225 | 0.040225 | 0.97935 | -0.39592 | 0.98027 | -0.37802 | 11.051
122 | 0.0027127 | 0.00067984 | -0.0027127 | -0.00067987 | 2.0702e-08 | -2.7066e-08 | 0.0041363 | 0.0041363 | 0.0041363 | 0.97589 | -0.46385 | 0.97588 | -0.46401 | 1.1364
123 | -0.029906 | -0.0075306 | 0.029909 | 0.0075321 | 2.4296e-06 | 1.5153e-06 | 0.045409 | 0.045409 | 0.045409 | 0.98027 | -0.37802 | 0.98035 | -0.37632 | 12.4751
124 | -0.034147 | -0.0085943 | 0.034164 | 0.0086051 | 1.7155e-05 | 1.0765e-05 | 0.051842 | 0.051842 | 0.051842 | 0.98035 | -0.37632 | 0.98089 | -0.36581 | 14.2424
125 | 0.059948 | 0.015072 | -0.059873 | -0.015024 | 7.5313e-05 | 4.7899e-05 | 0.091269 | 0.091269 | 0.091269 | 0.97756 | -0.43098 | 0.97622 | -0.45733 | 25.0738
126 | -0.062726 | -0.015768 | 0.062771 | 0.015797 | 4.4777e-05 | 2.8493e-05 | 0.095497 | 0.095497 | 0.095497 | 0.97756 | -0.43098 | 0.97832 | -0.41605 | 26.2354
127 | 0.024513 | 0.006152 | -0.024494 | -0.0061408 | 1.8218e-05 | 1.1225e-05 | 0.037367 | 0.037367 | 0.037367 | 0.97622 | -0.45733 | 0.97542 | -0.47292 | 10.2657
128 | 0.03536 | 0.0088722 | -0.035344 | -0.0088622 | 1.5794e-05 | 9.9268e-06 | 0.053902 | 0.053902 | 0.053902 | 0.97622 | -0.45733 | 0.97574 | -0.4667 | 14.8082
129 | -0.072065 | -0.018126 | 0.072177 | 0.018198 | 0.00011247 | 7.1666e-05 | 0.10963 | 0.10963 | 0.10963 | 0.97832 | -0.41605 | 0.97999 | -0.38343 | 30.1189
130 | 0.009294 | 0.0023294 | -0.0092929 | -0.0023288 | 1.1172e-06 | 5.2782e-07 | 0.014136 | 0.014136 | 0.014136 | 0.97832 | -0.41605 | 0.97819 | -0.41857 | 3.8836
131 | 0.021807 | 0.0054673 | -0.021805 | -0.0054662 | 1.8258e-06 | 1.1136e-06 | 0.033267 | 0.033268 | 0.033268 | 0.97542 | -0.47292 | 0.97534 | -0.47468 | 9.1394
132 | 0.02665 | 0.0066831 | -0.026642 | -0.0066786 | 7.2953e-06 | 4.5219e-06 | 0.040642 | 0.040642 | 0.040642 | 0.97574 | -0.4667 | 0.97545 | -0.47244 | 11.1655
133 | 0.0060685 | 0.0015207 | -0.0060684 | -0.0015207 | 1.8495e-07 | 4.5719e-08 | 0.0092313 | 0.0092314 | 0.0092314 | 0.97819 | -0.41857 | 0.97816 | -0.41921 | 2.5361
134 | 0.01606 | 0.0040264 | -0.016057 | -0.0040242 | 3.8305e-06 | 2.2393e-06 | 0.024503 | 0.024503 | 0.024503 | 0.97534 | -0.47468 | 0.97508 | -0.47969 | 6.7316
135 | 0.016588 | 0.0041587 | -0.016583 | -0.0041562 | 4.1968e-06 | 2.4678e-06 | 0.025304 | 0.025305 | 0.025305 | 0.97545 | -0.47244 | 0.97518 | -0.47776 | 6.9518
136 | 0.0026599 | 0.00066646 | -0.0026598 | -0.00066661 | 1.0482e-07 | -1.472e-07 | 0.0040463 | 0.0040464 | 0.0040464 | 0.97816 | -0.41921 | 0.97812 | -0.42004 | 1.1116
137 | 0.0078378 | 0.0019643 | -0.0078378 | -0.0019643 | 3.3204e-09 | 1.3549e-09 | 0.011961 | 0.011961 | 0.011961 | 0.97508 | -0.47969 | 0.97508 | -0.4797 | 3.2859
138 | 0.0037614 | 0.00094268 | -0.0037614 | -0.00094269 | 4.8002e-09 | -1.7741e-09 | 0.00574 | 0.00574 | 0.00574 | 0.97508 | -0.4797 | 0.97508 | -0.47972 | 1.5769
139 | 0.012185 | 0.0030542 | -0.012184 | -0.0030537 | 9.8127e-07 | 5.3224e-07 | 0.018527 | 0.018527 | 0.018527 | 0.97864 | -0.41161 | 0.97856 | -0.4133 | 5.0899
140 | 0.0066531 | 0.0016675 | -0.0066523 | -0.0016672 | 7.7814e-07 | 2.4335e-07 | 0.010117 | 0.010117 | 0.010117 | 0.97856 | -0.4133 | 0.97843 | -0.41576 | 2.7794
141 | 0.039867 | 0.010036 | -0.039862 | -0.010033 | 5.1189e-06 | 3.229e-06 | 0.060486 | 0.060486 | 0.060486 | 0.98103 | -0.36313 | 0.98089 | -0.36581 | 16.617

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51416 | 0.13121

## res_load
| p_mw | q_mvar
0 | 0.00016463 | 4.1261e-05
1 | 0.00025427 | 6.3726e-05
2 | 0.000119 | 2.9825e-05
3 | 0.00045612 | 0.00011431
4 | 0.0040556 | 0.0010164
5 | 0.00020875 | 5.2319e-05
6 | 0.0079434 | 0.0019908
7 | 0.0018842 | 0.00047222
8 | 0.0018814 | 0.00047153
9 | 0.00022237 | 5.5731e-05
10 | 0.0012034 | 0.0003016
11 | 0.00038872 | 9.7423e-05
12 | 0.00044439 | 0.00011137
13 | 0.00058212 | 0.00014589
14 | 0.00029899 | 7.4933e-05
15 | 8.543e-05 | 2.1411e-05
16 | 0.0049759 | 0.0012471
17 | 0.003103 | 0.00077769
18 | 0.0044937 | 0.0011262
19 | 0.01058 | 0.0026515
20 | 0.0041994 | 0.0010525
21 | 0.0033914 | 0.00084997
22 | 0.0073211 | 0.0018348
23 | 0.0054458 | 0.0013648
24 | 0.0074371 | 0.0018639
25 | 0.0045885 | 0.00115
26 | 0.00055438 | 0.00013894
27 | 0.0044684 | 0.0011199
28 | 0.012041 | 0.0030178
29 | 0.021118 | 0.0052927
30 | 0.0061582 | 0.0015434
31 | 0.0027643 | 0.0006928
32 | 0.00061666 | 0.00015455
33 | 0.0002422 | 6.0701e-05
34 | 0.0030369 | 0.00076111
35 | 0.0030759 | 0.00077089
36 | 0.0031225 | 0.00078257
37 | 0.006099 | 0.0015285
38 | 0.0023349 | 0.00058518
39 | 0.014624 | 0.0036651
40 | 0.0028143 | 0.00070533
41 | 0.00094096 | 0.00023583
42 | 0.00055441 | 0.00013895
43 | 0.0016918 | 0.000424
44 | 0.0077897 | 0.0019523
45 | 0.010571 | 0.0026492
46 | 0.0080875 | 0.0020269
47 | 0.0010344 | 0.00025925
48 | 0.03262 | 0.0081754
49 | 0.006766 | 0.0016957
50 | 0.0010557 | 0.00026458
51 | 0.0070008 | 0.0017546
52 | 0.004234 | 0.0010611
53 | 0.020388 | 0.0051098
54 | 0.0038134 | 0.00095573
55 | 0.0021217 | 0.00053175
56 | 0.00067284 | 0.00016863
57 | 0.00037581 | 9.4187e-05
58 | 0.0019287 | 0.00048338
59 | 0.006123 | 0.0015346
60 | 0.0028033 | 0.00070258
61 | 0.00359 | 0.00089974
62 | 0.0050055 | 0.0012545
63 | 0.0019006 | 0.00047633
64 | 0.0050392 | 0.0012629
65 | 0.0081854 | 0.0020514
66 | 0.00095718 | 0.00023989
67 | 0.025556 | 0.006405
68 | 0.037626 | 0.00943
69 | 0.010739 | 0.0026916
70 | 0.0032933 | 0.00082538
71 | 0.0047217 | 0.0011834
72 | 0.0046111 | 0.0011557
73 | 0.0030002 | 0.00075193
74 | 0.0034151 | 0.00085589
75 | 0.0027127 | 0.00067987
76 | 0.0042382 | 0.0010622
77 | 0.0027778 | 0.00069617
78 | 0.0026873 | 0.0006735
79 | 0.0086948 | 0.0021791
80 | 0.0043541 | 0.0010912
81 | 0.0032243 | 0.0008081
82 | 0.0057448 | 0.0014398
83 | 0.010055 | 0.0025199
84 | 0.0034085 | 0.00085424
85 | 0.0082189 | 0.0020598
86 | 0.016583 | 0.0041562
87 | 0.0026598 | 0.00066661
88 | 0.0040764 | 0.0010216
89 | 0.0043493 | 0.00109
90 | 0.005531 | 0.0013862
91 | 0.0066523 | 0.0016672
92 | 0.0037614 | 0.00094269
93 | 0.0028017 | 0.00070217
94 | 0.0056979 | 0.001428

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1