## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1064-3_1_2_node_42 | 0.4 | n |  | TRUE
1 | bus_LV_1064-3_1_2_node_43 | 0.4 | n |  | TRUE
2 | bus_LV_1064-3_1_2_node_44 | 0.4 | n |  | TRUE
3 | bus_LV_1064-3_1_2_node_45 | 0.4 | n |  | TRUE
4 | bus_LV_1064-3_1_2_node_46 | 0.4 | n |  | TRUE
5 | bus_LV_1064-3_1_2_node_67 | 0.4 | n |  | TRUE
6 | bus_LV_1064-3_1_2_node_78 | 0.4 | n |  | TRUE
7 | bus_LV_1064-3_1_2_node_95 | 0.4 | n |  | TRUE
8 | bus_LV_1064-3_1_2_node_166 | 0.4 | n |  | TRUE
9 | bus_LV_1064-3_1_2_node_71 | 0.4 | n |  | TRUE
10 | bus_LV_1064-3_1_2_node_72 | 0.4 | n |  | TRUE
11 | bus_LV_1064-3_1_2_node_202 | 0.4 | n |  | TRUE
12 | bus_LV_1064-3_1_2_node_96 | 0.4 | n |  | TRUE
13 | bus_LV_1064-3_1_2_node_99 | 0.4 | n |  | TRUE
14 | bus_LV_1064-3_1_2_node_205 | 0.4 | n |  | TRUE
15 | bus_LV_1064-3_1_2_node_101 | 0.4 | n |  | TRUE
16 | bus_LV_1064-3_1_2_node_165 | 0.4 | n |  | TRUE
17 | bus_LV_1064-3_1_2_node_103 | 0.4 | n |  | TRUE
18 | bus_LV_1064-3_1_2_node_104 | 0.4 | n |  | TRUE
19 | bus_LV_1064-3_1_2_node_105 | 0.4 | n |  | TRUE
20 | bus_LV_1064-3_1_2_node_106 | 0.4 | n |  | TRUE
21 | bus_LV_1064-3_1_2_node_107 | 0.4 | n |  | TRUE
22 | bus_LV_1064-3_1_2_node_108 | 0.4 | n |  | TRUE
23 | bus_LV_1064-3_1_2_node_144 | 0.4 | n |  | TRUE
24 | bus_LV_1064-3_1_2_node_132 | 0.4 | n |  | TRUE
25 | bus_LV_1064-3_1_2_node_114 | 0.4 | n |  | TRUE
26 | bus_LV_1064-3_1_2_node_115 | 0.4 | n |  | TRUE
27 | bus_LV_1064-3_1_2_node_116 | 0.4 | n |  | TRUE
28 | bus_LV_1064-3_1_2_node_143 | 0.4 | n |  | TRUE
29 | bus_LV_1064-3_1_2_node_117 | 0.4 | n |  | TRUE
30 | bus_LV_1064-3_1_2_node_118 | 0.4 | n |  | TRUE
31 | bus_LV_1064-3_1_2_node_120 | 0.4 | n |  | TRUE
32 | bus_LV_1064-3_1_2_node_170 | 0.4 | n |  | TRUE
33 | bus_LV_1064-3_1_2_node_121 | 0.4 | n |  | TRUE
34 | bus_LV_1064-3_1_2_node_122 | 0.4 | n |  | TRUE
35 | bus_LV_1064-3_1_2_node_155 | 0.4 | n |  | TRUE
36 | bus_LV_1064-3_1_2_node_128 | 0.4 | n |  | TRUE
37 | bus_LV_1064-3_1_2_node_130 | 0.4 | n |  | TRUE
38 | bus_LV_1064-3_1_2_node_141 | 0.4 | n |  | TRUE
39 | bus_LV_1064-3_1_2_node_129 | 0.4 | n |  | TRUE
40 | bus_LV_1064-3_1_2_node_238 | 0.4 | n |  | TRUE
41 | bus_LV_1064-3_1_2_node_136 | 0.4 | n |  | TRUE
42 | bus_LV_1064-3_1_2_node_137 | 0.4 | n |  | TRUE
43 | bus_LV_1064-3_1_2_node_138 | 0.4 | n |  | TRUE
44 | bus_LV_1064-3_1_2_node_139 | 0.4 | n |  | TRUE
45 | bus_LV_1064-3_1_2_node_140 | 0.4 | n |  | TRUE
46 | bus_LV_1064-3_1_2_node_157 | 0.4 | n |  | TRUE
47 | bus_LV_1064-3_1_2_node_154 | 0.4 | n |  | TRUE
48 | bus_LV_1064-3_1_2_node_147 | 0.4 | n |  | TRUE
49 | bus_LV_1064-3_1_2_node_148 | 0.4 | n |  | TRUE
50 | bus_LV_1064-3_1_2_node_162 | 0.4 | n |  | TRUE
51 | bus_LV_1064-3_1_2_node_152 | 0.4 | n |  | TRUE
52 | bus_LV_1064-3_1_2_node_153 | 0.4 | n |  | TRUE
53 | bus_LV_1064-3_1_2_node_231 | 0.4 | n |  | TRUE
54 | bus_LV_1064-3_1_2_node_158 | 0.4 | n |  | TRUE
55 | bus_LV_1064-3_1_2_node_159 | 0.4 | n |  | TRUE
56 | bus_LV_1064-3_1_2_node_208 | 0.4 | n |  | TRUE
57 | bus_LV_1064-3_1_2_node_161 | 0.4 | n |  | TRUE
58 | bus_LV_1064-3_1_2_node_164 | 0.4 | n |  | TRUE
59 | bus_LV_1064-3_1_2_node_163 | 0.4 | n |  | TRUE
60 | bus_LV_1064-3_1_2_node_204 | 0.4 | n |  | TRUE
61 | bus_LV_1064-3_1_2_node_167 | 0.4 | n |  | TRUE
62 | bus_LV_1064-3_1_2_node_171 | 0.4 | n |  | TRUE
63 | bus_LV_1064-3_1_2_node_168 | 0.4 | n |  | TRUE
64 | bus_LV_1064-3_1_2_node_169 | 0.4 | n |  | TRUE
65 | bus_LV_1064-3_1_2_node_203 | 0.4 | n |  | TRUE
66 | bus_LV_1064-3_1_2_node_206 | 0.4 | n |  | TRUE
67 | bus_LV_1064-3_1_2_node_207 | 0.4 | n |  | TRUE
68 | bus_LV_1064-3_1_2_node_210 | 0.4 | n |  | TRUE
69 | bus_LV_1064-3_1_2_node_232 | 0.4 | n |  | TRUE
70 | bus_MV_0_node_170 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1064-3_1_2_load_42 | 0 | 0.00083751 | 0.0002099 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1064-3_1_2_load_43 | 1 | 0.00099492 | 0.00024935 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1064-3_1_2_load_44 | 2 | 0.0015787 | 0.00039567 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1064-3_1_2_load_45 | 3 | 0.0021995 | 0.00055124 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1064-3_1_2_load_46 | 4 | 0.00083634 | 0.00020961 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1064-3_1_2_load_67 | 5 | 0.0040877 | 0.0010245 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1064-3_1_2_load_95 | 7 | 0.0025819 | 0.00064708 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1064-3_1_2_load_166 | 8 | 0.0011928 | 0.00029895 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1064-3_1_2_load_72 | 10 | 0.00054357 | 0.00013623 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1064-3_1_2_load_202 | 11 | 0.0028465 | 0.0007134 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1064-3_1_2_load_96 | 12 | 0.001408 | 0.00035287 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1064-3_1_2_load_99 | 13 | 0.0011911 | 0.00029851 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1064-3_1_2_load_205 | 14 | 0.0043345 | 0.0010863 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1064-3_1_2_load_101 | 15 | 0.00049958 | 0.00012521 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1064-3_1_2_load_165 | 16 | 0.00040755 | 0.00010214 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1064-3_1_2_load_103 | 17 | 0.00066874 | 0.0001676 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1064-3_1_2_load_104 | 18 | 0.0017449 | 0.0004373 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1064-3_1_2_load_106 | 20 | 0.0021241 | 0.00053236 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1064-3_1_2_load_107 | 21 | 0.00046538 | 0.00011663 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1064-3_1_2_load_108 | 22 | 9.5047e-05 | 2.3821e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1064-3_1_2_load_114 | 25 | 0.00068619 | 0.00017197 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1064-3_1_2_load_115 | 26 | 0.0002529 | 6.3383e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1064-3_1_2_load_116 | 27 | 0.00017124 | 4.2916e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1064-3_1_2_load_143 | 28 | 0.00022331 | 5.5968e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1064-3_1_2_load_117 | 29 | 0.00456 | 0.0011429 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1064-3_1_2_load_118 | 30 | 0.0016509 | 0.00041376 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1064-3_1_2_load_120 | 31 | 0.00044859 | 0.00011243 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1064-3_1_2_load_170 | 32 | 0.00011047 | 2.7686e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1064-3_1_2_load_121 | 33 | 0.00033093 | 8.294e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1064-3_1_2_load_122 | 34 | 0.0014173 | 0.0003552 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1064-3_1_2_load_155 | 35 | 0.00047834 | 0.00011988 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1064-3_1_2_load_130 | 37 | 0.0002037 | 5.1052e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1064-3_1_2_load_141 | 38 | 0.00015803 | 3.9607e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1064-3_1_2_load_129 | 39 | 0.0018342 | 0.00045969 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1064-3_1_2_load_238 | 40 | 0.00044588 | 0.00011175 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1064-3_1_2_load_136 | 41 | 0.00021298 | 5.3377e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1064-3_1_2_load_137 | 42 | 0.0018052 | 0.00045242 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1064-3_1_2_load_138 | 43 | 0.00034037 | 8.5304e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1064-3_1_2_load_140 | 45 | 0.00023748 | 5.9518e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1064-3_1_2_load_157 | 46 | 0.00017056 | 4.2747e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1064-3_1_2_load_147 | 48 | 0.00088098 | 0.00022079 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1064-3_1_2_load_162 | 50 | 0.0016604 | 0.00041613 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1064-3_1_2_load_152 | 51 | 0.00024918 | 6.2449e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1064-3_1_2_load_158 | 54 | 0.00049186 | 0.00012327 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1064-3_1_2_load_159 | 55 | 0.002051 | 0.00051402 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1064-3_1_2_load_161 | 57 | 0.00025242 | 6.3262e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1064-3_1_2_load_164 | 58 | 0.00018987 | 4.7586e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1064-3_1_2_load_167 | 61 | 0.00025339 | 6.3504e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1064-3_1_2_load_171 | 62 | 0.0019567 | 0.00049041 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1064-3_1_2_load_168 | 63 | 0.00054899 | 0.00013759 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1064-3_1_2_load_169 | 64 | 0.00046412 | 0.00011632 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1064-3_1_2_load_203 | 65 | 0.0020974 | 0.00052566 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1064-3_1_2_load_206 | 66 | 0.00070591 | 0.00017692 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1064-3_1_2_load_207 | 67 | 0.00021413 | 5.3667e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1064-3_1_2_load_210 | 68 | 0.0004277 | 0.00010719 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1064-3_1_2_load_232 | 69 | 0.00081962 | 0.00020542 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1064-3_1_2_line_0 |  | 0 | 1 | 0.018356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1064-3_1_2_line_1 |  | 0 | 2 | 0.011903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1064-3_1_2_line_2 |  | 1 | 3 | 0.031991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1064-3_1_2_line_3 |  | 2 | 4 | 0.0071682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1064-3_1_2_line_4 |  | 3 | 5 | 0.010456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1064-3_1_2_line_5 |  | 4 | 6 | 0.058949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1064-3_1_2_line_6 |  | 5 | 7 | 0.091817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1064-3_1_2_line_7 |  | 5 | 8 | 0.19698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1064-3_1_2_line_8 |  | 6 | 11 | 0.047012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1064-3_1_2_line_9 |  | 7 | 12 | 0.016521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1064-3_1_2_line_10 |  | 7 | 9 | 0.21446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1064-3_1_2_line_11 |  | 8 | 62 | 0.14923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1064-3_1_2_line_12 |  | 8 | 16 | 0.014663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1064-3_1_2_line_13 |  | 9 | 10 | 0.027086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1064-3_1_2_line_14 |  | 11 | 65 | 0.024504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1064-3_1_2_line_15 |  | 13 | 14 | 0.02495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1064-3_1_2_line_16 |  | 14 | 60 | 0.036728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1064-3_1_2_line_17 |  | 15 | 16 | 0.016065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1064-3_1_2_line_18 |  | 17 | 18 | 0.023031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1064-3_1_2_line_19 |  | 17 | 19 | 0.010997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1064-3_1_2_line_20 |  | 18 | 20 | 0.039212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1064-3_1_2_line_21 |  | 19 | 21 | 0.043085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1064-3_1_2_line_22 |  | 19 | 22 | 0.010433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1064-3_1_2_line_23 |  | 20 | 23 | 0.47536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1064-3_1_2_line_24 |  | 21 | 24 | 0.52901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1064-3_1_2_line_25 |  | 23 | 28 | 0.04918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1064-3_1_2_line_26 |  | 24 | 38 | 0.012196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1064-3_1_2_line_27 |  | 25 | 26 | 0.00090873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1064-3_1_2_line_28 |  | 26 | 27 | 0.0010711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1064-3_1_2_line_29 |  | 27 | 28 | 0.019321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1064-3_1_2_line_30 |  | 29 | 30 | 0.03229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1064-3_1_2_line_31 |  | 30 | 31 | 0.15649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1064-3_1_2_line_32 |  | 30 | 32 | 0.49899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1064-3_1_2_line_33 |  | 31 | 33 | 0.034465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1064-3_1_2_line_34 |  | 32 | 64 | 0.019085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1064-3_1_2_line_35 |  | 33 | 34 | 0.042792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1064-3_1_2_line_36 |  | 34 | 35 | 0.0017109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1064-3_1_2_line_37 |  | 35 | 52 | 0.038767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1064-3_1_2_line_38 |  | 36 | 37 | 0.010506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1064-3_1_2_line_39 |  | 36 | 38 | 0.038878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1064-3_1_2_line_40 |  | 37 | 39 | 0.01876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1064-3_1_2_line_41 |  | 39 | 40 | 0.14332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1064-3_1_2_line_42 |  | 40 | 47 | 0.12951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1064-3_1_2_line_43 |  | 41 | 42 | 0.0068253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1064-3_1_2_line_44 |  | 41 | 43 | 0.010564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1064-3_1_2_line_45 |  | 42 | 44 | 0.019447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1064-3_1_2_line_46 |  | 43 | 45 | 0.043485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1064-3_1_2_line_47 |  | 44 | 46 | 0.014281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1064-3_1_2_line_48 |  | 44 | 47 | 0.12479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1064-3_1_2_line_49 |  | 46 | 53 | 0.097736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1064-3_1_2_line_50 |  | 47 | 49 | 0.29976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1064-3_1_2_line_51 |  | 48 | 49 | 0.032529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1064-3_1_2_line_52 |  | 48 | 50 | 0.32759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1064-3_1_2_line_53 |  | 50 | 57 | 0.038287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1064-3_1_2_line_54 |  | 51 | 52 | 0.034323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1064-3_1_2_line_55 |  | 53 | 69 | 0.083899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1064-3_1_2_line_56 |  | 53 | 55 | 0.28114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1064-3_1_2_line_57 |  | 54 | 55 | 0.046462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1064-3_1_2_line_58 |  | 55 | 56 | 0.13749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1064-3_1_2_line_59 |  | 56 | 68 | 0.026052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1064-3_1_2_line_60 |  | 56 | 66 | 0.018426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1064-3_1_2_line_61 |  | 57 | 58 | 0.24531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1064-3_1_2_line_62 |  | 58 | 61 | 0.033763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1064-3_1_2_line_63 |  | 58 | 59 | 0.062216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1064-3_1_2_line_64 |  | 59 | 60 | 0.1727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1064-3_1_2_line_65 |  | 60 | 65 | 0.021432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1064-3_1_2_line_66 |  | 61 | 63 | 0.016637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1064-3_1_2_line_67 |  | 63 | 64 | 0.022682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1064-3_1_2_line_68 |  | 66 | 67 | 0.029763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1064-3_1_2_trafo_170 | 0.63 MVA 20/0.4 kV | 70 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2675547.8089 | 1218493.8636 | 2675557.4921 | 1218500.9841 | 2675562.6273 | 1218504.6964
1 | 2675547.8089 | 1218493.8636 | 2675539.3837 | 1218487.6681 | 2675538.2486 | 1218486.7732
2 | 2675562.6273 | 1218504.6964 | 2675578.8448 | 1218516.4204 | 2675588.4724 | 1218523.5491
3 | 2675532.6194 | 1218482.3353 | 2675538.2486 | 1218486.7732
4 | 2675588.4724 | 1218523.5491 | 2675596.8759 | 1218529.7713
5 | 2675487.9678 | 1218443.9216 | 2675499.9118 | 1218455.5471 | 2675521.6105 | 1218473.656 | 2675532.6194 | 1218482.3353
6 | 2675596.8759 | 1218529.7713 | 2675659.8067 | 1218462.9133
7 | 2675717.095 | 1218685.8076 | 2675596.8759 | 1218529.7713
8 | 2675487.9678 | 1218443.9216 | 2675490.8808 | 1218429.0822 | 2675487.5058 | 1218406.1134 | 2675484.6005 | 1218397.9403
9 | 2675659.8067 | 1218462.9133 | 2675655.0981 | 1218447.0772
10 | 2675752.4216 | 1218656.3485 | 2675659.8067 | 1218462.9133
11 | 2675717.095 | 1218685.8076 | 2675598.2744 | 1218776.094
12 | 2675717.095 | 1218685.8076 | 2675729.3857 | 1218693.8045
13 | 2675752.4216 | 1218656.3485 | 2675766.9434 | 1218679.213
14 | 2675484.6005 | 1218397.9403 | 2675482.7933 | 1218392.8562 | 2675478.8356 | 1218374.1626
15 | 2675506.712 | 1218319.5584 | 2675510.0774 | 1218325.4581 | 2675512.1229 | 1218331.1544 | 2675512.6916 | 1218335.987 | 2675511.7911 | 1218338.7662 | 2675508.5966 | 1218341.6721
16 | 2675476.384 | 1218352.9603 | 2675478.6703 | 1218349.2424 | 2675482.1374 | 1218345.784 | 2675486.0796 | 1218343.766 | 2675489.7773 | 1218343.079 | 2675494.4337 | 1218343.4049 | 2675501.0461 | 1218343.9112 | 2675505.0224 | 1218343.3946 | 2675508.5966 | 1218341.6721
17 | 2675729.3857 | 1218693.8045 | 2675742.8511 | 1218702.5657
18 | 2674306.8331 | 1219254.0323 | 2674309.3769 | 1219272.0794 | 2674310.6818 | 1219276.7046
19 | 2674305.2983 | 1219243.1431 | 2674306.8331 | 1219254.0323
20 | 2674341.0659 | 1219298.1636 | 2674338.1713 | 1219296.9324 | 2674326.2641 | 1219291.4359 | 2674318.8664 | 1219288.8642 | 2674314.5773 | 1219285.3195 | 2674311.9424 | 1219281.1728 | 2674310.6818 | 1219276.7046
21 | 2674305.2983 | 1219243.1431 | 2674291.3914 | 1219237.3326 | 2674280.6835 | 1219231.8178 | 2674266.9582 | 1219223.6572
22 | 2674305.2983 | 1219243.1431 | 2674306.3248 | 1219233.861 | 2674306.2702 | 1219232.7683
23 | 2674813.5194 | 1219350.6829 | 2674341.0659 | 1219298.1636
24 | 2674458.0824 | 1218730.3845 | 2674266.9582 | 1219223.6572
25 | 2674813.5194 | 1219350.6829 | 2674816.3144 | 1219342.6572 | 2674825.8013 | 1219329.3344 | 2674841.4264 | 1219310.6903
26 | 2674458.0824 | 1218730.3845 | 2674464.3855 | 1218719.943
27 | 2674851.534 | 1219292.5362 | 2674851.311 | 1219293.4172
28 | 2674851.311 | 1219293.4172 | 2674851.0481 | 1219294.4555
29 | 2674841.4264 | 1219310.6903 | 2674849.3237 | 1219301.2671 | 2674851.0481 | 1219294.4555
30 | 2675241.9368 | 1218911.0482 | 2675235.6741 | 1218896.3583 | 2675232.407 | 1218888.2228 | 2675229.8437 | 1218881.1171
31 | 2675076.2345 | 1218911.0147 | 2675229.8437 | 1218881.1171
32 | 2675229.8437 | 1218881.1171 | 2675214.5916 | 1218382.3586
33 | 2675048.8116 | 1218890.7656 | 2675049.3686 | 1218891.0167 | 2675057.652 | 1218894.9903 | 2675068.7621 | 1218902.9132 | 2675076.2345 | 1218911.0147
34 | 2675214.5916 | 1218382.3586 | 2675218.6261 | 1218369.4234 | 2675222.3673 | 1218365.3434
35 | 2675010.4188 | 1218876.6854 | 2675020.1302 | 1218884.6111 | 2675023.2349 | 1218886.9851 | 2675024.5575 | 1218887.4242 | 2675029.2852 | 1218887.4838 | 2675036.6114 | 1218887.3092 | 2675041.6557 | 1218887.5396 | 2675048.8116 | 1218890.7656
36 | 2675010.4188 | 1218876.6854 | 2675009.0933 | 1218875.6037
37 | 2674978.8742 | 1218851.3258 | 2674986.2713 | 1218856.9781 | 2675009.0933 | 1218875.6037
38 | 2674485.0152 | 1218686.993 | 2674479.9193 | 1218685.4172 | 2674476.0374 | 1218681.9997
39 | 2674485.0152 | 1218686.993 | 2674470.7389 | 1218709.418 | 2674464.3855 | 1218719.943
40 | 2674461.3331 | 1218670.3744 | 2674470.7979 | 1218677.3869 | 2674476.0374 | 1218681.9997
41 | 2674461.3331 | 1218670.3744 | 2674464.5633 | 1218527.0895
42 | 2674540.2018 | 1218421.967 | 2674464.5633 | 1218527.0895
43 | 2674443.1118 | 1218344.7279 | 2674440.2394 | 1218345.9129 | 2674436.5756 | 1218346.5462
44 | 2674426.1655 | 1218348.3457 | 2674436.5756 | 1218346.5462
45 | 2674455.4109 | 1218330.2589 | 2674446.2821 | 1218343.4201 | 2674443.1118 | 1218344.7279
46 | 2674383.0041 | 1218353.5143 | 2674405.7187 | 1218351.352 | 2674422.4242 | 1218348.9924 | 2674426.1655 | 1218348.3457
47 | 2674455.4109 | 1218330.2589 | 2674446.3101 | 1218322.9627 | 2674444.4983 | 1218321.0755
48 | 2674455.4109 | 1218330.2589 | 2674458.7251 | 1218332.9132 | 2674502.3205 | 1218379.9439 | 2674540.2018 | 1218421.967
49 | 2674375.8138 | 1218251.5698 | 2674400.8281 | 1218275.5864 | 2674444.4983 | 1218321.0755
50 | 2674540.2018 | 1218421.967 | 2674817.1548 | 1218307.2853
51 | 2674817.1548 | 1218307.2853 | 2674833.3726 | 1218319.608 | 2674841.3566 | 1218328.7809
52 | 2674841.3566 | 1218328.7809 | 2675085.5633 | 1218110.4207
53 | 2675117.0532 | 1218132.198 | 2675115.8565 | 1218131.3618 | 2675085.5633 | 1218110.4207
54 | 2674978.8742 | 1218851.3258 | 2674954.2917 | 1218832.5711 | 2674951.8603 | 1218830.1898
55 | 2674375.8138 | 1218251.5698 | 2674362.771 | 1218334.4384
56 | 2674375.8138 | 1218251.5698 | 2674450.2441 | 1217980.4584
57 | 2674446.437 | 1217945.2695 | 2674453.827 | 1217954.7854 | 2674463.2666 | 1217969.0236 | 2674450.2441 | 1217980.4584
58 | 2674586.7763 | 1217964.276 | 2674450.2441 | 1217980.4584
59 | 2674586.7763 | 1217964.276 | 2674595.9657 | 1217973.0188 | 2674602.1621 | 1217978.9002 | 2674604.7256 | 1217982.9873
60 | 2674586.7763 | 1217964.276 | 2674600.1821 | 1217951.6341
61 | 2675275.0631 | 1218319.8355 | 2675117.0532 | 1218132.198
62 | 2675275.0631 | 1218319.8355 | 2675262.4009 | 1218336.8993 | 2675254.0774 | 1218346.2443
63 | 2675320.8261 | 1218277.9437 | 2675280.007 | 1218313.173 | 2675275.0631 | 1218319.8355
64 | 2675476.384 | 1218352.9603 | 2675320.8261 | 1218277.9437
65 | 2675476.384 | 1218352.9603 | 2675476.1946 | 1218357.7276 | 2675477.3647 | 1218367.2153 | 2675478.8356 | 1218374.1626
66 | 2675254.0774 | 1218346.2443 | 2675243.814 | 1218357.7671 | 2675242.6207 | 1218357.94
67 | 2675222.3673 | 1218365.3434 | 2675227.0921 | 1218360.1909 | 2675242.6207 | 1218357.94
68 | 2674600.1821 | 1217951.6341 | 2674617.9944 | 1217934.8366 | 2674621.5994 | 1217930.9792

## bus_geodata
| x | y | coords
0 | 2675547.8089 | 1218493.8636
1 | 2675562.6273 | 1218504.6964
2 | 2675538.2486 | 1218486.7732
3 | 2675588.4724 | 1218523.5491
4 | 2675532.6194 | 1218482.3353
5 | 2675596.8759 | 1218529.7713
6 | 2675487.9678 | 1218443.9216
7 | 2675659.8067 | 1218462.9133
8 | 2675717.095 | 1218685.8076
9 | 2675752.4216 | 1218656.3485
10 | 2675766.9434 | 1218679.213
11 | 2675484.6005 | 1218397.9403
12 | 2675655.0981 | 1218447.0772
13 | 2675506.712 | 1218319.5584
14 | 2675508.5966 | 1218341.6721
15 | 2675742.8511 | 1218702.5657
16 | 2675729.3857 | 1218693.8045
17 | 2674306.8331 | 1219254.0323
18 | 2674310.6818 | 1219276.7046
19 | 2674305.2983 | 1219243.1431
20 | 2674341.0659 | 1219298.1636
21 | 2674266.9582 | 1219223.6572
22 | 2674306.2702 | 1219232.7683
23 | 2674813.5194 | 1219350.6829
24 | 2674458.0824 | 1218730.3845
25 | 2674851.534 | 1219292.5362
26 | 2674851.311 | 1219293.4172
27 | 2674851.0481 | 1219294.4555
28 | 2674841.4264 | 1219310.6903
29 | 2675241.9368 | 1218911.0482
30 | 2675229.8437 | 1218881.1171
31 | 2675076.2345 | 1218911.0147
32 | 2675214.5917 | 1218382.3586
33 | 2675048.8116 | 1218890.7656
34 | 2675010.4188 | 1218876.6854
35 | 2675009.0933 | 1218875.6037
36 | 2674485.0152 | 1218686.993
37 | 2674476.0374 | 1218681.9997
38 | 2674464.3855 | 1218719.943
39 | 2674461.3331 | 1218670.3744
40 | 2674464.5633 | 1218527.0895
41 | 2674436.5756 | 1218346.5462
42 | 2674443.1118 | 1218344.7279
43 | 2674426.1655 | 1218348.3457
44 | 2674455.4109 | 1218330.2589
45 | 2674383.0041 | 1218353.5143
46 | 2674444.4983 | 1218321.0755
47 | 2674540.2018 | 1218421.967
48 | 2674841.3566 | 1218328.7809
49 | 2674817.1548 | 1218307.2853
50 | 2675085.5633 | 1218110.4207
51 | 2674951.8603 | 1218830.1898
52 | 2674978.8742 | 1218851.3258
53 | 2674375.8138 | 1218251.5698
54 | 2674446.437 | 1217945.2695
55 | 2674450.2441 | 1217980.4584
56 | 2674586.7763 | 1217964.276
57 | 2675117.0532 | 1218132.198
58 | 2675275.0631 | 1218319.8355
59 | 2675320.8261 | 1218277.9437
60 | 2675476.384 | 1218352.9603
61 | 2675254.0774 | 1218346.2443
62 | 2675598.2744 | 1218776.094
63 | 2675242.6207 | 1218357.94
64 | 2675222.3673 | 1218365.3434
65 | 2675478.8356 | 1218374.1626
66 | 2674600.1821 | 1217951.6341
67 | 2674621.5994 | 1217930.9792
68 | 2674604.7256 | 1217982.9873
69 | 2674362.771 | 1218334.4384
70 | 2675214.5917 | 1218382.3586

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98625 | -0.26447 | 0.00083751 | 0.0002099
1 | 0.98598 | -0.2697 | 0.00099492 | 0.00024935
2 | 0.98643 | -0.2609 | 0.0015787 | 0.00039567
3 | 0.98555 | -0.27825 | 0.0021995 | 0.00055124
4 | 0.98656 | -0.25855 | 0.00083634 | 0.00020961
5 | 0.98542 | -0.28064 | 0.0040877 | 0.0010245
6 | 0.98759 | -0.23836 | 0 | 0
7 | 0.98504 | -0.28813 | 0.0025819 | 0.00064708
8 | 0.98469 | -0.29502 | 0.0011928 | 0.00029895
9 | 0.98493 | -0.29024 | 0 | 0
10 | 0.98492 | -0.2905 | 0.00054357 | 0.00013623
11 | 0.98842 | -0.22228 | 0.0028465 | 0.0007134
12 | 0.98502 | -0.28855 | 0.001408 | 0.00035287
13 | 0.98918 | -0.20761 | 0.0011911 | 0.00029851
14 | 0.9892 | -0.20708 | 0.0043345 | 0.0010863
15 | 0.98467 | -0.29541 | 0.00049958 | 0.00012521
16 | 0.98468 | -0.29526 | 0.00040755 | 0.00010214
17 | 0.9741 | -0.50214 | 0.00066874 | 0.0001676
18 | 0.97399 | -0.50435 | 0.0017449 | 0.0004373
19 | 0.97416 | -0.50095 | 0 | 0
20 | 0.97386 | -0.50685 | 0.0021241 | 0.00053236
21 | 0.9744 | -0.49621 | 0.00046538 | 0.00011663
22 | 0.97416 | -0.50097 | 9.5047e-05 | 2.3821e-05
23 | 0.97327 | -0.5186 | 0 | 0
24 | 0.97757 | -0.43367 | 0 | 0
25 | 0.97319 | -0.52023 | 0.00068619 | 0.00017197
26 | 0.97319 | -0.52022 | 0.0002529 | 6.3383e-05
27 | 0.97319 | -0.5202 | 0.00017124 | 4.2916e-05
28 | 0.97321 | -0.51981 | 0.00022331 | 5.5968e-05
29 | 0.99572 | -0.082542 | 0.00456 | 0.0011429
30 | 0.99585 | -0.079954 | 0.0016509 | 0.00041376
31 | 0.99543 | -0.088021 | 0.00044859 | 0.00011243
32 | 1 | 0 | -0.061977 | -0.015358
33 | 0.99536 | -0.089525 | 0.00033093 | 8.294e-05
34 | 0.99527 | -0.091142 | 0.0014173 | 0.0003552
35 | 0.99527 | -0.091164 | 0.00047834 | 0.00011988
36 | 0.97788 | -0.42753 | 0 | 0
37 | 0.97794 | -0.42626 | 0.0002037 | 5.1052e-05
38 | 0.97764 | -0.43223 | 0.00015803 | 3.9607e-05
39 | 0.97806 | -0.42392 | 0.0018342 | 0.00045969
40 | 0.97921 | -0.40131 | 0.00044588 | 0.00011175
41 | 0.97939 | -0.39788 | 0.00021298 | 5.3377e-05
42 | 0.97939 | -0.39778 | 0.0018052 | 0.00045242
43 | 0.97938 | -0.39799 | 0.00034037 | 8.5304e-05
44 | 0.97944 | -0.39686 | 0 | 0
45 | 0.97937 | -0.39817 | 0.00023748 | 5.9518e-05
46 | 0.97937 | -0.39813 | 0.00017056 | 4.2747e-05
47 | 0.9803 | -0.37986 | 0 | 0
48 | 0.9854 | -0.28012 | 0.00088098 | 0.00022079
49 | 0.9849 | -0.28984 | 0 | 0
50 | 0.9907 | -0.1776 | 0.0016604 | 0.00041613
51 | 0.99525 | -0.091486 | 0.00024918 | 6.2449e-05
52 | 0.99526 | -0.091335 | 0 | 0
53 | 0.97895 | -0.40654 | 0 | 0
54 | 0.97791 | -0.42694 | 0.00049186 | 0.00012327
55 | 0.97793 | -0.42652 | 0.002051 | 0.00051402
56 | 0.97776 | -0.42991 | 0 | 0
57 | 0.99138 | -0.16456 | 0.00025242 | 6.3262e-05
58 | 0.99578 | -0.080318 | 0.00018987 | 4.7586e-05
59 | 0.99409 | -0.11278 | 0 | 0
60 | 0.98939 | -0.20346 | 0 | 0
61 | 0.99731 | -0.051116 | 0.00025339 | 6.3504e-05
62 | 0.98442 | -0.30028 | 0.0019567 | 0.00049041
63 | 0.99807 | -0.036686 | 0.00054899 | 0.00013759
64 | 0.99911 | -0.01683 | 0.00046412 | 0.00011632
65 | 0.98891 | -0.21267 | 0.0020974 | 0.00052566
66 | 0.97775 | -0.43022 | 0.00070591 | 0.00017692
67 | 0.97774 | -0.43033 | 0.00021413 | 5.3667e-05
68 | 0.97775 | -0.43011 | 0.0004277 | 0.00010719
69 | 0.97888 | -0.40779 | 0.00081962 | 0.00020542
70 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.015889 | 0.0039784 | -0.015885 | -0.0039761 | 3.9553e-06 | 2.2972e-06 | 0.023971 | 0.023971 | 0.023971 | 0.98625 | -0.26447 | 0.98598 | -0.2697 | 6.5854
1 | -0.016726 | -0.0041883 | 0.016729 | 0.00419 | 2.8424e-06 | 1.6672e-06 | 0.025234 | 0.025234 | 0.025234 | 0.98625 | -0.26447 | 0.98643 | -0.2609 | 6.9325
2 | 0.01489 | 0.0037268 | -0.014884 | -0.0037233 | 6.0568e-06 | 3.4685e-06 | 0.022469 | 0.02247 | 0.02247 | 0.98598 | -0.2697 | 0.98555 | -0.27825 | 6.1729
3 | -0.018308 | -0.0045857 | 0.01831 | 0.0045869 | 2.05e-06 | 1.2205e-06 | 0.027616 | 0.027616 | 0.027616 | 0.98643 | -0.2609 | 0.98656 | -0.25855 | 7.5868
4 | 0.012684 | 0.0031721 | -0.012683 | -0.0031713 | 1.4378e-06 | 7.8694e-07 | 0.019149 | 0.019149 | 0.019149 | 0.98555 | -0.27825 | 0.98542 | -0.28064 | 5.2606
5 | -0.019146 | -0.0047965 | 0.019165 | 0.0048075 | 1.8434e-05 | 1.1044e-05 | 0.028877 | 0.028877 | 0.028877 | 0.98656 | -0.25855 | 0.98759 | -0.23836 | 7.9333
6 | 0.0045351 | 0.0011328 | -0.0045335 | -0.0011329 | 1.6142e-06 | -1.3619e-07 | 0.0068468 | 0.0068472 | 0.0068472 | 0.98542 | -0.28064 | 0.98504 | -0.28813 | 1.8811
7 | 0.00406 | 0.001014 | -0.0040572 | -0.0010147 | 2.7756e-06 | -7.3118e-07 | 0.0061294 | 0.0061303 | 0.0061303 | 0.98542 | -0.28064 | 0.98469 | -0.29502 | 1.6842
8 | -0.019165 | -0.0048075 | 0.019179 | 0.0048163 | 1.4701e-05 | 8.8065e-06 | 0.028877 | 0.028877 | 0.028877 | 0.98759 | -0.23836 | 0.98842 | -0.22228 | 7.9332
9 | 0.001408 | 0.00035267 | -0.001408 | -0.00035287 | 2.8026e-08 | -1.9237e-07 | 0.0021268 | 0.0021269 | 0.0021269 | 0.98504 | -0.28813 | 0.98502 | -0.28855 | 0.58432
10 | 0.00054363 | 0.0001332 | -0.00054357 | -0.00013589 | 5.4158e-08 | -2.6951e-06 | 0.00082014 | 0.0008211 | 0.0008211 | 0.98504 | -0.28813 | 0.98493 | -0.29024 | 0.22558
11 | 0.0019572 | 0.00048882 | -0.0019567 | -0.00049041 | 4.8946e-07 | -1.5845e-06 | 0.0029571 | 0.0029578 | 0.0029578 | 0.98469 | -0.29502 | 0.98442 | -0.30028 | 0.81257
12 | 0.00090715 | 0.00022697 | -0.00090713 | -0.00022715 | 1.0332e-08 | -1.7991e-07 | 0.0013707 | 0.0013708 | 0.0013708 | 0.98469 | -0.29502 | 0.98468 | -0.29526 | 0.37658
13 | 0.00054357 | 0.00013589 | -0.00054357 | -0.00013623 | 6.8491e-09 | -3.4034e-07 | 0.0008211 | 0.00082122 | 0.00082122 | 0.98493 | -0.29024 | 0.98492 | -0.2905 | 0.22561
14 | -0.022026 | -0.0055297 | 0.022036 | 0.0055359 | 1.0105e-05 | 6.1531e-06 | 0.033162 | 0.033162 | 0.033162 | 0.98842 | -0.22228 | 0.98891 | -0.21267 | 9.1104
15 | -0.0011911 | -0.00029851 | 0.0011911 | 0.00029821 | 3.0035e-08 | -3.0107e-07 | 0.0017917 | 0.0017916 | 0.0017917 | 0.98918 | -0.20761 | 0.9892 | -0.20708 | 0.49224
16 | -0.0055256 | -0.0013845 | 0.0055265 | 0.0013847 | 9.515e-07 | 1.3737e-07 | 0.0083118 | 0.0083116 | 0.0083118 | 0.9892 | -0.20708 | 0.98939 | -0.20346 | 2.2835
17 | -0.00049958 | -0.00012521 | 0.00049958 | 0.000125 | 3.4333e-09 | -2.0215e-07 | 0.00075496 | 0.00075489 | 0.00075496 | 0.98467 | -0.29541 | 0.98468 | -0.29526 | 0.20741
18 | 0.0052044 | 0.0012975 | -0.0052039 | -0.0012974 | 5.4555e-07 | 6.2481e-08 | 0.0079477 | 0.0079478 | 0.0079478 | 0.9741 | -0.50214 | 0.97399 | -0.50435 | 2.1835
19 | -0.0058732 | -0.0014651 | 0.0058735 | 0.0014652 | 3.3175e-07 | 7.5416e-08 | 0.0089692 | 0.0089692 | 0.0089692 | 0.9741 | -0.50214 | 0.97416 | -0.50095 | 2.4641
20 | 0.003459 | 0.00086012 | -0.0034586 | -0.00086035 | 4.1028e-07 | -2.2538e-07 | 0.0052821 | 0.0052823 | 0.0052823 | 0.97399 | -0.50435 | 0.97386 | -0.50685 | 1.4512
21 | -0.0059685 | -0.0014889 | 0.0059699 | 0.0014892 | 1.3421e-06 | 3.2242e-07 | 0.0091143 | 0.0091141 | 0.0091143 | 0.97416 | -0.50095 | 0.9744 | -0.49621 | 2.5039
22 | 9.5047e-05 | 2.3691e-05 | -9.5047e-05 | -2.3821e-05 | 8.2436e-11 | -1.2984e-07 | 0.00014514 | 0.00014518 | 0.00014518 | 0.97416 | -0.50095 | 0.97416 | -0.50097 | 0.039885
23 | 0.0013345 | 0.00032799 | -0.0013337 | -0.00033343 | 7.4023e-07 | -5.4374e-06 | 0.0020367 | 0.0020388 | 0.0020388 | 0.97386 | -0.50685 | 0.97327 | -0.5186 | 0.56012
24 | -0.0064353 | -0.0016058 | 0.0064544 | 0.0016115 | 1.9144e-05 | 5.6414e-06 | 0.0098248 | 0.0098225 | 0.0098248 | 0.9744 | -0.49621 | 0.97757 | -0.43367 | 2.6991
25 | 0.0013337 | 0.00033343 | -0.0013337 | -0.00033399 | 7.6669e-08 | -5.6207e-07 | 0.0020388 | 0.002039 | 0.002039 | 0.97327 | -0.5186 | 0.97321 | -0.51981 | 0.56018
26 | -0.0064544 | -0.0016115 | 0.0064548 | 0.0016116 | 4.4127e-07 | 1.2949e-07 | 0.0098225 | 0.0098224 | 0.0098225 | 0.97757 | -0.43367 | 0.97764 | -0.43223 | 2.6985
27 | -0.00068619 | -0.00017197 | 0.00068619 | 0.00017196 | 3.7505e-10 | -1.1051e-08 | 0.0010492 | 0.0010492 | 0.0010492 | 0.97319 | -0.52023 | 0.97319 | -0.52022 | 0.28824
28 | -0.00093909 | -0.00023535 | 0.00093909 | 0.00023533 | 8.2809e-10 | -1.2779e-08 | 0.0014359 | 0.0014359 | 0.0014359 | 0.97319 | -0.52022 | 0.97319 | -0.5202 | 0.39447
29 | -0.0011103 | -0.00027825 | 0.0011104 | 0.00027802 | 2.0882e-08 | -2.2672e-07 | 0.0016977 | 0.0016976 | 0.0016977 | 0.97319 | -0.5202 | 0.97321 | -0.51981 | 0.4664
30 | -0.00456 | -0.0011429 | 0.0045606 | 0.0011428 | 5.6231e-07 | -6.0181e-08 | 0.0068146 | 0.0068145 | 0.0068146 | 0.99572 | -0.082542 | 0.99585 | -0.079954 | 1.8721
31 | 0.0029258 | 0.00072983 | -0.0029247 | -0.00073115 | 1.1212e-06 | -1.3177e-06 | 0.0043705 | 0.0043713 | 0.0043713 | 0.99585 | -0.079954 | 0.99543 | -0.088021 | 1.2009
32 | -0.0091373 | -0.0022864 | 0.0091722 | 0.0023022 | 3.4869e-05 | 1.5797e-05 | 0.013652 | 0.01365 | 0.013652 | 0.99585 | -0.079954 | 1 | 0 | 3.7505
33 | 0.0024761 | 0.00061872 | -0.0024759 | -0.00061906 | 1.7701e-07 | -3.3472e-07 | 0.0037007 | 0.0037009 | 0.0037009 | 0.99543 | -0.088021 | 0.99536 | -0.089525 | 1.0167
34 | 0.051155 | 0.013056 | -0.051113 | -0.01303 | 4.156e-05 | 2.6348e-05 | 0.076203 | 0.076203 | 0.076203 | 1 | 0 | 0.99911 | -0.01683 | 20.9349
35 | 0.002145 | 0.00053612 | -0.0021448 | -0.00053657 | 1.6496e-07 | -4.5058e-07 | 0.0032061 | 0.0032063 | 0.0032063 | 0.99536 | -0.089525 | 0.99527 | -0.091142 | 0.88086
36 | 0.00072752 | 0.00018136 | -0.00072752 | -0.00018139 | 7.5864e-10 | -2.1749e-08 | 0.0010874 | 0.0010874 | 0.0010874 | 0.99527 | -0.091142 | 0.99527 | -0.091164 | 0.29873
37 | 0.00024918 | 6.1502e-05 | -0.00024918 | -6.2004e-05 | 2.015e-09 | -5.025e-07 | 0.00037221 | 0.00037239 | 0.00037239 | 0.99527 | -0.091164 | 0.99526 | -0.091335 | 0.1023
38 | -0.0066144 | -0.0016516 | 0.0066148 | 0.0016518 | 3.9893e-07 | 1.2351e-07 | 0.010063 | 0.010063 | 0.010063 | 0.97788 | -0.42753 | 0.97794 | -0.42626 | 2.7645
39 | 0.0066144 | 0.0016516 | -0.0066129 | -0.0016512 | 1.4763e-06 | 4.5722e-07 | 0.010063 | 0.010063 | 0.010063 | 0.97788 | -0.42753 | 0.97764 | -0.43223 | 2.7645
40 | -0.0068185 | -0.0017028 | 0.0068192 | 0.0017031 | 7.5691e-07 | 2.4901e-07 | 0.010373 | 0.010373 | 0.010373 | 0.97794 | -0.42626 | 0.97806 | -0.42392 | 2.8496
41 | -0.0086534 | -0.0021628 | 0.0086627 | 0.0021669 | 9.3119e-06 | 4.1588e-06 | 0.013163 | 0.013162 | 0.013163 | 0.97806 | -0.42392 | 0.97921 | -0.40131 | 3.6162
42 | -0.0091086 | -0.0022787 | 0.0091179 | 0.002283 | 9.3021e-06 | 4.3224e-06 | 0.01384 | 0.013839 | 0.01384 | 0.97921 | -0.40131 | 0.9803 | -0.37986 | 3.8022
43 | -0.00079083 | -0.00019752 | 0.00079083 | 0.00019744 | 3.6936e-09 | -8.3526e-08 | 0.0012013 | 0.0012013 | 0.0012013 | 0.97939 | -0.39788 | 0.97939 | -0.39778 | 0.33003
44 | 0.00057785 | 0.00014415 | -0.00057785 | -0.00014428 | 3.0521e-09 | -1.3099e-07 | 0.00087771 | 0.00087776 | 0.00087776 | 0.97939 | -0.39788 | 0.97938 | -0.39799 | 0.24114
45 | -0.002596 | -0.00064986 | 0.0025961 | 0.00064969 | 1.1343e-07 | -1.7214e-07 | 0.0039439 | 0.0039438 | 0.0039439 | 0.97939 | -0.39778 | 0.97944 | -0.39686 | 1.0835
46 | 0.00023748 | 5.8972e-05 | -0.00023748 | -5.9518e-05 | 2.1219e-09 | -5.4585e-07 | 0.00036062 | 0.00036082 | 0.00036082 | 0.97938 | -0.39799 | 0.97937 | -0.39817 | 0.099126
47 | 0.0048869 | 0.0012179 | -0.0048866 | -0.0012179 | 2.95e-07 | 9.0884e-09 | 0.007422 | 0.0074221 | 0.0074221 | 0.97944 | -0.39686 | 0.97937 | -0.39813 | 2.039
48 | -0.007483 | -0.0018676 | 0.0074891 | 0.0018699 | 6.045e-06 | 2.2969e-06 | 0.011366 | 0.011365 | 0.011366 | 0.97944 | -0.39686 | 0.9803 | -0.37986 | 3.1225
49 | 0.0047161 | 0.0011752 | -0.0047142 | -0.0011752 | 1.8806e-06 | -2.5757e-08 | 0.007163 | 0.0071634 | 0.0071634 | 0.97937 | -0.39813 | 0.97895 | -0.40654 | 1.968
50 | -0.016607 | -0.0041529 | 0.016678 | 0.0041948 | 7.1408e-05 | 4.1904e-05 | 0.025205 | 0.025203 | 0.025205 | 0.9803 | -0.37986 | 0.9849 | -0.28984 | 6.9244
51 | 0.016686 | 0.0041994 | -0.016678 | -0.0041948 | 7.7485e-06 | 4.5449e-06 | 0.025203 | 0.025203 | 0.025203 | 0.9854 | -0.28012 | 0.9849 | -0.28984 | 6.924
52 | -0.017567 | -0.0044202 | 0.017654 | 0.0044713 | 8.6484e-05 | 5.1154e-05 | 0.026534 | 0.026532 | 0.026534 | 0.9854 | -0.28012 | 0.9907 | -0.1776 | 7.2894
53 | -0.019314 | -0.0048874 | 0.019326 | 0.0048947 | 1.2096e-05 | 7.2482e-06 | 0.029026 | 0.029026 | 0.029026 | 0.9907 | -0.1776 | 0.99138 | -0.16456 | 7.9742
54 | -0.00024918 | -6.2449e-05 | 0.00024918 | 6.2004e-05 | 1.7856e-09 | -4.4489e-07 | 0.00037254 | 0.00037239 | 0.00037254 | 0.99525 | -0.091486 | 0.99526 | -0.091335 | 0.10235
55 | 0.00081967 | 0.00020439 | -0.00081962 | -0.00020542 | 4.8824e-08 | -1.0235e-06 | 0.0012455 | 0.0012459 | 0.0012459 | 0.97895 | -0.40654 | 0.97888 | -0.40779 | 0.34228
56 | 0.0038945 | 0.00097082 | -0.0038908 | -0.00097199 | 3.693e-06 | -1.1675e-06 | 0.0059179 | 0.0059191 | 0.0059191 | 0.97895 | -0.40654 | 0.97793 | -0.42652 | 1.6261
57 | -0.00049186 | -0.00012327 | 0.00049187 | 0.0001227 | 9.7568e-09 | -5.7668e-07 | 0.00074843 | 0.00074822 | 0.00074843 | 0.97791 | -0.42694 | 0.97793 | -0.42652 | 0.20561
58 | 0.001348 | 0.00033527 | -0.0013478 | -0.00033686 | 2.1677e-07 | -1.586e-06 | 0.0020502 | 0.0020508 | 0.0020508 | 0.97793 | -0.42652 | 0.97776 | -0.42991 | 0.5634
59 | 0.0004277 | 0.00010687 | -0.0004277 | -0.00010719 | 4.1383e-09 | -3.2409e-07 | 0.00065079 | 0.00065091 | 0.00065091 | 0.97776 | -0.42991 | 0.97775 | -0.43011 | 0.17882
60 | 0.00092006 | 0.00022999 | -0.00092005 | -0.00023021 | 1.3544e-08 | -2.2244e-07 | 0.0014 | 0.0014001 | 0.0014001 | 0.97776 | -0.42991 | 0.97775 | -0.43022 | 0.38464
61 | -0.019578 | -0.004958 | 0.019658 | 0.0050057 | 7.9534e-05 | 4.7725e-05 | 0.029405 | 0.029403 | 0.029405 | 0.99138 | -0.16456 | 0.99578 | -0.080318 | 8.0782
62 | -0.049694 | -0.012615 | 0.049764 | 0.01266 | 6.9925e-05 | 4.4312e-05 | 0.074315 | 0.074315 | 0.074315 | 0.99578 | -0.080318 | 0.99731 | -0.051116 | 20.4163
63 | 0.029846 | 0.007562 | -0.029799 | -0.0075331 | 4.6468e-05 | 2.8932e-05 | 0.044628 | 0.044629 | 0.044629 | 0.99578 | -0.080318 | 0.99409 | -0.11278 | 12.2606
64 | 0.029799 | 0.0075331 | -0.02967 | -0.0074527 | 0.00012899 | 8.0326e-05 | 0.044629 | 0.044629 | 0.044629 | 0.99409 | -0.11278 | 0.98939 | -0.20346 | 12.2608
65 | 0.024144 | 0.0060681 | -0.024133 | -0.0060616 | 1.0601e-05 | 6.5093e-06 | 0.036318 | 0.036318 | 0.036318 | 0.98939 | -0.20346 | 0.98891 | -0.21267 | 9.9774
66 | -0.050017 | -0.012723 | 0.050052 | 0.012745 | 3.4807e-05 | 2.2059e-05 | 0.074693 | 0.074693 | 0.074693 | 0.99731 | -0.051116 | 0.99807 | -0.036686 | 20.5202
67 | -0.050601 | -0.012883 | 0.050649 | 0.012913 | 4.8499e-05 | 3.0743e-05 | 0.075512 | 0.075512 | 0.075512 | 0.99807 | -0.036686 | 0.99911 | -0.01683 | 20.745
68 | 0.00021414 | 5.3295e-05 | -0.00021413 | -5.3667e-05 | 1.1849e-09 | -3.7252e-07 | 0.00032576 | 0.00032589 | 0.00032589 | 0.97775 | -0.43022 | 0.97774 | -0.43033 | 0.08953

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.062088 | 0.015386

## res_load
| p_mw | q_mvar
0 | 0.00083751 | 0.0002099
1 | 0.00099492 | 0.00024935
2 | 0.0015787 | 0.00039567
3 | 0.0021995 | 0.00055124
4 | 0.00083634 | 0.00020961
5 | 0.0040877 | 0.0010245
6 | 0.0025819 | 0.00064708
7 | 0.0011928 | 0.00029895
8 | 0.00054357 | 0.00013623
9 | 0.0028465 | 0.0007134
10 | 0.001408 | 0.00035287
11 | 0.0011911 | 0.00029851
12 | 0.0043345 | 0.0010863
13 | 0.00049958 | 0.00012521
14 | 0.00040755 | 0.00010214
15 | 0.00066874 | 0.0001676
16 | 0.0017449 | 0.0004373
17 | 0.0021241 | 0.00053236
18 | 0.00046538 | 0.00011663
19 | 9.5047e-05 | 2.3821e-05
20 | 0.00068619 | 0.00017197
21 | 0.0002529 | 6.3383e-05
22 | 0.00017124 | 4.2916e-05
23 | 0.00022331 | 5.5968e-05
24 | 0.00456 | 0.0011429
25 | 0.0016509 | 0.00041376
26 | 0.00044859 | 0.00011243
27 | 0.00011047 | 2.7686e-05
28 | 0.00033093 | 8.294e-05
29 | 0.0014173 | 0.0003552
30 | 0.00047834 | 0.00011988
31 | 0.0002037 | 5.1052e-05
32 | 0.00015803 | 3.9607e-05
33 | 0.0018342 | 0.00045969
34 | 0.00044588 | 0.00011175
35 | 0.00021298 | 5.3377e-05
36 | 0.0018052 | 0.00045242
37 | 0.00034037 | 8.5304e-05
38 | 0.00023748 | 5.9518e-05
39 | 0.00017056 | 4.2747e-05
40 | 0.00088098 | 0.00022079
41 | 0.0016604 | 0.00041613
42 | 0.00024918 | 6.2449e-05
43 | 0.00049186 | 0.00012327
44 | 0.002051 | 0.00051402
45 | 0.00025242 | 6.3262e-05
46 | 0.00018987 | 4.7586e-05
47 | 0.00025339 | 6.3504e-05
48 | 0.0019567 | 0.00049041
49 | 0.00054899 | 0.00013759
50 | 0.00046412 | 0.00011632
51 | 0.0020974 | 0.00052566
52 | 0.00070591 | 0.00017692
53 | 0.00021413 | 5.3667e-05
54 | 0.0004277 | 0.00010719
55 | 0.00081962 | 0.00020542

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1