## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1065-4_1_2_node_22 | 0.4 | n |  | TRUE
1 | bus_LV_1065-4_1_2_node_191 | 0.4 | n |  | TRUE
2 | bus_LV_1065-4_1_2_node_96 | 0.4 | n |  | TRUE
3 | bus_LV_1065-4_1_2_node_19 | 0.4 | n |  | TRUE
4 | bus_LV_1065-4_1_2_node_162 | 0.4 | n |  | TRUE
5 | bus_LV_1065-4_1_2_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_1065-4_1_2_node_192 | 0.4 | n |  | TRUE
7 | bus_LV_1065-4_1_2_node_42 | 0.4 | n |  | TRUE
8 | bus_LV_1065-4_1_2_node_194 | 0.4 | n |  | TRUE
9 | bus_LV_1065-4_1_2_node_43 | 0.4 | n |  | TRUE
10 | bus_LV_1065-4_1_2_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_1065-4_1_2_node_193 | 0.4 | n |  | TRUE
12 | bus_LV_1065-4_1_2_node_159 | 0.4 | n |  | TRUE
13 | bus_LV_1065-4_1_2_node_86 | 0.4 | n |  | TRUE
14 | bus_LV_1065-4_1_2_node_74 | 0.4 | n |  | TRUE
15 | bus_LV_1065-4_1_2_node_78 | 0.4 | n |  | TRUE
16 | bus_LV_1065-4_1_2_node_72 | 0.4 | n |  | TRUE
17 | bus_LV_1065-4_1_2_node_190 | 0.4 | n |  | TRUE
18 | bus_LV_1065-4_1_2_node_189 | 0.4 | n |  | TRUE
19 | bus_LV_1065-4_1_2_node_94 | 0.4 | n |  | TRUE
20 | bus_LV_1065-4_1_2_node_84 | 0.4 | n |  | TRUE
21 | bus_LV_1065-4_1_2_node_195 | 0.4 | n |  | TRUE
22 | bus_LV_1065-4_1_2_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_1065-4_1_2_node_45 | 0.4 | n |  | TRUE
24 | bus_LV_1065-4_1_2_node_46 | 0.4 | n |  | TRUE
25 | bus_LV_1065-4_1_2_node_47 | 0.4 | n |  | TRUE
26 | bus_LV_1065-4_1_2_node_48 | 0.4 | n |  | TRUE
27 | bus_LV_1065-4_1_2_node_62 | 0.4 | n |  | TRUE
28 | bus_LV_1065-4_1_2_node_51 | 0.4 | n |  | TRUE
29 | bus_LV_1065-4_1_2_node_63 | 0.4 | n |  | TRUE
30 | bus_LV_1065-4_1_2_node_49 | 0.4 | n |  | TRUE
31 | bus_LV_1065-4_1_2_node_53 | 0.4 | n |  | TRUE
32 | bus_LV_1065-4_1_2_node_68 | 0.4 | n |  | TRUE
33 | bus_LV_1065-4_1_2_node_50 | 0.4 | n |  | TRUE
34 | bus_LV_1065-4_1_2_node_55 | 0.4 | n |  | TRUE
35 | bus_LV_1065-4_1_2_node_184 | 0.4 | n |  | TRUE
36 | bus_LV_1065-4_1_2_node_56 | 0.4 | n |  | TRUE
37 | bus_LV_1065-4_1_2_node_169 | 0.4 | n |  | TRUE
38 | bus_LV_1065-4_1_2_node_52 | 0.4 | n |  | TRUE
39 | bus_LV_1065-4_1_2_node_161 | 0.4 | n |  | TRUE
40 | bus_LV_1065-4_1_2_node_85 | 0.4 | n |  | TRUE
41 | bus_LV_1065-4_1_2_node_61 | 0.4 | n |  | TRUE
42 | bus_LV_1065-4_1_2_node_54 | 0.4 | n |  | TRUE
43 | bus_LV_1065-4_1_2_node_73 | 0.4 | n |  | TRUE
44 | bus_LV_1065-4_1_2_node_170 | 0.4 | n |  | TRUE
45 | bus_LV_1065-4_1_2_node_165 | 0.4 | n |  | TRUE
46 | bus_LV_1065-4_1_2_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_1065-4_1_2_node_108 | 0.4 | n |  | TRUE
48 | bus_LV_1065-4_1_2_node_57 | 0.4 | n |  | TRUE
49 | bus_LV_1065-4_1_2_node_80 | 0.4 | n |  | TRUE
50 | bus_LV_1065-4_1_2_node_69 | 0.4 | n |  | TRUE
51 | bus_LV_1065-4_1_2_node_58 | 0.4 | n |  | TRUE
52 | bus_LV_1065-4_1_2_node_172 | 0.4 | n |  | TRUE
53 | bus_LV_1065-4_1_2_node_171 | 0.4 | n |  | TRUE
54 | bus_LV_1065-4_1_2_node_59 | 0.4 | n |  | TRUE
55 | bus_LV_1065-4_1_2_node_82 | 0.4 | n |  | TRUE
56 | bus_LV_1065-4_1_2_node_60 | 0.4 | n |  | TRUE
57 | bus_LV_1065-4_1_2_node_100 | 0.4 | n |  | TRUE
58 | bus_LV_1065-4_1_2_node_93 | 0.4 | n |  | TRUE
59 | bus_LV_1065-4_1_2_node_65 | 0.4 | n |  | TRUE
60 | bus_LV_1065-4_1_2_node_132 | 0.4 | n |  | TRUE
61 | bus_LV_1065-4_1_2_node_66 | 0.4 | n |  | TRUE
62 | bus_LV_1065-4_1_2_node_168 | 0.4 | n |  | TRUE
63 | bus_LV_1065-4_1_2_node_163 | 0.4 | n |  | TRUE
64 | bus_LV_1065-4_1_2_node_77 | 0.4 | n |  | TRUE
65 | bus_LV_1065-4_1_2_node_71 | 0.4 | n |  | TRUE
66 | bus_LV_1065-4_1_2_node_164 | 0.4 | n |  | TRUE
67 | bus_LV_1065-4_1_2_node_123 | 0.4 | n |  | TRUE
68 | bus_LV_1065-4_1_2_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_1065-4_1_2_node_76 | 0.4 | n |  | TRUE
70 | bus_LV_1065-4_1_2_node_81 | 0.4 | n |  | TRUE
71 | bus_LV_1065-4_1_2_node_95 | 0.4 | n |  | TRUE
72 | bus_LV_1065-4_1_2_node_91 | 0.4 | n |  | TRUE
73 | bus_LV_1065-4_1_2_node_113 | 0.4 | n |  | TRUE
74 | bus_LV_1065-4_1_2_node_135 | 0.4 | n |  | TRUE
75 | bus_LV_1065-4_1_2_node_130 | 0.4 | n |  | TRUE
76 | bus_LV_1065-4_1_2_node_131 | 0.4 | n |  | TRUE
77 | bus_LV_1065-4_1_2_node_114 | 0.4 | n |  | TRUE
78 | bus_LV_1065-4_1_2_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_1065-4_1_2_node_75 | 0.4 | n |  | TRUE
80 | bus_LV_1065-4_1_2_node_173 | 0.4 | n |  | TRUE
81 | bus_LV_1065-4_1_2_node_197 | 0.4 | n |  | TRUE
82 | bus_LV_1065-4_1_2_node_83 | 0.4 | n |  | TRUE
83 | bus_LV_1065-4_1_2_node_92 | 0.4 | n |  | TRUE
84 | bus_LV_1065-4_1_2_node_97 | 0.4 | n |  | TRUE
85 | bus_LV_1065-4_1_2_node_105 | 0.4 | n |  | TRUE
86 | bus_LV_1065-4_1_2_node_102 | 0.4 | n |  | TRUE
87 | bus_LV_1065-4_1_2_node_124 | 0.4 | n |  | TRUE
88 | bus_LV_1065-4_1_2_node_101 | 0.4 | n |  | TRUE
89 | bus_LV_1065-4_1_2_node_128 | 0.4 | n |  | TRUE
90 | bus_LV_1065-4_1_2_node_126 | 0.4 | n |  | TRUE
91 | bus_LV_1065-4_1_2_node_103 | 0.4 | n |  | TRUE
92 | bus_LV_1065-4_1_2_node_104 | 0.4 | n |  | TRUE
93 | bus_LV_1065-4_1_2_node_106 | 0.4 | n |  | TRUE
94 | bus_LV_1065-4_1_2_node_107 | 0.4 | n |  | TRUE
95 | bus_LV_1065-4_1_2_node_129 | 0.4 | n |  | TRUE
96 | bus_LV_1065-4_1_2_node_125 | 0.4 | n |  | TRUE
97 | bus_LV_1065-4_1_2_node_183 | 0.4 | n |  | TRUE
98 | bus_LV_1065-4_1_2_node_160 | 0.4 | n |  | TRUE
99 | bus_LV_1065-4_1_2_node_196 | 0.4 | n |  | TRUE
100 | bus_LV_1065-4_1_2_node_127 | 0.4 | n |  | TRUE
101 | bus_LV_1065-4_1_2_node_136 | 0.4 | n |  | TRUE
102 | bus_LV_1065-4_1_2_node_133 | 0.4 | n |  | TRUE
103 | bus_LV_1065-4_1_2_node_182 | 0.4 | n |  | TRUE
104 | bus_LV_1065-4_1_2_node_134 | 0.4 | n |  | TRUE
105 | bus_LV_1065-4_1_2_node_137 | 0.4 | n |  | TRUE
106 | bus_LV_1065-4_1_2_node_177 | 0.4 | n |  | TRUE
107 | bus_LV_1065-4_1_2_node_166 | 0.4 | n |  | TRUE
108 | bus_LV_1065-4_1_2_node_178 | 0.4 | n |  | TRUE
109 | bus_LV_1065-4_1_2_node_167 | 0.4 | n |  | TRUE
110 | bus_LV_1065-4_1_2_node_138 | 0.4 | n |  | TRUE
111 | bus_LV_1065-4_1_2_node_139 | 0.4 | n |  | TRUE
112 | bus_LV_1065-4_1_2_node_140 | 0.4 | n |  | TRUE
113 | bus_LV_1065-4_1_2_node_141 | 0.4 | n |  | TRUE
114 | bus_LV_1065-4_1_2_node_142 | 0.4 | n |  | TRUE
115 | bus_LV_1065-4_1_2_node_143 | 0.4 | n |  | TRUE
116 | bus_LV_1065-4_1_2_node_144 | 0.4 | n |  | TRUE
117 | bus_LV_1065-4_1_2_node_148 | 0.4 | n |  | TRUE
118 | bus_LV_1065-4_1_2_node_175 | 0.4 | n |  | TRUE
119 | bus_LV_1065-4_1_2_node_149 | 0.4 | n |  | TRUE
120 | bus_LV_1065-4_1_2_node_176 | 0.4 | n |  | TRUE
121 | bus_LV_1065-4_1_2_node_150 | 0.4 | n |  | TRUE
122 | bus_LV_1065-4_1_2_node_151 | 0.4 | n |  | TRUE
123 | bus_LV_1065-4_1_2_node_181 | 0.4 | n |  | TRUE
124 | bus_LV_1065-4_1_2_node_180 | 0.4 | n |  | TRUE
125 | bus_LV_1065-4_1_2_node_179 | 0.4 | n |  | TRUE
126 | bus_LV_1065-4_1_2_node_187 | 0.4 | n |  | TRUE
127 | bus_LV_1065-4_1_2_node_188 | 0.4 | n |  | TRUE
128 | bus_MV_5_0_node_32 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1065-4_1_2_load_191 | 1 | 0.0042027 | 0.0010533 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1065-4_1_2_load_96 | 2 | 0.0019699 | 0.0004937 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1065-4_1_2_load_162 | 4 | 0.0066729 | 0.0016724 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1065-4_1_2_load_192 | 6 | 0.0016628 | 0.00041674 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1065-4_1_2_load_194 | 8 | 0.0044886 | 0.0011249 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1065-4_1_2_load_193 | 11 | 0.0033223 | 0.00083265 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1065-4_1_2_load_159 | 12 | 0.010438 | 0.0026159 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1065-4_1_2_load_86 | 13 | 0.0025254 | 0.00063292 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1065-4_1_2_load_78 | 15 | 0.0028624 | 0.00071738 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1065-4_1_2_load_189 | 18 | 0.0044588 | 0.0011175 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1065-4_1_2_load_84 | 20 | 0.0025242 | 0.00063261 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1065-4_1_2_load_195 | 21 | 0.0063783 | 0.0015986 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1065-4_1_2_load_44 | 22 | 0.0014161 | 0.0003549 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1065-4_1_2_load_47 | 25 | 0.0017021 | 0.00042658 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1065-4_1_2_load_48 | 26 | 0.0019538 | 0.00048968 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1065-4_1_2_load_62 | 27 | 0.0015102 | 0.0003785 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1065-4_1_2_load_68 | 32 | 0.0030657 | 0.00076833 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1065-4_1_2_load_184 | 35 | 0.008578 | 0.0021499 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1065-4_1_2_load_169 | 37 | 0.0012413 | 0.0003111 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1065-4_1_2_load_161 | 39 | 0.0025246 | 0.00063271 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1065-4_1_2_load_85 | 40 | 0.0025237 | 0.00063251 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1065-4_1_2_load_170 | 44 | 0.0034702 | 0.00086971 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1065-4_1_2_load_165 | 45 | 0.0047203 | 0.001183 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1065-4_1_2_load_64 | 46 | 0.0044155 | 0.0011066 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1065-4_1_2_load_108 | 47 | 2.6776e-05 | 6.7107e-06 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1065-4_1_2_load_80 | 49 | 0.0041925 | 0.0010507 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1065-4_1_2_load_69 | 50 | 0.010331 | 0.0025893 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1065-4_1_2_load_172 | 52 | 0.0024509 | 0.00061426 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1065-4_1_2_load_82 | 55 | 0.0025266 | 0.00063323 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1065-4_1_2_load_100 | 57 | 0.0083917 | 0.0021032 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1065-4_1_2_load_65 | 59 | 0.00063225 | 0.00015846 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1065-4_1_2_load_132 | 60 | 0.00063461 | 0.00015905 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1065-4_1_2_load_66 | 61 | 0.0016919 | 0.00042404 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1065-4_1_2_load_168 | 62 | 0.00013857 | 3.473e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1065-4_1_2_load_163 | 63 | 0.00063423 | 0.00015895 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1065-4_1_2_load_77 | 64 | 0.00063409 | 0.00015892 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1065-4_1_2_load_71 | 65 | 0.00063469 | 0.00015907 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1065-4_1_2_load_164 | 66 | 0.0065891 | 0.0016514 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1065-4_1_2_load_67 | 68 | 0.0044297 | 0.0011102 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1065-4_1_2_load_81 | 70 | 0.0027704 | 0.00069433 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1065-4_1_2_load_95 | 71 | 0.0017554 | 0.00043996 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1065-4_1_2_load_91 | 72 | 0.0036632 | 0.00091807 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1065-4_1_2_load_113 | 73 | 0.0028962 | 0.00072585 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1065-4_1_2_load_135 | 74 | 0.00071291 | 0.00017867 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1065-4_1_2_load_130 | 75 | 0.0039662 | 0.00099402 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1065-4_1_2_load_114 | 77 | 0.001832 | 0.00045915 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1065-4_1_2_load_70 | 78 | 0.0012202 | 0.00030581 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1065-4_1_2_load_75 | 79 | 0.0014381 | 0.00036042 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1065-4_1_2_load_173 | 80 | 0.001039 | 0.0002604 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1065-4_1_2_load_83 | 82 | 0.0023355 | 0.00058532 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1065-4_1_2_load_92 | 83 | 0.0036649 | 0.00091851 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1065-4_1_2_load_105 | 85 | 0.0051875 | 0.0013001 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1065-4_1_2_load_102 | 86 | 0.0029105 | 0.00072945 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1065-4_1_2_load_124 | 87 | 0.0019084 | 0.00047829 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1065-4_1_2_load_101 | 88 | 0.0068825 | 0.0017249 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1065-4_1_2_load_128 | 89 | 0.0061677 | 0.0015458 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1065-4_1_2_load_103 | 91 | 0.0037043 | 0.00092839 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1065-4_1_2_load_106 | 93 | 0.0021874 | 0.00054821 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1065-4_1_2_load_107 | 94 | 0.0056251 | 0.0014098 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1065-4_1_2_load_129 | 95 | 0.0033878 | 0.00084907 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1065-4_1_2_load_125 | 96 | 0.0027928 | 0.00069994 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1065-4_1_2_load_183 | 97 | 0.0027232 | 0.00068249 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1065-4_1_2_load_160 | 98 | 0.0018098 | 0.00045357 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1065-4_1_2_load_196 | 99 | 0.0013549 | 0.00033957 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1065-4_1_2_load_127 | 100 | 0.0067469 | 0.0016909 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1065-4_1_2_load_133 | 102 | 0.0077543 | 0.0019434 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1065-4_1_2_load_182 | 103 | 0.0021235 | 0.0005322 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1065-4_1_2_load_134 | 104 | 0.0014683 | 0.000368 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1065-4_1_2_load_137 | 105 | 0.0043684 | 0.0010948 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1065-4_1_2_load_177 | 106 | 0.002421 | 0.00060675 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1065-4_1_2_load_166 | 107 | 0.0042235 | 0.0010585 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1065-4_1_2_load_178 | 108 | 0.00075704 | 0.00018973 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1065-4_1_2_load_167 | 109 | 0.0014319 | 0.00035886 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1065-4_1_2_load_138 | 110 | 0.0021849 | 0.0005476 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1065-4_1_2_load_139 | 111 | 0.0018693 | 0.00046848 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1065-4_1_2_load_141 | 113 | 0.0016796 | 0.00042095 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1065-4_1_2_load_142 | 114 | 0.0015504 | 0.00038858 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1065-4_1_2_load_143 | 115 | 0.0018793 | 0.00047099 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1065-4_1_2_load_144 | 116 | 0.0020327 | 0.00050944 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1065-4_1_2_load_148 | 117 | 0.0015504 | 0.00038857 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1065-4_1_2_load_175 | 118 | 0.0023051 | 0.00057772 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1065-4_1_2_load_176 | 120 | 0.0019934 | 0.0004996 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1065-4_1_2_load_150 | 121 | 0.0018673 | 0.00046799 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1065-4_1_2_load_151 | 122 | 0.0027739 | 0.0006952 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1065-4_1_2_load_181 | 123 | 0.00043827 | 0.00010984 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1065-4_1_2_load_180 | 124 | 0.0007647 | 0.00019165 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1065-4_1_2_load_179 | 125 | 0.0013306 | 0.00033347 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1065-4_1_2_load_187 | 126 | 0.005783 | 0.0014494 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1065-4_1_2_load_188 | 127 | 0.0015435 | 0.00038683 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 100 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1065-4_1_2_line_0 |  | 0 | 1 | 0.02392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1065-4_1_2_line_1 |  | 0 | 2 | 0.024556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1065-4_1_2_line_2 |  | 1 | 6 | 0.025914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1065-4_1_2_line_3 |  | 1 | 17 | 0.017794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1065-4_1_2_line_4 |  | 2 | 19 | 0.06893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1065-4_1_2_line_5 |  | 3 | 4 | 0.1414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1065-4_1_2_line_6 |  | 3 | 5 | 0.024662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1065-4_1_2_line_7 |  | 5 | 6 | 0.034139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1065-4_1_2_line_8 |  | 7 | 8 | 0.075682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1065-4_1_2_line_9 |  | 7 | 9 | 0.009325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1065-4_1_2_line_10 |  | 7 | 10 | 0.18435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1065-4_1_2_line_11 |  | 8 | 21 | 0.0039316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1065-4_1_2_line_12 |  | 9 | 11 | 0.082554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1065-4_1_2_line_13 |  | 10 | 12 | 0.019647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1065-4_1_2_line_14 |  | 10 | 13 | 0.13106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1065-4_1_2_line_15 |  | 13 | 20 | 0.0061108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1065-4_1_2_line_16 |  | 14 | 15 | 0.056662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1065-4_1_2_line_17 |  | 14 | 16 | 0.002893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1065-4_1_2_line_18 |  | 16 | 79 | 0.018355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1065-4_1_2_line_19 |  | 16 | 78 | 0.087812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1065-4_1_2_line_20 |  | 17 | 18 | 0.019083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1065-4_1_2_line_21 |  | 18 | 126 | 0.021826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1065-4_1_2_line_22 |  | 19 | 84 | 0.021471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1065-4_1_2_line_23 |  | 20 | 82 | 0.0075819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1065-4_1_2_line_24 |  | 22 | 23 | 0.016273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1065-4_1_2_line_25 |  | 22 | 24 | 0.042226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1065-4_1_2_line_26 |  | 23 | 25 | 0.018373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1065-4_1_2_line_27 |  | 23 | 26 | 0.036478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1065-4_1_2_line_28 |  | 24 | 27 | 0.013309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1065-4_1_2_line_29 |  | 24 | 28 | 0.028025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1065-4_1_2_line_30 |  | 25 | 29 | 0.018392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1065-4_1_2_line_31 |  | 27 | 59 | 0.012455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1065-4_1_2_line_32 |  | 28 | 36 | 0.18546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1065-4_1_2_line_33 |  | 28 | 37 | 0.39119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1065-4_1_2_line_34 |  | 29 | 60 | 0.010309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1065-4_1_2_line_35 |  | 30 | 31 | 0.037598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1065-4_1_2_line_36 |  | 30 | 32 | 0.013716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1065-4_1_2_line_37 |  | 31 | 41 | 0.020188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1065-4_1_2_line_38 |  | 31 | 35 | 0.022249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1065-4_1_2_line_39 |  | 32 | 61 | 0.024586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1065-4_1_2_line_40 |  | 33 | 34 | 0.019595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1065-4_1_2_line_41 |  | 33 | 35 | 0.033301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1065-4_1_2_line_42 |  | 34 | 45 | 0.021462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1065-4_1_2_line_43 |  | 34 | 46 | 0.028038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1065-4_1_2_line_44 |  | 36 | 47 | 0.2358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1065-4_1_2_line_45 |  | 37 | 62 | 0.13969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1065-4_1_2_line_46 |  | 38 | 39 | 0.0080919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1065-4_1_2_line_47 |  | 38 | 40 | 0.0079401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1065-4_1_2_line_48 |  | 39 | 63 | 0.020726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1065-4_1_2_line_49 |  | 40 | 54 | 0.004489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1065-4_1_2_line_50 |  | 41 | 54 | 0.006327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1065-4_1_2_line_51 |  | 41 | 56 | 0.021534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1065-4_1_2_line_52 |  | 42 | 43 | 0.01124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1065-4_1_2_line_53 |  | 42 | 44 | 0.0038656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1065-4_1_2_line_54 |  | 43 | 64 | 0.018883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1065-4_1_2_line_55 |  | 43 | 65 | 0.0096569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1065-4_1_2_line_56 |  | 44 | 53 | 0.032691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1065-4_1_2_line_57 |  | 45 | 66 | 0.0029391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1065-4_1_2_line_58 |  | 48 | 49 | 0.044685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1065-4_1_2_line_59 |  | 48 | 50 | 0.0090606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1065-4_1_2_line_60 |  | 49 | 67 | 0.056629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1065-4_1_2_line_61 |  | 50 | 68 | 0.02211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1065-4_1_2_line_62 |  | 51 | 52 | 0.02174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1065-4_1_2_line_63 |  | 51 | 53 | 0.027193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1065-4_1_2_line_64 |  | 53 | 69 | 0.009602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1065-4_1_2_line_65 |  | 54 | 55 | 0.010038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1065-4_1_2_line_66 |  | 55 | 70 | 0.0056541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1065-4_1_2_line_67 |  | 56 | 57 | 0.053974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1065-4_1_2_line_68 |  | 56 | 58 | 0.021318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1065-4_1_2_line_69 |  | 58 | 71 | 0.0055527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1065-4_1_2_line_70 |  | 58 | 72 | 0.015506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1065-4_1_2_line_71 |  | 59 | 73 | 0.0065096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1065-4_1_2_line_72 |  | 60 | 74 | 0.0026839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1065-4_1_2_line_73 |  | 61 | 68 | 0.010148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1065-4_1_2_line_74 |  | 63 | 64 | 0.0028126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1065-4_1_2_line_75 |  | 65 | 78 | 0.006162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1065-4_1_2_line_76 |  | 66 | 101 | 0.012629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1065-4_1_2_line_77 |  | 67 | 81 | 0.25158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1065-4_1_2_line_78 |  | 69 | 80 | 0.0076274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1065-4_1_2_line_79 |  | 70 | 82 | 0.00051088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1065-4_1_2_line_80 |  | 72 | 83 | 0.01622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1065-4_1_2_line_81 |  | 73 | 77 | 0.024919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1065-4_1_2_line_82 |  | 74 | 106 | 0.0036538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1065-4_1_2_line_83 |  | 75 | 76 | 0.012585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1065-4_1_2_line_84 |  | 76 | 102 | 0.024497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_1065-4_1_2_line_85 |  | 76 | 104 | 0.033891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_1065-4_1_2_line_86 |  | 77 | 98 | 0.014357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1065-4_1_2_line_87 |  | 81 | 99 | 0.066471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1065-4_1_2_line_88 |  | 84 | 85 | 0.012732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1065-4_1_2_line_89 |  | 84 | 86 | 0.039611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1065-4_1_2_line_90 |  | 85 | 87 | 0.0029789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1065-4_1_2_line_91 |  | 86 | 88 | 0.016907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1065-4_1_2_line_92 |  | 88 | 91 | 0.044261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1065-4_1_2_line_93 |  | 89 | 90 | 0.019166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1065-4_1_2_line_94 |  | 90 | 96 | 0.010215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1065-4_1_2_line_95 |  | 91 | 92 | 0.049236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1065-4_1_2_line_96 |  | 92 | 93 | 0.010895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1065-4_1_2_line_97 |  | 92 | 94 | 0.029353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1065-4_1_2_line_98 |  | 93 | 95 | 0.019529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1065-4_1_2_line_99 |  | 94 | 96 | 0.0052146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1065-4_1_2_line_100 |  | 95 | 97 | 0.0063719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1065-4_1_2_line_101 |  | 97 | 103 | 0.011972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1065-4_1_2_line_102 |  | 100 | 101 | 0.026625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_1065-4_1_2_line_103 |  | 101 | 102 | 0.021739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_1065-4_1_2_line_104 |  | 103 | 121 | 0.0058304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1065-4_1_2_line_105 |  | 104 | 105 | 0.001354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
106 | LV_1065-4_1_2_line_106 |  | 105 | 107 | 0.023533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_1065-4_1_2_line_107 |  | 106 | 108 | 0.021682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1065-4_1_2_line_108 |  | 107 | 109 | 0.0046839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1065-4_1_2_line_109 |  | 108 | 125 | 0.0045116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1065-4_1_2_line_110 |  | 109 | 122 | 0.023636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1065-4_1_2_line_111 |  | 110 | 111 | 0.0076254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1065-4_1_2_line_112 |  | 110 | 112 | 0.017259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1065-4_1_2_line_113 |  | 112 | 113 | 0.017223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1065-4_1_2_line_114 |  | 112 | 114 | 0.016109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1065-4_1_2_line_115 |  | 113 | 115 | 0.01429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1065-4_1_2_line_116 |  | 114 | 116 | 0.0033575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1065-4_1_2_line_117 |  | 115 | 117 | 0.011167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1065-4_1_2_line_118 |  | 116 | 118 | 0.020219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1065-4_1_2_line_119 |  | 117 | 119 | 0.0088885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1065-4_1_2_line_120 |  | 118 | 120 | 0.0014146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1065-4_1_2_line_121 |  | 119 | 121 | 0.019745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1065-4_1_2_line_122 |  | 119 | 122 | 0.01217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1065-4_1_2_line_123 |  | 120 | 123 | 0.012639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1065-4_1_2_line_124 |  | 123 | 124 | 0.0092199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1065-4_1_2_line_125 |  | 124 | 125 | 0.0019523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1065-4_1_2_line_126 |  | 126 | 127 | 0.0047073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1065-4_1_2_trafo_127 | 0.63 MVA 20/0.4 kV | 128 | 100 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2671963.2629 | 1218404.0386 | 2671960.6564 | 1218400.5271 | 2671948.454 | 1218385.2255
1 | 2671948.454 | 1218385.2255 | 2671925.4273 | 1218393.757
2 | 2671963.2629 | 1218404.0386 | 2671984.3964 | 1218389.0422
3 | 2671963.2629 | 1218404.0386 | 2671973.8911 | 1218418.3317
4 | 2671884.0688 | 1218414.5341 | 2671894.489 | 1218424.0659 | 2671904.4724 | 1218414.4469 | 2671897.7383 | 1218407.6613 | 2671905.5593 | 1218401.1181 | 2671925.4273 | 1218393.757
5 | 2672026.8442 | 1218389.1527 | 2672062.3861 | 1218440.8599 | 2672066.659 | 1218447.7938 | 2672069.8726 | 1218454.4481 | 2672071.4491 | 1218459.6594 | 2672071.5015 | 1218464.1073 | 2672069.0053 | 1218469.047 | 2672043.8994 | 1218498.9738 | 2672039.7698 | 1218506.5509
6 | 2672026.8442 | 1218389.1527 | 2672020.9564 | 1218380.1758 | 2672012.2378 | 1218369.2856
7 | 2672012.2378 | 1218369.2856 | 2671984.3964 | 1218389.0422
8 | 2672147.5246 | 1218554.3295 | 2672129.5966 | 1218569.4 | 2672119.3723 | 1218576.3362 | 2672113.4796 | 1218578.4552 | 2672103.7038 | 1218579.0706 | 2672096.5863 | 1218581.4194 | 2672081.5358 | 1218587.8163
9 | 2672152.0099 | 1218562.5113 | 2672147.5246 | 1218554.3295
10 | 2672040.638 | 1218523.8837 | 2672041.643 | 1218516.0908 | 2672043.5689 | 1218508.0978 | 2672050.452 | 1218497.5298 | 2672058.2001 | 1218488.8624 | 2672071.2683 | 1218475.2227 | 2672075.7962 | 1218470.4856 | 2672077.9104 | 1218468.2653 | 2672080.1375 | 1218469.8821 | 2672082.8168 | 1218470.5149 | 2672085.5318 | 1218470.0697 | 2672087.8644 | 1218468.6192 | 2672090.8479 | 1218472.3355 | 2672091.8274 | 1218473.5592 | 2672125.2785 | 1218519.2044 | 2672126.6971 | 1218521.145 | 2672140.7507 | 1218542.7178 | 2672147.5246 | 1218554.3295
11 | 2672077.9175 | 1218589.3542 | 2672081.5358 | 1218587.8163
12 | 2672152.0099 | 1218562.5113 | 2672139.7433 | 1218578.8955 | 2672131.4503 | 1218588.0566 | 2672117.0438 | 1218596.8879 | 2672107.8103 | 1218602.8689 | 2672103.0076 | 1218605.8572 | 2672088.6527 | 1218613.3087
13 | 2672040.638 | 1218523.8837 | 2672049.9086 | 1218531.7786 | 2672053.5815 | 1218538.2831
14 | 2672040.638 | 1218523.8837 | 2672040.6059 | 1218530.2985 | 2672042.211 | 1218539.4126 | 2672045.8921 | 1218550.72 | 2672052.079 | 1218564.4369 | 2672057.6143 | 1218581.1924 | 2672058.7796 | 1218589.6452 | 2672059.0291 | 1218597.2531 | 2672059.3066 | 1218608.1968 | 2672059.2026 | 1218619.9253 | 2672058.4072 | 1218636.7376 | 2672056.803 | 1218651.8016
15 | 2672056.803 | 1218651.8016 | 2672056.6347 | 1218653.3824 | 2672055.6265 | 1218657.7896
16 | 2672156.4192 | 1218701.6318 | 2672153.6152 | 1218693.1369 | 2672146.5967 | 1218689.2049 | 2672134.6912 | 1218690.2059 | 2672120.1475 | 1218666.6025
17 | 2672156.4192 | 1218701.6318 | 2672153.5953 | 1218702.2981
18 | 2672153.5953 | 1218702.2981 | 2672153.0788 | 1218714.2328 | 2672155.8084 | 1218720.0311
19 | 2672153.5953 | 1218702.2981 | 2672146.3287 | 1218705.6901 | 2672140.7132 | 1218706.2336 | 2672138.3256 | 1218704.7148 | 2672137.1924 | 1218701.777 | 2672138.0082 | 1218698.9628 | 2672140.4438 | 1218697.1467 | 2672143.7933 | 1218697.5764 | 2672146.647 | 1218700.0903 | 2672147.8075 | 1218704.5406 | 2672146.6909 | 1218708.374 | 2672144.1102 | 1218711.5114 | 2672140.0529 | 1218714.3752 | 2672131.9202 | 1218717.212 | 2672121.8733 | 1218718.9248 | 2672113.5267 | 1218719.3685 | 2672103.3808 | 1218717.9782
20 | 2671973.8911 | 1218418.3317 | 2671984.4706 | 1218434.2132
21 | 2671984.4706 | 1218434.2132 | 2671996.5708 | 1218452.3776
22 | 2671865.769 | 1218425.8429 | 2671869.9575 | 1218423.4363 | 2671884.0688 | 1218414.5341
23 | 2672053.9358 | 1218665.1805 | 2672055.6265 | 1218657.7896
24 | 2671850.2137 | 1218700.4094 | 2671834.0151 | 1218698.851
25 | 2671792.1668 | 1218693.4609 | 2671808.9879 | 1218696.4433 | 2671834.0151 | 1218698.851
26 | 2671850.2137 | 1218700.4094 | 2671850.3034 | 1218699.2653 | 2671851.6438 | 1218682.0917
27 | 2671850.2137 | 1218700.4094 | 2671886.5312 | 1218703.83
28 | 2671792.1668 | 1218693.4609 | 2671792.2517 | 1218692.717 | 2671793.656 | 1218680.2352
29 | 2671772.7165 | 1218701.4429 | 2671773.3542 | 1218695.758 | 2671791.6185 | 1218697.3902 | 2671792.1668 | 1218693.4609
30 | 2671853.3273 | 1218663.7789 | 2671852.4491 | 1218671.7735 | 2671851.6438 | 1218682.0917
31 | 2671792.2556 | 1218668.0784 | 2671792.5121 | 1218668.5936 | 2671793.5722 | 1218671.3192 | 2671793.9122 | 1218673.9694 | 2671793.9518 | 1218677.6056 | 2671793.656 | 1218680.2352
32 | 2671612.8441 | 1218618.7444 | 2671627.3105 | 1218623.1656 | 2671649.858 | 1218632.8094 | 2671681.9137 | 1218652.7077 | 2671712.8446 | 1218672.7148 | 2671735.992 | 1218686.0909 | 2671749.8767 | 1218691.5282 | 2671760.1249 | 1218693.8864 | 2671773.3542 | 1218695.758 | 2671772.7165 | 1218701.4429
33 | 2671772.7165 | 1218701.4429 | 2671757.3839 | 1218699.0123 | 2671746.2829 | 1218695.6209 | 2671736.0092 | 1218691.5946 | 2671641.7714 | 1218634.9803 | 2671631.2133 | 1218629.9724 | 2671609.5358 | 1218623.0853 | 2671486.6916 | 1218587.7545 | 2671461.9104 | 1218582.0537 | 2671421.1862 | 1218577.318 | 2671409.9074 | 1218574.1586 | 2671407.3698 | 1218573.2638
34 | 2671853.3273 | 1218663.7789 | 2671853.9308 | 1218653.4874
35 | 2672005.5063 | 1218708.8557 | 2672004.7486 | 1218704.3547 | 2672016.9762 | 1218701.812 | 2672025.3674 | 1218698.9337 | 2672031.4543 | 1218695.8164 | 2672029 | 1218691.6508
36 | 2672005.5063 | 1218708.8557 | 2672005.775 | 1218710.4822 | 2672007.7771 | 1218722.3819
37 | 2672029 | 1218691.6508 | 2672033.3687 | 1218688.7684 | 2672038.3895 | 1218684.0482 | 2672041.6636 | 1218680.0519 | 2672043.2789 | 1218677.6477
38 | 2672029 | 1218691.6508 | 2672027.4546 | 1218692.6661 | 2672024.5452 | 1218694.1207 | 2672013.1279 | 1218698.6968 | 2672008.3902 | 1218699.7212
39 | 2672011.6448 | 1218746.6572 | 2672011.1566 | 1218742.4678 | 2672007.7771 | 1218722.3819
40 | 2671975.336 | 1218703.2543 | 2671955.7113 | 1218704.2958
41 | 2671975.336 | 1218703.2543 | 2671990.6698 | 1218702.439 | 2672002.2688 | 1218701.0449 | 2672008.3902 | 1218699.7212
42 | 2671955.7113 | 1218704.2958 | 2671955.7689 | 1218703.2958 | 2671956.9631 | 1218682.975 | 2671956.9697 | 1218682.8705
43 | 2671955.7113 | 1218704.2958 | 2671933.2358 | 1218705.7143 | 2671927.7185 | 1218705.7602
44 | 2671612.8441 | 1218618.7444 | 2671610.2211 | 1218612.798 | 2671603.1334 | 1218603.8515 | 2671589.5489 | 1218591.725 | 2671572.5713 | 1218580.8919 | 2671542.086 | 1218564.7823 | 2671515.8722 | 1218543.1204 | 2671497.5455 | 1218525.7783 | 2671476.8166 | 1218516.9574 | 2671450.81 | 1218502.0248 | 2671428.7237 | 1218477.0926
45 | 2671288.2571 | 1218578.3891 | 2671306.0453 | 1218556.4593 | 2671311.6597 | 1218550.3003 | 2671316.5739 | 1218547.4795 | 2671321.9958 | 1218544.7204 | 2671329.3069 | 1218543.2959 | 2671334.4335 | 1218543.6575 | 2671345.4192 | 1218547.2135 | 2671393 | 1218568.1967 | 2671407.3698 | 1218573.2638
46 | 2672053.3018 | 1218690.4771 | 2672056.432 | 1218694.6065 | 2672058.4586 | 1218696.695
47 | 2672053.3018 | 1218690.4771 | 2672052.4435 | 1218685.508 | 2672052.888 | 1218682.6448
48 | 2672058.4586 | 1218696.695 | 2672067.1743 | 1218705.6768 | 2672072.2439 | 1218712.1353
49 | 2672048.9056 | 1218680.5731 | 2672052.888 | 1218682.6448
50 | 2672048.9056 | 1218680.5731 | 2672043.2789 | 1218677.6477
51 | 2672034.0027 | 1218663.3264 | 2672035.9097 | 1218670.6986 | 2672039.7462 | 1218676.0484 | 2672041.6636 | 1218680.0519 | 2672043.2789 | 1218677.6477
52 | 2672079.1667 | 1218729.4705 | 2672088.7261 | 1218723.5156
53 | 2672079.1667 | 1218729.4705 | 2672081.5179 | 1218732.5389
54 | 2672088.7261 | 1218723.5156 | 2672087.316 | 1218720.8746 | 2672085.4667 | 1218721.2858 | 2672082.7518 | 1218721.0973 | 2672079.6106 | 1218719.7585 | 2672075.8972 | 1218716.7894 | 2672073.9805 | 1218714.3477
55 | 2672088.7261 | 1218723.5156 | 2672091.1809 | 1218721.9888 | 2672097.2027 | 1218719.2265 | 2672097.3408 | 1218719.1986
56 | 2672089.7346 | 1218763.0977 | 2672089.7215 | 1218752.891 | 2672086.9747 | 1218739.6603 | 2672081.5179 | 1218732.5389
57 | 2671956.9697 | 1218682.8705 | 2671957.1531 | 1218679.9371
58 | 2672021.8212 | 1218785.0685 | 2672014.0357 | 1218800.6288 | 2672010.3543 | 1218827.6654
59 | 2672021.8212 | 1218785.0685 | 2672015.3786 | 1218778.6976
60 | 2672003.9513 | 1218883.9272 | 2672008.7383 | 1218839.5343 | 2672010.3543 | 1218827.6654
61 | 2672012.8194 | 1218756.7366 | 2672015.3786 | 1218778.6976 | 2672015.3786 | 1218778.6976
62 | 2672062.6288 | 1218762.6918 | 2672064.5928 | 1218775.3793 | 2672067.5765 | 1218783.7653
63 | 2672089.7346 | 1218763.0977 | 2672080.7361 | 1218764.1006 | 2672071.0824 | 1218764.0616 | 2672062.6288 | 1218762.6918
64 | 2672092.3328 | 1218772.2906 | 2672090.4925 | 1218767.5764 | 2672089.7346 | 1218763.0977
65 | 2672048.9056 | 1218680.5731 | 2672051.0863 | 1218674.7291 | 2672052.186 | 1218671.0908
66 | 2672053.8219 | 1218665.6786 | 2672053.8219 | 1218665.6786 | 2672052.186 | 1218671.0908
67 | 2672034.0027 | 1218663.3264 | 2672024.912 | 1218664.4172 | 2672023.8072 | 1218657.2437 | 2672023.1639 | 1218648.2968 | 2672018.5312 | 1218644.1382 | 2672014.7735 | 1218622.0918
68 | 2672034.0027 | 1218663.3264 | 2672033.0366 | 1218658.4893 | 2672033.2102 | 1218648.5295 | 2672034.7202 | 1218642.2882
69 | 2672034.7202 | 1218642.2882 | 2672039.455 | 1218639.3876
70 | 2672034.7202 | 1218642.2882 | 2672032.553 | 1218626.9344
71 | 2671792.2556 | 1218668.0784 | 2671791.6154 | 1218666.7927 | 2671789.6798 | 1218664.29 | 2671788.2856 | 1218662.9852
72 | 2671854.0879 | 1218650.8081 | 2671853.9308 | 1218653.4874
73 | 2672011.6448 | 1218746.6572 | 2672012.8194 | 1218756.7366
74 | 2672072.2439 | 1218712.1353 | 2672073.9805 | 1218714.3477
75 | 2672103.3808 | 1218717.9782 | 2672103.3808 | 1218717.9782 | 2672097.3408 | 1218719.1986
76 | 2671957.9415 | 1218667.3323 | 2671957.1531 | 1218679.9371
77 | 2672003.9513 | 1218883.9272 | 2672001.7627 | 1218902.3681 | 2671997.0632 | 1218903.123 | 2671989.7009 | 1218901.8999 | 2671982.1947 | 1218900.6529 | 2671960.7314 | 1218892.4773 | 2671939.3944 | 1218882.6356 | 2671908.7504 | 1218862.286 | 2671865.2567 | 1218838.1681 | 2671840.1863 | 1218826.3583 | 2671823.9531 | 1218818.7132 | 2671820.5995 | 1218820.5073 | 2671810.097 | 1218838.6257 | 2671807.7056 | 1218848.1252
78 | 2672092.3328 | 1218772.2906 | 2672087.583 | 1218774.0565 | 2672089.2324 | 1218776.0143
79 | 2672053.9358 | 1218665.1805 | 2672053.8219 | 1218665.6786
80 | 2672032.553 | 1218626.9344 | 2672030.2861 | 1218610.8732
81 | 2671764.483 | 1218657.0102 | 2671786.31 | 1218661.1363 | 2671788.2856 | 1218662.9852
82 | 2671854.0879 | 1218650.8081 | 2671854.3018 | 1218647.1606
83 | 2671913.124 | 1218659.7198 | 2671904.7002 | 1218664.032 | 2671901.5826 | 1218664.1969
84 | 2671913.124 | 1218659.7198 | 2671924.7653 | 1218665.5084 | 2671930.8201 | 1218665.6705 | 2671936.2545 | 1218665.8958
85 | 2671913.124 | 1218659.7198 | 2671916.9647 | 1218653.4176 | 2671919.8314 | 1218634.1176 | 2671919.9085 | 1218627.1192
86 | 2671750.3756 | 1218654.3434 | 2671764.483 | 1218657.0102
87 | 2671807.7056 | 1218848.1252 | 2671768.6356 | 1218842.3287 | 2671741.6682 | 1218841.7516
88 | 2671865.769 | 1218425.8429 | 2671854.8891 | 1218432.455
89 | 2671865.769 | 1218425.8429 | 2671869.1967 | 1218426.0955 | 2671873.1449 | 1218427.8776 | 2671878.4808 | 1218432.9119 | 2671885.1258 | 1218439.5296 | 2671895.8834 | 1218450.1662
90 | 2671852.3434 | 1218434.0021 | 2671854.8891 | 1218432.455
91 | 2671907.9624 | 1218461.9947 | 2671906.0376 | 1218460.2062 | 2671895.8834 | 1218450.1662
92 | 2671907.9624 | 1218461.9947 | 2671933.9447 | 1218486.1374 | 2671939.2163 | 1218493.1757
93 | 2671965.8852 | 1218581.5176 | 2671975.365 | 1218580.2646 | 2671984.9112 | 1218581.3148
94 | 2671965.8852 | 1218581.5176 | 2671965.4758 | 1218571.3106
95 | 2671960.0595 | 1218537.2521 | 2671958.9963 | 1218532.9032 | 2671953.168 | 1218515.2437 | 2671945.4405 | 1218501.486 | 2671939.2163 | 1218493.1757
96 | 2671960.0595 | 1218537.2521 | 2671951.9435 | 1218544.5199
97 | 2671960.0595 | 1218537.2521 | 2671962.938 | 1218549.0389 | 2671965.2669 | 1218566.1002
98 | 2671937.5877 | 1218550.2559 | 2671937.5877 | 1218550.2559 | 2671941.3526 | 1218554.0037 | 2671951.9435 | 1218544.5199
99 | 2671965.4758 | 1218571.3106 | 2671965.2669 | 1218566.1002
100 | 2671937.5877 | 1218550.2559 | 2671936.6182 | 1218553.8576 | 2671934.5491 | 1218555.5003
101 | 2671922.5998 | 1218554.8062 | 2671927.2238 | 1218554.9449 | 2671934.5491 | 1218555.5003 | 2671934.5491 | 1218555.5003
102 | 2671957.9415 | 1218667.3323 | 2671959.2404 | 1218646.5124 | 2671959.8267 | 1218640.7778
103 | 2671957.9415 | 1218667.3323 | 2671947.0309 | 1218666.4 | 2671939.9006 | 1218666.047 | 2671936.2545 | 1218665.8958
104 | 2671916.772 | 1218554.6314 | 2671922.5998 | 1218554.8062
105 | 2671919.9085 | 1218627.1192 | 2671919.9234 | 1218625.7652
106 | 2671916.9464 | 1218602.4965 | 2671919.9883 | 1218619.8659 | 2671919.9234 | 1218625.7652
107 | 2671855.5711 | 1218625.5153 | 2671854.3018 | 1218647.1606
108 | 2671916.9464 | 1218602.4965 | 2671916.9209 | 1218602.351 | 2671915.5386 | 1218598.0306
109 | 2671855.5711 | 1218625.5153 | 2671855.8352 | 1218621.0115
110 | 2671908.3357 | 1218575.5192 | 2671915.5386 | 1218598.0306
111 | 2671839.0465 | 1218537.6763 | 2671844.5817 | 1218542.9211
112 | 2671855.5051 | 1218556.2362 | 2671847.2408 | 1218545.4407 | 2671844.5817 | 1218542.9211
113 | 2671855.5051 | 1218556.2362 | 2671860.4501 | 1218552.7713 | 2671871.629 | 1218552.4152
114 | 2671855.5051 | 1218556.2362 | 2671857.248 | 1218572.2504
115 | 2671885.524 | 1218554.3832 | 2671879.4325 | 1218552.1665 | 2671871.629 | 1218552.4152
116 | 2671857.248 | 1218572.2504 | 2671857.4183 | 1218573.815 | 2671857.3745 | 1218575.598
117 | 2671895.4053 | 1218559.2324 | 2671892.9895 | 1218557.0999 | 2671885.524 | 1218554.3832
118 | 2671856.8788 | 1218595.8109 | 2671857.3745 | 1218575.598
119 | 2671902.0691 | 1218565.1146 | 2671895.4053 | 1218559.2324
120 | 2671856.8788 | 1218595.8109 | 2671856.8441 | 1218597.225
121 | 2671902.0691 | 1218565.1146 | 2671907.4489 | 1218561.466 | 2671911.7154 | 1218554.4797 | 2671916.772 | 1218554.6314
122 | 2671902.0691 | 1218565.1146 | 2671908.0856 | 1218574.7378 | 2671908.3357 | 1218575.5192
123 | 2671856.4893 | 1218609.8584 | 2671856.5667 | 1218608.5381 | 2671856.8441 | 1218597.225
124 | 2671856.4893 | 1218609.8584 | 2671855.9495 | 1218619.0625
125 | 2671855.9495 | 1218619.0625 | 2671855.8352 | 1218621.0115
126 | 2671999.1806 | 1218456.2953 | 2671996.5708 | 1218452.3776

## bus_geodata
| x | y | coords
0 | 2671948.454 | 1218385.2255
1 | 2671963.2629 | 1218404.0386
2 | 2671925.4273 | 1218393.757
3 | 2672026.8442 | 1218389.1527
4 | 2672039.7698 | 1218506.5509
5 | 2672012.2378 | 1218369.2856
6 | 2671984.3964 | 1218389.0422
7 | 2672147.5246 | 1218554.3295
8 | 2672081.5358 | 1218587.8163
9 | 2672152.0099 | 1218562.5113
10 | 2672040.638 | 1218523.8837
11 | 2672088.6527 | 1218613.3087
12 | 2672053.5815 | 1218538.2831
13 | 2672056.803 | 1218651.8016
14 | 2672156.4192 | 1218701.6318
15 | 2672120.1475 | 1218666.6025
16 | 2672153.5953 | 1218702.2981
17 | 2671973.8911 | 1218418.3317
18 | 2671984.4706 | 1218434.2132
19 | 2671884.0688 | 1218414.5341
20 | 2672055.6265 | 1218657.7896
21 | 2672077.9175 | 1218589.3542
22 | 2671834.0151 | 1218698.851
23 | 2671850.2137 | 1218700.4094
24 | 2671792.1668 | 1218693.4609
25 | 2671851.6438 | 1218682.0917
26 | 2671886.5312 | 1218703.83
27 | 2671793.656 | 1218680.2352
28 | 2671772.7165 | 1218701.4429
29 | 2671853.3273 | 1218663.7789
30 | 2672005.5063 | 1218708.8557
31 | 2672029 | 1218691.6507
32 | 2672007.7771 | 1218722.3819
33 | 2671975.336 | 1218703.2543
34 | 2671955.7113 | 1218704.2958
35 | 2672008.3902 | 1218699.7212
36 | 2671612.8441 | 1218618.7444
37 | 2671407.3698 | 1218573.2638
38 | 2672053.3018 | 1218690.4771
39 | 2672058.4586 | 1218696.695
40 | 2672052.888 | 1218682.6448
41 | 2672043.2789 | 1218677.6477
42 | 2672079.1667 | 1218729.4705
43 | 2672088.7261 | 1218723.5156
44 | 2672081.5179 | 1218732.5389
45 | 2671956.9697 | 1218682.8705
46 | 2671927.7185 | 1218705.7602
47 | 2671428.7237 | 1218477.0926
48 | 2672021.8212 | 1218785.0685
49 | 2672010.3543 | 1218827.6654
50 | 2672015.3786 | 1218778.6976
51 | 2672062.6288 | 1218762.6918
52 | 2672067.5765 | 1218783.7653
53 | 2672089.7346 | 1218763.0977
54 | 2672048.9056 | 1218680.5731
55 | 2672052.186 | 1218671.0908
56 | 2672034.0027 | 1218663.3264
57 | 2672014.7735 | 1218622.0918
58 | 2672034.7202 | 1218642.2882
59 | 2671792.2556 | 1218668.0784
60 | 2671853.9308 | 1218653.4874
61 | 2672011.6448 | 1218746.6572
62 | 2671288.2571 | 1218578.3891
63 | 2672072.2439 | 1218712.1353
64 | 2672073.9805 | 1218714.3477
65 | 2672097.3408 | 1218719.1986
66 | 2671957.1531 | 1218679.9371
67 | 2672003.9513 | 1218883.9272
68 | 2672012.8194 | 1218756.7366
69 | 2672092.3328 | 1218772.2906
70 | 2672053.8219 | 1218665.6786
71 | 2672039.455 | 1218639.3876
72 | 2672032.553 | 1218626.9344
73 | 2671788.2856 | 1218662.9852
74 | 2671854.0879 | 1218650.8081
75 | 2671901.5826 | 1218664.1969
76 | 2671913.124 | 1218659.7198
77 | 2671764.483 | 1218657.0102
78 | 2672103.3808 | 1218717.9782
79 | 2672155.8084 | 1218720.0311
80 | 2672089.2324 | 1218776.0143
81 | 2671807.7056 | 1218848.1252
82 | 2672053.9358 | 1218665.1805
83 | 2672030.2861 | 1218610.8732
84 | 2671865.769 | 1218425.8429
85 | 2671854.8891 | 1218432.455
86 | 2671895.8834 | 1218450.1662
87 | 2671852.3434 | 1218434.0021
88 | 2671907.9624 | 1218461.9947
89 | 2671984.9112 | 1218581.3148
90 | 2671965.8852 | 1218581.5176
91 | 2671939.2163 | 1218493.1757
92 | 2671960.0595 | 1218537.2521
93 | 2671951.9435 | 1218544.5199
94 | 2671965.2669 | 1218566.1002
95 | 2671937.5877 | 1218550.2559
96 | 2671965.4758 | 1218571.3106
97 | 2671934.5491 | 1218555.5003
98 | 2671750.3756 | 1218654.3434
99 | 2671741.6682 | 1218841.7516
100 | 2671959.8267 | 1218640.7778
101 | 2671957.9415 | 1218667.3323
102 | 2671936.2545 | 1218665.8958
103 | 2671922.5998 | 1218554.8062
104 | 2671919.9085 | 1218627.1192
105 | 2671919.9234 | 1218625.7652
106 | 2671854.3018 | 1218647.1606
107 | 2671916.9464 | 1218602.4965
108 | 2671855.5711 | 1218625.5153
109 | 2671915.5386 | 1218598.0306
110 | 2671844.5817 | 1218542.9211
111 | 2671839.0465 | 1218537.6763
112 | 2671855.5051 | 1218556.2362
113 | 2671871.629 | 1218552.4152
114 | 2671857.248 | 1218572.2504
115 | 2671885.524 | 1218554.3832
116 | 2671857.3745 | 1218575.598
117 | 2671895.4053 | 1218559.2324
118 | 2671856.8788 | 1218595.8109
119 | 2671902.0691 | 1218565.1146
120 | 2671856.8441 | 1218597.225
121 | 2671916.772 | 1218554.6314
122 | 2671908.3357 | 1218575.5192
123 | 2671856.4893 | 1218609.8584
124 | 2671855.9495 | 1218619.0625
125 | 2671855.8352 | 1218621.0115
126 | 2671996.5708 | 1218452.3776
127 | 2671999.1806 | 1218456.2953
128 | 2671957.9415 | 1218667.3323

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97296 | -0.52203 | 0 | 0
1 | 0.97242 | -0.53275 | 0.0042027 | 0.0010533
2 | 0.97352 | -0.51103 | 0.0019699 | 0.0004937
3 | 0.97185 | -0.54398 | 0 | 0
4 | 0.97097 | -0.56141 | 0.0066729 | 0.0016724
5 | 0.972 | -0.54094 | 0 | 0
6 | 0.97222 | -0.53674 | 0.0016628 | 0.00041674
7 | 0.97743 | -0.43537 | 0 | 0
8 | 0.97667 | -0.45039 | 0.0044886 | 0.0011249
9 | 0.97741 | -0.43594 | 0 | 0
10 | 0.97986 | -0.38774 | 0 | 0
11 | 0.97715 | -0.44095 | 0.0033223 | 0.00083265
12 | 0.97967 | -0.39147 | 0.010438 | 0.0026159
13 | 0.98285 | -0.3293 | 0.0025254 | 0.00063292
14 | 0.98245 | -0.33732 | 0 | 0
15 | 0.9823 | -0.34025 | 0.0028624 | 0.00071738
16 | 0.98246 | -0.33717 | 0 | 0
17 | 0.97222 | -0.53662 | 0 | 0
18 | 0.97201 | -0.54077 | 0.0044588 | 0.0011175
19 | 0.97521 | -0.47774 | 0 | 0
20 | 0.98301 | -0.3263 | 0.0025242 | 0.00063261
21 | 0.97665 | -0.45085 | 0.0063783 | 0.0015986
22 | 0.98153 | -0.35479 | 0.0014161 | 0.0003549
23 | 0.98171 | -0.35139 | 0 | 0
24 | 0.98114 | -0.36253 | 0 | 0
25 | 0.98194 | -0.34691 | 0.0017021 | 0.00042658
26 | 0.98164 | -0.35268 | 0.0019538 | 0.00048968
27 | 0.98103 | -0.36462 | 0.0015102 | 0.0003785
28 | 0.9811 | -0.36326 | 0 | 0
29 | 0.98219 | -0.34186 | 0 | 0
30 | 0.98461 | -0.29519 | 0 | 0
31 | 0.98548 | -0.27825 | 0 | 0
32 | 0.98429 | -0.30137 | 0.0030657 | 0.00076833
33 | 0.99083 | -0.17465 | 0 | 0
34 | 0.99279 | -0.13718 | 0 | 0
35 | 0.98752 | -0.23866 | 0.008578 | 0.0021499
36 | 0.9811 | -0.36338 | 0 | 0
37 | 0.98061 | -0.37311 | 0.0012413 | 0.0003111
38 | 0.98356 | -0.31564 | 0 | 0
39 | 0.98343 | -0.31811 | 0.0025246 | 0.00063271
40 | 0.98368 | -0.31322 | 0.0025237 | 0.00063251
41 | 0.98409 | -0.30518 | 0 | 0
42 | 0.98282 | -0.33007 | 0 | 0
43 | 0.98289 | -0.32866 | 0 | 0
44 | 0.98279 | -0.33056 | 0.0034702 | 0.00086971
45 | 0.99501 | -0.094646 | 0.0047203 | 0.001183
46 | 0.99267 | -0.13937 | 0.0044155 | 0.0011066
47 | 0.98109 | -0.36351 | 2.6776e-05 | 6.7107e-06
48 | 0.98323 | -0.32207 | 0 | 0
49 | 0.983 | -0.32655 | 0.0041925 | 0.0010507
50 | 0.98328 | -0.32116 | 0.010331 | 0.0025893
51 | 0.98263 | -0.33382 | 0 | 0
52 | 0.98258 | -0.33478 | 0.0024509 | 0.00061426
53 | 0.98269 | -0.33262 | 0 | 0
54 | 0.98376 | -0.31165 | 0 | 0
55 | 0.98341 | -0.3184 | 0.0025266 | 0.00063323
56 | 0.98375 | -0.31196 | 0 | 0
57 | 0.98333 | -0.32012 | 0.0083917 | 0.0021032
58 | 0.98357 | -0.31545 | 0 | 0
59 | 0.98095 | -0.36624 | 0.00063225 | 0.00015846
60 | 0.98234 | -0.33903 | 0.00063461 | 0.00015905
61 | 0.98379 | -0.31111 | 0.0016919 | 0.00042404
62 | 0.98059 | -0.37347 | 0.00013857 | 3.473e-05
63 | 0.98316 | -0.32349 | 0.00063423 | 0.00015895
64 | 0.98312 | -0.32419 | 0.00063409 | 0.00015892
65 | 0.98284 | -0.32973 | 0.00063469 | 0.00015907
66 | 0.99533 | -0.088591 | 0.0065891 | 0.0016514
67 | 0.98293 | -0.32795 | 0 | 0
68 | 0.9836 | -0.31483 | 0.0044297 | 0.0011102
69 | 0.98268 | -0.3328 | 0 | 0
70 | 0.98323 | -0.32195 | 0.0027704 | 0.00069433
71 | 0.98356 | -0.31563 | 0.0017554 | 0.00043996
72 | 0.98346 | -0.3175 | 0.0036632 | 0.00091807
73 | 0.98091 | -0.36701 | 0.0028962 | 0.00072585
74 | 0.98238 | -0.33826 | 0.00071291 | 0.00017867
75 | 0.99384 | -0.11694 | 0.0039662 | 0.00099402
76 | 0.99388 | -0.11606 | 0 | 0
77 | 0.98083 | -0.36865 | 0.001832 | 0.00045915
78 | 0.98281 | -0.33035 | 0.0012202 | 0.00030581
79 | 0.98243 | -0.33764 | 0.0014381 | 0.00036042
80 | 0.98267 | -0.33294 | 0.001039 | 0.0002604
81 | 0.98262 | -0.33413 | 0 | 0
82 | 0.98322 | -0.32224 | 0.0023355 | 0.00058532
83 | 0.98341 | -0.31857 | 0.0036649 | 0.00091851
84 | 0.97574 | -0.4674 | 0 | 0
85 | 0.97565 | -0.46905 | 0.0051875 | 0.0013001
86 | 0.97697 | -0.44321 | 0.0029105 | 0.00072945
87 | 0.97565 | -0.46916 | 0.0019084 | 0.00047829
88 | 0.97754 | -0.432 | 0.0068825 | 0.0017249
89 | 0.98086 | -0.36719 | 0.0061677 | 0.0015458
90 | 0.98097 | -0.36505 | 0 | 0
91 | 0.97932 | -0.39719 | 0.0037043 | 0.00092839
92 | 0.98147 | -0.35531 | 0 | 0
93 | 0.98209 | -0.3432 | 0.0021874 | 0.00054821
94 | 0.98108 | -0.36306 | 0.0056251 | 0.0014098
95 | 0.98325 | -0.32075 | 0.0033878 | 0.00084907
96 | 0.98103 | -0.36391 | 0.0027928 | 0.00069994
97 | 0.98365 | -0.31305 | 0.0027232 | 0.00068249
98 | 0.9808 | -0.36912 | 0.0018098 | 0.00045357
99 | 0.98254 | -0.33575 | 0.0013549 | 0.00033957
100 | 1 | 0 | -0.26849 | -0.068478
101 | 0.99677 | -0.061158 | 0 | 0
102 | 0.99537 | -0.087716 | 0.0077543 | 0.0019434
103 | 0.98442 | -0.29801 | 0.0021235 | 0.0005322
104 | 0.99189 | -0.15421 | 0.0014683 | 0.000368
105 | 0.99181 | -0.15572 | 0.0043684 | 0.0010948
106 | 0.98243 | -0.33717 | 0.002421 | 0.00060675
107 | 0.99048 | -0.1811 | 0.0042235 | 0.0010585
108 | 0.98281 | -0.32975 | 0.00075704 | 0.00018973
109 | 0.98997 | -0.19086 | 0.0014319 | 0.00035886
110 | 0.98437 | -0.2992 | 0.0021849 | 0.0005476
111 | 0.98436 | -0.29946 | 0.0018693 | 0.00046848
112 | 0.98444 | -0.29794 | 0 | 0
113 | 0.98498 | -0.28736 | 0.0016796 | 0.00042095
114 | 0.98399 | -0.30668 | 0.0015504 | 0.00038858
115 | 0.98545 | -0.27815 | 0.0018793 | 0.00047099
116 | 0.9839 | -0.30841 | 0.0020327 | 0.00050944
117 | 0.98584 | -0.27059 | 0.0015504 | 0.00038857
118 | 0.98341 | -0.31808 | 0.0023051 | 0.00057772
119 | 0.98616 | -0.26432 | 0 | 0
120 | 0.98338 | -0.3187 | 0.0019934 | 0.0004996
121 | 0.98481 | -0.29047 | 0.0018673 | 0.00046799
122 | 0.98744 | -0.23969 | 0.0027739 | 0.0006952
123 | 0.98312 | -0.32377 | 0.00043827 | 0.00010984
124 | 0.98293 | -0.3274 | 0.0007647 | 0.00019165
125 | 0.98289 | -0.32814 | 0.0013306 | 0.00033347
126 | 0.97186 | -0.54372 | 0.005783 | 0.0014494
127 | 0.97186 | -0.54385 | 0.0015435 | 0.00038683
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.024351 | 0.0061098 | -0.024339 | -0.0061021 | 1.2443e-05 | 7.6664e-06 | 0.037244 | 0.037245 | 0.037245 | 0.97296 | -0.52203 | 0.97242 | -0.53275 | 10.232
1 | -0.024351 | -0.0061098 | 0.024364 | 0.0061176 | 1.2774e-05 | 7.87e-06 | 0.037244 | 0.037244 | 0.037244 | 0.97296 | -0.52203 | 0.97352 | -0.51103 | 10.232
2 | 0.0083452 | 0.0020924 | -0.0083436 | -0.0020917 | 1.5848e-06 | 6.9285e-07 | 0.01277 | 0.01277 | 0.01277 | 0.97242 | -0.53275 | 0.97222 | -0.53674 | 3.5084
3 | 0.011791 | 0.0029564 | -0.011789 | -0.0029553 | 2.1723e-06 | 1.1696e-06 | 0.018043 | 0.018043 | 0.018043 | 0.97242 | -0.53275 | 0.97222 | -0.53662 | 4.9569
4 | -0.026334 | -0.0066113 | 0.026376 | 0.0066373 | 4.1887e-05 | 2.5949e-05 | 0.040255 | 0.040255 | 0.040255 | 0.97352 | -0.51103 | 0.97521 | -0.47774 | 11.0591
5 | 0.0066785 | 0.0016742 | -0.0066729 | -0.0016724 | 5.5448e-06 | 1.7982e-06 | 0.010226 | 0.010226 | 0.010226 | 0.97185 | -0.54398 | 0.97097 | -0.56141 | 2.8094
6 | -0.0066785 | -0.0016742 | 0.0066795 | 0.0016745 | 9.6703e-07 | 3.1326e-07 | 0.010226 | 0.010226 | 0.010226 | 0.97185 | -0.54398 | 0.972 | -0.54094 | 2.8093
7 | -0.0066795 | -0.0016745 | 0.0066808 | 0.0016749 | 1.3386e-06 | 4.3346e-07 | 0.010226 | 0.010225 | 0.010226 | 0.972 | -0.54094 | 0.97222 | -0.53674 | 2.8092
8 | 0.010875 | 0.0027276 | -0.010867 | -0.0027235 | 7.7796e-06 | 4.0311e-06 | 0.016556 | 0.016557 | 0.016557 | 0.97743 | -0.43537 | 0.97667 | -0.45039 | 4.5485
9 | 0.0033232 | 0.00083206 | -0.0033231 | -0.00083212 | 8.9492e-08 | -5.96e-08 | 0.0050588 | 0.0050589 | 0.0050589 | 0.97743 | -0.43537 | 0.97741 | -0.43594 | 1.3898
10 | -0.014198 | -0.0035596 | 0.01423 | 0.003578 | 3.2297e-05 | 1.8354e-05 | 0.021615 | 0.021614 | 0.021615 | 0.97743 | -0.43537 | 0.97986 | -0.38774 | 5.9382
11 | 0.0063785 | 0.0015986 | -0.0063783 | -0.0015986 | 1.3924e-07 | 3.9911e-08 | 0.009718 | 0.009718 | 0.009718 | 0.97667 | -0.45039 | 0.97665 | -0.45085 | 2.6698
12 | 0.0033231 | 0.00083212 | -0.0033223 | -0.00083265 | 7.9233e-07 | -5.273e-07 | 0.0050589 | 0.0050592 | 0.0050592 | 0.97741 | -0.43594 | 0.97715 | -0.44095 | 1.3899
13 | 0.01044 | 0.0026169 | -0.010438 | -0.0026159 | 1.8517e-06 | 9.3768e-07 | 0.015854 | 0.015854 | 0.015854 | 0.97986 | -0.38774 | 0.97967 | -0.39147 | 4.3554
14 | -0.02467 | -0.0061949 | 0.024739 | 0.0062374 | 6.8992e-05 | 4.2499e-05 | 0.037468 | 0.037467 | 0.037468 | 0.97986 | -0.38774 | 0.98285 | -0.3293 | 10.2934
15 | -0.027264 | -0.0068703 | 0.027268 | 0.0068727 | 3.9069e-06 | 2.4229e-06 | 0.041291 | 0.041291 | 0.041291 | 0.98285 | -0.3293 | 0.98301 | -0.3263 | 11.3436
16 | 0.0028628 | 0.00071692 | -0.0028624 | -0.00071738 | 3.9947e-07 | -4.6173e-07 | 0.0043358 | 0.004336 | 0.004336 | 0.98245 | -0.33732 | 0.9823 | -0.34025 | 1.1912
17 | -0.0028628 | -0.00071692 | 0.0028628 | 0.0007169 | 2.0395e-08 | -2.3581e-08 | 0.0043358 | 0.0043358 | 0.0043358 | 0.98245 | -0.33732 | 0.98246 | -0.33717 | 1.1912
18 | 0.0014381 | 0.0003602 | -0.0014381 | -0.00036042 | 3.2654e-08 | -2.1152e-07 | 0.0021781 | 0.0021781 | 0.0021781 | 0.98246 | -0.33717 | 0.98243 | -0.33764 | 0.59839
19 | -0.0043009 | -0.0010771 | 0.0043023 | 0.0010769 | 1.3971e-06 | -2.1821e-07 | 0.0065138 | 0.0065134 | 0.0065138 | 0.98246 | -0.33717 | 0.98281 | -0.33035 | 1.7895
20 | 0.011789 | 0.0029553 | -0.011786 | -0.002954 | 2.3297e-06 | 1.2544e-06 | 0.018043 | 0.018043 | 0.018043 | 0.97222 | -0.53662 | 0.97201 | -0.54077 | 4.9569
21 | 0.0073275 | 0.0018365 | -0.0073265 | -0.0018361 | 1.0299e-06 | 3.8864e-07 | 0.011217 | 0.011218 | 0.011218 | 0.97201 | -0.54077 | 0.97186 | -0.54372 | 3.0817
22 | -0.026376 | -0.0066373 | 0.026389 | 0.0066454 | 1.3047e-05 | 8.0822e-06 | 0.040255 | 0.040255 | 0.040255 | 0.97521 | -0.47774 | 0.97574 | -0.4674 | 11.059
23 | -0.029792 | -0.0075053 | 0.029798 | 0.0075089 | 5.786e-06 | 3.6069e-06 | 0.045111 | 0.045111 | 0.045111 | 0.98301 | -0.3263 | 0.98322 | -0.32224 | 12.3933
24 | -0.01151 | -0.0028732 | 0.011511 | 0.0028742 | 1.8571e-06 | 9.828e-07 | 0.017445 | 0.017444 | 0.017445 | 0.98153 | -0.35479 | 0.98171 | -0.35139 | 4.7925
25 | 0.010093 | 0.0025183 | -0.01009 | -0.0025165 | 3.7057e-06 | 1.8382e-06 | 0.015298 | 0.015298 | 0.015298 | 0.98153 | -0.35479 | 0.98114 | -0.36253 | 4.2027
26 | -0.013465 | -0.0033635 | 0.013468 | 0.0033651 | 2.869e-06 | 1.6038e-06 | 0.020406 | 0.020406 | 0.020406 | 0.98171 | -0.35139 | 0.98194 | -0.34691 | 5.606
27 | 0.0019539 | 0.00048929 | -0.0019538 | -0.00048968 | 1.1998e-07 | -3.844e-07 | 0.0029615 | 0.0029617 | 0.0029617 | 0.98171 | -0.35139 | 0.98164 | -0.35268 | 0.81365
28 | 0.0086824 | 0.0021759 | -0.0086815 | -0.0021755 | 8.654e-07 | 3.8579e-07 | 0.013168 | 0.013168 | 0.013168 | 0.98114 | -0.36253 | 0.98103 | -0.36462 | 3.6176
29 | 0.0014074 | 0.00034061 | -0.0014073 | -0.00034094 | 4.769e-08 | -3.234e-07 | 0.0021302 | 0.0021303 | 0.0021303 | 0.98114 | -0.36253 | 0.9811 | -0.36326 | 0.58524
30 | -0.01517 | -0.0037917 | 0.015174 | 0.0037938 | 3.6439e-06 | 2.0994e-06 | 0.022985 | 0.022985 | 0.022985 | 0.98194 | -0.34691 | 0.98219 | -0.34186 | 6.3146
31 | 0.0071713 | 0.001797 | -0.0071708 | -0.0017968 | 5.5259e-07 | 1.9641e-07 | 0.010877 | 0.010877 | 0.010877 | 0.98103 | -0.36462 | 0.98095 | -0.36624 | 2.9883
32 | 2.6776e-05 | 1.3911e-06 | -2.6776e-05 | -3.733e-06 | 1.0891e-10 | -2.3419e-06 | 3.9445e-05 | 3.9773e-05 | 3.9773e-05 | 0.9811 | -0.36326 | 0.9811 | -0.36338 | 0.010927
33 | 0.0013805 | 0.00033954 | -0.0013799 | -0.00034407 | 6.4225e-07 | -4.5264e-06 | 0.0020915 | 0.0020933 | 0.0020933 | 0.9811 | -0.36326 | 0.98061 | -0.37311 | 0.57507
34 | -0.015174 | -0.0037938 | 0.015176 | 0.003795 | 2.0425e-06 | 1.1767e-06 | 0.022985 | 0.022985 | 0.022985 | 0.98219 | -0.34186 | 0.98234 | -0.33903 | 6.3146
35 | -0.025094 | -0.0062937 | 0.025114 | 0.0063062 | 2.028e-05 | 1.25e-05 | 0.037926 | 0.037925 | 0.037926 | 0.98461 | -0.29519 | 0.98548 | -0.27825 | 10.4191
36 | 0.025094 | 0.0062937 | -0.025087 | -0.0062892 | 7.3979e-06 | 4.5603e-06 | 0.037926 | 0.037926 | 0.037926 | 0.98461 | -0.29519 | 0.98429 | -0.30137 | 10.4191
37 | 0.074497 | 0.018767 | -0.074401 | -0.018706 | 9.5849e-05 | 6.1086e-05 | 0.11252 | 0.11252 | 0.11252 | 0.98548 | -0.27825 | 0.98409 | -0.30518 | 30.9123
38 | -0.099611 | -0.025073 | 0.0998 | 0.025194 | 0.00018885 | 0.00012058 | 0.15045 | 0.15045 | 0.15045 | 0.98548 | -0.27825 | 0.98752 | -0.23866 | 41.3313
39 | 0.022021 | 0.0055208 | -0.022011 | -0.0055146 | 1.0218e-05 | 6.2273e-06 | 0.033291 | 0.033291 | 0.033291 | 0.98429 | -0.30137 | 0.98379 | -0.31111 | 9.1459
40 | -0.10871 | -0.027556 | 0.10891 | 0.027682 | 0.00019612 | 0.00012527 | 0.16337 | 0.16337 | 0.16337 | 0.99083 | -0.17465 | 0.99279 | -0.13718 | 44.8822
41 | 0.10871 | 0.027556 | -0.10838 | -0.027343 | 0.0003333 | 0.00021289 | 0.16337 | 0.16337 | 0.16337 | 0.99083 | -0.17465 | 0.98752 | -0.23866 | 44.8823
42 | -0.11332 | -0.028788 | 0.11356 | 0.028937 | 0.00023257 | 0.00014857 | 0.16999 | 0.16999 | 0.16999 | 0.99279 | -0.13718 | 0.99501 | -0.094646 | 46.7005
43 | 0.0044159 | 0.0011066 | -0.0044155 | -0.0011066 | 4.606e-07 | -6.7723e-08 | 0.0066187 | 0.0066188 | 0.0066188 | 0.99279 | -0.13718 | 0.99267 | -0.13937 | 1.8183
44 | 2.6776e-05 | 3.733e-06 | -2.6776e-05 | -6.7107e-06 | 1.4243e-10 | -2.9776e-06 | 3.9773e-05 | 4.0611e-05 | 4.0611e-05 | 0.9811 | -0.36338 | 0.98109 | -0.36351 | 0.011157
45 | 0.00013858 | 3.2969e-05 | -0.00013857 | -3.473e-05 | 2.3095e-09 | -1.7608e-06 | 0.00020967 | 0.00021028 | 0.00021028 | 0.98061 | -0.37311 | 0.98059 | -0.37347 | 0.05777
46 | 0.016921 | 0.0042413 | -0.016919 | -0.0042401 | 1.9886e-06 | 1.17e-06 | 0.0256 | 0.0256 | 0.0256 | 0.98356 | -0.31564 | 0.98343 | -0.31811 | 7.0329
47 | -0.016921 | -0.0042413 | 0.016923 | 0.0042424 | 1.9513e-06 | 1.1481e-06 | 0.0256 | 0.0256 | 0.0256 | 0.98356 | -0.31564 | 0.98368 | -0.31322 | 7.0329
48 | 0.014394 | 0.0036074 | -0.014391 | -0.0036053 | 3.6869e-06 | 2.0967e-06 | 0.02178 | 0.02178 | 0.02178 | 0.98343 | -0.31811 | 0.98316 | -0.32349 | 5.9835
49 | -0.019447 | -0.0048749 | 0.019448 | 0.0048758 | 1.4568e-06 | 8.7534e-07 | 0.029417 | 0.029417 | 0.029417 | 0.98368 | -0.31322 | 0.98376 | -0.31165 | 8.0817
50 | 0.056915 | 0.01432 | -0.056897 | -0.014309 | 1.758e-05 | 1.1171e-05 | 0.086079 | 0.086079 | 0.086079 | 0.98409 | -0.30518 | 0.98376 | -0.31165 | 23.6481
51 | 0.017487 | 0.0043853 | -0.017481 | -0.0043819 | 5.6459e-06 | 3.3399e-06 | 0.026442 | 0.026442 | 0.026442 | 0.98409 | -0.30518 | 0.98375 | -0.31196 | 7.2643
52 | -0.0069609 | -0.0017436 | 0.0069614 | 0.0017437 | 4.6813e-07 | 1.5716e-07 | 0.010539 | 0.010539 | 0.010539 | 0.98282 | -0.33007 | 0.98289 | -0.32866 | 2.8952
53 | 0.0069609 | 0.0017436 | -0.0069607 | -0.0017435 | 1.61e-07 | 5.4054e-08 | 0.010539 | 0.010539 | 0.010539 | 0.98282 | -0.33007 | 0.98279 | -0.33056 | 2.8952
54 | -0.013119 | -0.0032856 | 0.013122 | 0.0032871 | 2.793e-06 | 1.5481e-06 | 0.01986 | 0.01986 | 0.01986 | 0.98289 | -0.32866 | 0.98312 | -0.32419 | 5.4561
55 | 0.0061577 | 0.0015419 | -0.0061574 | -0.0015418 | 3.1468e-07 | 7.9007e-08 | 0.0093218 | 0.0093218 | 0.0093218 | 0.98289 | -0.32866 | 0.98284 | -0.32973 | 2.5609
56 | 0.0034906 | 0.0008738 | -0.0034902 | -0.000874 | 3.4237e-07 | -1.9509e-07 | 0.0052846 | 0.0052847 | 0.0052847 | 0.98279 | -0.33056 | 0.98269 | -0.33262 | 1.4518
57 | -0.11828 | -0.03012 | 0.11831 | 0.030142 | 3.4549e-05 | 2.2073e-05 | 0.17705 | 0.17705 | 0.17705 | 0.99501 | -0.094646 | 0.99533 | -0.088591 | 48.6398
58 | 0.0055492 | 0.0013861 | -0.005548 | -0.0013859 | 1.1814e-06 | 1.8948e-07 | 0.0083964 | 0.0083966 | 0.0083966 | 0.98323 | -0.32207 | 0.983 | -0.32655 | 2.3068
59 | -0.0055492 | -0.0013861 | 0.0055494 | 0.0013862 | 2.3954e-07 | 3.8383e-08 | 0.0083964 | 0.0083964 | 0.0083964 | 0.98323 | -0.32207 | 0.98328 | -0.32116 | 2.3067
60 | 0.0013555 | 0.0003352 | -0.0013554 | -0.00033586 | 8.9275e-08 | -6.607e-07 | 0.0020502 | 0.0020505 | 0.0020505 | 0.983 | -0.32655 | 0.98293 | -0.32795 | 0.56332
61 | -0.015881 | -0.0039754 | 0.015885 | 0.0039782 | 4.788e-06 | 2.7838e-06 | 0.024031 | 0.024031 | 0.024031 | 0.98328 | -0.32116 | 0.9836 | -0.31483 | 6.6019
62 | 0.0024511 | 0.00061406 | -0.0024509 | -0.00061426 | 1.1231e-07 | -2.0349e-07 | 0.0037116 | 0.0037117 | 0.0037117 | 0.98263 | -0.33382 | 0.98258 | -0.33478 | 1.0197
63 | -0.0024511 | -0.00061406 | 0.0024512 | 0.00061381 | 1.4047e-07 | -2.5458e-07 | 0.0037116 | 0.0037115 | 0.0037116 | 0.98263 | -0.33382 | 0.98269 | -0.33262 | 1.0197
64 | 0.001039 | 0.00026019 | -0.001039 | -0.00026031 | 8.9123e-09 | -1.1594e-07 | 0.0015732 | 0.0015733 | 0.0015733 | 0.98269 | -0.33262 | 0.98268 | -0.3328 | 0.43222
65 | 0.037449 | 0.0094334 | -0.037437 | -0.0094258 | 1.2086e-05 | 7.6075e-06 | 0.056662 | 0.056662 | 0.056662 | 0.98376 | -0.31165 | 0.98341 | -0.3184 | 15.5664
66 | 0.03491 | 0.0087926 | -0.034904 | -0.0087889 | 5.9197e-06 | 3.7169e-06 | 0.052839 | 0.052839 | 0.052839 | 0.98341 | -0.3184 | 0.98323 | -0.32195 | 14.5161
67 | 0.008395 | 0.0021046 | -0.0083917 | -0.0021032 | 3.2638e-06 | 1.4039e-06 | 0.012698 | 0.012699 | 0.012699 | 0.98375 | -0.31196 | 0.98333 | -0.32012 | 3.4887
68 | 0.0090859 | 0.0022773 | -0.0090844 | -0.0022766 | 1.51e-06 | 6.9578e-07 | 0.013743 | 0.013744 | 0.013744 | 0.98375 | -0.31196 | 0.98357 | -0.31545 | 3.7757
69 | 0.0017555 | 0.00043989 | -0.0017554 | -0.00043996 | 1.4686e-08 | -6.1073e-08 | 0.0026558 | 0.0026558 | 0.0026558 | 0.98357 | -0.31545 | 0.98356 | -0.31563 | 0.72961
70 | 0.0073289 | 0.0018368 | -0.0073282 | -0.0018365 | 7.1486e-07 | 2.6073e-07 | 0.011088 | 0.011088 | 0.011088 | 0.98357 | -0.31545 | 0.98346 | -0.3175 | 3.0461
71 | 0.0065385 | 0.0016384 | -0.0065383 | -0.0016383 | 2.4013e-07 | 7.1511e-08 | 0.0099182 | 0.0099183 | 0.0099183 | 0.98095 | -0.36624 | 0.98091 | -0.36701 | 2.7248
72 | -0.015811 | -0.003954 | 0.015811 | 0.0039544 | 5.7714e-07 | 3.3539e-07 | 0.023946 | 0.023946 | 0.023946 | 0.98234 | -0.33903 | 0.98238 | -0.33826 | 6.5787
73 | 0.020319 | 0.0050906 | -0.020315 | -0.0050884 | 3.594e-06 | 2.1713e-06 | 0.030732 | 0.030732 | 0.030732 | 0.98379 | -0.31111 | 0.9836 | -0.31483 | 8.4429
74 | 0.013756 | 0.0034463 | -0.013756 | -0.0034461 | 4.5719e-07 | 2.5694e-07 | 0.02082 | 0.02082 | 0.02082 | 0.98316 | -0.32349 | 0.98312 | -0.32419 | 5.7198
75 | 0.0055227 | 0.0013827 | -0.0055225 | -0.0013827 | 1.6153e-07 | 2.5293e-08 | 0.0083609 | 0.0083609 | 0.0083609 | 0.98284 | -0.32973 | 0.98281 | -0.33035 | 2.297
76 | -0.1249 | -0.031793 | 0.12507 | 0.031899 | 0.00016544 | 0.00010571 | 0.1869 | 0.1869 | 0.1869 | 0.99533 | -0.088591 | 0.99677 | -0.061158 | 51.346
77 | 0.0013554 | 0.00033586 | -0.001355 | -0.00033879 | 3.9689e-07 | -2.9339e-06 | 0.0020505 | 0.0020516 | 0.0020516 | 0.98293 | -0.32795 | 0.98262 | -0.33413 | 0.56363
78 | 0.001039 | 0.00026031 | -0.001039 | -0.0002604 | 7.0799e-09 | -9.2098e-08 | 0.0015733 | 0.0015733 | 0.0015733 | 0.98268 | -0.3328 | 0.98267 | -0.33294 | 0.43223
79 | 0.032134 | 0.0080945 | -0.032134 | -0.0080942 | 4.5336e-07 | 2.8367e-07 | 0.048646 | 0.048646 | 0.048646 | 0.98323 | -0.32195 | 0.98322 | -0.32224 | 13.3643
80 | 0.0036651 | 0.00091842 | -0.0036649 | -0.00091851 | 1.8705e-07 | -8.6097e-08 | 0.0055453 | 0.0055454 | 0.0055454 | 0.98346 | -0.3175 | 0.98341 | -0.31857 | 1.5235
81 | 0.0036421 | 0.00091243 | -0.0036418 | -0.00091256 | 2.8525e-07 | -1.3198e-07 | 0.0055249 | 0.005525 | 0.005525 | 0.98091 | -0.36701 | 0.98083 | -0.36865 | 1.5178
82 | -0.016524 | -0.004133 | 0.016525 | 0.0041335 | 8.5815e-07 | 5.0295e-07 | 0.025026 | 0.025026 | 0.025026 | 0.98238 | -0.33826 | 0.98243 | -0.33717 | 6.8753
83 | -0.0039662 | -0.00099402 | 0.0039664 | 0.00099397 | 1.6643e-07 | -5.6576e-08 | 0.0059384 | 0.0059383 | 0.0059384 | 0.99384 | -0.11694 | 0.99388 | -0.11606 | 1.6314
84 | -0.13287 | -0.033899 | 0.13305 | 0.034015 | 0.00018216 | 0.00011594 | 0.19914 | 0.19914 | 0.19914 | 0.99388 | -0.11606 | 0.99537 | -0.087716 | 27.3547
85 | 0.1289 | 0.032906 | -0.12867 | -0.032755 | 0.0002372 | 0.00015093 | 0.1932 | 0.1932 | 0.1932 | 0.99388 | -0.11606 | 0.99189 | -0.15421 | 26.539
86 | 0.0018098 | 0.00045342 | -0.0018098 | -0.00045357 | 4.0587e-08 | -1.5522e-07 | 0.0027456 | 0.0027457 | 0.0027457 | 0.98083 | -0.36865 | 0.9808 | -0.36912 | 0.75431
87 | 0.001355 | 0.00033879 | -0.0013549 | -0.00033957 | 1.0494e-07 | -7.7478e-07 | 0.0020516 | 0.0020519 | 0.0020519 | 0.98262 | -0.33413 | 0.98254 | -0.33575 | 0.56372
88 | 0.0070964 | 0.0017786 | -0.0070959 | -0.0017784 | 5.5917e-07 | 1.9886e-07 | 0.010822 | 0.010822 | 0.010822 | 0.97574 | -0.4674 | 0.97565 | -0.46905 | 2.9731
89 | -0.033485 | -0.0084239 | 0.033524 | 0.0084482 | 3.8752e-05 | 2.4306e-05 | 0.051077 | 0.051077 | 0.051077 | 0.97574 | -0.4674 | 0.97697 | -0.44321 | 14.0321
90 | 0.0019084 | 0.00047826 | -0.0019084 | -0.00047829 | 9.4635e-09 | -3.1145e-08 | 0.0029106 | 0.0029106 | 0.0029106 | 0.97565 | -0.46905 | 0.97565 | -0.46916 | 0.79962
91 | -0.036434 | -0.0091777 | 0.036454 | 0.00919 | 1.9536e-05 | 1.2291e-05 | 0.05551 | 0.05551 | 0.05551 | 0.97697 | -0.44321 | 0.97754 | -0.432 | 15.25
92 | -0.043336 | -0.010915 | 0.043409 | 0.010961 | 7.227e-05 | 4.5697e-05 | 0.065986 | 0.065986 | 0.065986 | 0.97754 | -0.432 | 0.97932 | -0.39719 | 18.1281
93 | -0.0061677 | -0.0015458 | 0.0061683 | 0.0015459 | 6.2923e-07 | 1.6076e-07 | 0.0093567 | 0.0093566 | 0.0093567 | 0.98086 | -0.36719 | 0.98097 | -0.36505 | 2.5705
94 | -0.0061683 | -0.0015459 | 0.0061687 | 0.001546 | 3.3536e-07 | 8.5659e-08 | 0.0093566 | 0.0093566 | 0.0093566 | 0.98097 | -0.36505 | 0.98103 | -0.36391 | 2.5705
95 | -0.047113 | -0.011889 | 0.047208 | 0.011949 | 9.4692e-05 | 5.9982e-05 | 0.071615 | 0.071614 | 0.071615 | 0.97932 | -0.39719 | 0.98147 | -0.35531 | 19.6743
96 | -0.0618 | -0.015608 | 0.061836 | 0.015631 | 3.5898e-05 | 2.2837e-05 | 0.093738 | 0.093738 | 0.093738 | 0.98147 | -0.35531 | 0.98209 | -0.3432 | 25.7523
97 | 0.014592 | 0.003659 | -0.014587 | -0.0036559 | 5.3879e-06 | 3.0774e-06 | 0.022124 | 0.022124 | 0.022124 | 0.98147 | -0.35531 | 0.98108 | -0.36306 | 6.0781
98 | -0.064023 | -0.016179 | 0.064092 | 0.016223 | 6.898e-05 | 4.39e-05 | 0.097053 | 0.097053 | 0.097053 | 0.98209 | -0.3432 | 0.98325 | -0.32075 | 26.6628
99 | 0.0089618 | 0.0022461 | -0.0089615 | -0.002246 | 3.6129e-07 | 1.6538e-07 | 0.013593 | 0.013593 | 0.013593 | 0.98108 | -0.36306 | 0.98103 | -0.36391 | 3.7342
100 | -0.06748 | -0.017072 | 0.067505 | 0.017088 | 2.4948e-05 | 1.5886e-05 | 0.10218 | 0.10218 | 0.10218 | 0.98325 | -0.32075 | 0.98365 | -0.31305 | 28.0713
101 | -0.070228 | -0.01777 | 0.070279 | 0.017803 | 5.0731e-05 | 3.2316e-05 | 0.1063 | 0.1063 | 0.1063 | 0.98365 | -0.31305 | 0.98442 | -0.29801 | 29.203
102 | 0.26684 | 0.068477 | -0.26605 | -0.067973 | 0.00078932 | 0.00050447 | 0.39763 | 0.39763 | 0.39763 | 1 | 0 | 0.99677 | -0.061158 | 54.62
103 | 0.14099 | 0.036074 | -0.14081 | -0.035959 | 0.00018101 | 0.00011528 | 0.21073 | 0.21073 | 0.21073 | 0.99677 | -0.061158 | 0.99537 | -0.087716 | 28.947
104 | -0.072403 | -0.018335 | 0.072429 | 0.018352 | 2.622e-05 | 1.6706e-05 | 0.10951 | 0.10951 | 0.10951 | 0.98442 | -0.29801 | 0.98481 | -0.29047 | 30.0848
105 | 0.1272 | 0.032387 | -0.12719 | -0.032381 | 9.2617e-06 | 5.8925e-06 | 0.191 | 0.191 | 0.191 | 0.99189 | -0.15421 | 0.99181 | -0.15572 | 26.2365
106 | 0.12282 | 0.031286 | -0.12267 | -0.03119 | 0.00015012 | 9.5469e-05 | 0.18445 | 0.18445 | 0.18445 | 0.99181 | -0.15572 | 0.99048 | -0.1811 | 25.3362
107 | -0.018946 | -0.0047403 | 0.018953 | 0.0047443 | 6.6941e-06 | 4.0096e-06 | 0.028693 | 0.028693 | 0.028693 | 0.98243 | -0.33717 | 0.98281 | -0.32975 | 7.8827
108 | 0.11845 | 0.030132 | -0.11839 | -0.030096 | 5.5716e-05 | 3.5598e-05 | 0.1781 | 0.1781 | 0.1781 | 0.99048 | -0.1811 | 0.98997 | -0.19086 | 48.9294
109 | -0.01971 | -0.004934 | 0.019711 | 0.0049349 | 1.5064e-06 | 9.0691e-07 | 0.029839 | 0.029839 | 0.029839 | 0.98281 | -0.32975 | 0.98289 | -0.32814 | 8.1976
110 | 0.11696 | 0.029737 | -0.11668 | -0.029562 | 0.0002744 | 0.00017531 | 0.17595 | 0.17595 | 0.17595 | 0.98997 | -0.19086 | 0.98744 | -0.23969 | 48.3381
111 | 0.0018693 | 0.0004684 | -0.0018693 | -0.00046848 | 2.2832e-08 | -8.2324e-08 | 0.0028256 | 0.0028257 | 0.0028257 | 0.98437 | -0.2992 | 0.98436 | -0.29946 | 0.77629
112 | -0.0040542 | -0.001016 | 0.0040545 | 0.0010159 | 2.4308e-07 | -6.3848e-08 | 0.0061285 | 0.0061284 | 0.0061285 | 0.98437 | -0.2992 | 0.98444 | -0.29794 | 1.6837
113 | -0.034219 | -0.0085845 | 0.034236 | 0.0085953 | 1.728e-05 | 1.084e-05 | 0.051726 | 0.051726 | 0.051726 | 0.98444 | -0.29794 | 0.98498 | -0.28736 | 14.2104
114 | 0.030164 | 0.0075686 | -0.030152 | -0.0075607 | 1.256e-05 | 7.8334e-06 | 0.045597 | 0.045597 | 0.045597 | 0.98444 | -0.29794 | 0.98399 | -0.30668 | 12.5268
115 | -0.035916 | -0.0090163 | 0.035931 | 0.0090262 | 1.5779e-05 | 9.9163e-06 | 0.054263 | 0.054263 | 0.054263 | 0.98498 | -0.28736 | 0.98545 | -0.27815 | 14.9075
116 | 0.028601 | 0.0071722 | -0.028599 | -0.0071707 | 2.3554e-06 | 1.4648e-06 | 0.043253 | 0.043253 | 0.043253 | 0.98399 | -0.30668 | 0.9839 | -0.30841 | 11.8826
117 | -0.037811 | -0.0094972 | 0.037824 | 0.0095058 | 1.3653e-05 | 8.5959e-06 | 0.057101 | 0.057101 | 0.057101 | 0.98545 | -0.27815 | 0.98584 | -0.27059 | 15.687
118 | 0.026566 | 0.0066613 | -0.026554 | -0.0066537 | 1.224e-05 | 7.5769e-06 | 0.040179 | 0.040179 | 0.040179 | 0.9839 | -0.30841 | 0.98341 | -0.31808 | 11.0381
119 | -0.039375 | -0.0098944 | 0.039386 | 0.0099018 | 1.1777e-05 | 7.4238e-06 | 0.059441 | 0.059441 | 0.059441 | 0.98584 | -0.27059 | 0.98616 | -0.26432 | 16.3299
120 | 0.024249 | 0.006076 | -0.024248 | -0.0060755 | 7.1414e-07 | 4.391e-07 | 0.036691 | 0.036691 | 0.036691 | 0.98341 | -0.31808 | 0.98338 | -0.3187 | 10.0799
121 | 0.074389 | 0.018879 | -0.074296 | -0.01882 | 9.343e-05 | 5.9544e-05 | 0.11233 | 0.11233 | 0.11233 | 0.98616 | -0.26432 | 0.98481 | -0.29047 | 30.8599
122 | -0.11378 | -0.028781 | 0.11391 | 0.028867 | 0.00013465 | 8.6021e-05 | 0.17177 | 0.17177 | 0.17177 | 0.98616 | -0.26432 | 0.98744 | -0.23969 | 47.1898
123 | 0.022255 | 0.0055759 | -0.022249 | -0.0055726 | 5.3746e-06 | 3.2794e-06 | 0.033674 | 0.033674 | 0.033674 | 0.98338 | -0.3187 | 0.98312 | -0.32377 | 9.2512
124 | 0.021811 | 0.0054628 | -0.021807 | -0.0054605 | 3.7677e-06 | 2.2944e-06 | 0.033011 | 0.033011 | 0.033011 | 0.98312 | -0.32377 | 0.98293 | -0.3274 | 9.069
125 | 0.021042 | 0.0052688 | -0.021042 | -0.0052684 | 7.4283e-07 | 4.5067e-07 | 0.031853 | 0.031853 | 0.031853 | 0.98293 | -0.3274 | 0.98289 | -0.32814 | 8.751
126 | 0.0015435 | 0.00038678 | -0.0015435 | -0.00038683 | 9.8584e-09 | -5.2021e-08 | 0.0023632 | 0.0023632 | 0.0023632 | 0.97186 | -0.54372 | 0.97186 | -0.54385 | 0.64923

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27524 | 0.070168

## res_load
| p_mw | q_mvar
0 | 0.0042027 | 0.0010533
1 | 0.0019699 | 0.0004937
2 | 0.0066729 | 0.0016724
3 | 0.0016628 | 0.00041674
4 | 0.0044886 | 0.0011249
5 | 0.0033223 | 0.00083265
6 | 0.010438 | 0.0026159
7 | 0.0025254 | 0.00063292
8 | 0.0028624 | 0.00071738
9 | 0.0044588 | 0.0011175
10 | 0.0025242 | 0.00063261
11 | 0.0063783 | 0.0015986
12 | 0.0014161 | 0.0003549
13 | 0.0017021 | 0.00042658
14 | 0.0019538 | 0.00048968
15 | 0.0015102 | 0.0003785
16 | 0.0030657 | 0.00076833
17 | 0.008578 | 0.0021499
18 | 0.0012413 | 0.0003111
19 | 0.0025246 | 0.00063271
20 | 0.0025237 | 0.00063251
21 | 0.0034702 | 0.00086971
22 | 0.0047203 | 0.001183
23 | 0.0044155 | 0.0011066
24 | 2.6776e-05 | 6.7107e-06
25 | 0.0041925 | 0.0010507
26 | 0.010331 | 0.0025893
27 | 0.0024509 | 0.00061426
28 | 0.0025266 | 0.00063323
29 | 0.0083917 | 0.0021032
30 | 0.00063225 | 0.00015846
31 | 0.00063461 | 0.00015905
32 | 0.0016919 | 0.00042404
33 | 0.00013857 | 3.473e-05
34 | 0.00063423 | 0.00015895
35 | 0.00063409 | 0.00015892
36 | 0.00063469 | 0.00015907
37 | 0.0065891 | 0.0016514
38 | 0.0044297 | 0.0011102
39 | 0.0027704 | 0.00069433
40 | 0.0017554 | 0.00043996
41 | 0.0036632 | 0.00091807
42 | 0.0028962 | 0.00072585
43 | 0.00071291 | 0.00017867
44 | 0.0039662 | 0.00099402
45 | 0.001832 | 0.00045915
46 | 0.0012202 | 0.00030581
47 | 0.0014381 | 0.00036042
48 | 0.001039 | 0.0002604
49 | 0.0023355 | 0.00058532
50 | 0.0036649 | 0.00091851
51 | 0.0051875 | 0.0013001
52 | 0.0029105 | 0.00072945
53 | 0.0019084 | 0.00047829
54 | 0.0068825 | 0.0017249
55 | 0.0061677 | 0.0015458
56 | 0.0037043 | 0.00092839
57 | 0.0021874 | 0.00054821
58 | 0.0056251 | 0.0014098
59 | 0.0033878 | 0.00084907
60 | 0.0027928 | 0.00069994
61 | 0.0027232 | 0.00068249
62 | 0.0018098 | 0.00045357
63 | 0.0013549 | 0.00033957
64 | 0.0067469 | 0.0016909
65 | 0.0077543 | 0.0019434
66 | 0.0021235 | 0.0005322
67 | 0.0014683 | 0.000368
68 | 0.0043684 | 0.0010948
69 | 0.002421 | 0.00060675
70 | 0.0042235 | 0.0010585
71 | 0.00075704 | 0.00018973
72 | 0.0014319 | 0.00035886
73 | 0.0021849 | 0.0005476
74 | 0.0018693 | 0.00046848
75 | 0.0016796 | 0.00042095
76 | 0.0015504 | 0.00038858
77 | 0.0018793 | 0.00047099
78 | 0.0020327 | 0.00050944
79 | 0.0015504 | 0.00038857
80 | 0.0023051 | 0.00057772
81 | 0.0019934 | 0.0004996
82 | 0.0018673 | 0.00046799
83 | 0.0027739 | 0.0006952
84 | 0.00043827 | 0.00010984
85 | 0.0007647 | 0.00019165
86 | 0.0013306 | 0.00033347
87 | 0.005783 | 0.0014494
88 | 0.0015435 | 0.00038683

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1