## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1065-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1065-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1065-8_0_4_node_10 | 0.4 | n |  | TRUE
3 | bus_LV_1065-8_0_4_node_11 | 0.4 | n |  | TRUE
4 | bus_LV_1065-8_0_4_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_1065-8_0_4_node_2 | 0.4 | n |  | TRUE
6 | bus_LV_1065-8_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1065-8_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1065-8_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1065-8_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1065-8_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1065-8_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1065-8_0_4_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1065-8_0_4_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_1065-8_0_4_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_1065-8_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_1065-8_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1065-8_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1065-8_0_4_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_1065-8_0_4_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1065-8_0_4_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_1065-8_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1065-8_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1065-8_0_4_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1065-8_0_4_node_23 | 0.4 | n |  | TRUE
25 | bus_MV_5_0_node_103 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1065-8_0_4_load_0 | 0 | 0.075116 | 0.018826 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1065-8_0_4_load_8 | 4 | 0.013647 | 0.0034204 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1065-8_0_4_load_2 | 5 | 0.013054 | 0.0032718 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1065-8_0_4_load_3 | 6 | 0.026899 | 0.0067416 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1065-8_0_4_load_4 | 7 | 0.047353 | 0.011868 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1065-8_0_4_load_5 | 8 | 0.055957 | 0.014024 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1065-8_0_4_load_6 | 9 | 0.024299 | 0.0060899 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1065-8_0_4_load_9 | 10 | 0.064093 | 0.016063 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1065-8_0_4_load_7 | 11 | 0.018888 | 0.0047339 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1065-8_0_4_load_16 | 15 | 0.0054763 | 0.0013725 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1065-8_0_4_load_13 | 17 | 0.0057953 | 0.0014524 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1065-8_0_4_load_25 | 18 | 0.02512 | 0.0062957 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1065-8_0_4_load_21 | 19 | 0.0095194 | 0.0023858 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1065-8_0_4_load_22 | 20 | 0.0022817 | 0.00057184 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1065-8_0_4_load_18 | 21 | 0.028728 | 0.0071999 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1065-8_0_4_load_24 | 23 | 0.015432 | 0.0038676 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1065-8_0_4_load_23 | 24 | 0.014379 | 0.0036037 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1065-8_0_4_line_0 |  | 0 | 1 | 0.038579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1065-8_0_4_line_1 |  | 1 | 2 | 0.060542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1065-8_0_4_line_2 |  | 2 | 3 | 0.094668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1065-8_0_4_line_3 |  | 2 | 4 | 0.011157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1065-8_0_4_line_4 |  | 3 | 17 | 0.046438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1065-8_0_4_line_5 |  | 4 | 10 | 0.010556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1065-8_0_4_line_6 |  | 5 | 6 | 0.019645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1065-8_0_4_line_7 |  | 5 | 7 | 0.016451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1065-8_0_4_line_8 |  | 6 | 8 | 0.012019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1065-8_0_4_line_9 |  | 7 | 9 | 0.020554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1065-8_0_4_line_10 |  | 8 | 10 | 0.024048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1065-8_0_4_line_11 |  | 9 | 11 | 0.013711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1065-8_0_4_line_12 |  | 11 | 15 | 0.0088487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1065-8_0_4_line_13 |  | 12 | 13 | 0.017678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1065-8_0_4_line_14 |  | 12 | 14 | 0.027031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1065-8_0_4_line_15 |  | 13 | 18 | 0.047222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1065-8_0_4_line_16 |  | 13 | 19 | 0.027163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1065-8_0_4_line_17 |  | 14 | 20 | 0.055395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1065-8_0_4_line_18 |  | 14 | 21 | 0.022505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1065-8_0_4_line_19 |  | 15 | 16 | 0.024837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1065-8_0_4_line_20 |  | 16 | 21 | 0.023548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1065-8_0_4_line_21 |  | 16 | 22 | 0.038378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1065-8_0_4_line_22 |  | 19 | 24 | 0.026065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1065-8_0_4_line_23 |  | 22 | 23 | 0.037602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1065-8_0_4_trafo_5 | 0.63 MVA 20/0.4 kV | 25 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2672354.0574 | 1219089.7333 | 2672327.6719 | 1219117.8781
1 | 2672413.7564 | 1219079.6631 | 2672354.0574 | 1219089.7333
2 | 2672413.7564 | 1219079.6631 | 2672404.1617 | 1219061.079 | 2672469.9131 | 1219027.6678
3 | 2672413.7564 | 1219079.6631 | 2672418.772 | 1219089.6294
4 | 2672469.9131 | 1219027.6678 | 2672501.3369 | 1219061.8586
5 | 2672418.772 | 1219089.6294 | 2672423.5171 | 1219099.0583
6 | 2672462.417 | 1219119.3715 | 2672462.123 | 1219119.0097 | 2672456.2874 | 1219113.9688 | 2672451.3626 | 1219113.2862 | 2672445.3861 | 1219115.8309
7 | 2672462.417 | 1219119.3715 | 2672472.7905 | 1219132.1394
8 | 2672434.3274 | 1219120.5394 | 2672445.3861 | 1219115.8309
9 | 2672472.7905 | 1219132.1394 | 2672485.7512 | 1219148.0915
10 | 2672434.3274 | 1219120.5394 | 2672423.5171 | 1219099.0583
11 | 2672494.3974 | 1219158.7332 | 2672485.7512 | 1219148.0915
12 | 2672494.3974 | 1219158.7332 | 2672499.9772 | 1219165.6009
13 | 2672453.4266 | 1219201.268 | 2672468.4462 | 1219191.8779
14 | 2672468.4462 | 1219191.8779 | 2672475.0887 | 1219204.8115 | 2672480.9652 | 1219215.8345
15 | 2672453.4266 | 1219201.268 | 2672428.6133 | 1219161.0516
16 | 2672453.4266 | 1219201.268 | 2672431.886 | 1219217.8151
17 | 2672480.9652 | 1219215.8345 | 2672467.4657 | 1219269.5598
18 | 2672480.9652 | 1219215.8345 | 2672497.7444 | 1219200.8364
19 | 2672515.3007 | 1219185.1436 | 2672507.0017 | 1219174.2467 | 2672499.9772 | 1219165.6009
20 | 2672515.3007 | 1219185.1436 | 2672497.7444 | 1219200.8364
21 | 2672539.8094 | 1219155.6117 | 2672534.9517 | 1219161.89 | 2672523.9727 | 1219175.9988 | 2672515.3007 | 1219185.1436
22 | 2672431.886 | 1219217.8151 | 2672429.1559 | 1219214.4037 | 2672425.6636 | 1219200.152 | 2672421.8425 | 1219194.2598
23 | 2672509.2731 | 1219133.5481 | 2672539.8094 | 1219155.6117

## bus_geodata
| x | y | coords
0 | 2672327.6719 | 1219117.8781
1 | 2672354.0574 | 1219089.7333
2 | 2672413.7564 | 1219079.6631
3 | 2672469.9131 | 1219027.6678
4 | 2672418.772 | 1219089.6294
5 | 2672462.417 | 1219119.3715
6 | 2672445.3861 | 1219115.8309
7 | 2672472.7905 | 1219132.1394
8 | 2672434.3274 | 1219120.5394
9 | 2672485.7512 | 1219148.0915
10 | 2672423.5171 | 1219099.0582
11 | 2672494.3974 | 1219158.7332
12 | 2672468.4462 | 1219191.8779
13 | 2672453.4266 | 1219201.268
14 | 2672480.9652 | 1219215.8345
15 | 2672499.9772 | 1219165.6009
16 | 2672515.3007 | 1219185.1436
17 | 2672501.3369 | 1219061.8586
18 | 2672428.6133 | 1219161.0516
19 | 2672431.886 | 1219217.8151
20 | 2672467.4657 | 1219269.5598
21 | 2672497.7444 | 1219200.8364
22 | 2672539.8094 | 1219155.6117
23 | 2672509.2731 | 1219133.5481
24 | 2672421.8425 | 1219194.2598
25 | 2672413.7564 | 1219079.6631

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9897 | -0.1982 | 0.075116 | 0.018826
1 | 0.99235 | -0.14677 | 0 | 0
2 | 0.99652 | -0.066616 | 0 | 0
3 | 0.99602 | -0.076256 | 0 | 0
4 | 0.99735 | -0.050783 | 0.013647 | 0.0034204
5 | 0.99689 | -0.059447 | 0.013054 | 0.0032718
6 | 0.99873 | -0.024274 | 0.026899 | 0.0067416
7 | 0.99544 | -0.087111 | 0.047353 | 0.011868
8 | 1 | 0 | -0.39443 | -0.099481
9 | 0.99408 | -0.1132 | 0.024299 | 0.0060899
10 | 0.99826 | -0.033309 | 0.064093 | 0.016063
11 | 0.99257 | -0.14223 | 0.018888 | 0.0047339
12 | 0.98555 | -0.27815 | 0 | 0
13 | 0.98475 | -0.29372 | 0 | 0
14 | 0.98677 | -0.2544 | 0 | 0
15 | 0.99175 | -0.15804 | 0.0054763 | 0.0013725
16 | 0.98957 | -0.20015 | 0 | 0
17 | 0.99577 | -0.080986 | 0.0057953 | 0.0014524
18 | 0.98366 | -0.31506 | 0.02512 | 0.0062957
19 | 0.98415 | -0.30539 | 0.0095194 | 0.0023858
20 | 0.98666 | -0.25667 | 0.0022817 | 0.00057184
21 | 0.98784 | -0.23376 | 0.028728 | 0.0071999
22 | 0.98903 | -0.2107 | 0 | 0
23 | 0.9885 | -0.22105 | 0.015432 | 0.0038676
24 | 0.98381 | -0.31214 | 0.014379 | 0.0036037
25 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.075116 | -0.018826 | 0.0753 | 0.018943 | 0.00018452 | 0.0001176 | 0.11294 | 0.11294 | 0.11294 | 0.9897 | -0.1982 | 0.99235 | -0.14677 | 31.0267
1 | -0.0753 | -0.018943 | 0.07559 | 0.019128 | 0.00028958 | 0.00018454 | 0.11294 | 0.11294 | 0.11294 | 0.99235 | -0.14677 | 0.99652 | -0.066616 | 31.0266
2 | 0.0057993 | 0.0014531 | -0.0057966 | -0.0014527 | 2.6622e-06 | 4.7108e-07 | 0.0086595 | 0.0086599 | 0.0086599 | 0.99652 | -0.066616 | 0.99602 | -0.076256 | 2.3791
3 | -0.081389 | -0.020581 | 0.081451 | 0.020621 | 6.1862e-05 | 3.9446e-05 | 0.1216 | 0.1216 | 0.1216 | 0.99652 | -0.066616 | 0.99735 | -0.050783 | 33.4055
4 | 0.0057966 | 0.0014527 | -0.0057953 | -0.0014524 | 1.306e-06 | 2.3159e-07 | 0.0086599 | 0.0086601 | 0.0086601 | 0.99602 | -0.076256 | 0.99577 | -0.080986 | 2.3792
5 | -0.095098 | -0.024041 | 0.095178 | 0.024092 | 7.9768e-05 | 5.0914e-05 | 0.14196 | 0.14196 | 0.14196 | 0.99735 | -0.050783 | 0.99826 | -0.033309 | 38.9993
6 | -0.20574 | -0.052027 | 0.20609 | 0.052249 | 0.00034775 | 0.00022205 | 0.30726 | 0.30726 | 0.30726 | 0.99689 | -0.059447 | 0.99873 | -0.024274 | 42.2061
7 | 0.19268 | 0.048755 | -0.19243 | -0.048592 | 0.00025544 | 0.00016306 | 0.28777 | 0.28777 | 0.28777 | 0.99689 | -0.059447 | 0.99544 | -0.087111 | 39.5295
8 | -0.23298 | -0.05899 | 0.23326 | 0.059164 | 0.00027188 | 0.00017369 | 0.34734 | 0.34734 | 0.34734 | 0.99873 | -0.024274 | 1 | 0 | 47.7113
9 | 0.14507 | 0.036724 | -0.14489 | -0.036608 | 0.00018146 | 0.0001156 | 0.21699 | 0.21699 | 0.21699 | 0.99544 | -0.087111 | 0.99408 | -0.1132 | 29.8064
10 | 0.15953 | 0.040317 | -0.15927 | -0.040155 | 0.00025432 | 0.00016214 | 0.2375 | 0.2375 | 0.2375 | 1 | 0 | 0.99826 | -0.033309 | 32.623
11 | 0.12059 | 0.030518 | -0.12043 | -0.030411 | 0.00016774 | 0.00010718 | 0.18062 | 0.18062 | 0.18062 | 0.99408 | -0.1132 | 0.99257 | -0.14223 | 49.6204
12 | 0.10154 | 0.025677 | -0.10146 | -0.025628 | 7.6969e-05 | 4.9146e-05 | 0.1523 | 0.1523 | 0.1523 | 0.99257 | -0.14223 | 0.99175 | -0.15804 | 41.8411
13 | 0.049098 | 0.012335 | -0.049062 | -0.012312 | 3.644e-05 | 2.3097e-05 | 0.074141 | 0.074141 | 0.074141 | 0.98555 | -0.27815 | 0.98475 | -0.29372 | 20.3684
14 | -0.049098 | -0.012335 | 0.049154 | 0.01237 | 5.572e-05 | 3.5316e-05 | 0.074141 | 0.074141 | 0.074141 | 0.98555 | -0.27815 | 0.98677 | -0.2544 | 20.3684
15 | 0.025146 | 0.0063115 | -0.02512 | -0.0062957 | 2.5571e-05 | 1.5765e-05 | 0.038 | 0.038 | 0.038 | 0.98475 | -0.29372 | 0.98366 | -0.31506 | 10.4397
16 | 0.023916 | 0.0060002 | -0.023903 | -0.0059921 | 1.3305e-05 | 8.1695e-06 | 0.036141 | 0.036141 | 0.036141 | 0.98475 | -0.29372 | 0.98415 | -0.30539 | 9.9288
17 | 0.0022819 | 0.00057129 | -0.0022817 | -0.00057184 | 2.4596e-07 | -5.5015e-07 | 0.0034408 | 0.0034411 | 0.0034411 | 0.98677 | -0.2544 | 0.98666 | -0.25667 | 0.94535
18 | -0.051436 | -0.012941 | 0.051487 | 0.012974 | 5.0796e-05 | 3.2222e-05 | 0.077582 | 0.077581 | 0.077582 | 0.98677 | -0.2544 | 0.98784 | -0.23376 | 21.3136
19 | 0.095984 | 0.024256 | -0.095791 | -0.024132 | 0.00019336 | 0.00012343 | 0.14408 | 0.14409 | 0.14409 | 0.99175 | -0.15804 | 0.98957 | -0.20015 | 39.5838
20 | 0.080344 | 0.020256 | -0.080215 | -0.020174 | 0.00012898 | 8.2243e-05 | 0.12086 | 0.12086 | 0.12086 | 0.98957 | -0.20015 | 0.98784 | -0.23376 | 33.202
21 | 0.015447 | 0.0038765 | -0.01544 | -0.003872 | 7.7662e-06 | 4.4776e-06 | 0.02323 | 0.02323 | 0.02323 | 0.98957 | -0.20015 | 0.98903 | -0.2107 | 6.3819
22 | 0.014383 | 0.0036063 | -0.014379 | -0.0036037 | 4.6231e-06 | 2.6277e-06 | 0.021748 | 0.021748 | 0.021748 | 0.98415 | -0.30539 | 0.98381 | -0.31214 | 5.9747
23 | 0.01544 | 0.003872 | -0.015432 | -0.0038676 | 7.6093e-06 | 4.3877e-06 | 0.02323 | 0.02323 | 0.02323 | 0.98903 | -0.2107 | 0.9885 | -0.22105 | 6.3819

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45039 | 0.11351

## res_load
| p_mw | q_mvar
0 | 0.075116 | 0.018826
1 | 0.013647 | 0.0034204
2 | 0.013054 | 0.0032718
3 | 0.026899 | 0.0067416
4 | 0.047353 | 0.011868
5 | 0.055957 | 0.014024
6 | 0.024299 | 0.0060899
7 | 0.064093 | 0.016063
8 | 0.018888 | 0.0047339
9 | 0.0054763 | 0.0013725
10 | 0.0057953 | 0.0014524
11 | 0.02512 | 0.0062957
12 | 0.0095194 | 0.0023858
13 | 0.0022817 | 0.00057184
14 | 0.028728 | 0.0071999
15 | 0.015432 | 0.0038676
16 | 0.014379 | 0.0036037

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1