## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1069-15_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1069-15_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1069-15_0_4_node_15 | 0.4 | n |  | TRUE
3 | bus_LV_1069-15_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1069-15_0_4_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_1069-15_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1069-15_0_4_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_1069-15_0_4_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1069-15_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1069-15_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1069-15_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1069-15_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1069-15_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1069-15_0_4_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_1069-15_0_4_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_1069-15_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1069-15_0_4_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1069-15_0_4_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1069-15_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1069-15_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1069-15_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1069-15_0_4_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1069-15_0_4_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_1069-15_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1069-15_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1069-15_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1069-15_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_MV_1_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1069-15_0_4_load_0 | 0 | 0.030605 | 0.0076703 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1069-15_0_4_load_1 | 1 | 0.0052877 | 0.0013252 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1069-15_0_4_load_15 | 2 | 0.0071099 | 0.0017819 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1069-15_0_4_load_2 | 3 | 0.011648 | 0.0029194 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1069-15_0_4_load_16 | 4 | 0.0032386 | 0.00081166 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1069-15_0_4_load_3 | 5 | 0.0029263 | 0.0007334 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1069-15_0_4_load_9 | 6 | 0.024595 | 0.0061642 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1069-15_0_4_load_10 | 7 | 0.024899 | 0.0062402 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1069-15_0_4_load_6 | 10 | 0.0046896 | 0.0011753 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1069-15_0_4_load_8 | 12 | 0.010061 | 0.0025214 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1069-15_0_4_load_21 | 13 | 0.022203 | 0.0055645 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1069-15_0_4_load_20 | 14 | 0.0083058 | 0.0020816 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1069-15_0_4_load_11 | 15 | 0.027561 | 0.0069074 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1069-15_0_4_load_25 | 16 | 0.025185 | 0.006312 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1069-15_0_4_load_23 | 17 | 0.025147 | 0.0063025 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1069-15_0_4_load_12 | 18 | 0.023715 | 0.0059434 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1069-15_0_4_load_13 | 19 | 0.016969 | 0.0042529 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1069-15_0_4_load_14 | 20 | 0.023255 | 0.0058283 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1069-15_0_4_load_22 | 21 | 0.025361 | 0.006356 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1069-15_0_4_load_26 | 22 | 0.022884 | 0.0057353 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1069-15_0_4_load_18 | 24 | 0.007043 | 0.0017651 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1069-15_0_4_load_19 | 25 | 0.0077681 | 0.0019469 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1069-15_0_4_load_24 | 26 | 0.02418 | 0.0060601 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1069-15_0_4_line_0 |  | 0 | 1 | 0.021927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_1069-15_0_4_line_1 |  | 0 | 2 | 0.14165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_1069-15_0_4_line_2 |  | 1 | 3 | 0.0049623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1069-15_0_4_line_3 |  | 2 | 4 | 0.06724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1069-15_0_4_line_4 |  | 3 | 5 | 0.027527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1069-15_0_4_line_5 |  | 4 | 23 | 0.0079006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1069-15_0_4_line_6 |  | 5 | 9 | 0.016945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1069-15_0_4_line_7 |  | 6 | 7 | 0.00053825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1069-15_0_4_line_8 |  | 6 | 8 | 0.10664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1069-15_0_4_line_9 |  | 7 | 15 | 0.0056047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1069-15_0_4_line_10 |  | 8 | 9 | 0.036646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1069-15_0_4_line_11 |  | 10 | 11 | 0.15221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1069-15_0_4_line_12 |  | 11 | 12 | 0.059296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1069-15_0_4_line_13 |  | 12 | 13 | 0.022397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1069-15_0_4_line_14 |  | 13 | 14 | 0.037212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1069-15_0_4_line_15 |  | 14 | 25 | 0.013914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1069-15_0_4_line_16 |  | 15 | 16 | 0.0038251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1069-15_0_4_line_17 |  | 16 | 17 | 0.0039118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1069-15_0_4_line_18 |  | 17 | 26 | 0.00012862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1069-15_0_4_line_19 |  | 18 | 19 | 0.013905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1069-15_0_4_line_20 |  | 19 | 20 | 0.018735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1069-15_0_4_line_21 |  | 20 | 21 | 0.00010132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1069-15_0_4_line_22 |  | 21 | 22 | 0.00017533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1069-15_0_4_line_23 |  | 22 | 26 | 0.00018618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1069-15_0_4_line_24 |  | 23 | 24 | 0.0035449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1069-15_0_4_line_25 |  | 24 | 25 | 0.028101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1069-15_0_4_trafo_9 | 0.63 MVA 20/0.4 kV | 27 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2674099.592 | 1210198.6901 | 2674119.3331 | 1210196.2367 | 2674120.9206 | 1210197.5085
1 | 2673979.8346 | 1210123.0466 | 2674099.592 | 1210198.6901
2 | 2674124.7934 | 1210200.6113 | 2674120.9206 | 1210197.5085
3 | 2673979.8346 | 1210123.0466 | 2673975.7661 | 1210124.8438 | 2673966.9633 | 1210127.9922 | 2673962.7124 | 1210125.7047 | 2673957.686 | 1210119.7498 | 2673953.536 | 1210109.3252 | 2673948.2782 | 1210089.5476 | 2673944.0636 | 1210081.4389
4 | 2674124.7934 | 1210200.6113 | 2674129.9897 | 1210204.7744 | 2674135.4189 | 1210224.9246
5 | 2673938.767 | 1210075.6432 | 2673943.4973 | 1210080.3492 | 2673944.0636 | 1210081.4389
6 | 2674139.8273 | 1210241.2863 | 2674135.4189 | 1210224.9246
7 | 2674226.1709 | 1210128.5129 | 2674225.8592 | 1210128.9517
8 | 2674225.8592 | 1210128.9517 | 2674164.1156 | 1210215.8943
9 | 2674229.4161 | 1210123.9433 | 2674226.1709 | 1210128.5129
10 | 2674139.8273 | 1210241.2863 | 2674147.3436 | 1210239.5119 | 2674164.1156 | 1210215.8943
11 | 2673983.8297 | 1209919.0253 | 2674134.3289 | 1209941.7912
12 | 2673983.8297 | 1209919.0253 | 2673972.3751 | 1209934.9377 | 2673968.3527 | 1209950.3754 | 2673964.536 | 1209973.8028
13 | 2673964.536 | 1209973.8028 | 2673963.0708 | 1209982.797 | 2673960.1893 | 1209995.7645
14 | 2673951.4465 | 1210031.9239 | 2673955.1252 | 1210018.5544 | 2673960.1893 | 1209995.7645
15 | 2673951.4465 | 1210031.9239 | 2673947.7552 | 1210045.3389
16 | 2674231.6308 | 1210120.8246 | 2674229.4161 | 1210123.9433
17 | 2674233.8958 | 1210117.6353 | 2674231.6308 | 1210120.8246
18 | 2674233.9703 | 1210117.5304 | 2674233.8958 | 1210117.6353
19 | 2674245.0861 | 1210101.8779 | 2674253.1371 | 1210090.5411
20 | 2674245.0861 | 1210101.8779 | 2674234.2383 | 1210117.153
21 | 2674234.2383 | 1210117.153 | 2674234.1796 | 1210117.2357
22 | 2674234.1796 | 1210117.2357 | 2674234.0781 | 1210117.3786
23 | 2674234.0781 | 1210117.3786 | 2674233.9703 | 1210117.5304
24 | 2673938.767 | 1210075.6432 | 2673940.169 | 1210072.3873
25 | 2673940.169 | 1210072.3873 | 2673940.5671 | 1210071.4629 | 2673947.7552 | 1210045.3389

## bus_geodata
| x | y | coords
0 | 2674099.592 | 1210198.6901
1 | 2674120.9206 | 1210197.5085
2 | 2673979.8346 | 1210123.0466
3 | 2674124.7934 | 1210200.6113
4 | 2673944.0636 | 1210081.4389
5 | 2674135.4189 | 1210224.9246
6 | 2674225.8592 | 1210128.9517
7 | 2674226.1709 | 1210128.5129
8 | 2674164.1156 | 1210215.8943
9 | 2674139.8273 | 1210241.2863
10 | 2674134.3289 | 1209941.7912
11 | 2673983.8297 | 1209919.0253
12 | 2673964.536 | 1209973.8028
13 | 2673960.1893 | 1209995.7645
14 | 2673951.4465 | 1210031.9239
15 | 2674229.4161 | 1210123.9433
16 | 2674231.6308 | 1210120.8246
17 | 2674233.8958 | 1210117.6353
18 | 2674253.1371 | 1210090.5411
19 | 2674245.0861 | 1210101.8779
20 | 2674234.2383 | 1210117.153
21 | 2674234.1796 | 1210117.2357
22 | 2674234.0781 | 1210117.3786
23 | 2673938.767 | 1210075.6432
24 | 2673940.169 | 1210072.3873
25 | 2673947.7552 | 1210045.3389
26 | 2674233.9703 | 1210117.5304
27 | 2674164.1156 | 1210215.8943

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98828 | -0.22367 | 0.030605 | 0.0076703
1 | 0.9893 | -0.20392 | 0.0052877 | 0.0013252
2 | 0.98365 | -0.31311 | 0.0071099 | 0.0017819
3 | 0.98955 | -0.19923 | 0.011648 | 0.0029194
4 | 0.97969 | -0.39012 | 0.0032386 | 0.00081166
5 | 0.99105 | -0.17036 | 0.0029263 | 0.0007334
6 | 1 | 0 | -0.36396 | -0.091674
7 | 0.99994 | -0.0011219 | 0.024899 | 0.0062402
8 | 0.99404 | -0.11304 | 0 | 0
9 | 0.99199 | -0.1522 | 0 | 0
10 | 0.97458 | -0.49063 | 0.0046896 | 0.0011753
11 | 0.97524 | -0.47754 | 0 | 0
12 | 0.9755 | -0.47244 | 0.010061 | 0.0025214
13 | 0.97581 | -0.46638 | 0.022203 | 0.0055645
14 | 0.97709 | -0.44124 | 0.0083058 | 0.0020816
15 | 0.9994 | -0.011594 | 0.027561 | 0.0069074
16 | 0.99907 | -0.017827 | 0.025185 | 0.006312
17 | 0.99879 | -0.023345 | 0.025147 | 0.0063025
18 | 0.99774 | -0.043503 | 0.023715 | 0.0059434
19 | 0.99804 | -0.037731 | 0.016969 | 0.0042529
20 | 0.99873 | -0.024403 | 0.023255 | 0.0058283
21 | 0.99874 | -0.02429 | 0.025361 | 0.006356
22 | 0.99875 | -0.024016 | 0.022884 | 0.0057353
23 | 0.97925 | -0.39874 | 0 | 0
24 | 0.97906 | -0.40261 | 0.007043 | 0.0017651
25 | 0.97767 | -0.42975 | 0.0077681 | 0.0019469
26 | 0.99877 | -0.023651 | 0.02418 | 0.0060601
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.10175 | -0.025772 | 0.10184 | 0.025834 | 9.6609e-05 | 6.1267e-05 | 0.15329 | 0.15329 | 0.15329 | 0.98828 | -0.22367 | 0.9893 | -0.20392 | 21.0565
1 | 0.07114 | 0.018102 | -0.070835 | -0.01791 | 0.00030528 | 0.00019176 | 0.10721 | 0.10721 | 0.10721 | 0.98828 | -0.22367 | 0.98365 | -0.31311 | 14.727
2 | -0.10713 | -0.027159 | 0.10715 | 0.027174 | 2.4191e-05 | 1.5355e-05 | 0.16124 | 0.16124 | 0.16124 | 0.9893 | -0.20392 | 0.98955 | -0.19923 | 22.149
3 | 0.063725 | 0.016128 | -0.063491 | -0.015979 | 0.0002346 | 0.00014929 | 0.096457 | 0.096457 | 0.096457 | 0.98365 | -0.31311 | 0.97969 | -0.39012 | 26.4992
4 | -0.1188 | -0.030094 | 0.11897 | 0.030199 | 0.00016493 | 0.00010485 | 0.17876 | 0.17876 | 0.17876 | 0.98955 | -0.19923 | 0.99105 | -0.17036 | 24.555
5 | 0.060252 | 0.015168 | -0.060227 | -0.015152 | 2.4825e-05 | 1.5789e-05 | 0.091538 | 0.091538 | 0.091538 | 0.97969 | -0.39012 | 0.97925 | -0.39874 | 25.1479
6 | -0.12189 | -0.030932 | 0.122 | 0.031 | 0.00010658 | 6.7775e-05 | 0.18315 | 0.18315 | 0.18315 | 0.99105 | -0.17036 | 0.99199 | -0.1522 | 25.1585
7 | 0.23941 | 0.060101 | -0.2394 | -0.060093 | 1.2811e-05 | 8.1848e-06 | 0.35628 | 0.35628 | 0.35628 | 1 | 0 | 0.99994 | -0.0011219 | 48.94
8 | 0.1229 | 0.031573 | -0.12223 | -0.031146 | 0.00067071 | 0.00042647 | 0.18315 | 0.18315 | 0.18315 | 1 | 0 | 0.99404 | -0.11304 | 25.1585
9 | 0.2145 | 0.053853 | -0.21439 | -0.053784 | 0.00010709 | 6.8393e-05 | 0.31923 | 0.31923 | 0.31923 | 0.99994 | -0.0011219 | 0.9994 | -0.011594 | 43.8505
10 | 0.12223 | 0.031146 | -0.122 | -0.031 | 0.00023049 | 0.00014657 | 0.18315 | 0.18315 | 0.18315 | 0.99404 | -0.11304 | 0.99199 | -0.1522 | 25.1585
11 | -0.0046896 | -0.0011753 | 0.0046925 | 0.0011753 | 2.9261e-06 | -2.5259e-08 | 0.0071602 | 0.0071595 | 0.0071602 | 0.97458 | -0.49063 | 0.97524 | -0.47754 | 1.9671
12 | -0.0046925 | -0.0011753 | 0.0046937 | 0.0011753 | 1.1397e-06 | -1.0636e-08 | 0.0071595 | 0.0071593 | 0.0071595 | 0.97524 | -0.47754 | 0.9755 | -0.47244 | 1.9669
13 | -0.014754 | -0.0036967 | 0.014758 | 0.0036991 | 4.2539e-06 | 2.4428e-06 | 0.022505 | 0.022505 | 0.022505 | 0.9755 | -0.47244 | 0.97581 | -0.46638 | 6.1828
14 | -0.036961 | -0.0092637 | 0.037006 | 0.0092916 | 4.433e-05 | 2.7906e-05 | 0.056363 | 0.056362 | 0.056363 | 0.97581 | -0.46638 | 0.97709 | -0.44124 | 15.4842
15 | -0.045311 | -0.011373 | 0.045336 | 0.011389 | 2.4849e-05 | 1.5729e-05 | 0.069011 | 0.069011 | 0.069011 | 0.97709 | -0.44124 | 0.97767 | -0.42975 | 18.9591
16 | 0.18683 | 0.046877 | -0.18678 | -0.046841 | 5.5507e-05 | 3.5424e-05 | 0.2782 | 0.2782 | 0.2782 | 0.9994 | -0.011594 | 0.99907 | -0.017827 | 38.2137
17 | 0.16159 | 0.040529 | -0.16155 | -0.040502 | 4.2489e-05 | 2.709e-05 | 0.24068 | 0.24069 | 0.24069 | 0.99907 | -0.017827 | 0.99879 | -0.023345 | 33.0611
18 | 0.1364 | 0.0342 | -0.1364 | -0.034199 | 1.9919e-06 | 1.2732e-06 | 0.20322 | 0.20322 | 0.20322 | 0.99879 | -0.023345 | 0.99877 | -0.023651 | 55.8296
19 | -0.023715 | -0.0059434 | 0.023721 | 0.0059474 | 6.5223e-06 | 3.9927e-06 | 0.035368 | 0.035368 | 0.035368 | 0.99774 | -0.043503 | 0.99804 | -0.037731 | 9.7164
20 | -0.04069 | -0.0102 | 0.040716 | 0.010217 | 2.5858e-05 | 1.6304e-05 | 0.060668 | 0.060668 | 0.060668 | 0.99804 | -0.037731 | 0.99873 | -0.024403 | 16.6669
21 | -0.063971 | -0.016045 | 0.063972 | 0.016045 | 3.4519e-07 | 2.1959e-07 | 0.095315 | 0.095315 | 0.095315 | 0.99873 | -0.024403 | 0.99874 | -0.02429 | 26.1856
22 | -0.089332 | -0.022401 | 0.089334 | 0.022402 | 1.1648e-06 | 7.4316e-07 | 0.1331 | 0.1331 | 0.1331 | 0.99874 | -0.02429 | 0.99875 | -0.024016 | 36.5661
23 | -0.11222 | -0.028137 | 0.11222 | 0.028138 | 1.9517e-06 | 1.2467e-06 | 0.1672 | 0.1672 | 0.1672 | 0.99875 | -0.024016 | 0.99877 | -0.023651 | 45.9327
24 | 0.060227 | 0.015152 | -0.060216 | -0.015145 | 1.1139e-05 | 7.0843e-06 | 0.091538 | 0.091538 | 0.091538 | 0.97925 | -0.39874 | 0.97906 | -0.40261 | 25.1479
25 | 0.053173 | 0.01338 | -0.053104 | -0.013336 | 6.8857e-05 | 4.3716e-05 | 0.080834 | 0.080834 | 0.080834 | 0.97906 | -0.40261 | 0.97767 | -0.42975 | 22.2072

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38856 | 0.097838

## res_load
| p_mw | q_mvar
0 | 0.030605 | 0.0076703
1 | 0.0052877 | 0.0013252
2 | 0.0071099 | 0.0017819
3 | 0.011648 | 0.0029194
4 | 0.0032386 | 0.00081166
5 | 0.0029263 | 0.0007334
6 | 0.024595 | 0.0061642
7 | 0.024899 | 0.0062402
8 | 0.0046896 | 0.0011753
9 | 0.010061 | 0.0025214
10 | 0.022203 | 0.0055645
11 | 0.0083058 | 0.0020816
12 | 0.027561 | 0.0069074
13 | 0.025185 | 0.006312
14 | 0.025147 | 0.0063025
15 | 0.023715 | 0.0059434
16 | 0.016969 | 0.0042529
17 | 0.023255 | 0.0058283
18 | 0.025361 | 0.006356
19 | 0.022884 | 0.0057353
20 | 0.007043 | 0.0017651
21 | 0.0077681 | 0.0019469
22 | 0.02418 | 0.0060601

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1