## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1069-4_1_4_node_9 | 0.4 | n |  | TRUE
1 | bus_LV_1069-4_1_4_node_10 | 0.4 | n |  | TRUE
2 | bus_LV_1069-4_1_4_node_11 | 0.4 | n |  | TRUE
3 | bus_LV_1069-4_1_4_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_1069-4_1_4_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_1069-4_1_4_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_1069-4_1_4_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_1069-4_1_4_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_1069-4_1_4_node_77 | 0.4 | n |  | TRUE
9 | bus_LV_1069-4_1_4_node_133 | 0.4 | n |  | TRUE
10 | bus_LV_1069-4_1_4_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_1069-4_1_4_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_1069-4_1_4_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_1069-4_1_4_node_49 | 0.4 | n |  | TRUE
14 | bus_LV_1069-4_1_4_node_63 | 0.4 | n |  | TRUE
15 | bus_LV_1069-4_1_4_node_75 | 0.4 | n |  | TRUE
16 | bus_LV_1069-4_1_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1069-4_1_4_node_105 | 0.4 | n |  | TRUE
18 | bus_LV_1069-4_1_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1069-4_1_4_node_206 | 0.4 | n |  | TRUE
20 | bus_LV_1069-4_1_4_node_61 | 0.4 | n |  | TRUE
21 | bus_LV_1069-4_1_4_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_1069-4_1_4_node_165 | 0.4 | n |  | TRUE
23 | bus_LV_1069-4_1_4_node_76 | 0.4 | n |  | TRUE
24 | bus_LV_1069-4_1_4_node_114 | 0.4 | n |  | TRUE
25 | bus_LV_1069-4_1_4_node_176 | 0.4 | n |  | TRUE
26 | bus_LV_1069-4_1_4_node_51 | 0.4 | n |  | TRUE
27 | bus_LV_1069-4_1_4_node_188 | 0.4 | n |  | TRUE
28 | bus_LV_1069-4_1_4_node_189 | 0.4 | n |  | TRUE
29 | bus_LV_1069-4_1_4_node_190 | 0.4 | n |  | TRUE
30 | bus_LV_1069-4_1_4_node_191 | 0.4 | n |  | TRUE
31 | bus_LV_1069-4_1_4_node_117 | 0.4 | n |  | TRUE
32 | bus_LV_1069-4_1_4_node_194 | 0.4 | n |  | TRUE
33 | bus_LV_1069-4_1_4_node_195 | 0.4 | n |  | TRUE
34 | bus_LV_1069-4_1_4_node_116 | 0.4 | n |  | TRUE
35 | bus_LV_1069-4_1_4_node_200 | 0.4 | n |  | TRUE
36 | bus_LV_1069-4_1_4_node_175 | 0.4 | n |  | TRUE
37 | bus_LV_1069-4_1_4_node_174 | 0.4 | n |  | TRUE
38 | bus_LV_1069-4_1_4_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_1069-4_1_4_node_128 | 0.4 | n |  | TRUE
40 | bus_LV_1069-4_1_4_node_48 | 0.4 | n |  | TRUE
41 | bus_LV_1069-4_1_4_node_50 | 0.4 | n |  | TRUE
42 | bus_LV_1069-4_1_4_node_60 | 0.4 | n |  | TRUE
43 | bus_LV_1069-4_1_4_node_62 | 0.4 | n |  | TRUE
44 | bus_LV_1069-4_1_4_node_146 | 0.4 | n |  | TRUE
45 | bus_LV_1069-4_1_4_node_124 | 0.4 | n |  | TRUE
46 | bus_LV_1069-4_1_4_node_131 | 0.4 | n |  | TRUE
47 | bus_LV_1069-4_1_4_node_136 | 0.4 | n |  | TRUE
48 | bus_LV_1069-4_1_4_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_1069-4_1_4_node_196 | 0.4 | n |  | TRUE
50 | bus_LV_1069-4_1_4_node_35 | 0.4 | n |  | TRUE
51 | bus_LV_1069-4_1_4_node_138 | 0.4 | n |  | TRUE
52 | bus_LV_1069-4_1_4_node_139 | 0.4 | n |  | TRUE
53 | bus_LV_1069-4_1_4_node_144 | 0.4 | n |  | TRUE
54 | bus_LV_1069-4_1_4_node_102 | 0.4 | n |  | TRUE
55 | bus_LV_1069-4_1_4_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_1069-4_1_4_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_1069-4_1_4_node_181 | 0.4 | n |  | TRUE
58 | bus_LV_1069-4_1_4_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_1069-4_1_4_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_1069-4_1_4_node_216 | 0.4 | n |  | TRUE
61 | bus_LV_1069-4_1_4_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_1069-4_1_4_node_215 | 0.4 | n |  | TRUE
63 | bus_LV_1069-4_1_4_node_217 | 0.4 | n |  | TRUE
64 | bus_LV_1069-4_1_4_node_93 | 0.4 | n |  | TRUE
65 | bus_LV_1069-4_1_4_node_94 | 0.4 | n |  | TRUE
66 | bus_LV_1069-4_1_4_node_95 | 0.4 | n |  | TRUE
67 | bus_LV_1069-4_1_4_node_115 | 0.4 | n |  | TRUE
68 | bus_LV_1069-4_1_4_node_110 | 0.4 | n |  | TRUE
69 | bus_LV_1069-4_1_4_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_1069-4_1_4_node_45 | 0.4 | n |  | TRUE
71 | bus_LV_1069-4_1_4_node_46 | 0.4 | n |  | TRUE
72 | bus_LV_1069-4_1_4_node_47 | 0.4 | n |  | TRUE
73 | bus_LV_1069-4_1_4_node_53 | 0.4 | n |  | TRUE
74 | bus_LV_1069-4_1_4_node_145 | 0.4 | n |  | TRUE
75 | bus_LV_1069-4_1_4_node_202 | 0.4 | n |  | TRUE
76 | bus_LV_1069-4_1_4_node_83 | 0.4 | n |  | TRUE
77 | bus_LV_1069-4_1_4_node_143 | 0.4 | n |  | TRUE
78 | bus_LV_1069-4_1_4_node_135 | 0.4 | n |  | TRUE
79 | bus_LV_1069-4_1_4_node_134 | 0.4 | n |  | TRUE
80 | bus_LV_1069-4_1_4_node_97 | 0.4 | n |  | TRUE
81 | bus_LV_1069-4_1_4_node_166 | 0.4 | n |  | TRUE
82 | bus_LV_1069-4_1_4_node_78 | 0.4 | n |  | TRUE
83 | bus_LV_1069-4_1_4_node_79 | 0.4 | n |  | TRUE
84 | bus_LV_1069-4_1_4_node_80 | 0.4 | n |  | TRUE
85 | bus_LV_1069-4_1_4_node_81 | 0.4 | n |  | TRUE
86 | bus_LV_1069-4_1_4_node_82 | 0.4 | n |  | TRUE
87 | bus_LV_1069-4_1_4_node_140 | 0.4 | n |  | TRUE
88 | bus_LV_1069-4_1_4_node_103 | 0.4 | n |  | TRUE
89 | bus_LV_1069-4_1_4_node_121 | 0.4 | n |  | TRUE
90 | bus_LV_1069-4_1_4_node_141 | 0.4 | n |  | TRUE
91 | bus_LV_1069-4_1_4_node_104 | 0.4 | n |  | TRUE
92 | bus_LV_1069-4_1_4_node_96 | 0.4 | n |  | TRUE
93 | bus_LV_1069-4_1_4_node_106 | 0.4 | n |  | TRUE
94 | bus_LV_1069-4_1_4_node_107 | 0.4 | n |  | TRUE
95 | bus_LV_1069-4_1_4_node_108 | 0.4 | n |  | TRUE
96 | bus_LV_1069-4_1_4_node_109 | 0.4 | n |  | TRUE
97 | bus_LV_1069-4_1_4_node_111 | 0.4 | n |  | TRUE
98 | bus_LV_1069-4_1_4_node_142 | 0.4 | n |  | TRUE
99 | bus_LV_1069-4_1_4_node_192 | 0.4 | n |  | TRUE
100 | bus_LV_1069-4_1_4_node_167 | 0.4 | n |  | TRUE
101 | bus_LV_1069-4_1_4_node_180 | 0.4 | n |  | TRUE
102 | bus_LV_1069-4_1_4_node_186 | 0.4 | n |  | TRUE
103 | bus_LV_1069-4_1_4_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_1069-4_1_4_node_209 | 0.4 | n |  | TRUE
105 | bus_LV_1069-4_1_4_node_210 | 0.4 | n |  | TRUE
106 | bus_LV_1069-4_1_4_node_123 | 0.4 | n |  | TRUE
107 | bus_LV_1069-4_1_4_node_125 | 0.4 | n |  | TRUE
108 | bus_LV_1069-4_1_4_node_127 | 0.4 | n |  | TRUE
109 | bus_LV_1069-4_1_4_node_199 | 0.4 | n |  | TRUE
110 | bus_LV_1069-4_1_4_node_184 | 0.4 | n |  | TRUE
111 | bus_LV_1069-4_1_4_node_198 | 0.4 | n |  | TRUE
112 | bus_LV_1069-4_1_4_node_129 | 0.4 | n |  | TRUE
113 | bus_LV_1069-4_1_4_node_130 | 0.4 | n |  | TRUE
114 | bus_LV_1069-4_1_4_node_132 | 0.4 | n |  | TRUE
115 | bus_LV_1069-4_1_4_node_182 | 0.4 | n |  | TRUE
116 | bus_LV_1069-4_1_4_node_183 | 0.4 | n |  | TRUE
117 | bus_LV_1069-4_1_4_node_197 | 0.4 | n |  | TRUE
118 | bus_MV_1_0_node_27 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1069-4_1_4_load_9 | 0 | 0.0039877 | 0.00099941 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1069-4_1_4_load_10 | 1 | 0.0038221 | 0.00095792 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1069-4_1_4_load_13 | 4 | 0.0036423 | 0.00091284 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1069-4_1_4_load_14 | 5 | 0.0038869 | 0.00097415 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1069-4_1_4_load_20 | 6 | 0.0032115 | 0.00080489 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1069-4_1_4_load_21 | 7 | 0.0031216 | 0.00078234 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1069-4_1_4_load_133 | 9 | 0.0064348 | 0.0016127 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1069-4_1_4_load_24 | 11 | 0.017171 | 0.0043035 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1069-4_1_4_load_25 | 12 | 0.003107 | 0.00077869 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1069-4_1_4_load_49 | 13 | 0.0025307 | 0.00063425 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1069-4_1_4_load_75 | 15 | 0.0041641 | 0.0010436 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1069-4_1_4_load_23 | 16 | 0.0025775 | 0.00064598 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1069-4_1_4_load_105 | 17 | 0.0047653 | 0.0011943 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1069-4_1_4_load_16 | 18 | 0.0011665 | 0.00029235 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1069-4_1_4_load_206 | 19 | 0.0018634 | 0.00046701 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1069-4_1_4_load_61 | 20 | 0.0021807 | 0.00054653 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1069-4_1_4_load_59 | 21 | 0.0049622 | 0.0012436 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1069-4_1_4_load_165 | 22 | 0.0022086 | 0.00055352 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1069-4_1_4_load_76 | 23 | 0.0025395 | 0.00063645 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1069-4_1_4_load_114 | 24 | 0.0041374 | 0.0010369 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1069-4_1_4_load_176 | 25 | 0.0034789 | 0.00087189 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1069-4_1_4_load_51 | 26 | 0.0034296 | 0.00085955 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1069-4_1_4_load_188 | 27 | 0.0013925 | 0.00034898 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1069-4_1_4_load_189 | 28 | 0.0015014 | 0.00037629 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1069-4_1_4_load_190 | 29 | 0.00060308 | 0.00015114 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1069-4_1_4_load_191 | 30 | 0.0022808 | 0.00057163 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1069-4_1_4_load_117 | 31 | 0.00055912 | 0.00014013 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1069-4_1_4_load_194 | 32 | 0.0021929 | 0.0005496 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1069-4_1_4_load_195 | 33 | 0.0047425 | 0.0011886 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1069-4_1_4_load_116 | 34 | 0.0020807 | 0.00052147 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1069-4_1_4_load_200 | 35 | 0.0026085 | 0.00065375 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1069-4_1_4_load_175 | 36 | 0.0025562 | 0.00064064 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1069-4_1_4_load_174 | 37 | 0.0029716 | 0.00074476 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1069-4_1_4_load_38 | 38 | 0.0034735 | 0.00087054 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1069-4_1_4_load_128 | 39 | 0.0066903 | 0.0016768 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1069-4_1_4_load_48 | 40 | 0.0029188 | 0.00073152 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1069-4_1_4_load_50 | 41 | 0.0025339 | 0.00063506 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1069-4_1_4_load_60 | 42 | 0.0032354 | 0.00081086 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1069-4_1_4_load_62 | 43 | 0.0038359 | 0.00096137 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1069-4_1_4_load_146 | 44 | 0.0042371 | 0.0010619 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1069-4_1_4_load_124 | 45 | 0.0035864 | 0.00089883 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1069-4_1_4_load_131 | 46 | 0.004226 | 0.0010591 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1069-4_1_4_load_136 | 47 | 0.0018102 | 0.00045368 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1069-4_1_4_load_52 | 48 | 0.0021437 | 0.00053725 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1069-4_1_4_load_139 | 52 | 0.0034348 | 0.00086085 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1069-4_1_4_load_144 | 53 | 0.0026043 | 0.00065271 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1069-4_1_4_load_102 | 54 | 0.0026259 | 0.00065811 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1069-4_1_4_load_39 | 55 | 0.0021892 | 0.00054867 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1069-4_1_4_load_40 | 56 | 0.0032561 | 0.00081606 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1069-4_1_4_load_181 | 57 | 0.0045598 | 0.0011428 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1069-4_1_4_load_41 | 58 | 0.00077836 | 0.00019507 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1069-4_1_4_load_42 | 59 | 0.003072 | 0.00076991 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1069-4_1_4_load_43 | 61 | 0.0014054 | 0.00035222 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1069-4_1_4_load_215 | 62 | 0.0013741 | 0.00034437 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1069-4_1_4_load_217 | 63 | 0.00064106 | 0.00016066 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1069-4_1_4_load_93 | 64 | 0.004023 | 0.0010083 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1069-4_1_4_load_94 | 65 | 0.0041779 | 0.0010471 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1069-4_1_4_load_95 | 66 | 0.0022451 | 0.00056267 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1069-4_1_4_load_115 | 67 | 0.00055746 | 0.00013971 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1069-4_1_4_load_44 | 69 | 0.0011728 | 0.00029392 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1069-4_1_4_load_45 | 70 | 0.0033489 | 0.00083931 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1069-4_1_4_load_46 | 71 | 0.0014013 | 0.00035121 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1069-4_1_4_load_47 | 72 | 0.0015711 | 0.00039376 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1069-4_1_4_load_53 | 73 | 0.0020929 | 0.00052452 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1069-4_1_4_load_145 | 74 | 0.0030144 | 0.00075547 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1069-4_1_4_load_202 | 75 | 0.0040193 | 0.0010073 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1069-4_1_4_load_83 | 76 | 0.0053291 | 0.0013356 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1069-4_1_4_load_143 | 77 | 0.0038054 | 0.00095373 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1069-4_1_4_load_135 | 78 | 0.0030886 | 0.00077407 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1069-4_1_4_load_134 | 79 | 0.0019107 | 0.00047887 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1069-4_1_4_load_97 | 80 | 0.0022464 | 0.000563 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1069-4_1_4_load_166 | 81 | 0.0027419 | 0.00068718 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1069-4_1_4_load_78 | 82 | 0.0029413 | 0.00073716 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1069-4_1_4_load_79 | 83 | 0.0043089 | 0.0010799 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1069-4_1_4_load_81 | 85 | 0.00098984 | 0.00024808 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1069-4_1_4_load_82 | 86 | 0.0022466 | 0.00056304 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1069-4_1_4_load_140 | 87 | 0.0017757 | 0.00044502 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1069-4_1_4_load_103 | 88 | 0.0041197 | 0.0010325 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1069-4_1_4_load_121 | 89 | 0.004876 | 0.0012221 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1069-4_1_4_load_141 | 90 | 0.0026033 | 0.00065244 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1069-4_1_4_load_104 | 91 | 0.0027708 | 0.00069442 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1069-4_1_4_load_96 | 92 | 0.0028812 | 0.00072209 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1069-4_1_4_load_106 | 93 | 0.00075151 | 0.00018835 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1069-4_1_4_load_107 | 94 | 0.00092559 | 0.00023198 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1069-4_1_4_load_109 | 96 | 0.0014755 | 0.0003698 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1069-4_1_4_load_111 | 97 | 0.00077364 | 0.00019389 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1069-4_1_4_load_142 | 98 | 0.0030456 | 0.00076329 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1069-4_1_4_load_192 | 99 | 0.0018567 | 0.00046532 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1069-4_1_4_load_167 | 100 | 0.0038586 | 0.00096705 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1069-4_1_4_load_180 | 101 | 0.0035069 | 0.00087892 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1069-4_1_4_load_186 | 102 | 0.0023847 | 0.00059766 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1069-4_1_4_load_100 | 103 | 0.0038825 | 0.00097304 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1069-4_1_4_load_209 | 104 | 0.0051904 | 0.0013008 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1069-4_1_4_load_210 | 105 | 0.0022783 | 0.00057101 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1069-4_1_4_load_123 | 106 | 0.004259 | 0.0010674 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1069-4_1_4_load_125 | 107 | 0.0027837 | 0.00069765 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1069-4_1_4_load_199 | 109 | 0.0031127 | 0.00078011 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1069-4_1_4_load_184 | 110 | 0.0027889 | 0.00069898 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1069-4_1_4_load_198 | 111 | 0.0019648 | 0.00049242 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1069-4_1_4_load_129 | 112 | 0.0020221 | 0.00050679 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1069-4_1_4_load_130 | 113 | 0.0098959 | 0.0024802 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1069-4_1_4_load_132 | 114 | 0.0064065 | 0.0016056 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1069-4_1_4_load_182 | 115 | 0.011264 | 0.0028231 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1069-4_1_4_load_183 | 116 | 0.0028212 | 0.00070706 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1069-4_1_4_load_197 | 117 | 0.0025972 | 0.00065093 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1069-4_1_4_line_0 |  | 0 | 1 | 0.032367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_1069-4_1_4_line_1 |  | 0 | 2 | 0.015032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_1069-4_1_4_line_2 |  | 1 | 3 | 0.019592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1069-4_1_4_line_3 |  | 2 | 4 | 0.046632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1069-4_1_4_line_4 |  | 2 | 5 | 0.023975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1069-4_1_4_line_5 |  | 3 | 8 | 0.056266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1069-4_1_4_line_6 |  | 5 | 9 | 0.028749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1069-4_1_4_line_7 |  | 6 | 7 | 0.024931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1069-4_1_4_line_8 |  | 7 | 16 | 0.018273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1069-4_1_4_line_9 |  | 8 | 14 | 0.021171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1069-4_1_4_line_10 |  | 8 | 15 | 0.013358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1069-4_1_4_line_11 |  | 9 | 17 | 0.029565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1069-4_1_4_line_12 |  | 10 | 11 | 0.025234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1069-4_1_4_line_13 |  | 10 | 12 | 0.036446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1069-4_1_4_line_14 |  | 10 | 13 | 0.041492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1069-4_1_4_line_15 |  | 11 | 38 | 0.014996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1069-4_1_4_line_16 |  | 12 | 39 | 0.032191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1069-4_1_4_line_17 |  | 13 | 26 | 0.029218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1069-4_1_4_line_18 |  | 13 | 40 | 0.00073769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1069-4_1_4_line_19 |  | 14 | 22 | 0.074082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1069-4_1_4_line_20 |  | 14 | 20 | 0.0065492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1069-4_1_4_line_21 |  | 15 | 23 | 0.049414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1069-4_1_4_line_22 |  | 16 | 35 | 0.012545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1069-4_1_4_line_23 |  | 17 | 91 | 0.018768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1069-4_1_4_line_24 |  | 18 | 19 | 0.045969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1069-4_1_4_line_25 |  | 19 | 52 | 0.022352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1069-4_1_4_line_26 |  | 20 | 21 | 0.030124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1069-4_1_4_line_27 |  | 21 | 42 | 0.018048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1069-4_1_4_line_28 |  | 22 | 81 | 0.014941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1069-4_1_4_line_29 |  | 24 | 25 | 0.027131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1069-4_1_4_line_30 |  | 24 | 26 | 0.04016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1069-4_1_4_line_31 |  | 25 | 36 | 0.0033704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1069-4_1_4_line_32 |  | 27 | 28 | 0.016583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1069-4_1_4_line_33 |  | 27 | 29 | 0.01245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1069-4_1_4_line_34 |  | 28 | 30 | 0.010184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1069-4_1_4_line_35 |  | 29 | 31 | 0.022406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1069-4_1_4_line_36 |  | 31 | 68 | 0.017571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1069-4_1_4_line_37 |  | 32 | 33 | 0.044218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1069-4_1_4_line_38 |  | 32 | 34 | 0.030976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1069-4_1_4_line_39 |  | 34 | 68 | 0.022135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1069-4_1_4_line_40 |  | 35 | 37 | 0.029557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1069-4_1_4_line_41 |  | 36 | 37 | 0.024895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1069-4_1_4_line_42 |  | 39 | 112 | 0.025792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1069-4_1_4_line_43 |  | 39 | 113 | 0.0084449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1069-4_1_4_line_44 |  | 40 | 41 | 0.036451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_1069-4_1_4_line_45 |  | 41 | 48 | 0.0070999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_1069-4_1_4_line_46 |  | 42 | 43 | 0.017154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1069-4_1_4_line_47 |  | 43 | 78 | 0.0098766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1069-4_1_4_line_48 |  | 44 | 45 | 0.06448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1069-4_1_4_line_49 |  | 44 | 46 | 0.026729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1069-4_1_4_line_50 |  | 44 | 47 | 0.020772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1069-4_1_4_line_51 |  | 45 | 103 | 0.057288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1069-4_1_4_line_52 |  | 45 | 106 | 0.035504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1069-4_1_4_line_53 |  | 46 | 112 | 0.0037199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1069-4_1_4_line_54 |  | 48 | 49 | 0.064662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_1069-4_1_4_line_55 |  | 49 | 75 | 0.054239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1069-4_1_4_line_56 |  | 49 | 76 | 0.046621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_1069-4_1_4_line_57 |  | 50 | 51 | 0.040566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1069-4_1_4_line_58 |  | 50 | 52 | 0.018762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1069-4_1_4_line_59 |  | 51 | 53 | 0.013508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1069-4_1_4_line_60 |  | 51 | 54 | 0.011217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1069-4_1_4_line_61 |  | 53 | 77 | 0.015744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1069-4_1_4_line_62 |  | 54 | 103 | 0.020146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1069-4_1_4_line_63 |  | 55 | 56 | 0.030251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1069-4_1_4_line_64 |  | 56 | 57 | 0.059067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1069-4_1_4_line_65 |  | 57 | 115 | 0.020506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1069-4_1_4_line_66 |  | 58 | 59 | 0.0051846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1069-4_1_4_line_67 |  | 58 | 60 | 0.22441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1069-4_1_4_line_68 |  | 59 | 61 | 0.01765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1069-4_1_4_line_69 |  | 60 | 63 | 0.057143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1069-4_1_4_line_70 |  | 60 | 62 | 0.041103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1069-4_1_4_line_71 |  | 61 | 67 | 0.015024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1069-4_1_4_line_72 |  | 64 | 65 | 0.020555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1069-4_1_4_line_73 |  | 64 | 66 | 0.033494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1069-4_1_4_line_74 |  | 65 | 92 | 0.021005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1069-4_1_4_line_75 |  | 66 | 80 | 0.0071691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1069-4_1_4_line_76 |  | 67 | 68 | 0.016603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1069-4_1_4_line_77 |  | 68 | 95 | 0.009837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1069-4_1_4_line_78 |  | 69 | 70 | 0.017056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1069-4_1_4_line_79 |  | 69 | 71 | 0.013404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1069-4_1_4_line_80 |  | 70 | 72 | 0.0073567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1069-4_1_4_line_81 |  | 72 | 73 | 0.026406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1069-4_1_4_line_82 |  | 73 | 74 | 0.0019015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1069-4_1_4_line_83 |  | 74 | 77 | 0.017263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1069-4_1_4_line_84 |  | 75 | 104 | 0.028159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1069-4_1_4_line_85 |  | 75 | 89 | 0.060539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1069-4_1_4_line_86 |  | 76 | 84 | 0.013778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_1069-4_1_4_line_87 |  | 78 | 79 | 0.052762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1069-4_1_4_line_88 |  | 79 | 97 | 0.026948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1069-4_1_4_line_89 |  | 80 | 89 | 0.03827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1069-4_1_4_line_90 |  | 81 | 100 | 0.028406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1069-4_1_4_line_91 |  | 82 | 83 | 0.0024351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1069-4_1_4_line_92 |  | 82 | 84 | 0.02257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1069-4_1_4_line_93 |  | 83 | 85 | 0.003683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1069-4_1_4_line_94 |  | 84 | 86 | 0.015649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_1069-4_1_4_line_95 |  | 85 | 87 | 0.036142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1069-4_1_4_line_96 |  | 86 | 88 | 0.01233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_1069-4_1_4_line_97 |  | 87 | 90 | 0.006209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1069-4_1_4_line_98 |  | 88 | 91 | 0.019378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_1069-4_1_4_line_99 |  | 90 | 98 | 0.01472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1069-4_1_4_line_100 |  | 92 | 102 | 0.0033587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1069-4_1_4_line_101 |  | 93 | 94 | 0.018552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1069-4_1_4_line_102 |  | 93 | 95 | 0.017795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1069-4_1_4_line_103 |  | 94 | 96 | 0.0059494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1069-4_1_4_line_104 |  | 95 | 97 | 0.065282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1069-4_1_4_line_105 |  | 98 | 99 | 0.011455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1069-4_1_4_line_106 |  | 100 | 101 | 0.017136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1069-4_1_4_line_107 |  | 104 | 105 | 0.020439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1069-4_1_4_line_108 |  | 106 | 107 | 0.031864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1069-4_1_4_line_109 |  | 107 | 108 | 0.011411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1069-4_1_4_line_110 |  | 108 | 109 | 0.054573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1069-4_1_4_line_111 |  | 108 | 110 | 0.025627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1069-4_1_4_line_112 |  | 109 | 111 | 0.012052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1069-4_1_4_line_113 |  | 111 | 117 | 0.02441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1069-4_1_4_line_114 |  | 113 | 114 | 0.023047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1069-4_1_4_line_115 |  | 115 | 116 | 0.047651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1069-4_1_4_line_116 |  | 116 | 117 | 0.0071454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1069-4_1_4_trafo_48 | 0.63 MVA 20/0.4 kV | 118 | 40 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2677343.8027 | 1209021.6564 | 2677331.7277 | 1209024.1861 | 2677312.318 | 1209029.1298
1 | 2677358.5152 | 1209018.5741 | 2677343.8027 | 1209021.6564
2 | 2677296.4602 | 1209037.6934 | 2677296.9642 | 1209034.5869 | 2677301.4464 | 1209031.8988 | 2677312.318 | 1209029.1298
3 | 2677358.5152 | 1209018.5741 | 2677360.8716 | 1209021.5288 | 2677371.4171 | 1209023.8002 | 2677380.1626 | 1209023.002 | 2677402.1981 | 1209015.4824
4 | 2677358.5152 | 1209018.5741 | 2677373.0989 | 1209013.1152 | 2677380.5646 | 1209009.2583
5 | 2677351.9981 | 1209044.5172 | 2677335.968 | 1209039.5731 | 2677318.8381 | 1209037.372 | 2677296.4602 | 1209037.6934
6 | 2677406.6416 | 1208997.2522 | 2677395.3099 | 1209001.6403 | 2677380.5646 | 1209009.2583
7 | 2677250.0635 | 1208966.2663 | 2677255.5793 | 1208962.7944 | 2677263.7407 | 1208958.3751 | 2677272.3675 | 1208955.3783
8 | 2677235.0823 | 1208976.7215 | 2677247.4621 | 1208967.9037 | 2677250.0635 | 1208966.2663
9 | 2677351.9981 | 1209044.5172 | 2677371.8177 | 1209052.1123
10 | 2677351.9981 | 1209044.5172 | 2677347.7724 | 1209049.6991 | 2677341.1296 | 1209050.32
11 | 2677435.121 | 1208989.405 | 2677410.561 | 1208995.7344 | 2677406.6416 | 1208997.2522
12 | 2677332.8053 | 1208917.021 | 2677331.3825 | 1208915.3459 | 2677328.5419 | 1208914.5531 | 2677324.7641 | 1208914.5041 | 2677308.6431 | 1208916.9737
13 | 2677332.8053 | 1208917.021 | 2677359.0783 | 1208891.7609
14 | 2677332.8053 | 1208917.021 | 2677358.3278 | 1208949.7349
15 | 2677308.6431 | 1208916.9737 | 2677302.7491 | 1208917.8766 | 2677293.7783 | 1208918.939
16 | 2677359.0783 | 1208891.7609 | 2677348.5401 | 1208861.3442
17 | 2677333.4236 | 1208965.0144 | 2677358.3278 | 1208949.7349
18 | 2677358.3278 | 1208949.7349 | 2677358.9566 | 1208949.3492
19 | 2677371.8177 | 1209052.1123 | 2677376.6558 | 1209050.1182 | 2677399.8377 | 1209050.519 | 2677445.4782 | 1209049.0656
20 | 2677371.8177 | 1209052.1123 | 2677377.7965 | 1209054.7853
21 | 2677341.1296 | 1209050.32 | 2677340.5643 | 1209050.3728 | 2677319.5959 | 1209048.1108 | 2677311.4622 | 1209049.2284 | 2677299.7521 | 1209054.1132 | 2677293.6757 | 1209057.2934
22 | 2677235.0823 | 1208976.7215 | 2677224.8646 | 1208983.9993
23 | 2677435.121 | 1208989.405 | 2677439.9285 | 1208988.166 | 2677450.9148 | 1208986.93 | 2677453.6299 | 1208987.3538
24 | 2677241.7349 | 1208728.5445 | 2677217.2902 | 1208689.6134
25 | 2677241.7349 | 1208728.5445 | 2677258.6112 | 1208732.2097 | 2677263.658 | 1208732.8064
26 | 2677377.7965 | 1209054.7853 | 2677405.2972 | 1209067.0806
27 | 2677405.2972 | 1209067.0806 | 2677421.7731 | 1209074.4468
28 | 2677445.4782 | 1209049.0656 | 2677445.4782 | 1209049.0656 | 2677449.8025 | 1209049.7666 | 2677459.5093 | 1209053.9252
29 | 2677271.5818 | 1208990.7351 | 2677289.8429 | 1208981.0274 | 2677296.0183 | 1208979.1651
30 | 2677333.4236 | 1208965.0144 | 2677332.8016 | 1208965.3961 | 2677320.4559 | 1208971.7957 | 2677296.0183 | 1208979.1651
31 | 2677271.5818 | 1208990.7351 | 2677268.6058 | 1208992.3172
32 | 2677380.0539 | 1209154.4964 | 2677390.1385 | 1209151.7909 | 2677396.28 | 1209151.8705
33 | 2677408.4943 | 1209153.9528 | 2677399.7917 | 1209151.9161 | 2677396.28 | 1209151.8705
34 | 2677380.0539 | 1209154.4964 | 2677374.9191 | 1209155.8739 | 2677370.4681 | 1209157.8433
35 | 2677430.0959 | 1209159.8802 | 2677414.0254 | 1209155.2472 | 2677408.4943 | 1209153.9528
36 | 2677446.9792 | 1209164.7474 | 2677430.0959 | 1209159.8802
37 | 2677408.6706 | 1209128.5164 | 2677394.5097 | 1209124.8415 | 2677365.0964 | 1209121.6271
38 | 2677408.6706 | 1209128.5164 | 2677408.6706 | 1209128.5164 | 2677417.5634 | 1209134.5133 | 2677432.1046 | 1209148.6071
39 | 2677446.9792 | 1209164.7474 | 2677446.2894 | 1209162.8373 | 2677443.5027 | 1209159.6547 | 2677432.1046 | 1209148.6071
40 | 2677224.8646 | 1208983.9993 | 2677246.6238 | 1209004.003
41 | 2677246.6238 | 1209004.003 | 2677268.6058 | 1208992.3172
42 | 2677372.5049 | 1208851.8089 | 2677348.5401 | 1208861.3442
43 | 2677340.6935 | 1208864.4663 | 2677348.5401 | 1208861.3442
44 | 2677358.9566 | 1208949.3492 | 2677374.5059 | 1208939.8092 | 2677391.8838 | 1208934.3713
45 | 2677398.7883 | 1208932.8698 | 2677395.5896 | 1208933.2116 | 2677391.8838 | 1208934.3713
46 | 2677437.2865 | 1209081.7645 | 2677425.2939 | 1209076.0209 | 2677421.7731 | 1209074.4468
47 | 2677445.7933 | 1209086.7469 | 2677440.3743 | 1209083.2433 | 2677437.2865 | 1209081.7645
48 | 2677402.1832 | 1208855.3672 | 2677362.9731 | 1208804.1792
49 | 2677402.1832 | 1208855.3672 | 2677375.9285 | 1208850.3567
50 | 2677402.1832 | 1208855.3672 | 2677408.5627 | 1208835.5988
51 | 2677362.9731 | 1208804.1792 | 2677322.1214 | 1208764.0163
52 | 2677334.3237 | 1208825.0384 | 2677353.1425 | 1208812.6182 | 2677362.9731 | 1208804.1792
53 | 2677372.5049 | 1208851.8089 | 2677374.2728 | 1208851.1054 | 2677375.9285 | 1208850.3567
54 | 2677461.1731 | 1208946.9155 | 2677453.5659 | 1208943.7704 | 2677417.9639 | 1208933.1907 | 2677407.0929 | 1208931.9822 | 2677398.7883 | 1208932.8698
55 | 2677461.1731 | 1208946.9155 | 2677461.8113 | 1208945.1894 | 2677463.24 | 1208944.652 | 2677465.6356 | 1208944.5831 | 2677469.0476 | 1208945.2833 | 2677472.7369 | 1208947.4659 | 2677476.6582 | 1208951.6862 | 2677479.4575 | 1208956.2476 | 2677481.4735 | 1208957.8971 | 2677483.9085 | 1208958.896 | 2677485.6442 | 1208958.7184 | 2677486.7305 | 1208957.6096 | 2677487.3723 | 1208955.0274 | 2677486.0419 | 1208951.5079 | 2677483.6241 | 1208949.1861 | 2677474.1888 | 1208942.9962
56 | 2677461.1731 | 1208946.9155 | 2677467.2505 | 1208950.1965 | 2677472.1936 | 1208954.1743 | 2677475.8546 | 1208958.5357 | 2677491.6379 | 1208981.2691
57 | 2677280.4015 | 1208738.5958 | 2677275.7234 | 1208741.715 | 2677273.0429 | 1208747.3394 | 2677273.1017 | 1208755.1229 | 2677277.1676 | 1208760.5234 | 2677282.647 | 1208763.0403 | 2677286.6916 | 1208763.6264 | 2677290.759 | 1208764.2128
58 | 2677280.4015 | 1208738.5958 | 2677277.9979 | 1208735.1625 | 2677274.135 | 1208734.0451 | 2677263.658 | 1208732.8064
59 | 2677290.759 | 1208764.2128 | 2677288.4016 | 1208771.8871 | 2677284.3929 | 1208775.6233
60 | 2677290.759 | 1208764.2128 | 2677301.9755 | 1208764.1425
61 | 2677268.7889 | 1208777.5928 | 2677284.3306 | 1208775.6813 | 2677284.3929 | 1208775.6233
62 | 2677301.9755 | 1208764.1425 | 2677322.1214 | 1208764.0163
63 | 2677210.6114 | 1208907.7598 | 2677200.8523 | 1208909.6971 | 2677191.1348 | 1208912.1619 | 2677181.5017 | 1208915.7396
64 | 2677181.5017 | 1208915.7396 | 2677158.2233 | 1208861.4526
65 | 2677173.1362 | 1208847.3912 | 2677167.6976 | 1208852.1097 | 2677158.2233 | 1208861.4526
66 | 2677484.0007 | 1209191.9711 | 2677488.801 | 1209193.9299
67 | 2677488.801 | 1209193.9299 | 2677599.0273 | 1209389.3984
68 | 2677484.0007 | 1209191.9711 | 2677467.6588 | 1209185.3026
69 | 2677653.8141 | 1209401.6743 | 2677626.265 | 1209390.5644 | 2677613.5403 | 1209388.153 | 2677601.5994 | 1209388.6091 | 2677599.0273 | 1209389.3984
70 | 2677599.0273 | 1209389.3984 | 2677632.8711 | 1209366.0741
71 | 2677453.9193 | 1209179.3933 | 2677454.3016 | 1209179.8521 | 2677467.6588 | 1209185.3026
72 | 2677578.945 | 1208964.5746 | 2677586.048 | 1208968.2064 | 2677590.6147 | 1208970.1448 | 2677594.7329 | 1208970.9099 | 2677598.1555 | 1208970.7222
73 | 2677552.484 | 1208944.2186 | 2677558.7003 | 1208950.2174 | 2677565.4098 | 1208955.7414 | 2677578.7073 | 1208964.4531 | 2677578.945 | 1208964.5746
74 | 2677618.4868 | 1208965.7641 | 2677604.0181 | 1208970.119 | 2677599.3204 | 1208970.6583 | 2677598.1555 | 1208970.7222
75 | 2677552.484 | 1208944.2186 | 2677547.3252 | 1208939.2404 | 2677547.3252 | 1208939.2404
76 | 2677446.9792 | 1209164.7474 | 2677449.3462 | 1209173.9062 | 2677453.9193 | 1209179.3933
77 | 2677446.9792 | 1209164.7474 | 2677456.6955 | 1209166.4524
78 | 2677199.5135 | 1208769.3464 | 2677203.6887 | 1208769.2448 | 2677216.4137 | 1208771.2313
79 | 2677199.5135 | 1208769.3464 | 2677199.5135 | 1208769.3464 | 2677191.7091 | 1208774.949 | 2677188.2125 | 1208776.4292
80 | 2677216.4137 | 1208771.2313 | 2677223.6824 | 1208772.366
81 | 2677249.7721 | 1208776.4388 | 2677223.6824 | 1208772.366
82 | 2677249.7721 | 1208776.4388 | 2677251.6508 | 1208776.7321
83 | 2677251.6508 | 1208776.7321 | 2677252.1491 | 1208776.8099 | 2677263.8849 | 1208778.196 | 2677268.7889 | 1208777.5928
84 | 2677447.8716 | 1208933.5249 | 2677454.1437 | 1208934.9834 | 2677464.7002 | 1208938.1668 | 2677470.4322 | 1208940.5316 | 2677474.1888 | 1208942.9962
85 | 2677524.1462 | 1208908.8023 | 2677474.1888 | 1208942.9962
86 | 2677495.8939 | 1208993.707 | 2677496.3783 | 1208991.5341 | 2677495.7172 | 1208987.4118 | 2677494.3698 | 1208985.204 | 2677491.6379 | 1208981.2691
87 | 2677488.9361 | 1209117.0349 | 2677482.6666 | 1209111.8659 | 2677468.7511 | 1209101.5899 | 2677445.7933 | 1209086.7469
88 | 2677488.9361 | 1209117.0349 | 2677490.4214 | 1209118.2595 | 2677496.5272 | 1209126.3662 | 2677500.3429 | 1209134.0206 | 2677501.9746 | 1209140.1273
89 | 2677547.3252 | 1208939.2404 | 2677538.5477 | 1208928.4528 | 2677524.1462 | 1208908.8023
90 | 2677485.6197 | 1209065.1113 | 2677459.5093 | 1209053.9252
91 | 2677516.2817 | 1209007.6918 | 2677514.1352 | 1209006.542
92 | 2677495.8939 | 1208993.707 | 2677501.9018 | 1208999.989 | 2677514.1352 | 1209006.542
93 | 2677516.2817 | 1209007.6918 | 2677519.5283 | 1209009.4309
94 | 2677495.8939 | 1208993.707 | 2677494.0692 | 1208996.6407 | 2677490.9814 | 1208999.08 | 2677488.8299 | 1208999.6635 | 2677486.5842 | 1208999.8901 | 2677482.98 | 1208998.7759
95 | 2677519.5283 | 1209009.4309 | 2677528.364 | 1209014.1639 | 2677546.8391 | 1209024.5883 | 2677548.9529 | 1209029.0148
96 | 2677471.9209 | 1208993.3232 | 2677482.98 | 1208998.7759
97 | 2677548.9529 | 1209029.0148 | 2677551.6285 | 1209034.6177
98 | 2677471.9209 | 1208993.3232 | 2677465.4017 | 1208990.1089 | 2677457.9859 | 1208988.0336 | 2677453.6299 | 1208987.3538
99 | 2677557.9714 | 1209047.9004 | 2677551.6285 | 1209034.6177
100 | 2677621.7029 | 1208964.7961 | 2677618.4868 | 1208965.7641
101 | 2677468.6052 | 1209133.3081 | 2677469.0309 | 1209136.2377 | 2677468.0194 | 1209142.7065 | 2677466.0347 | 1209151.5308
102 | 2677456.6955 | 1209166.4524 | 2677457.8891 | 1209162.9323 | 2677460.1676 | 1209159.0038 | 2677464.6431 | 1209153.9031 | 2677466.0347 | 1209151.5308
103 | 2677463.3814 | 1209130.4607 | 2677468.6052 | 1209133.3081
104 | 2677456.6955 | 1209166.4524 | 2677469.5318 | 1209169.0873 | 2677480.9556 | 1209168.0905 | 2677488.9333 | 1209166.1039 | 2677493.75 | 1209163.9985 | 2677498.5922 | 1209159.9365 | 2677501.8086 | 1209155.1975 | 2677502.4122 | 1209150.8692 | 2677502.525 | 1209142.1874 | 2677501.9746 | 1209140.1273
105 | 2677562.9076 | 1209058.2372 | 2677557.9714 | 1209047.9004
106 | 2677500.881 | 1209072.8974 | 2677486.9763 | 1209065.6925 | 2677485.6197 | 1209065.1113
107 | 2677427.9637 | 1208928.8954 | 2677447.8716 | 1208933.5249
108 | 2677306.655 | 1208840.7948 | 2677327.4846 | 1208829.5521 | 2677334.3237 | 1208825.0384
109 | 2677297.2033 | 1208847.16 | 2677304.4319 | 1208841.9947 | 2677306.655 | 1208840.7948
110 | 2677297.2033 | 1208847.16 | 2677299.1428 | 1208854.7232 | 2677295.5056 | 1208857.9003 | 2677285.4016 | 1208860.8492 | 2677268.9064 | 1208858.901 | 2677264.4418 | 1208857.2867 | 2677260.3101 | 1208855.7989 | 2677254.9903 | 1208853.8624
111 | 2677297.2033 | 1208847.16 | 2677293.1798 | 1208849.0535 | 2677288.4203 | 1208850.8374 | 2677282.2498 | 1208852.3808 | 2677272.6387 | 1208853.938
112 | 2677243.647 | 1208849.7906 | 2677243.647 | 1208849.7906 | 2677251.7595 | 1208852.6863 | 2677254.9903 | 1208853.8624
113 | 2677222.3197 | 1208837.9302 | 2677228.6677 | 1208841.1579 | 2677243.647 | 1208849.7906
114 | 2677340.6935 | 1208864.4663 | 2677333.7626 | 1208867.224 | 2677318.7948 | 1208871.5777
115 | 2677215.8524 | 1208834.9132 | 2677208.183 | 1208832.0094 | 2677195.0164 | 1208833.6846 | 2677183.6828 | 1208838.2409 | 2677173.1362 | 1208847.3912
116 | 2677222.3197 | 1208837.9302 | 2677217.9426 | 1208835.7046 | 2677215.8524 | 1208834.9132

## bus_geodata
| x | y | coords
0 | 2677343.8027 | 1209021.6564
1 | 2677312.318 | 1209029.1298
2 | 2677358.5152 | 1209018.5741
3 | 2677296.4602 | 1209037.6934
4 | 2677402.1981 | 1209015.4824
5 | 2677380.5646 | 1209009.2583
6 | 2677272.3675 | 1208955.3784
7 | 2677250.0635 | 1208966.2663
8 | 2677351.9981 | 1209044.5172
9 | 2677406.6416 | 1208997.2522
10 | 2677332.8053 | 1208917.021
11 | 2677308.6431 | 1208916.9737
12 | 2677359.0783 | 1208891.7609
13 | 2677358.3278 | 1208949.7349
14 | 2677371.8177 | 1209052.1123
15 | 2677341.1296 | 1209050.32
16 | 2677235.0823 | 1208976.7215
17 | 2677435.121 | 1208989.405
18 | 2677217.2902 | 1208689.6134
19 | 2677241.7349 | 1208728.5445
20 | 2677377.7965 | 1209054.7853
21 | 2677405.2972 | 1209067.0806
22 | 2677445.4782 | 1209049.0656
23 | 2677293.6757 | 1209057.2934
24 | 2677296.0183 | 1208979.1651
25 | 2677271.5818 | 1208990.7351
26 | 2677333.4236 | 1208965.0144
27 | 2677396.28 | 1209151.8705
28 | 2677380.0539 | 1209154.4964
29 | 2677408.4943 | 1209153.9528
30 | 2677370.4681 | 1209157.8433
31 | 2677430.0959 | 1209159.8802
32 | 2677408.6706 | 1209128.5164
33 | 2677365.0964 | 1209121.6271
34 | 2677432.1046 | 1209148.6071
35 | 2677224.8646 | 1208983.9993
36 | 2677268.6058 | 1208992.3172
37 | 2677246.6238 | 1209004.003
38 | 2677293.7783 | 1208918.939
39 | 2677348.5401 | 1208861.3442
40 | 2677358.9566 | 1208949.3492
41 | 2677391.8838 | 1208934.3713
42 | 2677421.7731 | 1209074.4468
43 | 2677437.2865 | 1209081.7645
44 | 2677402.1832 | 1208855.3672
45 | 2677362.9731 | 1208804.1792
46 | 2677375.9285 | 1208850.3567
47 | 2677408.5627 | 1208835.5988
48 | 2677398.7883 | 1208932.8698
49 | 2677461.1731 | 1208946.9155
50 | 2677280.4015 | 1208738.5958
51 | 2677290.759 | 1208764.2128
52 | 2677263.658 | 1208732.8064
53 | 2677284.3929 | 1208775.6233
54 | 2677301.9755 | 1208764.1425
55 | 2677210.6114 | 1208907.7598
56 | 2677181.5017 | 1208915.7396
57 | 2677158.2233 | 1208861.4526
58 | 2677488.801 | 1209193.9299
59 | 2677484.0007 | 1209191.9711
60 | 2677599.0273 | 1209389.3984
61 | 2677467.6588 | 1209185.3026
62 | 2677632.8711 | 1209366.0741
63 | 2677653.8141 | 1209401.6743
64 | 2677578.945 | 1208964.5746
65 | 2677598.1555 | 1208970.7222
66 | 2677552.484 | 1208944.2186
67 | 2677453.9193 | 1209179.3933
68 | 2677446.9792 | 1209164.7474
69 | 2677199.5135 | 1208769.3464
70 | 2677216.4137 | 1208771.2313
71 | 2677188.2125 | 1208776.4292
72 | 2677223.6824 | 1208772.366
73 | 2677249.7721 | 1208776.4388
74 | 2677251.6508 | 1208776.7321
75 | 2677474.1888 | 1208942.9962
76 | 2677491.6379 | 1208981.2691
77 | 2677268.7889 | 1208777.5928
78 | 2677445.7933 | 1209086.7469
79 | 2677488.9361 | 1209117.0349
80 | 2677547.3252 | 1208939.2404
81 | 2677459.5093 | 1209053.9252
82 | 2677514.1352 | 1209006.542
83 | 2677516.2817 | 1209007.6918
84 | 2677495.8939 | 1208993.707
85 | 2677519.5283 | 1209009.4309
86 | 2677482.98 | 1208998.7759
87 | 2677548.9529 | 1209029.0148
88 | 2677471.9209 | 1208993.3232
89 | 2677524.1462 | 1208908.8023
90 | 2677551.6285 | 1209034.6177
91 | 2677453.6299 | 1208987.3538
92 | 2677618.4867 | 1208965.7641
93 | 2677466.0347 | 1209151.5308
94 | 2677468.6052 | 1209133.3081
95 | 2677456.6955 | 1209166.4524
96 | 2677463.3814 | 1209130.4607
97 | 2677501.9746 | 1209140.1273
98 | 2677557.9714 | 1209047.9004
99 | 2677562.9076 | 1209058.2372
100 | 2677485.6197 | 1209065.1113
101 | 2677500.881 | 1209072.8974
102 | 2677621.7029 | 1208964.7961
103 | 2677322.1214 | 1208764.0163
104 | 2677447.8716 | 1208933.5249
105 | 2677427.9637 | 1208928.8954
106 | 2677334.3237 | 1208825.0384
107 | 2677306.655 | 1208840.7948
108 | 2677297.2033 | 1208847.16
109 | 2677254.9903 | 1208853.8624
110 | 2677272.6387 | 1208853.938
111 | 2677243.647 | 1208849.7906
112 | 2677372.5049 | 1208851.8089
113 | 2677340.6935 | 1208864.4663
114 | 2677318.7948 | 1208871.5777
115 | 2677173.1362 | 1208847.3912
116 | 2677215.8524 | 1208834.9132
117 | 2677222.3197 | 1208837.9302
118 | 2677461.1731 | 1208946.9155

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98197 | -0.34543 | 0.0039877 | 0.00099941
1 | 0.98093 | -0.3657 | 0.0038221 | 0.00095792
2 | 0.98248 | -0.33549 | 0 | 0
3 | 0.98033 | -0.37731 | 0 | 0
4 | 0.98233 | -0.33856 | 0.0036423 | 0.00091284
5 | 0.98334 | -0.31888 | 0.0038869 | 0.00097415
6 | 0.99682 | -0.06114 | 0.0032115 | 0.00080489
7 | 0.99689 | -0.059735 | 0.0031216 | 0.00078234
8 | 0.97862 | -0.41072 | 0 | 0
9 | 0.98442 | -0.29798 | 0.0064348 | 0.0016127
10 | 0.99471 | -0.10013 | 0 | 0
11 | 0.99423 | -0.10931 | 0.017171 | 0.0043035
12 | 0.9908 | -0.17463 | 0.003107 | 0.00077869
13 | 0.99994 | -0.0010728 | 0.0025307 | 0.00063425
14 | 0.97805 | -0.42203 | 0 | 0
15 | 0.97854 | -0.41235 | 0.0041641 | 0.0010436
16 | 0.997 | -0.057706 | 0.0025775 | 0.00064598
17 | 0.98562 | -0.27484 | 0.0047653 | 0.0011943
18 | 0.97532 | -0.47488 | 0.0011665 | 0.00029235
19 | 0.97537 | -0.47389 | 0.0018634 | 0.00046701
20 | 0.97776 | -0.42756 | 0.0021807 | 0.00054653
21 | 0.97652 | -0.45185 | 0.0049622 | 0.0012436
22 | 0.9772 | -0.43867 | 0.0022086 | 0.00055352
23 | 0.97842 | -0.41463 | 0.0025395 | 0.00063645
24 | 0.9983 | -0.032705 | 0.0041374 | 0.0010369
25 | 0.99779 | -0.042452 | 0.0034789 | 0.00087189
26 | 0.9992 | -0.015395 | 0.0034296 | 0.00085955
27 | 0.97078 | -0.56509 | 0.0013925 | 0.00034898
28 | 0.97072 | -0.56625 | 0.0015014 | 0.00037629
29 | 0.97084 | -0.5639 | 0.00060308 | 0.00015114
30 | 0.9707 | -0.56668 | 0.0022808 | 0.00057163
31 | 0.97096 | -0.5615 | 0.00055912 | 0.00014013
32 | 0.97067 | -0.56711 | 0.0021929 | 0.0005496
33 | 0.97048 | -0.57099 | 0.0047425 | 0.0011886
34 | 0.97087 | -0.56313 | 0.0020807 | 0.00052147
35 | 0.9971 | -0.055745 | 0.0026085 | 0.00065375
36 | 0.99774 | -0.043458 | 0.0025562 | 0.00064064
37 | 0.99741 | -0.049777 | 0.0029716 | 0.00074476
38 | 0.99419 | -0.11023 | 0.0034735 | 0.00087054
39 | 0.98744 | -0.23914 | 0.0066903 | 0.0016768
40 | 1 | 0 | -0.33658 | -0.085933
41 | 0.99726 | -0.051903 | 0.0025339 | 0.00063506
42 | 0.97586 | -0.46479 | 0.0032354 | 0.00081086
43 | 0.97529 | -0.47609 | 0.0038359 | 0.00096137
44 | 0.98292 | -0.32639 | 0.0042371 | 0.0010619
45 | 0.97829 | -0.4166 | 0.0035864 | 0.00089883
46 | 0.98499 | -0.28633 | 0.004226 | 0.0010591
47 | 0.98289 | -0.32706 | 0.0018102 | 0.00045368
48 | 0.99673 | -0.061888 | 0.0021437 | 0.00053725
49 | 0.992 | -0.15209 | 0 | 0
50 | 0.97555 | -0.47043 | 0 | 0
51 | 0.97579 | -0.46562 | 0 | 0
52 | 0.97544 | -0.47265 | 0.0034348 | 0.00086085
53 | 0.97555 | -0.47033 | 0.0026043 | 0.00065271
54 | 0.97606 | -0.46039 | 0.0026259 | 0.00065811
55 | 0.97123 | -0.5555 | 0.0021892 | 0.00054867
56 | 0.97129 | -0.55427 | 0.0032561 | 0.00081606
57 | 0.97159 | -0.54833 | 0.0045598 | 0.0011428
58 | 0.97073 | -0.56606 | 0.00077836 | 0.00019507
59 | 0.97074 | -0.56579 | 0.003072 | 0.00076991
60 | 0.97031 | -0.57445 | 0 | 0
61 | 0.97084 | -0.56387 | 0.0014054 | 0.00035222
62 | 0.97025 | -0.5755 | 0.0013741 | 0.00034437
63 | 0.97027 | -0.57513 | 0.00064106 | 0.00016066
64 | 0.98788 | -0.23205 | 0.004023 | 0.0010083
65 | 0.9877 | -0.23552 | 0.0041779 | 0.0010471
66 | 0.98829 | -0.22399 | 0.0022451 | 0.00056267
67 | 0.97094 | -0.56185 | 0.00055746 | 0.00013971
68 | 0.97106 | -0.55944 | 0 | 0
69 | 0.97483 | -0.48462 | 0.0011728 | 0.00029392
70 | 0.97487 | -0.48381 | 0.0033489 | 0.00083931
71 | 0.97481 | -0.48496 | 0.0014013 | 0.00035121
72 | 0.97491 | -0.48301 | 0.0015711 | 0.00039376
73 | 0.9751 | -0.47938 | 0.0020929 | 0.00052452
74 | 0.97511 | -0.47905 | 0.0030144 | 0.00075547
75 | 0.99029 | -0.18512 | 0.0040193 | 0.0010073
76 | 0.98932 | -0.20339 | 0.0053291 | 0.0013356
77 | 0.97531 | -0.47506 | 0.0038054 | 0.00095373
78 | 0.97499 | -0.4819 | 0.0030886 | 0.00077407
79 | 0.97356 | -0.51004 | 0.0019107 | 0.00047887
80 | 0.98839 | -0.22198 | 0.0022464 | 0.000563
81 | 0.97706 | -0.44143 | 0.0027419 | 0.00068718
82 | 0.9882 | -0.22501 | 0.0029413 | 0.00073716
83 | 0.98817 | -0.22564 | 0.0043089 | 0.0010799
84 | 0.98857 | -0.21795 | 0 | 0
85 | 0.98814 | -0.22631 | 0.00098984 | 0.00024808
86 | 0.98783 | -0.23206 | 0.0022466 | 0.00056304
87 | 0.98783 | -0.2323 | 0.0017757 | 0.00044502
88 | 0.98727 | -0.24295 | 0.0041197 | 0.0010325
89 | 0.98902 | -0.20973 | 0.004876 | 0.0012221
90 | 0.98779 | -0.23314 | 0.0026033 | 0.00065244
91 | 0.98642 | -0.25937 | 0.0027708 | 0.00069442
92 | 0.9876 | -0.23749 | 0.0028812 | 0.00072209
93 | 0.97122 | -0.55626 | 0.00075151 | 0.00018835
94 | 0.97118 | -0.55709 | 0.00092559 | 0.00023198
95 | 0.97127 | -0.55523 | 0 | 0
96 | 0.97117 | -0.55725 | 0.0014755 | 0.0003698
97 | 0.97288 | -0.52349 | 0.00077364 | 0.00019389
98 | 0.98772 | -0.23443 | 0.0030456 | 0.00076329
99 | 0.9877 | -0.23481 | 0.0018567 | 0.00046532
100 | 0.97686 | -0.44525 | 0.0038586 | 0.00096705
101 | 0.97681 | -0.44635 | 0.0035069 | 0.00087892
102 | 0.98759 | -0.23764 | 0.0023847 | 0.00059766
103 | 0.97659 | -0.45004 | 0.0038825 | 0.00097304
104 | 0.9901 | -0.18886 | 0.0051904 | 0.0013008
105 | 0.99006 | -0.18969 | 0.0022783 | 0.00057101
106 | 0.97691 | -0.44354 | 0.004259 | 0.0010674
107 | 0.9758 | -0.4653 | 0.0027837 | 0.00069765
108 | 0.97544 | -0.47252 | 0 | 0
109 | 0.97382 | -0.50434 | 0.0031127 | 0.00078011
110 | 0.97537 | -0.47383 | 0.0027889 | 0.00069898
111 | 0.9735 | -0.51069 | 0.0019648 | 0.00049242
112 | 0.98529 | -0.28049 | 0.0020221 | 0.00050679
113 | 0.98731 | -0.2416 | 0.0098959 | 0.0024802
114 | 0.98718 | -0.24424 | 0.0064065 | 0.0016056
115 | 0.97178 | -0.54454 | 0.011264 | 0.0028231
116 | 0.97273 | -0.52585 | 0.0028212 | 0.00070706
117 | 0.97289 | -0.52268 | 0.0025972 | 0.00065093
118 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.069644 | 0.017626 | -0.069576 | -0.017583 | 6.7669e-05 | 4.249e-05 | 0.1056 | 0.1056 | 0.1056 | 0.98197 | -0.34543 | 0.98093 | -0.3657 | 14.5049
1 | -0.073632 | -0.018625 | 0.073667 | 0.018647 | 3.5127e-05 | 2.2101e-05 | 0.11164 | 0.11164 | 0.11164 | 0.98197 | -0.34543 | 0.98248 | -0.33549 | 15.3349
2 | 0.065754 | 0.016625 | -0.065718 | -0.016602 | 3.6587e-05 | 2.2921e-05 | 0.099798 | 0.099798 | 0.099798 | 0.98093 | -0.3657 | 0.98033 | -0.37731 | 13.7085
3 | 0.0036428 | 0.00091259 | -0.0036423 | -0.00091284 | 5.3229e-07 | -2.4977e-07 | 0.0055171 | 0.0055173 | 0.0055173 | 0.98248 | -0.33549 | 0.98233 | -0.33856 | 1.5157
4 | -0.07731 | -0.01956 | 0.077371 | 0.019599 | 6.1699e-05 | 3.888e-05 | 0.11715 | 0.11715 | 0.11715 | 0.98248 | -0.33549 | 0.98334 | -0.31888 | 16.0927
5 | 0.065718 | 0.016602 | -0.065612 | -0.016537 | 0.00010507 | 6.583e-05 | 0.099798 | 0.099798 | 0.099798 | 0.98033 | -0.37731 | 0.97862 | -0.41072 | 13.7086
6 | -0.081258 | -0.020573 | 0.08134 | 0.020624 | 8.1599e-05 | 5.1493e-05 | 0.12304 | 0.12304 | 0.12304 | 0.98334 | -0.31888 | 0.98442 | -0.29798 | 16.9006
7 | -0.0032115 | -0.00080489 | 0.0032117 | 0.0008047 | 2.1487e-07 | -1.8751e-07 | 0.0047941 | 0.0047939 | 0.0047941 | 0.99682 | -0.06114 | 0.99689 | -0.059735 | 1.317
8 | -0.0063333 | -0.001587 | 0.0063339 | 0.0015872 | 6.1236e-07 | 1.5365e-07 | 0.0094534 | 0.0094533 | 0.0094534 | 0.99689 | -0.059735 | 0.997 | -0.057706 | 2.5971
9 | 0.058908 | 0.014857 | -0.058876 | -0.014837 | 3.1872e-05 | 1.9866e-05 | 0.089604 | 0.089605 | 0.089605 | 0.97862 | -0.41072 | 0.97805 | -0.42203 | 12.3083
10 | 0.0067044 | 0.0016798 | -0.0067038 | -0.0016796 | 5.2055e-07 | 1.6533e-07 | 0.010194 | 0.010194 | 0.010194 | 0.97862 | -0.41072 | 0.97854 | -0.41235 | 2.8005
11 | -0.087775 | -0.022237 | 0.087872 | 0.022299 | 9.771e-05 | 6.1782e-05 | 0.13276 | 0.13276 | 0.13276 | 0.98442 | -0.29798 | 0.98562 | -0.27484 | 18.2367
12 | 0.020654 | 0.0051794 | -0.020645 | -0.0051739 | 9.0338e-06 | 5.4542e-06 | 0.030898 | 0.030898 | 0.030898 | 0.99471 | -0.10013 | 0.99423 | -0.10931 | 8.4884
13 | 0.11733 | 0.030084 | -0.11691 | -0.029814 | 0.00042222 | 0.00026975 | 0.17576 | 0.17576 | 0.17576 | 0.99471 | -0.10013 | 0.9908 | -0.17463 | 48.2867
14 | -0.13799 | -0.035263 | 0.13865 | 0.035688 | 0.00066453 | 0.00042476 | 0.20666 | 0.20666 | 0.20666 | 0.99471 | -0.10013 | 0.99994 | -0.0010728 | 56.7749
15 | 0.0034736 | 0.00087044 | -0.0034735 | -0.00087054 | 1.5199e-07 | -9.7195e-08 | 0.0051987 | 0.0051988 | 0.0051988 | 0.99423 | -0.10931 | 0.99419 | -0.11023 | 1.4282
16 | 0.1138 | 0.029036 | -0.11345 | -0.02881 | 0.00035338 | 0.00022575 | 0.1711 | 0.1711 | 0.1711 | 0.9908 | -0.17463 | 0.98744 | -0.23914 | 47.0049
17 | 0.028152 | 0.0070759 | -0.028133 | -0.007064 | 1.9236e-05 | 1.1928e-05 | 0.0419 | 0.0419 | 0.0419 | 0.99994 | -0.0010728 | 0.9992 | -0.015395 | 11.5111
18 | -0.16933 | -0.043398 | 0.16934 | 0.043404 | 8.8064e-06 | 5.6167e-06 | 0.25233 | 0.25233 | 0.25233 | 0.99994 | -0.0010728 | 1 | 0 | 34.6602
19 | 0.012329 | 0.0030931 | -0.012319 | -0.0030877 | 9.7752e-06 | 5.3272e-06 | 0.018758 | 0.018758 | 0.018758 | 0.97805 | -0.42203 | 0.9772 | -0.43867 | 5.1534
20 | 0.046548 | 0.011744 | -0.046535 | -0.011736 | 1.2327e-05 | 7.8071e-06 | 0.070847 | 0.070847 | 0.070847 | 0.97805 | -0.42203 | 0.97776 | -0.42756 | 19.4634
21 | 0.0025398 | 0.00063601 | -0.0025395 | -0.00063645 | 2.7638e-07 | -4.438e-07 | 0.0038619 | 0.0038621 | 0.0038621 | 0.97854 | -0.41235 | 0.97842 | -0.41463 | 1.061
22 | -0.0089114 | -0.0022332 | 0.0089123 | 0.0022335 | 8.3216e-07 | 3.6897e-07 | 0.0133 | 0.0133 | 0.0133 | 0.997 | -0.057706 | 0.9971 | -0.055745 | 3.6539
23 | -0.092638 | -0.023493 | 0.092707 | 0.023537 | 6.8931e-05 | 4.3637e-05 | 0.13996 | 0.13996 | 0.13996 | 0.98562 | -0.27484 | 0.98642 | -0.25937 | 19.2248
24 | -0.0011665 | -0.00029235 | 0.0011665 | 0.00029181 | 5.4591e-08 | -5.3878e-07 | 0.0017797 | 0.0017794 | 0.0017797 | 0.97532 | -0.47488 | 0.97537 | -0.47389 | 0.48892
25 | -0.0030299 | -0.00075882 | 0.0030301 | 0.00075865 | 1.7907e-07 | -1.6438e-07 | 0.0046222 | 0.0046221 | 0.0046222 | 0.97537 | -0.47389 | 0.97544 | -0.47265 | 1.2698
26 | 0.044355 | 0.01119 | -0.044303 | -0.011157 | 5.1513e-05 | 3.2591e-05 | 0.067528 | 0.067528 | 0.067528 | 0.97776 | -0.42756 | 0.97652 | -0.45185 | 18.5517
27 | 0.039341 | 0.0099133 | -0.039317 | -0.009898 | 2.4337e-05 | 1.535e-05 | 0.059967 | 0.059967 | 0.059967 | 0.97652 | -0.45185 | 0.97586 | -0.46479 | 16.4744
28 | 0.01011 | 0.0025342 | -0.010109 | -0.0025335 | 1.328e-06 | 6.6274e-07 | 0.015395 | 0.015395 | 0.015395 | 0.9772 | -0.43867 | 0.97706 | -0.44143 | 4.2295
29 | 0.020545 | 0.005155 | -0.020536 | -0.0051492 | 9.543e-06 | 5.753e-06 | 0.030626 | 0.030626 | 0.030626 | 0.9983 | -0.032705 | 0.99779 | -0.042452 | 8.4138
30 | -0.024683 | -0.0061919 | 0.024703 | 0.0062044 | 2.0387e-05 | 1.2522e-05 | 0.036793 | 0.036793 | 0.036793 | 0.9983 | -0.032705 | 0.9992 | -0.015395 | 10.108
31 | 0.017057 | 0.0042774 | -0.017056 | -0.0042769 | 8.1788e-07 | 4.7942e-07 | 0.025438 | 0.025438 | 0.025438 | 0.99779 | -0.042452 | 0.99774 | -0.043458 | 6.9885
32 | 0.0037825 | 0.00094776 | -0.0037823 | -0.00094783 | 2.0904e-07 | -7.1232e-08 | 0.0057978 | 0.0057979 | 0.0057979 | 0.97078 | -0.56509 | 0.97072 | -0.56625 | 1.5928
33 | -0.005175 | -0.0012967 | 0.0051753 | 0.0012968 | 2.9375e-07 | 3.4063e-08 | 0.0079322 | 0.0079321 | 0.0079322 | 0.97078 | -0.56509 | 0.97084 | -0.5639 | 2.1792
34 | 0.0022809 | 0.00057154 | -0.0022808 | -0.00057163 | 4.6684e-08 | -9.6011e-08 | 0.0034963 | 0.0034964 | 0.0034964 | 0.97072 | -0.56625 | 0.9707 | -0.56668 | 0.96055
35 | -0.0057783 | -0.0014479 | 0.005779 | 0.0014481 | 6.5902e-07 | 1.4469e-07 | 0.0088564 | 0.0088563 | 0.0088564 | 0.97084 | -0.5639 | 0.97096 | -0.5615 | 2.4331
36 | -0.0063381 | -0.0015882 | 0.0063387 | 0.0015884 | 6.2165e-07 | 1.8051e-07 | 0.0097132 | 0.0097131 | 0.0097132 | 0.97096 | -0.5615 | 0.97106 | -0.55944 | 2.6685
37 | 0.0047434 | 0.0011886 | -0.0047425 | -0.0011886 | 8.7676e-07 | 1.4652e-08 | 0.0072714 | 0.0072716 | 0.0072716 | 0.97067 | -0.56711 | 0.97048 | -0.57099 | 1.9977
38 | -0.0069363 | -0.0017382 | 0.0069376 | 0.0017387 | 1.3133e-06 | 4.5756e-07 | 0.010633 | 0.010633 | 0.010633 | 0.97067 | -0.56711 | 0.97087 | -0.56313 | 2.9212
39 | -0.0090183 | -0.0022601 | 0.0090199 | 0.0022609 | 1.5858e-06 | 7.4112e-07 | 0.013822 | 0.013822 | 0.013822 | 0.97087 | -0.56313 | 0.97106 | -0.55944 | 3.7972
40 | -0.011521 | -0.0028873 | 0.011524 | 0.002889 | 3.2763e-06 | 1.7112e-06 | 0.017193 | 0.017193 | 0.017193 | 0.9971 | -0.055745 | 0.99741 | -0.049777 | 4.7233
41 | 0.0145 | 0.0036362 | -0.014496 | -0.0036338 | 4.3661e-06 | 2.4693e-06 | 0.021626 | 0.021626 | 0.021626 | 0.99774 | -0.043458 | 0.99741 | -0.049777 | 5.9412
42 | 0.090455 | 0.023046 | -0.090275 | -0.022931 | 0.00018007 | 0.00011491 | 0.13644 | 0.13644 | 0.13644 | 0.98744 | -0.23914 | 0.98529 | -0.28049 | 37.4848
43 | 0.016305 | 0.0040871 | -0.016303 | -0.004086 | 1.912e-06 | 1.1157e-06 | 0.024571 | 0.024571 | 0.024571 | 0.98744 | -0.23914 | 0.98731 | -0.2416 | 6.7504
44 | 0.16559 | 0.042529 | -0.16517 | -0.042264 | 0.00041617 | 0.0002654 | 0.24676 | 0.24676 | 0.24676 | 1 | 0 | 0.99726 | -0.051903 | 33.896
45 | 0.16264 | 0.041629 | -0.16256 | -0.041579 | 7.8596e-05 | 5.0116e-05 | 0.24298 | 0.24298 | 0.24298 | 0.99726 | -0.051903 | 0.99673 | -0.061888 | 33.3766
46 | 0.036081 | 0.0090871 | -0.036062 | -0.0090749 | 1.9482e-05 | 1.2255e-05 | 0.055033 | 0.055034 | 0.055034 | 0.97586 | -0.46479 | 0.97529 | -0.47609 | 15.1191
47 | 0.032226 | 0.0081135 | -0.032217 | -0.0081079 | 8.9585e-06 | 5.6102e-06 | 0.049181 | 0.049181 | 0.049181 | 0.97529 | -0.47609 | 0.97499 | -0.4819 | 13.5113
48 | 0.077793 | 0.019731 | -0.077457 | -0.019517 | 0.00033584 | 0.00021412 | 0.11785 | 0.11785 | 0.11785 | 0.98292 | -0.32639 | 0.97829 | -0.4166 | 32.377
49 | -0.08384 | -0.021246 | 0.084002 | 0.021349 | 0.00016168 | 0.00010314 | 0.12701 | 0.12701 | 0.12701 | 0.98292 | -0.32639 | 0.98499 | -0.28633 | 34.892
50 | 0.0018103 | 0.00045346 | -0.0018102 | -0.00045368 | 5.8502e-08 | -2.2584e-07 | 0.0027404 | 0.0027405 | 0.0027405 | 0.98292 | -0.32639 | 0.98289 | -0.32706 | 0.7529
51 | 0.03207 | 0.0080669 | -0.032019 | -0.0080349 | 5.1141e-05 | 3.2012e-05 | 0.04879 | 0.048791 | 0.048791 | 0.97829 | -0.4166 | 0.97659 | -0.45004 | 13.404
52 | 0.0418 | 0.010551 | -0.041747 | -0.010517 | 5.3866e-05 | 3.4029e-05 | 0.063607 | 0.063607 | 0.063607 | 0.97829 | -0.4166 | 0.97691 | -0.44354 | 17.4745
53 | -0.088228 | -0.022408 | 0.088253 | 0.022424 | 2.4821e-05 | 1.5838e-05 | 0.13339 | 0.13339 | 0.13339 | 0.98499 | -0.28633 | 0.98529 | -0.28049 | 36.6459
54 | 0.16042 | 0.041042 | -0.15972 | -0.040597 | 0.00069708 | 0.00044446 | 0.23978 | 0.23978 | 0.23978 | 0.99673 | -0.061888 | 0.992 | -0.15209 | 32.9371
55 | 0.034424 | 0.0086634 | -0.03437 | -0.0086294 | 5.426e-05 | 3.4027e-05 | 0.051649 | 0.05165 | 0.05165 | 0.992 | -0.15209 | 0.99029 | -0.18512 | 14.1894
56 | 0.12529 | 0.031934 | -0.12498 | -0.031737 | 0.00030939 | 0.00019681 | 0.18813 | 0.18813 | 0.18813 | 0.992 | -0.15209 | 0.98932 | -0.20339 | 25.8425
57 | -0.0064656 | -0.0016197 | 0.0064671 | 0.0016201 | 1.4794e-06 | 4.4023e-07 | 0.0098618 | 0.0098616 | 0.0098618 | 0.97555 | -0.47043 | 0.97579 | -0.46562 | 2.7093
58 | 0.0064656 | 0.0016197 | -0.0064649 | -0.0016195 | 6.8428e-07 | 2.0371e-07 | 0.0098618 | 0.0098619 | 0.0098619 | 0.97555 | -0.47043 | 0.97544 | -0.47265 | 2.7093
59 | 0.019023 | 0.004771 | -0.019019 | -0.0047684 | 4.2632e-06 | 2.5597e-06 | 0.02901 | 0.02901 | 0.02901 | 0.97579 | -0.46562 | 0.97555 | -0.47033 | 7.9699
60 | -0.02549 | -0.0063912 | 0.025497 | 0.0063951 | 6.3557e-06 | 3.9275e-06 | 0.038872 | 0.038872 | 0.038872 | 0.97579 | -0.46562 | 0.97606 | -0.46039 | 10.6791
61 | 0.016415 | 0.0041157 | -0.016411 | -0.0041136 | 3.7012e-06 | 2.1722e-06 | 0.025038 | 0.025038 | 0.025038 | 0.97555 | -0.47033 | 0.97531 | -0.47506 | 6.8786
62 | -0.028123 | -0.0070532 | 0.028136 | 0.0070618 | 1.3888e-05 | 8.6363e-06 | 0.042875 | 0.042875 | 0.042875 | 0.97606 | -0.46039 | 0.97659 | -0.45004 | 11.7789
63 | -0.0021892 | -0.00054867 | 0.0021893 | 0.00054838 | 1.2761e-07 | -2.9271e-07 | 0.0033541 | 0.0033539 | 0.0033541 | 0.97123 | -0.5555 | 0.97129 | -0.55427 | 0.92145
64 | -0.0054455 | -0.0013644 | 0.005447 | 0.0013647 | 1.5415e-06 | 2.5526e-07 | 0.0083423 | 0.0083421 | 0.0083423 | 0.97129 | -0.55427 | 0.97159 | -0.54833 | 2.2918
65 | -0.010007 | -0.0025075 | 0.010009 | 0.0025084 | 1.8061e-06 | 9.0191e-07 | 0.015326 | 0.015325 | 0.015326 | 0.97159 | -0.54833 | 0.97178 | -0.54454 | 4.2103
66 | -0.0027944 | -0.0006967 | 0.0027944 | 0.00069666 | 3.5651e-08 | -4.1279e-08 | 0.0042822 | 0.0042821 | 0.0042822 | 0.97073 | -0.56606 | 0.97074 | -0.56579 | 1.1764
67 | 0.002016 | 0.00050162 | -0.0020152 | -0.00050388 | 8.0324e-07 | -2.2589e-06 | 0.003089 | 0.00309 | 0.00309 | 0.97073 | -0.56606 | 0.97031 | -0.57445 | 0.84891
68 | -0.0058664 | -0.0014666 | 0.0058669 | 0.0014667 | 5.3505e-07 | 1.2421e-07 | 0.008991 | 0.008991 | 0.008991 | 0.97074 | -0.56579 | 0.97084 | -0.56387 | 2.4701
69 | 0.00064108 | 0.00015997 | -0.00064106 | -0.00016066 | 2.0707e-08 | -6.9254e-07 | 0.00098288 | 0.00098314 | 0.00098314 | 0.97031 | -0.57445 | 0.97027 | -0.57513 | 0.27009
70 | 0.0013741 | 0.00034391 | -0.0013741 | -0.00034437 | 6.8442e-08 | -4.6386e-07 | 0.0021071 | 0.0021073 | 0.0021073 | 0.97031 | -0.57445 | 0.97025 | -0.5755 | 0.57894
71 | -0.0072723 | -0.0018189 | 0.007273 | 0.0018192 | 6.9979e-07 | 2.6207e-07 | 0.011145 | 0.011145 | 0.011145 | 0.97084 | -0.56387 | 0.97094 | -0.56185 | 3.0618
72 | 0.0094458 | 0.0023676 | -0.0094443 | -0.0023668 | 1.5604e-06 | 7.3557e-07 | 0.014228 | 0.014228 | 0.014228 | 0.98788 | -0.23205 | 0.9877 | -0.23552 | 3.9089
73 | -0.013469 | -0.0033758 | 0.013474 | 0.0033787 | 5.1697e-06 | 2.8796e-06 | 0.020288 | 0.020288 | 0.020288 | 0.98788 | -0.23205 | 0.98829 | -0.22399 | 5.5736
74 | 0.0052664 | 0.0013198 | -0.0052659 | -0.0013197 | 4.9585e-07 | 4.8539e-08 | 0.007934 | 0.0079341 | 0.0079341 | 0.9877 | -0.23552 | 0.9876 | -0.23749 | 2.1797
75 | -0.015719 | -0.0039414 | 0.015721 | 0.0039422 | 1.506e-06 | 8.7194e-07 | 0.023668 | 0.023668 | 0.023668 | 0.98829 | -0.22399 | 0.98839 | -0.22198 | 6.5022
76 | -0.0078305 | -0.0019589 | 0.0078314 | 0.0019593 | 8.9643e-07 | 3.6835e-07 | 0.011999 | 0.011999 | 0.011999 | 0.97094 | -0.56185 | 0.97106 | -0.55944 | 3.2965
77 | -0.02319 | -0.0058085 | 0.023195 | 0.0058114 | 4.6579e-06 | 2.8593e-06 | 0.035534 | 0.035534 | 0.035534 | 0.97106 | -0.55944 | 0.97127 | -0.55523 | 9.7621
78 | -0.0025741 | -0.00064498 | 0.0025742 | 0.00064483 | 9.874e-08 | -1.4945e-07 | 0.0039292 | 0.0039291 | 0.0039292 | 0.97483 | -0.48462 | 0.97487 | -0.48381 | 1.0794
79 | 0.0014014 | 0.00035106 | -0.0014013 | -0.00035121 | 2.2999e-08 | -1.5239e-07 | 0.002139 | 0.0021391 | 0.0021391 | 0.97483 | -0.48462 | 0.97481 | -0.48496 | 0.58766
80 | -0.0059231 | -0.0014841 | 0.0059233 | 0.0014842 | 2.2549e-07 | 5.2583e-08 | 0.0090407 | 0.0090407 | 0.0090407 | 0.97487 | -0.48381 | 0.97491 | -0.48301 | 2.4837
81 | -0.0074944 | -0.0018779 | 0.0074957 | 0.0018784 | 1.2956e-06 | 4.9987e-07 | 0.011439 | 0.011439 | 0.011439 | 0.97491 | -0.48301 | 0.9751 | -0.47938 | 3.1425
82 | -0.0095886 | -0.002403 | 0.0095888 | 0.002403 | 1.5267e-07 | 7.3988e-08 | 0.014632 | 0.014632 | 0.014632 | 0.9751 | -0.47938 | 0.97511 | -0.47905 | 4.0199
83 | -0.012603 | -0.0031585 | 0.012606 | 0.0031598 | 2.3944e-06 | 1.317e-06 | 0.019232 | 0.019232 | 0.019232 | 0.97511 | -0.47905 | 0.97531 | -0.47506 | 5.2836
84 | 0.0074701 | 0.0018721 | -0.0074688 | -0.0018716 | 1.3305e-06 | 4.8927e-07 | 0.011225 | 0.011225 | 0.011225 | 0.99029 | -0.18512 | 0.9901 | -0.18886 | 3.0837
85 | 0.02288 | 0.0057499 | -0.022853 | -0.0057335 | 2.6842e-05 | 1.6401e-05 | 0.034386 | 0.034386 | 0.034386 | 0.99029 | -0.18512 | 0.98902 | -0.20973 | 9.4467
86 | 0.11966 | 0.030401 | -0.11957 | -0.030348 | 8.3811e-05 | 5.3286e-05 | 0.18012 | 0.18012 | 0.18012 | 0.98932 | -0.20339 | 0.98857 | -0.21795 | 24.7415
87 | 0.029128 | 0.0073338 | -0.029089 | -0.0073094 | 3.9124e-05 | 2.4382e-05 | 0.044467 | 0.044468 | 0.044468 | 0.97499 | -0.4819 | 0.97356 | -0.51004 | 12.2164
88 | 0.027179 | 0.0068306 | -0.027161 | -0.0068197 | 1.7444e-05 | 1.0829e-05 | 0.041547 | 0.041547 | 0.041547 | 0.97356 | -0.51004 | 0.97288 | -0.52349 | 11.4141
89 | -0.017967 | -0.0045053 | 0.017977 | 0.0045115 | 1.0501e-05 | 6.2297e-06 | 0.02705 | 0.02705 | 0.02705 | 0.98839 | -0.22198 | 0.98902 | -0.20973 | 7.4313
90 | 0.007367 | 0.0018464 | -0.0073657 | -0.0018459 | 1.3409e-06 | 5.0249e-07 | 0.01122 | 0.01122 | 0.01122 | 0.97706 | -0.44143 | 0.97686 | -0.44525 | 3.0823
91 | 0.014584 | 0.0036557 | -0.014583 | -0.0036554 | 4.4039e-07 | 2.5065e-07 | 0.02196 | 0.02196 | 0.02196 | 0.9882 | -0.22501 | 0.98817 | -0.22564 | 6.0331
92 | -0.017525 | -0.0043929 | 0.017531 | 0.0043963 | 5.8942e-06 | 3.483e-06 | 0.026389 | 0.026389 | 0.026389 | 0.9882 | -0.22501 | 0.98857 | -0.21795 | 7.2498
93 | 0.010275 | 0.0025755 | -0.010274 | -0.0025754 | 3.3061e-07 | 1.6441e-07 | 0.015472 | 0.015472 | 0.015472 | 0.98817 | -0.22564 | 0.98814 | -0.22631 | 4.2505
94 | 0.10204 | 0.025952 | -0.10197 | -0.025908 | 6.9342e-05 | 4.3978e-05 | 0.15373 | 0.15373 | 0.15373 | 0.98857 | -0.21795 | 0.98783 | -0.23206 | 21.1167
95 | 0.0092844 | 0.0023273 | -0.0092818 | -0.0023261 | 2.6494e-06 | 1.2328e-06 | 0.013981 | 0.013982 | 0.013982 | 0.98814 | -0.22631 | 0.98783 | -0.2323 | 3.8411
96 | 0.099725 | 0.025345 | -0.099673 | -0.025312 | 5.2258e-05 | 3.313e-05 | 0.15035 | 0.15035 | 0.15035 | 0.98783 | -0.23206 | 0.98727 | -0.24295 | 20.6518
97 | 0.0075061 | 0.001881 | -0.0075058 | -0.0018809 | 2.9767e-07 | 1.1102e-07 | 0.011307 | 0.011307 | 0.011307 | 0.98783 | -0.2323 | 0.98779 | -0.23314 | 3.1063
98 | 0.095553 | 0.024279 | -0.095477 | -0.024231 | 7.5484e-05 | 4.7815e-05 | 0.14414 | 0.14414 | 0.14414 | 0.98727 | -0.24295 | 0.98642 | -0.25937 | 19.799
99 | 0.0049026 | 0.0012285 | -0.0049022 | -0.0012285 | 3.0106e-07 | 4.2698e-09 | 0.0073852 | 0.0073853 | 0.0073853 | 0.98779 | -0.23314 | 0.98772 | -0.23443 | 2.0289
100 | 0.0023847 | 0.00059763 | -0.0023847 | -0.00059766 | 1.626e-08 | -3.257e-08 | 0.003593 | 0.0035931 | 0.0035931 | 0.9876 | -0.23749 | 0.98759 | -0.23764 | 0.9871
101 | 0.0024012 | 0.00060154 | -0.0024011 | -0.00060171 | 9.4158e-08 | -1.6932e-07 | 0.0036788 | 0.0036789 | 0.0036789 | 0.97122 | -0.55626 | 0.97118 | -0.55709 | 1.0107
102 | -0.0031527 | -0.00078988 | 0.0031529 | 0.00078976 | 1.5568e-07 | -1.2058e-07 | 0.0048302 | 0.0048301 | 0.0048302 | 0.97122 | -0.55626 | 0.97127 | -0.55523 | 1.327
103 | 0.0014755 | 0.00036973 | -0.0014755 | -0.0003698 | 1.1403e-08 | -6.632e-08 | 0.0022607 | 0.0022607 | 0.0022607 | 0.97118 | -0.55709 | 0.97117 | -0.55725 | 0.62108
104 | -0.026348 | -0.0066011 | 0.026387 | 0.0066258 | 3.9886e-05 | 2.4718e-05 | 0.040364 | 0.040364 | 0.040364 | 0.97127 | -0.55523 | 0.97288 | -0.52349 | 11.0891
105 | 0.0018567 | 0.0004652 | -0.0018567 | -0.00046532 | 3.3608e-08 | -1.251e-07 | 0.0027971 | 0.0027971 | 0.0027971 | 0.98772 | -0.23443 | 0.9877 | -0.23481 | 0.76844
106 | 0.0035071 | 0.00087882 | -0.0035069 | -0.00087892 | 1.834e-07 | -9.7149e-08 | 0.0053422 | 0.0053422 | 0.0053422 | 0.97686 | -0.44525 | 0.97681 | -0.44635 | 1.4676
107 | 0.0022784 | 0.0005708 | -0.0022783 | -0.00057101 | 8.987e-08 | -2.0533e-07 | 0.0034242 | 0.0034243 | 0.0034243 | 0.9901 | -0.18886 | 0.99006 | -0.18969 | 0.94073
108 | 0.037488 | 0.0094495 | -0.037449 | -0.0094249 | 3.8986e-05 | 2.4553e-05 | 0.05712 | 0.05712 | 0.05712 | 0.97691 | -0.44354 | 0.9758 | -0.4653 | 15.6923
109 | 0.034665 | 0.0087273 | -0.034653 | -0.0087197 | 1.1963e-05 | 7.5139e-06 | 0.052875 | 0.052875 | 0.052875 | 0.9758 | -0.4653 | 0.97544 | -0.47252 | 14.5262
110 | 0.031864 | 0.008021 | -0.031815 | -0.0079907 | 4.8378e-05 | 3.0282e-05 | 0.048621 | 0.048621 | 0.048621 | 0.97544 | -0.47252 | 0.97382 | -0.50434 | 13.3574
111 | 0.0027891 | 0.00069877 | -0.0027889 | -0.00069898 | 1.7397e-07 | -2.0853e-07 | 0.0042547 | 0.0042548 | 0.0042548 | 0.97544 | -0.47252 | 0.97537 | -0.47383 | 1.1689
112 | 0.028703 | 0.0072106 | -0.028694 | -0.0072052 | 8.6959e-06 | 5.4155e-06 | 0.043865 | 0.043865 | 0.043865 | 0.97382 | -0.50434 | 0.9735 | -0.51069 | 12.0507
113 | 0.026729 | 0.0067127 | -0.026714 | -0.0067033 | 1.5284e-05 | 9.4783e-06 | 0.040861 | 0.040861 | 0.040861 | 0.9735 | -0.51069 | 0.97289 | -0.52268 | 11.2257
114 | 0.0064074 | 0.0016059 | -0.0064065 | -0.0016056 | 8.0597e-07 | 2.2112e-07 | 0.0096568 | 0.0096569 | 0.0096569 | 0.98731 | -0.2416 | 0.98718 | -0.24424 | 2.653
115 | -0.021273 | -0.0053315 | 0.021292 | 0.005343 | 1.896e-05 | 1.1543e-05 | 0.032574 | 0.032573 | 0.032574 | 0.97178 | -0.54454 | 0.97273 | -0.52585 | 8.9488
116 | -0.024113 | -0.0060501 | 0.024117 | 0.0060523 | 3.6463e-06 | 2.2449e-06 | 0.036889 | 0.036889 | 0.036889 | 0.97273 | -0.52585 | 0.97289 | -0.52268 | 10.1344

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3395 | 0.086665

## res_load
| p_mw | q_mvar
0 | 0.0039877 | 0.00099941
1 | 0.0038221 | 0.00095792
2 | 0.0036423 | 0.00091284
3 | 0.0038869 | 0.00097415
4 | 0.0032115 | 0.00080489
5 | 0.0031216 | 0.00078234
6 | 0.0064348 | 0.0016127
7 | 0.017171 | 0.0043035
8 | 0.003107 | 0.00077869
9 | 0.0025307 | 0.00063425
10 | 0.0041641 | 0.0010436
11 | 0.0025775 | 0.00064598
12 | 0.0047653 | 0.0011943
13 | 0.0011665 | 0.00029235
14 | 0.0018634 | 0.00046701
15 | 0.0021807 | 0.00054653
16 | 0.0049622 | 0.0012436
17 | 0.0022086 | 0.00055352
18 | 0.0025395 | 0.00063645
19 | 0.0041374 | 0.0010369
20 | 0.0034789 | 0.00087189
21 | 0.0034296 | 0.00085955
22 | 0.0013925 | 0.00034898
23 | 0.0015014 | 0.00037629
24 | 0.00060308 | 0.00015114
25 | 0.0022808 | 0.00057163
26 | 0.00055912 | 0.00014013
27 | 0.0021929 | 0.0005496
28 | 0.0047425 | 0.0011886
29 | 0.0020807 | 0.00052147
30 | 0.0026085 | 0.00065375
31 | 0.0025562 | 0.00064064
32 | 0.0029716 | 0.00074476
33 | 0.0034735 | 0.00087054
34 | 0.0066903 | 0.0016768
35 | 0.0029188 | 0.00073152
36 | 0.0025339 | 0.00063506
37 | 0.0032354 | 0.00081086
38 | 0.0038359 | 0.00096137
39 | 0.0042371 | 0.0010619
40 | 0.0035864 | 0.00089883
41 | 0.004226 | 0.0010591
42 | 0.0018102 | 0.00045368
43 | 0.0021437 | 0.00053725
44 | 0.0034348 | 0.00086085
45 | 0.0026043 | 0.00065271
46 | 0.0026259 | 0.00065811
47 | 0.0021892 | 0.00054867
48 | 0.0032561 | 0.00081606
49 | 0.0045598 | 0.0011428
50 | 0.00077836 | 0.00019507
51 | 0.003072 | 0.00076991
52 | 0.0014054 | 0.00035222
53 | 0.0013741 | 0.00034437
54 | 0.00064106 | 0.00016066
55 | 0.004023 | 0.0010083
56 | 0.0041779 | 0.0010471
57 | 0.0022451 | 0.00056267
58 | 0.00055746 | 0.00013971
59 | 0.0011728 | 0.00029392
60 | 0.0033489 | 0.00083931
61 | 0.0014013 | 0.00035121
62 | 0.0015711 | 0.00039376
63 | 0.0020929 | 0.00052452
64 | 0.0030144 | 0.00075547
65 | 0.0040193 | 0.0010073
66 | 0.0053291 | 0.0013356
67 | 0.0038054 | 0.00095373
68 | 0.0030886 | 0.00077407
69 | 0.0019107 | 0.00047887
70 | 0.0022464 | 0.000563
71 | 0.0027419 | 0.00068718
72 | 0.0029413 | 0.00073716
73 | 0.0043089 | 0.0010799
74 | 0.00098984 | 0.00024808
75 | 0.0022466 | 0.00056304
76 | 0.0017757 | 0.00044502
77 | 0.0041197 | 0.0010325
78 | 0.004876 | 0.0012221
79 | 0.0026033 | 0.00065244
80 | 0.0027708 | 0.00069442
81 | 0.0028812 | 0.00072209
82 | 0.00075151 | 0.00018835
83 | 0.00092559 | 0.00023198
84 | 0.0014755 | 0.0003698
85 | 0.00077364 | 0.00019389
86 | 0.0030456 | 0.00076329
87 | 0.0018567 | 0.00046532
88 | 0.0038586 | 0.00096705
89 | 0.0035069 | 0.00087892
90 | 0.0023847 | 0.00059766
91 | 0.0038825 | 0.00097304
92 | 0.0051904 | 0.0013008
93 | 0.0022783 | 0.00057101
94 | 0.004259 | 0.0010674
95 | 0.0027837 | 0.00069765
96 | 0.0031127 | 0.00078011
97 | 0.0027889 | 0.00069898
98 | 0.0019648 | 0.00049242
99 | 0.0020221 | 0.00050679
100 | 0.0098959 | 0.0024802
101 | 0.0064065 | 0.0016056
102 | 0.011264 | 0.0028231
103 | 0.0028212 | 0.00070706
104 | 0.0025972 | 0.00065093

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1