## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_117-18_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_117-18_0_6_node_97 | 0.4 | n |  | TRUE
2 | bus_LV_117-18_0_6_node_95 | 0.4 | n |  | TRUE
3 | bus_LV_117-18_0_6_node_1 | 0.4 | n |  | TRUE
4 | bus_LV_117-18_0_6_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_117-18_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_117-18_0_6_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_117-18_0_6_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_117-18_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_117-18_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_117-18_0_6_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_117-18_0_6_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_117-18_0_6_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_117-18_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_117-18_0_6_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_117-18_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_117-18_0_6_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_117-18_0_6_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_117-18_0_6_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_117-18_0_6_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_117-18_0_6_node_62 | 0.4 | n |  | TRUE
21 | bus_LV_117-18_0_6_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_117-18_0_6_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_117-18_0_6_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_117-18_0_6_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_117-18_0_6_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_117-18_0_6_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_117-18_0_6_node_73 | 0.4 | n |  | TRUE
28 | bus_LV_117-18_0_6_node_71 | 0.4 | n |  | TRUE
29 | bus_LV_117-18_0_6_node_74 | 0.4 | n |  | TRUE
30 | bus_LV_117-18_0_6_node_72 | 0.4 | n |  | TRUE
31 | bus_LV_117-18_0_6_node_69 | 0.4 | n |  | TRUE
32 | bus_LV_117-18_0_6_node_45 | 0.4 | n |  | TRUE
33 | bus_LV_117-18_0_6_node_61 | 0.4 | n |  | TRUE
34 | bus_LV_117-18_0_6_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_117-18_0_6_node_58 | 0.4 | n |  | TRUE
36 | bus_LV_117-18_0_6_node_57 | 0.4 | n |  | TRUE
37 | bus_LV_117-18_0_6_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_117-18_0_6_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_117-18_0_6_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_117-18_0_6_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_117-18_0_6_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_117-18_0_6_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_117-18_0_6_node_135 | 0.4 | n |  | TRUE
44 | bus_LV_117-18_0_6_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_117-18_0_6_node_128 | 0.4 | n |  | TRUE
46 | bus_LV_117-18_0_6_node_130 | 0.4 | n |  | TRUE
47 | bus_LV_117-18_0_6_node_131 | 0.4 | n |  | TRUE
48 | bus_LV_117-18_0_6_node_129 | 0.4 | n |  | TRUE
49 | bus_LV_117-18_0_6_node_81 | 0.4 | n |  | TRUE
50 | bus_LV_117-18_0_6_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_117-18_0_6_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_117-18_0_6_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_117-18_0_6_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_117-18_0_6_node_125 | 0.4 | n |  | TRUE
55 | bus_LV_117-18_0_6_node_116 | 0.4 | n |  | TRUE
56 | bus_LV_117-18_0_6_node_39 | 0.4 | n |  | TRUE
57 | bus_LV_117-18_0_6_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_117-18_0_6_node_126 | 0.4 | n |  | TRUE
59 | bus_LV_117-18_0_6_node_36 | 0.4 | n |  | TRUE
60 | bus_LV_117-18_0_6_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_117-18_0_6_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_117-18_0_6_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_117-18_0_6_node_127 | 0.4 | n |  | TRUE
64 | bus_LV_117-18_0_6_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_117-18_0_6_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_117-18_0_6_node_41 | 0.4 | n |  | TRUE
67 | bus_LV_117-18_0_6_node_115 | 0.4 | n |  | TRUE
68 | bus_LV_117-18_0_6_node_44 | 0.4 | n |  | TRUE
69 | bus_LV_117-18_0_6_node_113 | 0.4 | n |  | TRUE
70 | bus_LV_117-18_0_6_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_117-18_0_6_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_117-18_0_6_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_117-18_0_6_node_50 | 0.4 | n |  | TRUE
74 | bus_LV_117-18_0_6_node_51 | 0.4 | n |  | TRUE
75 | bus_LV_117-18_0_6_node_93 | 0.4 | n |  | TRUE
76 | bus_LV_117-18_0_6_node_112 | 0.4 | n |  | TRUE
77 | bus_LV_117-18_0_6_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_117-18_0_6_node_91 | 0.4 | n |  | TRUE
79 | bus_LV_117-18_0_6_node_53 | 0.4 | n |  | TRUE
80 | bus_LV_117-18_0_6_node_54 | 0.4 | n |  | TRUE
81 | bus_LV_117-18_0_6_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_117-18_0_6_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_117-18_0_6_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_117-18_0_6_node_87 | 0.4 | n |  | TRUE
85 | bus_LV_117-18_0_6_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_117-18_0_6_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_117-18_0_6_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_117-18_0_6_node_86 | 0.4 | n |  | TRUE
89 | bus_LV_117-18_0_6_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_117-18_0_6_node_70 | 0.4 | n |  | TRUE
91 | bus_LV_117-18_0_6_node_75 | 0.4 | n |  | TRUE
92 | bus_LV_117-18_0_6_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_117-18_0_6_node_83 | 0.4 | n |  | TRUE
94 | bus_LV_117-18_0_6_node_84 | 0.4 | n |  | TRUE
95 | bus_LV_117-18_0_6_node_133 | 0.4 | n |  | TRUE
96 | bus_LV_117-18_0_6_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_117-18_0_6_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_117-18_0_6_node_78 | 0.4 | n |  | TRUE
99 | bus_LV_117-18_0_6_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_117-18_0_6_node_138 | 0.4 | n |  | TRUE
101 | bus_LV_117-18_0_6_node_140 | 0.4 | n |  | TRUE
102 | bus_LV_117-18_0_6_node_141 | 0.4 | n |  | TRUE
103 | bus_LV_117-18_0_6_node_139 | 0.4 | n |  | TRUE
104 | bus_LV_117-18_0_6_node_134 | 0.4 | n |  | TRUE
105 | bus_LV_117-18_0_6_node_85 | 0.4 | n |  | TRUE
106 | bus_LV_117-18_0_6_node_147 | 0.4 | n |  | TRUE
107 | bus_LV_117-18_0_6_node_146 | 0.4 | n |  | TRUE
108 | bus_LV_117-18_0_6_node_92 | 0.4 | n |  | TRUE
109 | bus_LV_117-18_0_6_node_94 | 0.4 | n |  | TRUE
110 | bus_LV_117-18_0_6_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_117-18_0_6_node_104 | 0.4 | n |  | TRUE
112 | bus_LV_117-18_0_6_node_96 | 0.4 | n |  | TRUE
113 | bus_LV_117-18_0_6_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_117-18_0_6_node_99 | 0.4 | n |  | TRUE
115 | bus_LV_117-18_0_6_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_117-18_0_6_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_117-18_0_6_node_102 | 0.4 | n |  | TRUE
118 | bus_LV_117-18_0_6_node_121 | 0.4 | n |  | TRUE
119 | bus_LV_117-18_0_6_node_118 | 0.4 | n |  | TRUE
120 | bus_LV_117-18_0_6_node_154 | 0.4 | n |  | TRUE
121 | bus_LV_117-18_0_6_node_117 | 0.4 | n |  | TRUE
122 | bus_LV_117-18_0_6_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_117-18_0_6_node_106 | 0.4 | n |  | TRUE
124 | bus_LV_117-18_0_6_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_117-18_0_6_node_114 | 0.4 | n |  | TRUE
126 | bus_LV_117-18_0_6_node_108 | 0.4 | n |  | TRUE
127 | bus_LV_117-18_0_6_node_109 | 0.4 | n |  | TRUE
128 | bus_LV_117-18_0_6_node_110 | 0.4 | n |  | TRUE
129 | bus_LV_117-18_0_6_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_117-18_0_6_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_117-18_0_6_node_120 | 0.4 | n |  | TRUE
132 | bus_LV_117-18_0_6_node_122 | 0.4 | n |  | TRUE
133 | bus_LV_117-18_0_6_node_123 | 0.4 | n |  | TRUE
134 | bus_LV_117-18_0_6_node_124 | 0.4 | n |  | TRUE
135 | bus_LV_117-18_0_6_node_132 | 0.4 | n |  | TRUE
136 | bus_LV_117-18_0_6_node_136 | 0.4 | n |  | TRUE
137 | bus_LV_117-18_0_6_node_137 | 0.4 | n |  | TRUE
138 | bus_LV_117-18_0_6_node_144 | 0.4 | n |  | TRUE
139 | bus_LV_117-18_0_6_node_143 | 0.4 | n |  | TRUE
140 | bus_LV_117-18_0_6_node_142 | 0.4 | n |  | TRUE
141 | bus_LV_117-18_0_6_node_145 | 0.4 | n |  | TRUE
142 | bus_LV_117-18_0_6_node_149 | 0.4 | n |  | TRUE
143 | bus_LV_117-18_0_6_node_150 | 0.4 | n |  | TRUE
144 | bus_LV_117-18_0_6_node_151 | 0.4 | n |  | TRUE
145 | bus_LV_117-18_0_6_node_152 | 0.4 | n |  | TRUE
146 | bus_LV_117-18_0_6_node_153 | 0.4 | n |  | TRUE
147 | bus_MV_8_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_117-18_0_6_load_0 | 0 | 0.00044843 | 0.00011239 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_117-18_0_6_load_97 | 1 | 0.0012622 | 0.00031634 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_117-18_0_6_load_95 | 2 | 0.0012912 | 0.00032361 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_117-18_0_6_load_1 | 3 | 0.0082965 | 0.0020793 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_117-18_0_6_load_2 | 4 | 0.0078372 | 0.0019642 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_117-18_0_6_load_10 | 6 | 0.0043909 | 0.0011005 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_117-18_0_6_load_11 | 7 | 0.0026393 | 0.00066147 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_117-18_0_6_load_6 | 8 | 0.0043595 | 0.0010926 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_117-18_0_6_load_24 | 10 | 0.021182 | 0.0053087 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_117-18_0_6_load_13 | 11 | 0.0077749 | 0.0019486 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_117-18_0_6_load_7 | 14 | 0.0064002 | 0.001604 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_117-18_0_6_load_8 | 15 | 0.0043668 | 0.0010944 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_117-18_0_6_load_14 | 16 | 0.004532 | 0.0011358 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_117-18_0_6_load_20 | 17 | 0.012395 | 0.0031064 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_117-18_0_6_load_12 | 18 | 0.0035193 | 0.00088201 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_117-18_0_6_load_62 | 20 | 0.011566 | 0.0028988 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_117-18_0_6_load_15 | 21 | 0.0054919 | 0.0013764 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_117-18_0_6_load_17 | 23 | 0.0045834 | 0.0011487 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_117-18_0_6_load_18 | 24 | 0.011259 | 0.0028218 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_117-18_0_6_load_19 | 25 | 0.0072245 | 0.0018106 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_117-18_0_6_load_73 | 27 | 0.0014854 | 0.00037228 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_117-18_0_6_load_72 | 30 | 0.0022676 | 0.00056832 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_117-18_0_6_load_69 | 31 | 0.001308 | 0.00032782 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_117-18_0_6_load_45 | 32 | 0.004511 | 0.0011306 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_117-18_0_6_load_61 | 33 | 0.0136 | 0.0034085 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_117-18_0_6_load_25 | 37 | 0.0022471 | 0.00056317 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_117-18_0_6_load_26 | 38 | 0.0029047 | 0.00072798 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_117-18_0_6_load_29 | 41 | 0.0028179 | 0.00070622 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_117-18_0_6_load_30 | 42 | 0.0068315 | 0.0017121 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_117-18_0_6_load_135 | 43 | 0.0020952 | 0.00052511 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_117-18_0_6_load_31 | 44 | 0.0056011 | 0.0014038 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_117-18_0_6_load_131 | 47 | 0.0090833 | 0.0022765 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_117-18_0_6_load_129 | 48 | 0.0085757 | 0.0021493 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_117-18_0_6_load_34 | 51 | 0.0068075 | 0.0017061 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_117-18_0_6_load_125 | 54 | 0.005885 | 0.0014749 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_117-18_0_6_load_35 | 57 | 0.0078455 | 0.0019663 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_117-18_0_6_load_36 | 59 | 0.0060081 | 0.0015058 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_117-18_0_6_load_40 | 61 | 0.019401 | 0.0048623 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_117-18_0_6_load_127 | 63 | 0.0058255 | 0.00146 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_117-18_0_6_load_48 | 64 | 0.0027363 | 0.00068578 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_117-18_0_6_load_46 | 65 | 0.011663 | 0.0029231 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_117-18_0_6_load_41 | 66 | 0.0076624 | 0.0019204 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_117-18_0_6_load_44 | 68 | 0.01096 | 0.0027469 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_117-18_0_6_load_113 | 69 | 0.005791 | 0.0014514 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_117-18_0_6_load_49 | 72 | 0.0028216 | 0.00070715 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_117-18_0_6_load_50 | 73 | 0.0052187 | 0.0013079 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_117-18_0_6_load_51 | 74 | 0.0022195 | 0.00055627 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_117-18_0_6_load_112 | 76 | 0.0022629 | 0.00056714 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_117-18_0_6_load_52 | 77 | 0.0022087 | 0.00055356 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_117-18_0_6_load_91 | 78 | 0.0021436 | 0.00053723 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_117-18_0_6_load_53 | 79 | 0.002904 | 0.0007278 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_117-18_0_6_load_54 | 80 | 0.0022315 | 0.00055926 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_117-18_0_6_load_60 | 81 | 0.012828 | 0.0032151 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_117-18_0_6_load_67 | 83 | 0.0015233 | 0.00038178 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_117-18_0_6_load_87 | 84 | 0.0033537 | 0.00084052 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_117-18_0_6_load_63 | 85 | 0.0033189 | 0.00083178 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_117-18_0_6_load_64 | 86 | 0.0056226 | 0.0014091 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_117-18_0_6_load_66 | 87 | 0.0021376 | 0.00053573 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_117-18_0_6_load_86 | 88 | 0.0029367 | 0.00073601 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_117-18_0_6_load_68 | 89 | 0.0042133 | 0.001056 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_117-18_0_6_load_70 | 90 | 0.0064612 | 0.0016193 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_117-18_0_6_load_75 | 91 | 0.0092522 | 0.0023188 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_117-18_0_6_load_76 | 92 | 0.0013192 | 0.00033063 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_117-18_0_6_load_83 | 93 | 0.0014635 | 0.00036678 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_117-18_0_6_load_84 | 94 | 0.0039489 | 0.00098968 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_117-18_0_6_load_133 | 95 | 0.0059414 | 0.0014891 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_117-18_0_6_load_77 | 97 | 0.016232 | 0.0040682 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_117-18_0_6_load_78 | 98 | 0.010408 | 0.0026084 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_117-18_0_6_load_82 | 99 | 0.0061024 | 0.0015294 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_117-18_0_6_load_138 | 100 | 0.0053211 | 0.0013336 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_117-18_0_6_load_139 | 103 | 0.0050606 | 0.0012683 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_117-18_0_6_load_147 | 106 | 0.010738 | 0.0026913 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_117-18_0_6_load_146 | 107 | 0.0087874 | 0.0022023 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_117-18_0_6_load_92 | 108 | 0.002565 | 0.00064284 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_117-18_0_6_load_94 | 109 | 0.0020205 | 0.00050639 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_117-18_0_6_load_103 | 110 | 0.0014768 | 0.00037011 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_117-18_0_6_load_104 | 111 | 0.0018487 | 0.00046333 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_117-18_0_6_load_96 | 112 | 0.0027386 | 0.00068635 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_117-18_0_6_load_98 | 113 | 0.0022486 | 0.00056356 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_117-18_0_6_load_99 | 114 | 0.00307 | 0.00076942 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_117-18_0_6_load_100 | 115 | 0.0020026 | 0.00050189 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_117-18_0_6_load_101 | 116 | 0.0031662 | 0.00079354 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_117-18_0_6_load_121 | 118 | 0.002447 | 0.00061328 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_117-18_0_6_load_118 | 119 | 0.0056036 | 0.0014044 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_117-18_0_6_load_154 | 120 | 0.00085246 | 0.00021365 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_117-18_0_6_load_117 | 121 | 0.0062251 | 0.0015601 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_117-18_0_6_load_105 | 122 | 0.002795 | 0.0007005 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_117-18_0_6_load_106 | 123 | 0.0026358 | 0.0006606 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_117-18_0_6_load_107 | 124 | 0.0054298 | 0.0013608 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_117-18_0_6_load_114 | 125 | 0.0030719 | 0.00076988 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_117-18_0_6_load_108 | 126 | 0.013353 | 0.0033467 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_117-18_0_6_load_109 | 127 | 0.0036449 | 0.00091349 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_117-18_0_6_load_110 | 128 | 0.0036457 | 0.00091369 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_117-18_0_6_load_119 | 130 | 0.0026913 | 0.0006745 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_117-18_0_6_load_120 | 131 | 0.0034002 | 0.00085216 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_117-18_0_6_load_122 | 132 | 0.0036793 | 0.00092213 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_117-18_0_6_load_123 | 133 | 0.0047819 | 0.0011985 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_117-18_0_6_load_124 | 134 | 0.0073228 | 0.0018353 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_117-18_0_6_load_132 | 135 | 0.00239 | 0.00059899 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_117-18_0_6_load_136 | 136 | 0.0067958 | 0.0017032 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_117-18_0_6_load_137 | 137 | 0.009219 | 0.0023105 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_117-18_0_6_load_144 | 138 | 0.005605 | 0.0014048 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_117-18_0_6_load_142 | 140 | 0.0052876 | 0.0013252 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_117-18_0_6_load_149 | 142 | 0.0021788 | 0.00054605 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_117-18_0_6_load_150 | 143 | 0.0021796 | 0.00054625 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_117-18_0_6_load_151 | 144 | 0.0021797 | 0.00054627 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_117-18_0_6_load_152 | 145 | 0.0021796 | 0.00054625 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_117-18_0_6_load_153 | 146 | 0.0036819 | 0.00092277 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_117-18_0_6_line_0 |  | 0 | 1 | 0.48632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_117-18_0_6_line_1 |  | 1 | 2 | 0.014972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_117-18_0_6_line_2 |  | 2 | 112 | 0.028984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_117-18_0_6_line_3 |  | 3 | 4 | 0.007039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_117-18_0_6_line_4 |  | 4 | 5 | 0.019695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_117-18_0_6_line_5 |  | 5 | 9 | 0.024424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_117-18_0_6_line_6 |  | 6 | 7 | 0.016236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_117-18_0_6_line_7 |  | 6 | 8 | 0.02413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_117-18_0_6_line_8 |  | 7 | 18 | 0.0076622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_117-18_0_6_line_9 |  | 8 | 14 | 0.023597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_117-18_0_6_line_10 |  | 8 | 15 | 0.012928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_117-18_0_6_line_11 |  | 9 | 11 | 0.024699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_117-18_0_6_line_12 |  | 9 | 10 | 0.014961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_117-18_0_6_line_13 |  | 11 | 12 | 0.020932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_117-18_0_6_line_14 |  | 11 | 13 | 0.037122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_117-18_0_6_line_15 |  | 12 | 22 | 0.016773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_117-18_0_6_line_16 |  | 13 | 17 | 0.034119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_117-18_0_6_line_17 |  | 13 | 14 | 0.010419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_117-18_0_6_line_18 |  | 15 | 16 | 0.026662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_117-18_0_6_line_19 |  | 18 | 19 | 0.011822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_117-18_0_6_line_20 |  | 19 | 20 | 0.019929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_117-18_0_6_line_21 |  | 19 | 21 | 0.014303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_117-18_0_6_line_22 |  | 22 | 32 | 0.0098583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_117-18_0_6_line_23 |  | 22 | 33 | 0.0409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_117-18_0_6_line_24 |  | 23 | 24 | 0.030865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_117-18_0_6_line_25 |  | 23 | 25 | 0.037586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_117-18_0_6_line_26 |  | 25 | 26 | 0.015978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_117-18_0_6_line_27 |  | 26 | 27 | 0.010918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_117-18_0_6_line_28 |  | 26 | 28 | 0.021428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_117-18_0_6_line_29 |  | 27 | 29 | 0.019411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_117-18_0_6_line_30 |  | 28 | 30 | 0.007541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_117-18_0_6_line_31 |  | 28 | 31 | 0.02464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_117-18_0_6_line_32 |  | 29 | 91 | 0.033131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_117-18_0_6_line_33 |  | 29 | 92 | 0.026695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_117-18_0_6_line_34 |  | 30 | 87 | 0.0016504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_117-18_0_6_line_35 |  | 31 | 89 | 0.013525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_117-18_0_6_line_36 |  | 32 | 34 | 0.012226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_117-18_0_6_line_37 |  | 33 | 35 | 0.015202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_117-18_0_6_line_38 |  | 34 | 66 | 0.0070136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_117-18_0_6_line_39 |  | 35 | 36 | 0.034895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_117-18_0_6_line_40 |  | 36 | 71 | 0.076207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_117-18_0_6_line_41 |  | 36 | 68 | 0.00037909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_117-18_0_6_line_42 |  | 37 | 38 | 0.01894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_117-18_0_6_line_43 |  | 37 | 39 | 0.0068188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_117-18_0_6_line_44 |  | 38 | 40 | 0.022656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_117-18_0_6_line_45 |  | 39 | 41 | 0.013109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_117-18_0_6_line_46 |  | 39 | 42 | 0.018803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_117-18_0_6_line_47 |  | 40 | 43 | 0.0035149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_117-18_0_6_line_48 |  | 41 | 44 | 0.021655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_117-18_0_6_line_49 |  | 42 | 45 | 0.010821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_117-18_0_6_line_50 |  | 43 | 49 | 0.028398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_117-18_0_6_line_51 |  | 44 | 50 | 0.0058272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_117-18_0_6_line_52 |  | 45 | 48 | 0.028454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_117-18_0_6_line_53 |  | 46 | 47 | 0.0032528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_117-18_0_6_line_54 |  | 46 | 48 | 0.015476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_117-18_0_6_line_55 |  | 47 | 135 | 0.022245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_117-18_0_6_line_56 |  | 49 | 95 | 0.023148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_117-18_0_6_line_57 |  | 49 | 96 | 0.007621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_117-18_0_6_line_58 |  | 49 | 92 | 0.017273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_117-18_0_6_line_59 |  | 50 | 51 | 0.019007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_117-18_0_6_line_60 |  | 51 | 55 | 0.014455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_117-18_0_6_line_61 |  | 52 | 53 | 0.018544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_117-18_0_6_line_62 |  | 52 | 54 | 0.018916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_117-18_0_6_line_63 |  | 53 | 56 | 0.008034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_117-18_0_6_line_64 |  | 53 | 57 | 0.027905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_117-18_0_6_line_65 |  | 54 | 58 | 0.014767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_117-18_0_6_line_66 |  | 55 | 58 | 0.030507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_117-18_0_6_line_67 |  | 56 | 62 | 0.052963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_117-18_0_6_line_68 |  | 56 | 63 | 0.01985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_117-18_0_6_line_69 |  | 57 | 59 | 0.0041362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_117-18_0_6_line_70 |  | 59 | 60 | 0.035539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_117-18_0_6_line_71 |  | 60 | 61 | 0.0061831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_117-18_0_6_line_72 |  | 61 | 66 | 0.026155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_117-18_0_6_line_73 |  | 62 | 64 | 0.01797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_117-18_0_6_line_74 |  | 62 | 65 | 0.018874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_117-18_0_6_line_75 |  | 63 | 67 | 0.016001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_117-18_0_6_line_76 |  | 64 | 69 | 0.0082024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_117-18_0_6_line_77 |  | 65 | 70 | 0.023539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_117-18_0_6_line_78 |  | 67 | 129 | 0.019326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_117-18_0_6_line_79 |  | 69 | 76 | 0.011599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_117-18_0_6_line_80 |  | 70 | 72 | 0.042616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_117-18_0_6_line_81 |  | 70 | 73 | 0.020055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_117-18_0_6_line_82 |  | 71 | 81 | 0.024409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_117-18_0_6_line_83 |  | 72 | 74 | 0.00975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_117-18_0_6_line_84 |  | 73 | 75 | 0.0082055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_117-18_0_6_line_85 |  | 74 | 77 | 0.0071473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_117-18_0_6_line_86 |  | 75 | 78 | 0.022182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_117-18_0_6_line_87 |  | 76 | 125 | 0.012806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_117-18_0_6_line_88 |  | 77 | 79 | 0.00066524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_117-18_0_6_line_89 |  | 78 | 108 | 0.0044907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_117-18_0_6_line_90 |  | 79 | 80 | 0.021285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_117-18_0_6_line_91 |  | 82 | 83 | 0.012751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_117-18_0_6_line_92 |  | 82 | 84 | 0.056932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_117-18_0_6_line_93 |  | 82 | 85 | 0.016948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_117-18_0_6_line_94 |  | 84 | 88 | 0.016058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_117-18_0_6_line_95 |  | 85 | 86 | 0.0020937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_117-18_0_6_line_96 |  | 86 | 87 | 0.021834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_117-18_0_6_line_97 |  | 89 | 90 | 0.011325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_117-18_0_6_line_98 |  | 91 | 93 | 0.00090413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_117-18_0_6_line_99 |  | 93 | 94 | 0.027887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_117-18_0_6_line_100 |  | 94 | 105 | 0.063664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_117-18_0_6_line_101 |  | 95 | 104 | 0.023364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_117-18_0_6_line_102 |  | 96 | 99 | 0.028038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_117-18_0_6_line_103 |  | 96 | 97 | 0.02466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_117-18_0_6_line_104 |  | 97 | 98 | 0.041482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_117-18_0_6_line_105 |  | 99 | 100 | 0.032084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_117-18_0_6_line_106 |  | 100 | 103 | 0.031858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_117-18_0_6_line_107 |  | 101 | 102 | 0.009463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_117-18_0_6_line_108 |  | 101 | 103 | 0.042252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_117-18_0_6_line_109 |  | 102 | 140 | 0.01672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_117-18_0_6_line_110 |  | 104 | 136 | 0.0079418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_117-18_0_6_line_111 |  | 105 | 106 | 0.054229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_117-18_0_6_line_112 |  | 106 | 107 | 0.024886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_117-18_0_6_line_113 |  | 108 | 109 | 0.026059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_117-18_0_6_line_114 |  | 110 | 111 | 0.016825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_117-18_0_6_line_115 |  | 111 | 122 | 0.026272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_117-18_0_6_line_116 |  | 112 | 113 | 0.042894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_117-18_0_6_line_117 |  | 113 | 114 | 0.034153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_117-18_0_6_line_118 |  | 114 | 115 | 0.031339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_117-18_0_6_line_119 |  | 115 | 116 | 0.013822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_117-18_0_6_line_120 |  | 116 | 117 | 0.014918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_117-18_0_6_line_121 |  | 117 | 118 | 0.017015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_117-18_0_6_line_122 |  | 117 | 119 | 0.035708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_117-18_0_6_line_123 |  | 118 | 120 | 0.01124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_117-18_0_6_line_124 |  | 119 | 121 | 0.00027264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_117-18_0_6_line_125 |  | 121 | 130 | 0.036847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_117-18_0_6_line_126 |  | 122 | 123 | 0.0094848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_117-18_0_6_line_127 |  | 123 | 124 | 0.0081948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_117-18_0_6_line_128 |  | 124 | 125 | 0.015196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_117-18_0_6_line_129 |  | 126 | 127 | 0.017464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_117-18_0_6_line_130 |  | 126 | 128 | 0.010673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_117-18_0_6_line_131 |  | 127 | 129 | 0.0037388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_117-18_0_6_line_132 |  | 130 | 131 | 0.021841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_117-18_0_6_line_133 |  | 131 | 132 | 0.00041073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_117-18_0_6_line_134 |  | 132 | 133 | 0.026106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_117-18_0_6_line_135 |  | 133 | 134 | 0.0015461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_117-18_0_6_line_136 |  | 134 | 135 | 0.022082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_117-18_0_6_line_137 |  | 137 | 138 | 0.027636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_117-18_0_6_line_138 |  | 138 | 139 | 0.03036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_117-18_0_6_line_139 |  | 139 | 141 | 0.018904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_117-18_0_6_line_140 |  | 139 | 140 | 0.01746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_117-18_0_6_line_141 |  | 141 | 142 | 0.0099162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_117-18_0_6_line_142 |  | 142 | 143 | 0.017995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_117-18_0_6_line_143 |  | 143 | 144 | 0.018568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_117-18_0_6_line_144 |  | 144 | 145 | 0.018636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_117-18_0_6_line_145 |  | 145 | 146 | 0.015255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_117-18_0_6_trafo_31 | 0.63 MVA 20/0.4 kV | 147 | 44 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2706267.6123 | 1239247.1662 | 2706604.5002 | 1238896.4345
1 | 2706267.6123 | 1239247.1662 | 2706262.9962 | 1239261.4089
2 | 2706262.9962 | 1239261.4089 | 2706254.0601 | 1239288.9809
3 | 2706134.2203 | 1239638.2839 | 2706131.5625 | 1239631.766
4 | 2706124.1258 | 1239613.5287 | 2706131.5625 | 1239631.766
5 | 2706124.1258 | 1239613.5287 | 2706116.066 | 1239590.4668
6 | 2706205.338 | 1239654.4345 | 2706197.0832 | 1239640.4539
7 | 2706197.0832 | 1239640.4539 | 2706189.966 | 1239617.3977
8 | 2706209.2337 | 1239661.0324 | 2706205.338 | 1239654.4345
9 | 2706189.966 | 1239617.3977 | 2706181.1854 | 1239595.4956
10 | 2706201.5881 | 1239611.7345 | 2706189.966 | 1239617.3977
11 | 2706116.066 | 1239590.4668 | 2706138.8582 | 1239585.8039 | 2706140.2908 | 1239585.7263
12 | 2706121.1785 | 1239576.4061 | 2706116.066 | 1239590.4668
13 | 2706141.3516 | 1239564.821 | 2706140.2908 | 1239585.7263
14 | 2706177.3083 | 1239585.8246 | 2706163.8756 | 1239584.4501 | 2706140.2908 | 1239585.7263
15 | 2706141.3516 | 1239564.821 | 2706138.4006 | 1239550.4905 | 2706138.1588 | 1239548.3623
16 | 2706209.9752 | 1239575.9759 | 2706177.3083 | 1239585.8246
17 | 2706177.3083 | 1239585.8246 | 2706181.1854 | 1239595.4956
18 | 2706219.9288 | 1239631.0863 | 2706201.5881 | 1239611.7345
19 | 2706217.2746 | 1239669.3265 | 2706211.9474 | 1239665.6283 | 2706209.2337 | 1239661.0324
20 | 2706217.2746 | 1239669.3265 | 2706215.7176 | 1239672.212 | 2706230.43 | 1239680.0072
21 | 2706217.2746 | 1239669.3265 | 2706224.0589 | 1239656.735
22 | 2706138.1588 | 1239548.3623 | 2706137.8555 | 1239538.5086
23 | 2706138.1588 | 1239548.3623 | 2706097.7392 | 1239554.6112
24 | 2706273.3008 | 1239610.4943 | 2706261.263 | 1239601.2607 | 2706247.1871 | 1239594.3213
25 | 2706273.3008 | 1239610.4943 | 2706281.9103 | 1239617.0981 | 2706301.4409 | 1239635.3564
26 | 2706313.1131 | 1239646.2682 | 2706301.4409 | 1239635.3564
27 | 2706313.1131 | 1239646.2682 | 2706324.0273 | 1239646.541
28 | 2706300.6152 | 1239662.8129 | 2706303.7431 | 1239660.4893 | 2706308.6993 | 1239656.6084 | 2706310.4078 | 1239653.2919 | 2706313.1131 | 1239646.2682
29 | 2706342.64 | 1239641.0485 | 2706324.122 | 1239646.5434 | 2706324.0273 | 1239646.541
30 | 2706300.6152 | 1239662.8129 | 2706295.356 | 1239668.2172
31 | 2706300.6152 | 1239662.8129 | 2706296.295 | 1239653.1503 | 2706285.5646 | 1239644.0719
32 | 2706342.64 | 1239641.0485 | 2706361.4848 | 1239668.2983
33 | 2706342.64 | 1239641.0485 | 2706344.2076 | 1239621.1166 | 2706347.3831 | 1239615.2148
34 | 2706294.205 | 1239669.4 | 2706295.356 | 1239668.2172
35 | 2706275.2393 | 1239635.3362 | 2706285.5646 | 1239644.0719
36 | 2706137.4795 | 1239526.2886 | 2706137.8555 | 1239538.5086
37 | 2706082.716 | 1239556.9337 | 2706097.7392 | 1239554.6112
38 | 2706137.4795 | 1239526.2886 | 2706144.4754 | 1239525.7922
39 | 2706070.9504 | 1239530.8477 | 2706072.748 | 1239553.8533 | 2706081.3689 | 1239554.0074 | 2706082.716 | 1239556.9337
40 | 2706009.3162 | 1239538.3529 | 2706017.2693 | 1239553.8625 | 2706060.1758 | 1239532.69 | 2706070.9504 | 1239530.8477
41 | 2706071.3286 | 1239530.8218 | 2706070.9504 | 1239530.8477
42 | 2706300.01 | 1239558.2272 | 2706316.1863 | 1239568.0784
43 | 2706294.1861 | 1239554.6805 | 2706300.01 | 1239558.2272
44 | 2706335.5367 | 1239579.8626 | 2706316.1863 | 1239568.0784
45 | 2706294.1861 | 1239554.6805 | 2706282.9878 | 1239547.8649
46 | 2706294.1861 | 1239554.6805 | 2706304.449 | 1239538.9252
47 | 2706335.5367 | 1239579.8626 | 2706338.0623 | 1239582.3071
48 | 2706282.9878 | 1239547.8649 | 2706276.6984 | 1239544.037 | 2706267.97 | 1239532.7191
49 | 2706311.3841 | 1239530.8365 | 2706308.2264 | 1239533.1262 | 2706304.449 | 1239538.9252
50 | 2706358.4679 | 1239602.0572 | 2706338.0623 | 1239582.3071
51 | 2706264.4114 | 1239528.1047 | 2706267.97 | 1239532.7191
52 | 2706311.3841 | 1239530.8365 | 2706321.8916 | 1239523.2187 | 2706335.083 | 1239531.3112
53 | 2706348.2744 | 1239539.4038 | 2706348.4754 | 1239536.6274 | 2706348.3333 | 1239536.1803
54 | 2706348.2744 | 1239539.4038 | 2706335.083 | 1239531.3112
55 | 2706348.3333 | 1239536.1803 | 2706343.8996 | 1239522.2343 | 2706339.2351 | 1239516.2204
56 | 2706358.4679 | 1239602.0572 | 2706374.8365 | 1239585.6895
57 | 2706358.4679 | 1239602.0572 | 2706364.3336 | 1239606.9439
58 | 2706358.4679 | 1239602.0572 | 2706348.6757 | 1239612.8124 | 2706347.3831 | 1239615.2148
59 | 2706264.4114 | 1239528.1047 | 2706279.5866 | 1239516.6599
60 | 2706291.1274 | 1239507.9561 | 2706279.5866 | 1239516.6599
61 | 2706234.1966 | 1239488.9114 | 2706245.5299 | 1239503.6145
62 | 2706245.5299 | 1239503.6145 | 2706260.7608 | 1239492.3971
63 | 2706234.1966 | 1239488.9114 | 2706228.2803 | 1239483.4569
64 | 2706234.1966 | 1239488.9114 | 2706212.3242 | 1239506.2405
65 | 2706272.6514 | 1239483.6399 | 2706260.7608 | 1239492.3971
66 | 2706291.1274 | 1239507.9561 | 2706272.6514 | 1239483.6399
67 | 2706184.9497 | 1239453.4586 | 2706190.3348 | 1239456.8909 | 2706215.1974 | 1239471.4024 | 2706228.2803 | 1239483.4569
68 | 2706228.2803 | 1239483.4569 | 2706232.6485 | 1239476.0848 | 2706241.7058 | 1239469.3591
69 | 2706212.3242 | 1239506.2405 | 2706209.0822 | 1239508.8091
70 | 2706176.5833 | 1239522.3513 | 2706193.5909 | 1239517.574 | 2706205.4977 | 1239511.649 | 2706209.0822 | 1239508.8091
71 | 2706176.5833 | 1239522.3513 | 2706170.5066 | 1239523.493
72 | 2706170.5066 | 1239523.493 | 2706166.6402 | 1239524.2194 | 2706144.4754 | 1239525.7922
73 | 2706184.9497 | 1239453.4586 | 2706195.6714 | 1239439.0377
74 | 2706184.9497 | 1239453.4586 | 2706169.593 | 1239442.4866
75 | 2706254.5521 | 1239459.8197 | 2706241.7058 | 1239469.3591
76 | 2706195.6714 | 1239439.0377 | 2706200.5653 | 1239432.4552
77 | 2706153.6769 | 1239425.1441 | 2706169.593 | 1239442.4866
78 | 2706272.5497 | 1239453.8371 | 2706266.2229 | 1239453.9907 | 2706254.5521 | 1239459.8197
79 | 2706207.4859 | 1239423.147 | 2706200.5653 | 1239432.4552
80 | 2706153.6769 | 1239425.1441 | 2706115.5245 | 1239444.1309
81 | 2706153.6769 | 1239425.1441 | 2706142.8884 | 1239408.2376
82 | 2706009.3162 | 1239538.3529 | 2706006.914 | 1239533.5062 | 2706001.116 | 1239521.8492 | 2705998.856 | 1239516.3125
83 | 2706115.5245 | 1239444.1309 | 2706113.6665 | 1239445.0555 | 2706106.0816 | 1239446.2255
84 | 2706138.4744 | 1239401.3205 | 2706142.8884 | 1239408.2376
85 | 2706099.2268 | 1239445.0491 | 2706103.6534 | 1239446.6 | 2706106.0816 | 1239446.2255
86 | 2706138.4744 | 1239401.3205 | 2706157.0354 | 1239389.1747
87 | 2706207.4859 | 1239423.147 | 2706215.1264 | 1239412.8704
88 | 2706098.599 | 1239444.8291 | 2706099.2268 | 1239445.0491
89 | 2706157.0354 | 1239389.1747 | 2706160.7931 | 1239386.7158
90 | 2706078.5113 | 1239437.7911 | 2706098.599 | 1239444.8291
91 | 2706265.6981 | 1239698.6935 | 2706256.4637 | 1239707.4871
92 | 2706265.6981 | 1239698.6935 | 2706303.3833 | 1239741.3679
93 | 2706265.6981 | 1239698.6935 | 2706277.5176 | 1239686.5478
94 | 2706319.4403 | 1239741.1668 | 2706303.3833 | 1239741.3679 | 2706303.3833 | 1239741.3679
95 | 2706277.5176 | 1239686.5478 | 2706278.9778 | 1239685.0473
96 | 2706294.205 | 1239669.4 | 2706278.9778 | 1239685.0473
97 | 2706266.5932 | 1239628.0213 | 2706275.2393 | 1239635.3362
98 | 2706361.4848 | 1239668.2983 | 2706361.9991 | 1239669.0419
99 | 2706361.9991 | 1239669.0419 | 2706370.5701 | 1239681.4357 | 2706379.1306 | 1239690.9764
100 | 2706423.2225 | 1239736.8779 | 2706392.2403 | 1239705.5872 | 2706379.1306 | 1239690.9764
101 | 2706392.5496 | 1239570.6434 | 2706385.0035 | 1239575.5231 | 2706374.8365 | 1239585.6895
102 | 2706364.3336 | 1239606.9439 | 2706373.8723 | 1239609.906 | 2706391.8356 | 1239611.6687
103 | 2706364.3336 | 1239606.9439 | 2706372.3055 | 1239612.491 | 2706386.3384 | 1239617.6412
104 | 2706427.3435 | 1239620.1503 | 2706408.0297 | 1239620.2482 | 2706393.6482 | 1239620.3239 | 2706386.3384 | 1239617.6412
105 | 2706423.9034 | 1239612.242 | 2706394.9477 | 1239611.9741 | 2706391.8356 | 1239611.6687
106 | 2706423.9034 | 1239612.242 | 2706435.9255 | 1239612.3532 | 2706455.365 | 1239608.4113
107 | 2706498.0592 | 1239599.3572 | 2706496.4394 | 1239608.6798
108 | 2706496.4394 | 1239608.6798 | 2706478.7983 | 1239603.6596 | 2706455.365 | 1239608.4113
109 | 2706498.0592 | 1239599.3572 | 2706493.9085 | 1239583.1602
110 | 2706392.5496 | 1239570.6434 | 2706400.148 | 1239568.3333
111 | 2706423.2225 | 1239736.8779 | 2706458.633 | 1239695.8057
112 | 2706474.8827 | 1239676.9578 | 2706458.633 | 1239695.8057
113 | 2706183.3553 | 1239373.8937 | 2706175.5752 | 1239377.0428 | 2706160.7931 | 1239386.7158
114 | 2706227.9093 | 1239362.2117 | 2706227.9093 | 1239362.2117 | 2706215.8013 | 1239360.7606 | 2706211.5094 | 1239362.4979
115 | 2706227.9093 | 1239362.2117 | 2706233.803 | 1239371.4688 | 2706236.1411 | 1239380.7289 | 2706233.9624 | 1239386.0477
116 | 2706254.0601 | 1239288.9809 | 2706251.7176 | 1239296.2087 | 2706244.2598 | 1239313.0439 | 2706250.0796 | 1239328.8921
117 | 2706250.0796 | 1239328.8921 | 2706253.204 | 1239337.4006 | 2706267.6869 | 1239357.8867
118 | 2706296.1559 | 1239370.9895 | 2706267.6869 | 1239357.8867 | 2706267.6869 | 1239357.8867
119 | 2706308.7116 | 1239376.7682 | 2706296.1559 | 1239370.9895
120 | 2706322.2634 | 1239383.0054 | 2706308.7116 | 1239376.7682
121 | 2706322.2634 | 1239383.0054 | 2706330.1594 | 1239367.933
122 | 2706322.2634 | 1239383.0054 | 2706311.4156 | 1239417.0258
123 | 2706335.3754 | 1239357.9763 | 2706330.1594 | 1239367.933
124 | 2706311.4156 | 1239417.0258 | 2706311.3328 | 1239417.2855
125 | 2706311.3328 | 1239417.2855 | 2706308.6937 | 1239425.5622 | 2706308.1892 | 1239453.7172
126 | 2706229.0824 | 1239394.0993 | 2706232.6051 | 1239389.3612 | 2706233.9624 | 1239386.0477
127 | 2706229.0824 | 1239394.0993 | 2706224.193 | 1239400.6756
128 | 2706224.193 | 1239400.6756 | 2706215.1264 | 1239412.8704
129 | 2706274.3439 | 1239432.7106 | 2706272.8661 | 1239450.1117
130 | 2706275.2471 | 1239422.0758 | 2706274.3439 | 1239432.7106
131 | 2706272.5497 | 1239453.8371 | 2706272.8661 | 1239450.1117
132 | 2706311.5155 | 1239474.923 | 2706307.9805 | 1239465.3692 | 2706308.1892 | 1239453.7172
133 | 2706311.5155 | 1239474.923 | 2706311.658 | 1239475.3082
134 | 2706311.658 | 1239475.3082 | 2706315.4483 | 1239485.5519 | 2706324.754 | 1239497.5497
135 | 2706324.754 | 1239497.5497 | 2706325.7015 | 1239498.7714
136 | 2706339.2351 | 1239516.2204 | 2706325.7015 | 1239498.7714
137 | 2706435.3834 | 1239579.3706 | 2706462.2895 | 1239573.0618
138 | 2706491.8474 | 1239566.1311 | 2706462.2895 | 1239573.0618
139 | 2706491.8474 | 1239566.1311 | 2706489.4075 | 1239560.8832 | 2706491.4178 | 1239547.9203
140 | 2706491.8474 | 1239566.1311 | 2706490.9968 | 1239571.798 | 2706493.9085 | 1239583.1602
141 | 2706491.4178 | 1239547.9203 | 2706486.2901 | 1239539.4329 | 2706486.2901 | 1239539.4329
142 | 2706486.2901 | 1239539.4329 | 2706468.3374 | 1239538.1991
143 | 2706468.3374 | 1239538.1991 | 2706449.8135 | 1239536.926
144 | 2706449.8135 | 1239536.926 | 2706431.2219 | 1239535.6483
145 | 2706416.0032 | 1239534.6024 | 2706431.2219 | 1239535.6483

## bus_geodata
| x | y | coords
0 | 2706604.5002 | 1238896.4345
1 | 2706267.6123 | 1239247.1662
2 | 2706262.9962 | 1239261.4089
3 | 2706134.2203 | 1239638.2839
4 | 2706131.5625 | 1239631.766
5 | 2706124.1258 | 1239613.5287
6 | 2706197.0832 | 1239640.4539
7 | 2706205.338 | 1239654.4345
8 | 2706189.966 | 1239617.3977
9 | 2706116.066 | 1239590.4668
10 | 2706121.1785 | 1239576.4061
11 | 2706140.2908 | 1239585.7263
12 | 2706141.3516 | 1239564.821
13 | 2706177.3083 | 1239585.8246
14 | 2706181.1854 | 1239595.4956
15 | 2706201.5881 | 1239611.7345
16 | 2706219.9288 | 1239631.0863
17 | 2706209.9752 | 1239575.9759
18 | 2706209.2337 | 1239661.0324
19 | 2706217.2746 | 1239669.3265
20 | 2706230.43 | 1239680.0072
21 | 2706224.0589 | 1239656.735
22 | 2706138.1588 | 1239548.3623
23 | 2706273.3008 | 1239610.4943
24 | 2706247.1871 | 1239594.3213
25 | 2706301.4409 | 1239635.3564
26 | 2706313.1131 | 1239646.2682
27 | 2706324.0273 | 1239646.541
28 | 2706300.6152 | 1239662.8129
29 | 2706342.64 | 1239641.0485
30 | 2706295.356 | 1239668.2172
31 | 2706285.5646 | 1239644.0719
32 | 2706137.8555 | 1239538.5086
33 | 2706097.7392 | 1239554.6112
34 | 2706137.4795 | 1239526.2886
35 | 2706082.716 | 1239556.9337
36 | 2706070.9504 | 1239530.8477
37 | 2706300.01 | 1239558.2272
38 | 2706316.1863 | 1239568.0784
39 | 2706294.1861 | 1239554.6805
40 | 2706335.5367 | 1239579.8626
41 | 2706282.9878 | 1239547.8649
42 | 2706304.449 | 1239538.9252
43 | 2706338.0623 | 1239582.3071
44 | 2706267.97 | 1239532.7191
45 | 2706311.3841 | 1239530.8365
46 | 2706348.2744 | 1239539.4038
47 | 2706348.3333 | 1239536.1803
48 | 2706335.083 | 1239531.3112
49 | 2706358.4679 | 1239602.0572
50 | 2706264.4114 | 1239528.1047
51 | 2706279.5866 | 1239516.6599
52 | 2706245.5299 | 1239503.6145
53 | 2706234.1966 | 1239488.9114
54 | 2706260.7608 | 1239492.3971
55 | 2706291.1274 | 1239507.9561
56 | 2706228.2803 | 1239483.4569
57 | 2706212.3242 | 1239506.2405
58 | 2706272.6514 | 1239483.6399
59 | 2706209.0822 | 1239508.8091
60 | 2706176.5833 | 1239522.3513
61 | 2706170.5066 | 1239523.493
62 | 2706184.9497 | 1239453.4586
63 | 2706241.7058 | 1239469.3591
64 | 2706195.6714 | 1239439.0377
65 | 2706169.593 | 1239442.4866
66 | 2706144.4754 | 1239525.7922
67 | 2706254.5521 | 1239459.8197
68 | 2706071.3286 | 1239530.8218
69 | 2706200.5653 | 1239432.4552
70 | 2706153.6769 | 1239425.1441
71 | 2706009.3162 | 1239538.3529
72 | 2706115.5245 | 1239444.1309
73 | 2706142.8884 | 1239408.2376
74 | 2706106.0816 | 1239446.2255
75 | 2706138.4744 | 1239401.3205
76 | 2706207.4859 | 1239423.147
77 | 2706099.2268 | 1239445.0491
78 | 2706157.0354 | 1239389.1747
79 | 2706098.599 | 1239444.8291
80 | 2706078.5113 | 1239437.7911
81 | 2705998.856 | 1239516.3125
82 | 2706265.6981 | 1239698.6935
83 | 2706256.4637 | 1239707.4871
84 | 2706303.3833 | 1239741.3679
85 | 2706277.5176 | 1239686.5478
86 | 2706278.9778 | 1239685.0473
87 | 2706294.205 | 1239669.4
88 | 2706319.4403 | 1239741.1668
89 | 2706275.2393 | 1239635.3362
90 | 2706266.5932 | 1239628.0213
91 | 2706361.4848 | 1239668.2983
92 | 2706347.3831 | 1239615.2148
93 | 2706361.9991 | 1239669.0419
94 | 2706379.1306 | 1239690.9764
95 | 2706374.8365 | 1239585.6895
96 | 2706364.3336 | 1239606.9439
97 | 2706386.3384 | 1239617.6412
98 | 2706427.3435 | 1239620.1503
99 | 2706391.8356 | 1239611.6687
100 | 2706423.9034 | 1239612.242
101 | 2706496.4394 | 1239608.6798
102 | 2706498.0592 | 1239599.3572
103 | 2706455.365 | 1239608.4113
104 | 2706392.5496 | 1239570.6434
105 | 2706423.2225 | 1239736.8778
106 | 2706458.633 | 1239695.8057
107 | 2706474.8827 | 1239676.9578
108 | 2706160.7931 | 1239386.7158
109 | 2706183.3553 | 1239373.8937
110 | 2706211.5094 | 1239362.4979
111 | 2706227.9093 | 1239362.2117
112 | 2706254.0601 | 1239288.9809
113 | 2706250.0796 | 1239328.8921
114 | 2706267.6869 | 1239357.8867
115 | 2706296.1559 | 1239370.9895
116 | 2706308.7116 | 1239376.7682
117 | 2706322.2634 | 1239383.0054
118 | 2706330.1594 | 1239367.933
119 | 2706311.4156 | 1239417.0258
120 | 2706335.3754 | 1239357.9763
121 | 2706311.3328 | 1239417.2855
122 | 2706233.9624 | 1239386.0477
123 | 2706229.0824 | 1239394.0993
124 | 2706224.193 | 1239400.6756
125 | 2706215.1264 | 1239412.8704
126 | 2706274.3439 | 1239432.7106
127 | 2706272.8661 | 1239450.1117
128 | 2706275.2471 | 1239422.0758
129 | 2706272.5497 | 1239453.8371
130 | 2706308.1892 | 1239453.7172
131 | 2706311.5155 | 1239474.923
132 | 2706311.658 | 1239475.3082
133 | 2706324.754 | 1239497.5497
134 | 2706325.7015 | 1239498.7714
135 | 2706339.2351 | 1239516.2204
136 | 2706400.148 | 1239568.3333
137 | 2706435.3834 | 1239579.3706
138 | 2706462.2895 | 1239573.0618
139 | 2706491.8474 | 1239566.1311
140 | 2706493.9085 | 1239583.1602
141 | 2706491.4178 | 1239547.9203
142 | 2706486.2901 | 1239539.4329
143 | 2706468.3374 | 1239538.1991
144 | 2706449.8135 | 1239536.926
145 | 2706431.2219 | 1239535.6483
146 | 2706416.0032 | 1239534.6024
147 | 2706267.97 | 1239532.7191

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98482 | -0.29277 | 0.00044843 | 0.00011239
1 | 0.98502 | -0.28879 | 0.0012622 | 0.00031634
2 | 0.98504 | -0.28832 | 0.0012912 | 0.00032361
3 | 0.97723 | -0.43826 | 0.0082965 | 0.0020793
4 | 0.97729 | -0.4372 | 0.0078372 | 0.0019642
5 | 0.97758 | -0.4314 | 0 | 0
6 | 0.97477 | -0.48668 | 0.0043909 | 0.0011005
7 | 0.97442 | -0.4936 | 0.0026393 | 0.00066147
8 | 0.97539 | -0.47447 | 0.0043595 | 0.0010926
9 | 0.97795 | -0.42422 | 0 | 0
10 | 0.97765 | -0.42999 | 0.021182 | 0.0053087
11 | 0.9788 | -0.40743 | 0.0077749 | 0.0019486
12 | 0.98084 | -0.36762 | 0 | 0
13 | 0.97674 | -0.44782 | 0 | 0
14 | 0.97629 | -0.45682 | 0.0064002 | 0.001604
15 | 0.97528 | -0.47658 | 0.0043668 | 0.0010944
16 | 0.97517 | -0.47879 | 0.004532 | 0.0011358
17 | 0.97635 | -0.45555 | 0.012395 | 0.0031064
18 | 0.97427 | -0.4965 | 0.0035193 | 0.00088201
19 | 0.97408 | -0.5002 | 0 | 0
20 | 0.97387 | -0.50443 | 0.011566 | 0.0028988
21 | 0.97401 | -0.50164 | 0.0054919 | 0.0013764
22 | 0.98247 | -0.33584 | 0 | 0
23 | 0.98558 | -0.27744 | 0.0045834 | 0.0011487
24 | 0.98526 | -0.28367 | 0.011259 | 0.0028218
25 | 0.98612 | -0.26676 | 0.0072245 | 0.0018106
26 | 0.98646 | -0.26015 | 0 | 0
27 | 0.98703 | -0.24916 | 0.0014854 | 0.00037228
28 | 0.98581 | -0.27288 | 0 | 0
29 | 0.98806 | -0.22915 | 0 | 0
30 | 0.98566 | -0.27575 | 0.0022676 | 0.00056832
31 | 0.98554 | -0.27818 | 0.001308 | 0.00032782
32 | 0.98312 | -0.3232 | 0.004511 | 0.0011306
33 | 0.98106 | -0.3635 | 0.0136 | 0.0034085
34 | 0.98368 | -0.31242 | 0 | 0
35 | 0.98072 | -0.37005 | 0 | 0
36 | 0.97995 | -0.38511 | 0 | 0
37 | 0.99672 | -0.062374 | 0.0022471 | 0.00056317
38 | 0.99564 | -0.083067 | 0.0029047 | 0.00072798
39 | 0.99712 | -0.054846 | 0 | 0
40 | 0.99437 | -0.10749 | 0 | 0
41 | 0.9982 | -0.034261 | 0.0028179 | 0.00070622
42 | 0.99574 | -0.0813 | 0.0068315 | 0.0017121
43 | 0.99417 | -0.11129 | 0.0020952 | 0.00052511
44 | 1 | 0 | -0.57217 | -0.14604
45 | 0.99501 | -0.095255 | 0 | 0
46 | 0.99218 | -0.14977 | 0 | 0
47 | 0.99198 | -0.1535 | 0.0090833 | 0.0022765
48 | 0.9931 | -0.13205 | 0.0085757 | 0.0021493
49 | 0.9918 | -0.15687 | 0 | 0
50 | 0.99948 | -0.0098512 | 0 | 0
51 | 0.99777 | -0.042055 | 0.0068075 | 0.0017061
52 | 0.99092 | -0.17265 | 0 | 0
53 | 0.98933 | -0.20322 | 0 | 0
54 | 0.99254 | -0.14158 | 0.005885 | 0.0014749
55 | 0.99651 | -0.066045 | 0 | 0
56 | 0.98866 | -0.21618 | 0 | 0
57 | 0.98771 | -0.23434 | 0.0078455 | 0.0019663
58 | 0.99384 | -0.11687 | 0 | 0
59 | 0.98748 | -0.23877 | 0.0060081 | 0.0015058
60 | 0.98558 | -0.27563 | 0 | 0
61 | 0.98524 | -0.28206 | 0.019401 | 0.0048623
62 | 0.98554 | -0.27687 | 0 | 0
63 | 0.98818 | -0.22555 | 0.0058255 | 0.00146
64 | 0.98507 | -0.28592 | 0.0027363 | 0.00068578
65 | 0.98491 | -0.28907 | 0.011663 | 0.0029231
66 | 0.984 | -0.30625 | 0.0076624 | 0.0019204
67 | 0.98788 | -0.23145 | 0 | 0
68 | 0.97995 | -0.38518 | 0.01096 | 0.0027469
69 | 0.98488 | -0.28965 | 0.005791 | 0.0014514
70 | 0.98438 | -0.29937 | 0 | 0
71 | 0.97905 | -0.40287 | 0 | 0
72 | 0.9839 | -0.30887 | 0.0028216 | 0.00070715
73 | 0.98416 | -0.30368 | 0.0052187 | 0.0013079
74 | 0.98381 | -0.31055 | 0.0022195 | 0.00055627
75 | 0.98411 | -0.30467 | 0 | 0
76 | 0.98467 | -0.29372 | 0.0022629 | 0.00056714
77 | 0.98376 | -0.31149 | 0.0022087 | 0.00055356
78 | 0.98397 | -0.30736 | 0.0021436 | 0.00053723
79 | 0.98376 | -0.31155 | 0.002904 | 0.0007278
80 | 0.98372 | -0.31241 | 0.0022315 | 0.00055926
81 | 0.97876 | -0.40856 | 0.012828 | 0.0032151
82 | 0.98515 | -0.28567 | 0 | 0
83 | 0.98514 | -0.28602 | 0.0015233 | 0.00038178
84 | 0.98482 | -0.2921 | 0.0033537 | 0.00084052
85 | 0.98528 | -0.28329 | 0.0033189 | 0.00083178
86 | 0.9853 | -0.28287 | 0.0056226 | 0.0014091
87 | 0.98563 | -0.2763 | 0.0021376 | 0.00053573
88 | 0.98478 | -0.29295 | 0.0029367 | 0.00073601
89 | 0.9854 | -0.28077 | 0.0042133 | 0.001056
90 | 0.98534 | -0.28208 | 0.0064612 | 0.0016193
91 | 0.98702 | -0.24939 | 0.0092522 | 0.0023188
92 | 0.99032 | -0.18544 | 0.0013192 | 0.00033063
93 | 0.98699 | -0.2498 | 0.0014635 | 0.00036678
94 | 0.98639 | -0.26152 | 0.0039489 | 0.00098968
95 | 0.99153 | -0.1621 | 0.0059414 | 0.0014891
96 | 0.99127 | -0.16709 | 0 | 0
97 | 0.99067 | -0.17875 | 0.016232 | 0.0040682
98 | 0.99027 | -0.18642 | 0.010408 | 0.0026084
99 | 0.99 | -0.19149 | 0.0061024 | 0.0015294
100 | 0.98874 | -0.216 | 0.0053211 | 0.0013336
101 | 0.98637 | -0.26195 | 0 | 0
102 | 0.98609 | -0.26747 | 0 | 0
103 | 0.98764 | -0.23737 | 0.0050606 | 0.0012683
104 | 0.99138 | -0.16491 | 0 | 0
105 | 0.98525 | -0.28382 | 0 | 0
106 | 0.98427 | -0.30285 | 0.010738 | 0.0026913
107 | 0.98407 | -0.30679 | 0.0087874 | 0.0022023
108 | 0.98396 | -0.30773 | 0.002565 | 0.00064284
109 | 0.98391 | -0.30868 | 0.0020205 | 0.00050639
110 | 0.98405 | -0.30593 | 0.0014768 | 0.00037011
111 | 0.98407 | -0.30548 | 0.0018487 | 0.00046333
112 | 0.98512 | -0.28675 | 0.0027386 | 0.00068635
113 | 0.98535 | -0.28232 | 0.0022486 | 0.00056356
114 | 0.9856 | -0.27741 | 0.00307 | 0.00076942
115 | 0.98592 | -0.27118 | 0.0020026 | 0.00050189
116 | 0.98609 | -0.26794 | 0.0031662 | 0.00079354
117 | 0.98631 | -0.26359 | 0 | 0
118 | 0.98626 | -0.2646 | 0.002447 | 0.00061328
119 | 0.98695 | -0.25109 | 0.0056036 | 0.0014044
120 | 0.98625 | -0.26477 | 0.00085246 | 0.00021365
121 | 0.98696 | -0.25097 | 0.0062251 | 0.0015601
122 | 0.98415 | -0.30391 | 0.002795 | 0.0007005
123 | 0.9842 | -0.30286 | 0.0026358 | 0.0006606
124 | 0.98427 | -0.30157 | 0.0054298 | 0.0013608
125 | 0.98447 | -0.29769 | 0.0030719 | 0.00076988
126 | 0.98717 | -0.24527 | 0.013353 | 0.0033467
127 | 0.98744 | -0.23996 | 0.0036449 | 0.00091349
128 | 0.98713 | -0.24597 | 0.0036457 | 0.00091369
129 | 0.98751 | -0.23858 | 0 | 0
130 | 0.98802 | -0.2303 | 0.0026913 | 0.0006745
131 | 0.9887 | -0.21703 | 0.0034002 | 0.00085216
132 | 0.98872 | -0.21675 | 0.0036793 | 0.00092213
133 | 0.9897 | -0.19762 | 0.0047819 | 0.0011985
134 | 0.98977 | -0.19635 | 0.0073228 | 0.0018353
135 | 0.99085 | -0.17545 | 0.00239 | 0.00059899
136 | 0.99133 | -0.16587 | 0.0067958 | 0.0017032
137 | 0.9845 | -0.29842 | 0.009219 | 0.0023105
138 | 0.98474 | -0.29384 | 0.005605 | 0.0014048
139 | 0.98515 | -0.28575 | 0 | 0
140 | 0.98559 | -0.27722 | 0.0052876 | 0.0013252
141 | 0.98493 | -0.28996 | 0 | 0
142 | 0.98482 | -0.29217 | 0.0021788 | 0.00054605
143 | 0.98465 | -0.29548 | 0.0021796 | 0.00054625
144 | 0.98451 | -0.29816 | 0.0021797 | 0.00054627
145 | 0.98441 | -0.30013 | 0.0021796 | 0.00054625
146 | 0.98436 | -0.30114 | 0.0036819 | 0.00092277
147 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00044843 | -0.00011239 | 0.00044851 | 0.00010625 | 8.3454e-08 | -6.1358e-06 | 0.00067756 | 0.00067541 | 0.00067756 | 0.98482 | -0.29277 | 0.98502 | -0.28879 | 0.18614
1 | -0.0017107 | -0.00042259 | 0.0017108 | 0.00042242 | 3.7433e-08 | -1.6663e-07 | 0.0025821 | 0.002582 | 0.0025821 | 0.98502 | -0.28879 | 0.98504 | -0.28832 | 0.70937
2 | -0.003002 | -0.00074603 | 0.0030022 | 0.0007458 | 2.2329e-07 | -2.2609e-07 | 0.0045325 | 0.0045324 | 0.0045325 | 0.98504 | -0.28832 | 0.98512 | -0.28675 | 1.2452
3 | -0.0082965 | -0.0020793 | 0.0082969 | 0.0020795 | 4.2126e-07 | 1.8141e-07 | 0.012633 | 0.012633 | 0.012633 | 0.97723 | -0.43826 | 0.97729 | -0.4372 | 3.4706
4 | -0.016134 | -0.0040437 | 0.016139 | 0.0040463 | 4.4571e-06 | 2.6057e-06 | 0.024566 | 0.024566 | 0.024566 | 0.97729 | -0.4372 | 0.97758 | -0.4314 | 6.7489
5 | -0.016139 | -0.0040463 | 0.016144 | 0.0040495 | 5.5272e-06 | 3.2311e-06 | 0.024566 | 0.024566 | 0.024566 | 0.97758 | -0.4314 | 0.97795 | -0.42422 | 6.7488
6 | 0.023233 | 0.0058282 | -0.023225 | -0.0058235 | 7.6591e-06 | 4.6995e-06 | 0.035468 | 0.035468 | 0.035468 | 0.97477 | -0.48668 | 0.97442 | -0.4936 | 9.744
7 | -0.027624 | -0.0069287 | 0.02764 | 0.0069387 | 1.6092e-05 | 9.9978e-06 | 0.042171 | 0.042171 | 0.042171 | 0.97477 | -0.48668 | 0.97539 | -0.47447 | 11.5854
8 | 0.020586 | 0.005162 | -0.020583 | -0.0051603 | 2.8398e-06 | 1.722e-06 | 0.031438 | 0.031438 | 0.031438 | 0.97442 | -0.4936 | 0.97427 | -0.4965 | 8.6367
9 | -0.0409 | -0.010262 | 0.040934 | 0.010284 | 3.4454e-05 | 2.1756e-05 | 0.062399 | 0.062399 | 0.062399 | 0.97539 | -0.47447 | 0.97629 | -0.45682 | 17.1427
10 | 0.0089002 | 0.0022306 | -0.0088993 | -0.0022302 | 8.9379e-07 | 4.1068e-07 | 0.013578 | 0.013578 | 0.013578 | 0.97539 | -0.47447 | 0.97528 | -0.47658 | 3.7302
11 | -0.037332 | -0.0093618 | 0.037362 | 0.0093806 | 2.9887e-05 | 1.8818e-05 | 0.056805 | 0.056805 | 0.056805 | 0.97795 | -0.42422 | 0.9788 | -0.40743 | 15.6058
12 | 0.021188 | 0.0053123 | -0.021182 | -0.0053087 | 5.8315e-06 | 3.5445e-06 | 0.03224 | 0.03224 | 0.03224 | 0.97795 | -0.42422 | 0.97765 | -0.42999 | 8.8571
13 | -0.10501 | -0.026412 | 0.10521 | 0.02654 | 0.00020012 | 0.00012781 | 0.15967 | 0.15967 | 0.15967 | 0.9788 | -0.40743 | 0.98084 | -0.36762 | 43.8651
14 | 0.059869 | 0.015083 | -0.059754 | -0.015009 | 0.00011539 | 7.3384e-05 | 0.091044 | 0.091044 | 0.091044 | 0.9788 | -0.40743 | 0.97674 | -0.44782 | 25.0122
15 | -0.10521 | -0.02654 | 0.10537 | 0.026642 | 0.00016035 | 0.00010242 | 0.15967 | 0.15967 | 0.15967 | 0.98084 | -0.36762 | 0.98247 | -0.33584 | 43.8651
16 | 0.012399 | 0.0031089 | -0.012395 | -0.0031064 | 4.5657e-06 | 2.4952e-06 | 0.01889 | 0.01889 | 0.01889 | 0.97674 | -0.44782 | 0.97635 | -0.45555 | 5.1896
17 | 0.047355 | 0.011901 | -0.047334 | -0.011888 | 2.0342e-05 | 1.2888e-05 | 0.072154 | 0.072154 | 0.072154 | 0.97674 | -0.44782 | 0.97629 | -0.45682 | 19.8226
18 | 0.0045325 | 0.0011358 | -0.004532 | -0.0011358 | 4.7815e-07 | -2.6657e-08 | 0.0069153 | 0.0069155 | 0.0069155 | 0.97528 | -0.47658 | 0.97517 | -0.47879 | 1.8999
19 | 0.017064 | 0.0042783 | -0.017061 | -0.0042765 | 3.0114e-06 | 1.7801e-06 | 0.026063 | 0.026063 | 0.026063 | 0.97427 | -0.4965 | 0.97408 | -0.5002 | 7.1601
20 | 0.011569 | 0.0029 | -0.011566 | -0.0028988 | 2.3341e-06 | 1.2458e-06 | 0.017673 | 0.017673 | 0.017673 | 0.97408 | -0.5002 | 0.97387 | -0.50443 | 4.8551
21 | 0.0054923 | 0.0013765 | -0.0054919 | -0.0013764 | 3.7757e-07 | 6.3613e-08 | 0.0083901 | 0.0083902 | 0.0083902 | 0.97408 | -0.5002 | 0.97401 | -0.50164 | 2.305
22 | -0.14284 | -0.036067 | 0.14293 | 0.036122 | 8.6593e-05 | 5.517e-05 | 0.21644 | 0.21644 | 0.21644 | 0.98247 | -0.33584 | 0.98312 | -0.3232 | 29.731
23 | 0.037477 | 0.0094246 | -0.037427 | -0.0093935 | 4.9435e-05 | 3.1121e-05 | 0.056773 | 0.056773 | 0.056773 | 0.98247 | -0.33584 | 0.98106 | -0.3635 | 15.5969
24 | 0.011263 | 0.0028236 | -0.011259 | -0.0028218 | 3.3467e-06 | 1.7487e-06 | 0.017004 | 0.017005 | 0.017005 | 0.98558 | -0.27744 | 0.98526 | -0.28367 | 4.6716
25 | -0.015846 | -0.0039723 | 0.015854 | 0.003977 | 8.0676e-06 | 4.684e-06 | 0.023924 | 0.023924 | 0.023924 | 0.98558 | -0.27744 | 0.98612 | -0.26676 | 6.5727
26 | -0.023079 | -0.0057876 | 0.023086 | 0.005792 | 7.2671e-06 | 4.447e-06 | 0.034826 | 0.034826 | 0.034826 | 0.98612 | -0.26676 | 0.98646 | -0.26015 | 9.5675
27 | -0.056265 | -0.014119 | 0.056295 | 0.014138 | 2.9496e-05 | 1.8738e-05 | 0.084879 | 0.084879 | 0.084879 | 0.98646 | -0.26015 | 0.98703 | -0.24916 | 23.3184
28 | 0.03318 | 0.0083272 | -0.033159 | -0.0083146 | 2.0132e-05 | 1.2611e-05 | 0.050053 | 0.050054 | 0.050054 | 0.98646 | -0.26015 | 0.98581 | -0.27288 | 13.751
29 | -0.05778 | -0.01451 | 0.057836 | 0.014545 | 5.5245e-05 | 3.5109e-05 | 0.087118 | 0.087118 | 0.087118 | 0.98703 | -0.24916 | 0.98806 | -0.22915 | 23.9336
30 | 0.021172 | 0.0053091 | -0.021169 | -0.0053074 | 2.8883e-06 | 1.7524e-06 | 0.031959 | 0.031959 | 0.031959 | 0.98581 | -0.27288 | 0.98566 | -0.27575 | 8.78
31 | 0.011987 | 0.0030055 | -0.011984 | -0.0030039 | 3.0253e-06 | 1.6221e-06 | 0.018094 | 0.018095 | 0.018095 | 0.98581 | -0.27288 | 0.98554 | -0.27818 | 4.971
32 | 0.034277 | 0.0086219 | -0.034244 | -0.0086011 | 3.3122e-05 | 2.0774e-05 | 0.051633 | 0.051633 | 0.051633 | 0.98806 | -0.22915 | 0.98702 | -0.24939 | 14.1848
33 | -0.092113 | -0.023167 | 0.092305 | 0.02329 | 0.00019272 | 0.000123 | 0.13875 | 0.13875 | 0.13875 | 0.98806 | -0.22915 | 0.99032 | -0.18544 | 38.1184
34 | 0.018902 | 0.0047391 | -0.018901 | -0.0047388 | 5.0397e-07 | 3.0151e-07 | 0.028536 | 0.028536 | 0.028536 | 0.98566 | -0.27575 | 0.98563 | -0.2763 | 7.8395
35 | 0.010676 | 0.0026761 | -0.010675 | -0.0026754 | 1.3179e-06 | 6.7113e-07 | 0.01612 | 0.01612 | 0.01612 | 0.98554 | -0.27818 | 0.9854 | -0.28077 | 4.4285
36 | -0.14744 | -0.037253 | 0.14752 | 0.037301 | 7.6181e-05 | 4.829e-05 | 0.22327 | 0.22327 | 0.22327 | 0.98312 | -0.3232 | 0.98368 | -0.31242 | 20.4459
37 | 0.023828 | 0.005985 | -0.02382 | -0.0059804 | 7.4477e-06 | 4.5746e-06 | 0.036145 | 0.036145 | 0.036145 | 0.98106 | -0.3635 | 0.98072 | -0.37005 | 9.93
38 | -0.14752 | -0.037301 | 0.14756 | 0.037329 | 4.3702e-05 | 2.7702e-05 | 0.22327 | 0.22327 | 0.22327 | 0.98368 | -0.31242 | 0.984 | -0.30625 | 20.4459
39 | 0.02382 | 0.0059804 | -0.023803 | -0.0059699 | 1.7096e-05 | 1.0502e-05 | 0.036145 | 0.036145 | 0.036145 | 0.98072 | -0.37005 | 0.97995 | -0.38511 | 9.93
40 | 0.012843 | 0.003223 | -0.012832 | -0.003217 | 1.087e-05 | 5.9974e-06 | 0.019503 | 0.019503 | 0.019503 | 0.97995 | -0.38511 | 0.97905 | -0.40287 | 5.358
41 | 0.01096 | 0.0027469 | -0.01096 | -0.0027469 | 3.9375e-08 | 2.0424e-08 | 0.016643 | 0.016643 | 0.016643 | 0.97995 | -0.38511 | 0.97995 | -0.38518 | 4.5722
42 | 0.18826 | 0.04782 | -0.18807 | -0.047701 | 0.00018731 | 0.00011914 | 0.28128 | 0.28128 | 0.28128 | 0.99672 | -0.062374 | 0.99564 | -0.083067 | 25.7579
43 | -0.1905 | -0.048383 | 0.19057 | 0.048427 | 6.9053e-05 | 4.3927e-05 | 0.28463 | 0.28463 | 0.28463 | 0.99672 | -0.062374 | 0.99712 | -0.054846 | 26.0651
44 | 0.18516 | 0.046973 | -0.18495 | -0.046835 | 0.0002172 | 0.00013812 | 0.27694 | 0.27694 | 0.27694 | 0.99564 | -0.083067 | 0.99437 | -0.10749 | 25.3604
45 | -0.27126 | -0.068863 | 0.27153 | 0.069034 | 0.00026894 | 0.00017161 | 0.40512 | 0.40512 | 0.40512 | 0.99712 | -0.054846 | 0.9982 | -0.034261 | 37.099
46 | 0.08069 | 0.020436 | -0.080587 | -0.02037 | 0.00010237 | 6.527e-05 | 0.12049 | 0.12049 | 0.12049 | 0.99712 | -0.054846 | 0.99574 | -0.0813 | 33.1016
47 | 0.18495 | 0.046835 | -0.18491 | -0.046813 | 3.3696e-05 | 2.1429e-05 | 0.27694 | 0.27694 | 0.27694 | 0.99437 | -0.10749 | 0.99417 | -0.11129 | 25.3604
48 | -0.27435 | -0.069741 | 0.2748 | 0.07003 | 0.00045353 | 0.00028941 | 0.40932 | 0.40932 | 0.40932 | 0.9982 | -0.034261 | 1 | 0 | 37.4836
49 | 0.073756 | 0.018658 | -0.073706 | -0.018627 | 4.9353e-05 | 3.1445e-05 | 0.11028 | 0.11028 | 0.11028 | 0.99574 | -0.0813 | 0.99501 | -0.095255 | 30.297
50 | 0.18282 | 0.046288 | -0.18242 | -0.046033 | 0.00039917 | 0.00025473 | 0.2738 | 0.2738 | 0.2738 | 0.99417 | -0.11129 | 0.9918 | -0.15687 | 37.6099
51 | 0.29571 | 0.076014 | -0.29557 | -0.075923 | 0.00014147 | 9.0311e-05 | 0.4407 | 0.4407 | 0.4407 | 1 | 0 | 0.99948 | -0.0098512 | 40.3574
52 | 0.073706 | 0.018627 | -0.073577 | -0.018544 | 0.00012977 | 8.2685e-05 | 0.11028 | 0.11028 | 0.11028 | 0.99501 | -0.095255 | 0.9931 | -0.13205 | 30.297
53 | 0.064946 | 0.01636 | -0.064934 | -0.016352 | 1.158e-05 | 7.369e-06 | 0.097432 | 0.097432 | 0.097432 | 0.99218 | -0.14977 | 0.99198 | -0.1535 | 26.767
54 | -0.064946 | -0.01636 | 0.065001 | 0.016395 | 5.5092e-05 | 3.5059e-05 | 0.097432 | 0.097432 | 0.097432 | 0.99218 | -0.14977 | 0.9931 | -0.13205 | 26.767
55 | 0.055851 | 0.014076 | -0.055792 | -0.014039 | 5.8588e-05 | 3.721e-05 | 0.083806 | 0.083807 | 0.083807 | 0.99198 | -0.1535 | 0.99085 | -0.17545 | 23.0238
56 | 0.012742 | 0.0031944 | -0.012738 | -0.0031926 | 3.1724e-06 | 1.7317e-06 | 0.019117 | 0.019117 | 0.019117 | 0.9918 | -0.15687 | 0.99153 | -0.1621 | 5.2519
57 | 0.075925 | 0.019136 | -0.075888 | -0.019113 | 3.7108e-05 | 2.3651e-05 | 0.11395 | 0.11395 | 0.11395 | 0.9918 | -0.15687 | 0.99127 | -0.16709 | 31.305
58 | 0.093753 | 0.023703 | -0.093625 | -0.023621 | 0.00012829 | 8.1883e-05 | 0.14073 | 0.14073 | 0.14073 | 0.9918 | -0.15687 | 0.99032 | -0.18544 | 38.6629
59 | 0.29557 | 0.075923 | -0.29511 | -0.075629 | 0.00046144 | 0.00029458 | 0.4407 | 0.4407 | 0.4407 | 0.99948 | -0.0098512 | 0.99777 | -0.042055 | 40.3574
60 | 0.2883 | 0.073923 | -0.28797 | -0.073709 | 0.00033495 | 0.0002138 | 0.43055 | 0.43055 | 0.43055 | 0.99777 | -0.042055 | 0.99651 | -0.066045 | 39.4278
61 | 0.28061 | 0.071296 | -0.2802 | -0.071033 | 0.00041227 | 0.00026314 | 0.42173 | 0.42173 | 0.42173 | 0.99092 | -0.17265 | 0.98933 | -0.20322 | 38.6199
62 | -0.28061 | -0.071296 | 0.28103 | 0.071564 | 0.00042054 | 0.00026841 | 0.42173 | 0.42173 | 0.42173 | 0.99092 | -0.17265 | 0.99254 | -0.14158 | 38.6199
63 | 0.090858 | 0.022899 | -0.090801 | -0.022863 | 5.63e-05 | 3.5929e-05 | 0.1367 | 0.1367 | 0.1367 | 0.98933 | -0.20322 | 0.98866 | -0.21618 | 37.5553
64 | 0.18934 | 0.048134 | -0.18906 | -0.047954 | 0.00028338 | 0.00018029 | 0.28503 | 0.28503 | 0.28503 | 0.98933 | -0.20322 | 0.98771 | -0.23434 | 26.1016
65 | -0.28692 | -0.073039 | 0.28726 | 0.073258 | 0.00034219 | 0.00021843 | 0.43055 | 0.43055 | 0.43055 | 0.99254 | -0.14158 | 0.99384 | -0.11687 | 39.4278
66 | 0.28797 | 0.073709 | -0.28726 | -0.073258 | 0.0007069 | 0.00045123 | 0.43055 | 0.43055 | 0.43055 | 0.99651 | -0.066045 | 0.99384 | -0.11687 | 39.4278
67 | 0.064302 | 0.016211 | -0.064115 | -0.016092 | 0.00018616 | 0.00011846 | 0.096813 | 0.096813 | 0.096813 | 0.98866 | -0.21618 | 0.98554 | -0.27687 | 26.5971
68 | 0.0265 | 0.0066522 | -0.026488 | -0.0066449 | 1.1844e-05 | 7.3256e-06 | 0.039888 | 0.039888 | 0.039888 | 0.98866 | -0.21618 | 0.98818 | -0.22555 | 10.9583
69 | 0.18122 | 0.045987 | -0.18118 | -0.045963 | 3.8593e-05 | 2.4541e-05 | 0.27321 | 0.27321 | 0.27321 | 0.98771 | -0.23434 | 0.98748 | -0.23877 | 25.0192
70 | 0.17517 | 0.044457 | -0.17486 | -0.04426 | 0.00030998 | 0.00019702 | 0.26416 | 0.26416 | 0.26416 | 0.98748 | -0.23877 | 0.98558 | -0.27563 | 24.1902
71 | 0.17486 | 0.04426 | -0.1748 | -0.044226 | 5.3931e-05 | 3.4279e-05 | 0.26416 | 0.26416 | 0.26416 | 0.98558 | -0.27563 | 0.98524 | -0.28206 | 24.1902
72 | 0.1554 | 0.039363 | -0.15522 | -0.039249 | 0.00018033 | 0.00011441 | 0.23486 | 0.23486 | 0.23486 | 0.98524 | -0.28206 | 0.984 | -0.30625 | 21.5069
73 | 0.028076 | 0.0070455 | -0.028064 | -0.007038 | 1.2111e-05 | 7.522e-06 | 0.042393 | 0.042393 | 0.042393 | 0.98554 | -0.27687 | 0.98507 | -0.28592 | 11.6465
74 | 0.03604 | 0.0090468 | -0.036019 | -0.0090336 | 2.0961e-05 | 1.3174e-05 | 0.05442 | 0.05442 | 0.05442 | 0.98554 | -0.27687 | 0.98491 | -0.28907 | 14.9506
75 | 0.020662 | 0.0051849 | -0.020657 | -0.0051814 | 5.8096e-06 | 3.5132e-06 | 0.031116 | 0.031116 | 0.031116 | 0.98818 | -0.22555 | 0.98788 | -0.23145 | 8.5484
76 | 0.025327 | 0.0063522 | -0.025323 | -0.0063494 | 4.5026e-06 | 2.7773e-06 | 0.03826 | 0.03826 | 0.03826 | 0.98507 | -0.28592 | 0.98488 | -0.28965 | 10.511
77 | 0.024356 | 0.0061105 | -0.024344 | -0.0061032 | 1.1953e-05 | 7.3508e-06 | 0.036799 | 0.036799 | 0.036799 | 0.98491 | -0.28907 | 0.98438 | -0.29937 | 10.1096
78 | 0.020657 | 0.0051814 | -0.02065 | -0.0051771 | 7.0169e-06 | 4.2435e-06 | 0.031116 | 0.031116 | 0.031116 | 0.98788 | -0.23145 | 0.98751 | -0.23858 | 8.5484
79 | 0.019532 | 0.004898 | -0.019528 | -0.0048958 | 3.788e-06 | 2.2768e-06 | 0.029511 | 0.029511 | 0.029511 | 0.98488 | -0.28965 | 0.98467 | -0.29372 | 8.1074
80 | 0.012392 | 0.0031074 | -0.012386 | -0.0031043 | 5.608e-06 | 3.0476e-06 | 0.018733 | 0.018733 | 0.018733 | 0.98438 | -0.29937 | 0.9839 | -0.30887 | 5.1464
81 | 0.011952 | 0.0029958 | -0.011949 | -0.0029945 | 2.4548e-06 | 1.3161e-06 | 0.018066 | 0.018066 | 0.018066 | 0.98438 | -0.29937 | 0.98416 | -0.30368 | 4.9633
82 | 0.012832 | 0.003217 | -0.012828 | -0.0032151 | 3.4816e-06 | 1.9214e-06 | 0.019503 | 0.019503 | 0.019503 | 0.97905 | -0.40287 | 0.97876 | -0.40856 | 5.358
83 | 0.0095649 | 0.0023972 | -0.0095641 | -0.0023968 | 7.6509e-07 | 3.6584e-07 | 0.014466 | 0.014466 | 0.014466 | 0.9839 | -0.30887 | 0.98381 | -0.31055 | 3.9741
84 | 0.0067304 | 0.0016866 | -0.0067301 | -0.0016865 | 3.1864e-07 | 9.9666e-08 | 0.010176 | 0.010176 | 0.010176 | 0.98416 | -0.30368 | 0.98411 | -0.30467 | 2.7956
85 | 0.0073446 | 0.0018405 | -0.0073443 | -0.0018404 | 3.3075e-07 | 1.2093e-07 | 0.011109 | 0.011109 | 0.011109 | 0.98381 | -0.31055 | 0.98376 | -0.31149 | 3.0518
86 | 0.0067301 | 0.0016865 | -0.0067293 | -0.0016862 | 8.6138e-07 | 2.6949e-07 | 0.010176 | 0.010176 | 0.010176 | 0.98411 | -0.30467 | 0.98397 | -0.30736 | 2.7957
87 | 0.017265 | 0.0043286 | -0.017262 | -0.0043267 | 3.269e-06 | 1.9293e-06 | 0.026091 | 0.026091 | 0.026091 | 0.98467 | -0.29372 | 0.98447 | -0.29769 | 7.1679
88 | 0.0051355 | 0.0012869 | -0.0051355 | -0.0012868 | 1.5052e-08 | 1.1871e-09 | 0.0077678 | 0.0077678 | 0.0077678 | 0.98376 | -0.31149 | 0.98376 | -0.31155 | 2.134
89 | 0.0045857 | 0.001149 | -0.0045856 | -0.001149 | 8.0982e-08 | -5.2125e-09 | 0.0069346 | 0.0069346 | 0.0069346 | 0.98397 | -0.30736 | 0.98396 | -0.30773 | 1.9051
90 | 0.0022316 | 0.00055905 | -0.0022315 | -0.00055926 | 9.0939e-08 | -2.1203e-07 | 0.0033753 | 0.0033754 | 0.0033754 | 0.98376 | -0.31155 | 0.98372 | -0.31241 | 0.92732
91 | 0.0015234 | 0.00038164 | -0.0015233 | -0.00038178 | 2.5316e-08 | -1.4615e-07 | 0.0023009 | 0.0023009 | 0.0023009 | 0.98515 | -0.28567 | 0.98514 | -0.28602 | 0.63213
92 | 0.0062925 | 0.0015769 | -0.0062906 | -0.0015764 | 1.9286e-06 | 5.0968e-07 | 0.0095044 | 0.0095047 | 0.0095047 | 0.98515 | -0.28567 | 0.98482 | -0.2921 | 2.6112
93 | -0.0078159 | -0.0019586 | 0.0078167 | 0.0019589 | 8.8571e-07 | 3.5104e-07 | 0.011805 | 0.011805 | 0.011805 | 0.98515 | -0.28567 | 0.98528 | -0.28329 | 3.2432
94 | 0.0029369 | 0.00073589 | -0.0029367 | -0.00073601 | 1.1857e-07 | -1.2843e-07 | 0.0044374 | 0.0044374 | 0.0044374 | 0.98482 | -0.2921 | 0.98478 | -0.29295 | 1.2191
95 | -0.011136 | -0.0027907 | 0.011136 | 0.0027908 | 2.2206e-07 | 1.1545e-07 | 0.016818 | 0.016818 | 0.016818 | 0.98528 | -0.28329 | 0.9853 | -0.28287 | 4.6202
96 | -0.016758 | -0.0042 | 0.016764 | 0.004203 | 5.2444e-06 | 3.0783e-06 | 0.025309 | 0.025309 | 0.025309 | 0.9853 | -0.28287 | 0.98563 | -0.2763 | 6.953
97 | 0.0064616 | 0.0016194 | -0.0064612 | -0.0016193 | 4.0434e-07 | 1.1451e-07 | 0.0097574 | 0.0097574 | 0.0097574 | 0.9854 | -0.28077 | 0.98534 | -0.28208 | 2.6806
98 | 0.024992 | 0.0062823 | -0.024991 | -0.006282 | 4.8148e-07 | 2.9659e-07 | 0.037684 | 0.037684 | 0.037684 | 0.98702 | -0.24939 | 0.98699 | -0.2498 | 10.3528
99 | 0.023528 | 0.0059152 | -0.023515 | -0.0059072 | 1.3163e-05 | 8.068e-06 | 0.035478 | 0.035478 | 0.035478 | 0.98699 | -0.2498 | 0.98639 | -0.26152 | 9.7467
100 | 0.019566 | 0.0049175 | -0.019545 | -0.004905 | 2.0806e-05 | 1.2504e-05 | 0.029521 | 0.029521 | 0.029521 | 0.98639 | -0.26152 | 0.98525 | -0.28382 | 8.1102
101 | 0.006797 | 0.0017036 | -0.0067961 | -0.0017033 | 9.1167e-07 | 2.8216e-07 | 0.010201 | 0.010201 | 0.010201 | 0.99153 | -0.1621 | 0.99138 | -0.16491 | 2.8024
102 | 0.049229 | 0.012425 | -0.049172 | -0.012389 | 5.7467e-05 | 3.6418e-05 | 0.07393 | 0.073931 | 0.073931 | 0.99127 | -0.16709 | 0.99 | -0.19149 | 20.3106
103 | 0.026658 | 0.0066876 | -0.026644 | -0.0066785 | 1.4811e-05 | 9.1612e-06 | 0.04002 | 0.04002 | 0.04002 | 0.99127 | -0.16709 | 0.99067 | -0.17875 | 10.9945
104 | 0.010411 | 0.0026103 | -0.010408 | -0.0026084 | 3.8045e-06 | 1.901e-06 | 0.015639 | 0.015639 | 0.015639 | 0.99067 | -0.17875 | 0.99027 | -0.18642 | 4.2964
105 | 0.04307 | 0.010859 | -0.043019 | -0.010827 | 5.0456e-05 | 3.188e-05 | 0.064758 | 0.064759 | 0.064759 | 0.99 | -0.19149 | 0.98874 | -0.216 | 17.7908
106 | 0.037698 | 0.0094937 | -0.03766 | -0.0094695 | 3.8476e-05 | 2.4216e-05 | 0.05675 | 0.056751 | 0.056751 | 0.98874 | -0.216 | 0.98764 | -0.23737 | 15.5908
107 | 0.032561 | 0.0081773 | -0.032552 | -0.0081719 | 8.5642e-06 | 5.3604e-06 | 0.049126 | 0.049126 | 0.049126 | 0.98637 | -0.26195 | 0.98609 | -0.26747 | 13.4962
108 | -0.032561 | -0.0081773 | 0.032599 | 0.0082012 | 3.8239e-05 | 2.3933e-05 | 0.049126 | 0.049126 | 0.049126 | 0.98637 | -0.26195 | 0.98764 | -0.23737 | 13.4962
109 | 0.032552 | 0.0081719 | -0.032537 | -0.0081624 | 1.5132e-05 | 9.4715e-06 | 0.049126 | 0.049126 | 0.049126 | 0.98609 | -0.26747 | 0.98559 | -0.27722 | 13.4963
110 | 0.0067961 | 0.0017033 | -0.0067958 | -0.0017032 | 3.0989e-07 | 9.5933e-08 | 0.010201 | 0.010201 | 0.010201 | 0.99138 | -0.16491 | 0.99133 | -0.16587 | 2.8024
111 | 0.019545 | 0.004905 | -0.019527 | -0.0048943 | 1.7723e-05 | 1.0653e-05 | 0.029521 | 0.029521 | 0.029521 | 0.98525 | -0.28382 | 0.98427 | -0.30285 | 8.1103
112 | 0.0087891 | 0.0022031 | -0.0087874 | -0.0022023 | 1.6476e-06 | 7.3826e-07 | 0.013287 | 0.013288 | 0.013288 | 0.98427 | -0.30285 | 0.98407 | -0.30679 | 3.6504
113 | 0.0020206 | 0.00050612 | -0.0020205 | -0.00050639 | 9.1244e-08 | -2.7258e-07 | 0.0030556 | 0.0030557 | 0.0030557 | 0.98396 | -0.30773 | 0.98391 | -0.30868 | 0.83949
114 | -0.0014768 | -0.00037011 | 0.0014768 | 0.00036992 | 3.1461e-08 | -1.9361e-07 | 0.0022331 | 0.002233 | 0.0022331 | 0.98405 | -0.30593 | 0.98407 | -0.30548 | 0.61348
115 | -0.0033255 | -0.00083325 | 0.0033257 | 0.00083307 | 2.4911e-07 | -1.7438e-07 | 0.0050284 | 0.0050283 | 0.0050284 | 0.98407 | -0.30548 | 0.98415 | -0.30391 | 1.3814
116 | -0.0057408 | -0.0014322 | 0.005742 | 0.0014324 | 1.2088e-06 | 2.2739e-07 | 0.008669 | 0.0086688 | 0.008669 | 0.98512 | -0.28675 | 0.98535 | -0.28232 | 2.3816
117 | -0.0079906 | -0.0019959 | 0.0079925 | 0.0019967 | 1.8641e-06 | 7.5789e-07 | 0.012065 | 0.012064 | 0.012065 | 0.98535 | -0.28232 | 0.9856 | -0.27741 | 3.3144
118 | -0.011063 | -0.0027661 | 0.011066 | 0.0027678 | 3.2773e-06 | 1.698e-06 | 0.016699 | 0.016699 | 0.016699 | 0.9856 | -0.27741 | 0.98592 | -0.27118 | 4.5877
119 | -0.013068 | -0.0032697 | 0.01307 | 0.0032708 | 2.0159e-06 | 1.1139e-06 | 0.019722 | 0.019722 | 0.019722 | 0.98592 | -0.27118 | 0.98609 | -0.26794 | 5.418
120 | -0.016237 | -0.0040644 | 0.01624 | 0.0040663 | 3.3579e-06 | 1.9587e-06 | 0.0245 | 0.024499 | 0.0245 | 0.98609 | -0.26794 | 0.98631 | -0.26359 | 6.7306
121 | 0.0032996 | 0.00082667 | -0.0032995 | -0.00082678 | 1.5812e-07 | -1.1595e-07 | 0.0049779 | 0.004978 | 0.004978 | 0.98631 | -0.26359 | 0.98626 | -0.2646 | 1.3676
122 | -0.01954 | -0.004893 | 0.019551 | 0.0049 | 1.1635e-05 | 6.9905e-06 | 0.029477 | 0.029477 | 0.029477 | 0.98631 | -0.26359 | 0.98695 | -0.25109 | 8.0982
123 | 0.00085246 | 0.00021351 | -0.00085246 | -0.00021365 | 6.9723e-09 | -1.3897e-07 | 0.0012861 | 0.0012862 | 0.0012862 | 0.98626 | -0.2646 | 0.98625 | -0.26477 | 0.35334
124 | -0.025155 | -0.0063044 | 0.025155 | 0.0063045 | 1.4706e-07 | 9.0633e-08 | 0.037926 | 0.037926 | 0.037926 | 0.98695 | -0.25109 | 0.98696 | -0.25097 | 10.4192
125 | -0.03138 | -0.0078646 | 0.031411 | 0.0078839 | 3.0928e-05 | 1.9323e-05 | 0.047311 | 0.047311 | 0.047311 | 0.98696 | -0.25097 | 0.98802 | -0.2303 | 12.9976
126 | -0.0061208 | -0.0015336 | 0.0061211 | 0.0015336 | 3.0461e-07 | 7.4424e-08 | 0.0092543 | 0.0092543 | 0.0092543 | 0.98415 | -0.30391 | 0.9842 | -0.30286 | 2.5424
127 | -0.0087569 | -0.0021942 | 0.0087574 | 0.0021945 | 5.3864e-07 | 2.4058e-07 | 0.013239 | 0.013239 | 0.013239 | 0.9842 | -0.30286 | 0.98427 | -0.30157 | 3.6372
128 | -0.014187 | -0.0035553 | 0.01419 | 0.0035568 | 2.6214e-06 | 1.4845e-06 | 0.021448 | 0.021448 | 0.021448 | 0.98427 | -0.30157 | 0.98447 | -0.29769 | 5.8923
129 | -0.016999 | -0.0042603 | 0.017003 | 0.0042628 | 4.2998e-06 | 2.5286e-06 | 0.025624 | 0.025624 | 0.025624 | 0.98717 | -0.24527 | 0.98744 | -0.23996 | 7.0395
130 | 0.0036458 | 0.00091363 | -0.0036457 | -0.00091369 | 1.2088e-07 | -5.9087e-08 | 0.0054955 | 0.0054955 | 0.0054955 | 0.98717 | -0.24527 | 0.98713 | -0.24597 | 1.5098
131 | -0.020648 | -0.0051763 | 0.02065 | 0.0051771 | 1.3575e-06 | 8.2098e-07 | 0.031116 | 0.031116 | 0.031116 | 0.98744 | -0.23996 | 0.98751 | -0.23858 | 8.5484
132 | -0.034102 | -0.0085584 | 0.034124 | 0.008572 | 2.1608e-05 | 1.3549e-05 | 0.051364 | 0.051364 | 0.051364 | 0.98802 | -0.2303 | 0.9887 | -0.21703 | 14.1111
133 | -0.037524 | -0.0094242 | 0.037525 | 0.0094245 | 4.9136e-07 | 3.0921e-07 | 0.056481 | 0.056481 | 0.056481 | 0.9887 | -0.21703 | 0.98872 | -0.21675 | 15.5169
134 | -0.041204 | -0.010347 | 0.041242 | 0.01037 | 3.7655e-05 | 2.3764e-05 | 0.062019 | 0.062019 | 0.062019 | 0.98872 | -0.21675 | 0.9897 | -0.19762 | 17.0382
135 | -0.046023 | -0.011569 | 0.046026 | 0.011571 | 2.777e-06 | 1.7574e-06 | 0.069208 | 0.069208 | 0.069208 | 0.9897 | -0.19762 | 0.98977 | -0.19635 | 19.0133
136 | -0.053349 | -0.013406 | 0.053402 | 0.01344 | 5.3286e-05 | 3.3819e-05 | 0.080217 | 0.080217 | 0.080217 | 0.98977 | -0.19635 | 0.99085 | -0.17545 | 22.0378
137 | -0.009219 | -0.0023105 | 0.009221 | 0.0023114 | 2.0121e-06 | 9.3624e-07 | 0.013934 | 0.013934 | 0.013934 | 0.9845 | -0.29842 | 0.98474 | -0.29384 | 3.828
138 | -0.014826 | -0.0037162 | 0.014832 | 0.0037194 | 5.7142e-06 | 3.2707e-06 | 0.022403 | 0.022403 | 0.022403 | 0.98474 | -0.29384 | 0.98515 | -0.28575 | 6.1548
139 | 0.012407 | 0.0031109 | -0.012404 | -0.0031096 | 2.4896e-06 | 1.3527e-06 | 0.01874 | 0.01874 | 0.01874 | 0.98515 | -0.28575 | 0.98493 | -0.28996 | 5.1484
140 | -0.027238 | -0.0068304 | 0.027249 | 0.0068372 | 1.1083e-05 | 6.8709e-06 | 0.041143 | 0.041143 | 0.041143 | 0.98515 | -0.28575 | 0.98559 | -0.27722 | 11.3031
141 | 0.012404 | 0.0031096 | -0.012403 | -0.0031088 | 1.3059e-06 | 7.0961e-07 | 0.01874 | 0.01874 | 0.01874 | 0.98493 | -0.28996 | 0.98482 | -0.29217 | 5.1484
142 | 0.010224 | 0.0025628 | -0.010222 | -0.002562 | 1.6104e-06 | 8.0173e-07 | 0.015448 | 0.015448 | 0.015448 | 0.98482 | -0.29217 | 0.98465 | -0.29548 | 4.244
143 | 0.0080428 | 0.0020157 | -0.0080418 | -0.0020153 | 1.0286e-06 | 4.2218e-07 | 0.012154 | 0.012155 | 0.012155 | 0.98465 | -0.29548 | 0.98451 | -0.29816 | 3.3392
144 | 0.0058622 | 0.001469 | -0.0058616 | -0.0014689 | 5.486e-07 | 1.1416e-07 | 0.0088602 | 0.0088602 | 0.0088602 | 0.98451 | -0.29816 | 0.98441 | -0.30013 | 2.4341
145 | 0.0036821 | 0.00092269 | -0.0036819 | -0.00092277 | 1.772e-07 | -8.0519e-08 | 0.0055657 | 0.0055657 | 0.0055657 | 0.98441 | -0.30013 | 0.98436 | -0.30114 | 1.5291

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57777 | 0.14745

## res_load
| p_mw | q_mvar
0 | 0.00044843 | 0.00011239
1 | 0.0012622 | 0.00031634
2 | 0.0012912 | 0.00032361
3 | 0.0082965 | 0.0020793
4 | 0.0078372 | 0.0019642
5 | 0.0043909 | 0.0011005
6 | 0.0026393 | 0.00066147
7 | 0.0043595 | 0.0010926
8 | 0.021182 | 0.0053087
9 | 0.0077749 | 0.0019486
10 | 0.0064002 | 0.001604
11 | 0.0043668 | 0.0010944
12 | 0.004532 | 0.0011358
13 | 0.012395 | 0.0031064
14 | 0.0035193 | 0.00088201
15 | 0.011566 | 0.0028988
16 | 0.0054919 | 0.0013764
17 | 0.0045834 | 0.0011487
18 | 0.011259 | 0.0028218
19 | 0.0072245 | 0.0018106
20 | 0.0014854 | 0.00037228
21 | 0.0022676 | 0.00056832
22 | 0.001308 | 0.00032782
23 | 0.004511 | 0.0011306
24 | 0.0136 | 0.0034085
25 | 0.0022471 | 0.00056317
26 | 0.0029047 | 0.00072798
27 | 0.0028179 | 0.00070622
28 | 0.0068315 | 0.0017121
29 | 0.0020952 | 0.00052511
30 | 0.0056011 | 0.0014038
31 | 0.0090833 | 0.0022765
32 | 0.0085757 | 0.0021493
33 | 0.0068075 | 0.0017061
34 | 0.005885 | 0.0014749
35 | 0.0078455 | 0.0019663
36 | 0.0060081 | 0.0015058
37 | 0.019401 | 0.0048623
38 | 0.0058255 | 0.00146
39 | 0.0027363 | 0.00068578
40 | 0.011663 | 0.0029231
41 | 0.0076624 | 0.0019204
42 | 0.01096 | 0.0027469
43 | 0.005791 | 0.0014514
44 | 0.0028216 | 0.00070715
45 | 0.0052187 | 0.0013079
46 | 0.0022195 | 0.00055627
47 | 0.0022629 | 0.00056714
48 | 0.0022087 | 0.00055356
49 | 0.0021436 | 0.00053723
50 | 0.002904 | 0.0007278
51 | 0.0022315 | 0.00055926
52 | 0.012828 | 0.0032151
53 | 0.0015233 | 0.00038178
54 | 0.0033537 | 0.00084052
55 | 0.0033189 | 0.00083178
56 | 0.0056226 | 0.0014091
57 | 0.0021376 | 0.00053573
58 | 0.0029367 | 0.00073601
59 | 0.0042133 | 0.001056
60 | 0.0064612 | 0.0016193
61 | 0.0092522 | 0.0023188
62 | 0.0013192 | 0.00033063
63 | 0.0014635 | 0.00036678
64 | 0.0039489 | 0.00098968
65 | 0.0059414 | 0.0014891
66 | 0.016232 | 0.0040682
67 | 0.010408 | 0.0026084
68 | 0.0061024 | 0.0015294
69 | 0.0053211 | 0.0013336
70 | 0.0050606 | 0.0012683
71 | 0.010738 | 0.0026913
72 | 0.0087874 | 0.0022023
73 | 0.002565 | 0.00064284
74 | 0.0020205 | 0.00050639
75 | 0.0014768 | 0.00037011
76 | 0.0018487 | 0.00046333
77 | 0.0027386 | 0.00068635
78 | 0.0022486 | 0.00056356
79 | 0.00307 | 0.00076942
80 | 0.0020026 | 0.00050189
81 | 0.0031662 | 0.00079354
82 | 0.002447 | 0.00061328
83 | 0.0056036 | 0.0014044
84 | 0.00085246 | 0.00021365
85 | 0.0062251 | 0.0015601
86 | 0.002795 | 0.0007005
87 | 0.0026358 | 0.0006606
88 | 0.0054298 | 0.0013608
89 | 0.0030719 | 0.00076988
90 | 0.013353 | 0.0033467
91 | 0.0036449 | 0.00091349
92 | 0.0036457 | 0.00091369
93 | 0.0026913 | 0.0006745
94 | 0.0034002 | 0.00085216
95 | 0.0036793 | 0.00092213
96 | 0.0047819 | 0.0011985
97 | 0.0073228 | 0.0018353
98 | 0.00239 | 0.00059899
99 | 0.0067958 | 0.0017032
100 | 0.009219 | 0.0023105
101 | 0.005605 | 0.0014048
102 | 0.0052876 | 0.0013252
103 | 0.0021788 | 0.00054605
104 | 0.0021796 | 0.00054625
105 | 0.0021797 | 0.00054627
106 | 0.0021796 | 0.00054625
107 | 0.0036819 | 0.00092277

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1