## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_117-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_117-3_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_117-3_0_3_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_117-3_0_3_node_190 | 0.4 | n |  | TRUE
4 | bus_LV_117-3_0_3_node_72 | 0.4 | n |  | TRUE
5 | bus_LV_117-3_0_3_node_234 | 0.4 | n |  | TRUE
6 | bus_LV_117-3_0_3_node_236 | 0.4 | n |  | TRUE
7 | bus_LV_117-3_0_3_node_71 | 0.4 | n |  | TRUE
8 | bus_LV_117-3_0_3_node_162 | 0.4 | n |  | TRUE
9 | bus_LV_117-3_0_3_node_165 | 0.4 | n |  | TRUE
10 | bus_LV_117-3_0_3_node_158 | 0.4 | n |  | TRUE
11 | bus_LV_117-3_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_117-3_0_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_117-3_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_117-3_0_3_node_120 | 0.4 | n |  | TRUE
15 | bus_LV_117-3_0_3_node_122 | 0.4 | n |  | TRUE
16 | bus_LV_117-3_0_3_node_123 | 0.4 | n |  | TRUE
17 | bus_LV_117-3_0_3_node_121 | 0.4 | n |  | TRUE
18 | bus_LV_117-3_0_3_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_117-3_0_3_node_58 | 0.4 | n |  | TRUE
20 | bus_LV_117-3_0_3_node_59 | 0.4 | n |  | TRUE
21 | bus_LV_117-3_0_3_node_55 | 0.4 | n |  | TRUE
22 | bus_LV_117-3_0_3_node_56 | 0.4 | n |  | TRUE
23 | bus_LV_117-3_0_3_node_57 | 0.4 | n |  | TRUE
24 | bus_LV_117-3_0_3_node_109 | 0.4 | n |  | TRUE
25 | bus_LV_117-3_0_3_node_114 | 0.4 | n |  | TRUE
26 | bus_LV_117-3_0_3_node_107 | 0.4 | n |  | TRUE
27 | bus_LV_117-3_0_3_node_232 | 0.4 | n |  | TRUE
28 | bus_LV_117-3_0_3_node_116 | 0.4 | n |  | TRUE
29 | bus_LV_117-3_0_3_node_60 | 0.4 | n |  | TRUE
30 | bus_LV_117-3_0_3_node_61 | 0.4 | n |  | TRUE
31 | bus_LV_117-3_0_3_node_62 | 0.4 | n |  | TRUE
32 | bus_LV_117-3_0_3_node_63 | 0.4 | n |  | TRUE
33 | bus_LV_117-3_0_3_node_64 | 0.4 | n |  | TRUE
34 | bus_LV_117-3_0_3_node_191 | 0.4 | n |  | TRUE
35 | bus_LV_117-3_0_3_node_65 | 0.4 | n |  | TRUE
36 | bus_LV_117-3_0_3_node_66 | 0.4 | n |  | TRUE
37 | bus_LV_117-3_0_3_node_67 | 0.4 | n |  | TRUE
38 | bus_LV_117-3_0_3_node_70 | 0.4 | n |  | TRUE
39 | bus_LV_117-3_0_3_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_117-3_0_3_node_69 | 0.4 | n |  | TRUE
41 | bus_LV_117-3_0_3_node_74 | 0.4 | n |  | TRUE
42 | bus_LV_117-3_0_3_node_75 | 0.4 | n |  | TRUE
43 | bus_LV_117-3_0_3_node_129 | 0.4 | n |  | TRUE
44 | bus_LV_117-3_0_3_node_135 | 0.4 | n |  | TRUE
45 | bus_LV_117-3_0_3_node_73 | 0.4 | n |  | TRUE
46 | bus_LV_117-3_0_3_node_233 | 0.4 | n |  | TRUE
47 | bus_LV_117-3_0_3_node_235 | 0.4 | n |  | TRUE
48 | bus_LV_117-3_0_3_node_81 | 0.4 | n |  | TRUE
49 | bus_LV_117-3_0_3_node_86 | 0.4 | n |  | TRUE
50 | bus_LV_117-3_0_3_node_76 | 0.4 | n |  | TRUE
51 | bus_LV_117-3_0_3_node_77 | 0.4 | n |  | TRUE
52 | bus_LV_117-3_0_3_node_78 | 0.4 | n |  | TRUE
53 | bus_LV_117-3_0_3_node_79 | 0.4 | n |  | TRUE
54 | bus_LV_117-3_0_3_node_80 | 0.4 | n |  | TRUE
55 | bus_LV_117-3_0_3_node_82 | 0.4 | n |  | TRUE
56 | bus_LV_117-3_0_3_node_119 | 0.4 | n |  | TRUE
57 | bus_LV_117-3_0_3_node_125 | 0.4 | n |  | TRUE
58 | bus_LV_117-3_0_3_node_229 | 0.4 | n |  | TRUE
59 | bus_LV_117-3_0_3_node_126 | 0.4 | n |  | TRUE
60 | bus_LV_117-3_0_3_node_230 | 0.4 | n |  | TRUE
61 | bus_LV_117-3_0_3_node_83 | 0.4 | n |  | TRUE
62 | bus_LV_117-3_0_3_node_84 | 0.4 | n |  | TRUE
63 | bus_LV_117-3_0_3_node_85 | 0.4 | n |  | TRUE
64 | bus_LV_117-3_0_3_node_87 | 0.4 | n |  | TRUE
65 | bus_LV_117-3_0_3_node_136 | 0.4 | n |  | TRUE
66 | bus_LV_117-3_0_3_node_195 | 0.4 | n |  | TRUE
67 | bus_LV_117-3_0_3_node_192 | 0.4 | n |  | TRUE
68 | bus_LV_117-3_0_3_node_88 | 0.4 | n |  | TRUE
69 | bus_LV_117-3_0_3_node_198 | 0.4 | n |  | TRUE
70 | bus_LV_117-3_0_3_node_137 | 0.4 | n |  | TRUE
71 | bus_LV_117-3_0_3_node_196 | 0.4 | n |  | TRUE
72 | bus_LV_117-3_0_3_node_193 | 0.4 | n |  | TRUE
73 | bus_LV_117-3_0_3_node_199 | 0.4 | n |  | TRUE
74 | bus_LV_117-3_0_3_node_106 | 0.4 | n |  | TRUE
75 | bus_LV_117-3_0_3_node_112 | 0.4 | n |  | TRUE
76 | bus_LV_117-3_0_3_node_110 | 0.4 | n |  | TRUE
77 | bus_LV_117-3_0_3_node_111 | 0.4 | n |  | TRUE
78 | bus_LV_117-3_0_3_node_238 | 0.4 | n |  | TRUE
79 | bus_LV_117-3_0_3_node_237 | 0.4 | n |  | TRUE
80 | bus_LV_117-3_0_3_node_115 | 0.4 | n |  | TRUE
81 | bus_LV_117-3_0_3_node_113 | 0.4 | n |  | TRUE
82 | bus_LV_117-3_0_3_node_118 | 0.4 | n |  | TRUE
83 | bus_LV_117-3_0_3_node_117 | 0.4 | n |  | TRUE
84 | bus_LV_117-3_0_3_node_231 | 0.4 | n |  | TRUE
85 | bus_LV_117-3_0_3_node_132 | 0.4 | n |  | TRUE
86 | bus_LV_117-3_0_3_node_124 | 0.4 | n |  | TRUE
87 | bus_LV_117-3_0_3_node_134 | 0.4 | n |  | TRUE
88 | bus_LV_117-3_0_3_node_133 | 0.4 | n |  | TRUE
89 | bus_LV_117-3_0_3_node_127 | 0.4 | n |  | TRUE
90 | bus_LV_117-3_0_3_node_128 | 0.4 | n |  | TRUE
91 | bus_LV_117-3_0_3_node_130 | 0.4 | n |  | TRUE
92 | bus_LV_117-3_0_3_node_131 | 0.4 | n |  | TRUE
93 | bus_LV_117-3_0_3_node_138 | 0.4 | n |  | TRUE
94 | bus_LV_117-3_0_3_node_139 | 0.4 | n |  | TRUE
95 | bus_LV_117-3_0_3_node_140 | 0.4 | n |  | TRUE
96 | bus_LV_117-3_0_3_node_141 | 0.4 | n |  | TRUE
97 | bus_LV_117-3_0_3_node_143 | 0.4 | n |  | TRUE
98 | bus_LV_117-3_0_3_node_142 | 0.4 | n |  | TRUE
99 | bus_LV_117-3_0_3_node_144 | 0.4 | n |  | TRUE
100 | bus_LV_117-3_0_3_node_145 | 0.4 | n |  | TRUE
101 | bus_LV_117-3_0_3_node_148 | 0.4 | n |  | TRUE
102 | bus_LV_117-3_0_3_node_146 | 0.4 | n |  | TRUE
103 | bus_LV_117-3_0_3_node_150 | 0.4 | n |  | TRUE
104 | bus_LV_117-3_0_3_node_210 | 0.4 | n |  | TRUE
105 | bus_LV_117-3_0_3_node_149 | 0.4 | n |  | TRUE
106 | bus_LV_117-3_0_3_node_147 | 0.4 | n |  | TRUE
107 | bus_LV_117-3_0_3_node_151 | 0.4 | n |  | TRUE
108 | bus_LV_117-3_0_3_node_152 | 0.4 | n |  | TRUE
109 | bus_LV_117-3_0_3_node_155 | 0.4 | n |  | TRUE
110 | bus_LV_117-3_0_3_node_153 | 0.4 | n |  | TRUE
111 | bus_LV_117-3_0_3_node_209 | 0.4 | n |  | TRUE
112 | bus_LV_117-3_0_3_node_211 | 0.4 | n |  | TRUE
113 | bus_LV_117-3_0_3_node_163 | 0.4 | n |  | TRUE
114 | bus_LV_117-3_0_3_node_205 | 0.4 | n |  | TRUE
115 | bus_LV_117-3_0_3_node_154 | 0.4 | n |  | TRUE
116 | bus_LV_117-3_0_3_node_208 | 0.4 | n |  | TRUE
117 | bus_LV_117-3_0_3_node_156 | 0.4 | n |  | TRUE
118 | bus_LV_117-3_0_3_node_164 | 0.4 | n |  | TRUE
119 | bus_LV_117-3_0_3_node_161 | 0.4 | n |  | TRUE
120 | bus_LV_117-3_0_3_node_159 | 0.4 | n |  | TRUE
121 | bus_LV_117-3_0_3_node_160 | 0.4 | n |  | TRUE
122 | bus_LV_117-3_0_3_node_179 | 0.4 | n |  | TRUE
123 | bus_LV_117-3_0_3_node_178 | 0.4 | n |  | TRUE
124 | bus_LV_117-3_0_3_node_177 | 0.4 | n |  | TRUE
125 | bus_LV_117-3_0_3_node_180 | 0.4 | n |  | TRUE
126 | bus_LV_117-3_0_3_node_203 | 0.4 | n |  | TRUE
127 | bus_LV_117-3_0_3_node_202 | 0.4 | n |  | TRUE
128 | bus_LV_117-3_0_3_node_194 | 0.4 | n |  | TRUE
129 | bus_LV_117-3_0_3_node_197 | 0.4 | n |  | TRUE
130 | bus_LV_117-3_0_3_node_200 | 0.4 | n |  | TRUE
131 | bus_LV_117-3_0_3_node_201 | 0.4 | n |  | TRUE
132 | bus_LV_117-3_0_3_node_206 | 0.4 | n |  | TRUE
133 | bus_LV_117-3_0_3_node_207 | 0.4 | n |  | TRUE
134 | bus_LV_117-3_0_3_node_204 | 0.4 | n |  | TRUE
135 | bus_MV_8_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_117-3_0_3_load_0 | 0 | 0.0021477 | 0.00053826 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_117-3_0_3_load_2 | 1 | 0.0012889 | 0.00032302 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_117-3_0_3_load_190 | 3 | 0.0015525 | 0.00038911 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_117-3_0_3_load_234 | 5 | 0.0031499 | 0.00078945 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_117-3_0_3_load_236 | 6 | 0.0015292 | 0.00038326 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_117-3_0_3_load_162 | 8 | 0.0019016 | 0.0004766 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_117-3_0_3_load_165 | 9 | 0.0019164 | 0.0004803 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_117-3_0_3_load_11 | 11 | 0.0019077 | 0.00047812 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_117-3_0_3_load_120 | 14 | 0.0015107 | 0.00037862 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_117-3_0_3_load_123 | 16 | 0.0023412 | 0.00058675 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_117-3_0_3_load_121 | 17 | 0.0010726 | 0.00026883 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_117-3_0_3_load_51 | 18 | 0.0057339 | 0.0014371 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_117-3_0_3_load_58 | 19 | 0.0027466 | 0.00068836 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_117-3_0_3_load_59 | 20 | 0.0021394 | 0.0005362 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_117-3_0_3_load_55 | 21 | 0.002664 | 0.00066765 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_117-3_0_3_load_114 | 25 | 0.0027146 | 0.00068034 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_117-3_0_3_load_107 | 26 | 0.0036735 | 0.00092068 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_117-3_0_3_load_232 | 27 | 0.0074398 | 0.0018646 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_117-3_0_3_load_60 | 29 | 0.0042289 | 0.0010599 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_117-3_0_3_load_62 | 31 | 0.0019533 | 0.00048954 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_117-3_0_3_load_63 | 32 | 0.0017829 | 0.00044684 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_117-3_0_3_load_191 | 34 | 0.0016859 | 0.00042252 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_117-3_0_3_load_65 | 35 | 0.0075323 | 0.0018878 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_117-3_0_3_load_66 | 36 | 0.0024911 | 0.00062432 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_117-3_0_3_load_67 | 37 | 0.0068016 | 0.0017046 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_117-3_0_3_load_70 | 38 | 0.0018025 | 0.00045174 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_117-3_0_3_load_68 | 39 | 0.0032329 | 0.00081025 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_117-3_0_3_load_74 | 41 | 0.0011547 | 0.00028938 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_117-3_0_3_load_75 | 42 | 0.0023391 | 0.00058624 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_117-3_0_3_load_129 | 43 | 0.0011282 | 0.00028275 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_117-3_0_3_load_135 | 44 | 0.0025116 | 0.00062948 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_117-3_0_3_load_73 | 45 | 0.001453 | 0.00036415 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_117-3_0_3_load_233 | 46 | 0.0024325 | 0.00060964 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_117-3_0_3_load_235 | 47 | 0.0023317 | 0.00058437 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_117-3_0_3_load_76 | 50 | 0.0069169 | 0.0017335 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_117-3_0_3_load_77 | 51 | 0.0097115 | 0.0024339 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_117-3_0_3_load_79 | 53 | 0.0072496 | 0.0018169 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_117-3_0_3_load_82 | 55 | 0.0069786 | 0.001749 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_117-3_0_3_load_119 | 56 | 0.0034109 | 0.00085485 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_117-3_0_3_load_125 | 57 | 0.0020867 | 0.00052299 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_117-3_0_3_load_229 | 58 | 0.0079417 | 0.0019904 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_117-3_0_3_load_230 | 60 | 0.0070461 | 0.0017659 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_117-3_0_3_load_83 | 61 | 0.0017588 | 0.0004408 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_117-3_0_3_load_84 | 62 | 0.0006531 | 0.00016368 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_117-3_0_3_load_87 | 64 | 0.00068963 | 0.00017284 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_117-3_0_3_load_136 | 65 | 0.0016444 | 0.00041213 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_117-3_0_3_load_195 | 66 | 0.00093147 | 0.00023345 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_117-3_0_3_load_192 | 67 | 0.0007217 | 0.00018087 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_117-3_0_3_load_88 | 68 | 0.00059306 | 0.00014864 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_117-3_0_3_load_198 | 69 | 0.0012897 | 0.00032323 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_117-3_0_3_load_137 | 70 | 0.0018014 | 0.00045146 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_117-3_0_3_load_196 | 71 | 0.000711 | 0.00017819 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_117-3_0_3_load_193 | 72 | 0.00073274 | 0.00018364 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_117-3_0_3_load_199 | 73 | 0.0016331 | 0.00040929 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_117-3_0_3_load_106 | 74 | 0.0041366 | 0.0010367 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_117-3_0_3_load_110 | 76 | 0.0013144 | 0.00032941 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_117-3_0_3_load_111 | 77 | 0.0047231 | 0.0011837 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_117-3_0_3_load_237 | 79 | 0.0051451 | 0.0012895 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_117-3_0_3_load_113 | 81 | 0.0039366 | 0.0009866 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_117-3_0_3_load_118 | 82 | 0.0043725 | 0.0010958 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_117-3_0_3_load_117 | 83 | 0.0024981 | 0.00062608 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_117-3_0_3_load_231 | 84 | 0.0072983 | 0.0018291 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_117-3_0_3_load_134 | 87 | 0.002326 | 0.00058295 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_117-3_0_3_load_133 | 88 | 0.0023219 | 0.00058193 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_117-3_0_3_load_127 | 89 | 0.0016532 | 0.00041433 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_117-3_0_3_load_128 | 90 | 0.0010659 | 0.00026713 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_117-3_0_3_load_130 | 91 | 0.0012601 | 0.00031581 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_117-3_0_3_load_131 | 92 | 0.0022249 | 0.0005576 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_117-3_0_3_load_139 | 94 | 0.0018879 | 0.00047315 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_117-3_0_3_load_140 | 95 | 0.0014604 | 0.00036601 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_117-3_0_3_load_141 | 96 | 0.0021683 | 0.00054344 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_117-3_0_3_load_142 | 98 | 0.0027404 | 0.00068681 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_117-3_0_3_load_145 | 100 | 0.0017058 | 0.0004275 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_117-3_0_3_load_148 | 101 | 0.0041516 | 0.0010405 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_117-3_0_3_load_146 | 102 | 0.00239 | 0.00059899 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_117-3_0_3_load_150 | 103 | 0.0015056 | 0.00037733 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_117-3_0_3_load_210 | 104 | 0.0013776 | 0.00034527 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_117-3_0_3_load_147 | 106 | 0.0076769 | 0.001924 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_117-3_0_3_load_152 | 108 | 0.0013779 | 0.00034534 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_117-3_0_3_load_153 | 110 | 0.0017658 | 0.00044254 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_117-3_0_3_load_211 | 112 | 0.0016176 | 0.00040541 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_117-3_0_3_load_205 | 114 | 0.0019143 | 0.00047978 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_117-3_0_3_load_208 | 116 | 0.0016224 | 0.00040662 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_117-3_0_3_load_156 | 117 | 0.0018429 | 0.00046187 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_117-3_0_3_load_164 | 118 | 0.010496 | 0.0026306 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_117-3_0_3_load_161 | 119 | 0.0037917 | 0.00095028 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_117-3_0_3_load_159 | 120 | 0.0020511 | 0.00051406 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_117-3_0_3_load_160 | 121 | 0.0021026 | 0.00052696 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_117-3_0_3_load_179 | 122 | 0.001468 | 0.00036792 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_117-3_0_3_load_177 | 124 | 0.0041507 | 0.0010403 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_117-3_0_3_load_180 | 125 | 0.00089667 | 0.00022473 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_117-3_0_3_load_203 | 126 | 0.0019371 | 0.00048548 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_117-3_0_3_load_202 | 127 | 0.0012276 | 0.00030766 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_117-3_0_3_load_194 | 128 | 0.0014513 | 0.00036373 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_117-3_0_3_load_197 | 129 | 0.0015264 | 0.00038254 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_117-3_0_3_load_200 | 130 | 0.0014388 | 0.0003606 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_117-3_0_3_load_201 | 131 | 0.0014479 | 0.00036288 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_117-3_0_3_load_207 | 133 | 0.0014219 | 0.00035636 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_117-3_0_3_load_204 | 134 | 0.0019365 | 0.00048534 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_117-3_0_3_line_0 |  | 0 | 1 | 0.020854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_117-3_0_3_line_1 |  | 1 | 2 | 0.0099172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_117-3_0_3_line_2 |  | 2 | 3 | 0.040429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_117-3_0_3_line_3 |  | 2 | 4 | 0.005789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_117-3_0_3_line_4 |  | 3 | 5 | 0.044901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_117-3_0_3_line_5 |  | 4 | 6 | 0.021502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_117-3_0_3_line_6 |  | 4 | 7 | 0.020539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_117-3_0_3_line_7 |  | 6 | 47 | 0.022318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_117-3_0_3_line_8 |  | 7 | 45 | 0.025935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_117-3_0_3_line_9 |  | 7 | 38 | 0.035572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_117-3_0_3_line_10 |  | 8 | 9 | 0.033909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_117-3_0_3_line_11 |  | 8 | 10 | 0.0098274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_117-3_0_3_line_12 |  | 10 | 120 | 0.0087705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_117-3_0_3_line_13 |  | 11 | 12 | 0.10154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_117-3_0_3_line_14 |  | 12 | 13 | 0.045762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_117-3_0_3_line_15 |  | 13 | 14 | 0.019921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_117-3_0_3_line_16 |  | 13 | 15 | 0.058294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_117-3_0_3_line_17 |  | 15 | 16 | 0.034143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_117-3_0_3_line_18 |  | 15 | 17 | 0.034782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_117-3_0_3_line_19 |  | 16 | 85 | 0.019346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_117-3_0_3_line_20 |  | 17 | 54 | 0.0039401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_117-3_0_3_line_21 |  | 18 | 19 | 0.022938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_117-3_0_3_line_22 |  | 19 | 20 | 0.009874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_117-3_0_3_line_23 |  | 20 | 29 | 0.022364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_117-3_0_3_line_24 |  | 21 | 22 | 0.0067145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_117-3_0_3_line_25 |  | 22 | 23 | 0.034778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_117-3_0_3_line_26 |  | 23 | 24 | 0.033455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_117-3_0_3_line_27 |  | 24 | 25 | 0.028549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_117-3_0_3_line_28 |  | 24 | 26 | 0.024712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_117-3_0_3_line_29 |  | 25 | 80 | 0.010777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_117-3_0_3_line_30 |  | 26 | 75 | 0.050951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_117-3_0_3_line_31 |  | 26 | 74 | 0.016657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_117-3_0_3_line_32 |  | 27 | 28 | 0.033063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_117-3_0_3_line_33 |  | 28 | 84 | 0.0037054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_117-3_0_3_line_34 |  | 28 | 80 | 0.026564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_117-3_0_3_line_35 |  | 29 | 30 | 0.013937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_117-3_0_3_line_36 |  | 30 | 31 | 0.019227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_117-3_0_3_line_37 |  | 30 | 32 | 0.017296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_117-3_0_3_line_38 |  | 31 | 33 | 0.019148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_117-3_0_3_line_39 |  | 32 | 34 | 0.022387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_117-3_0_3_line_40 |  | 33 | 35 | 0.0082951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_117-3_0_3_line_41 |  | 33 | 36 | 0.033712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_117-3_0_3_line_42 |  | 35 | 37 | 0.028695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_117-3_0_3_line_43 |  | 36 | 38 | 0.017995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_117-3_0_3_line_44 |  | 37 | 39 | 0.029867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_117-3_0_3_line_45 |  | 39 | 40 | 0.028684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_117-3_0_3_line_46 |  | 40 | 41 | 0.0055124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_117-3_0_3_line_47 |  | 40 | 42 | 0.022513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_117-3_0_3_line_48 |  | 41 | 43 | 0.026094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_117-3_0_3_line_49 |  | 42 | 44 | 0.022202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_117-3_0_3_line_50 |  | 43 | 48 | 0.016787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_117-3_0_3_line_51 |  | 44 | 49 | 0.015881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_117-3_0_3_line_52 |  | 45 | 46 | 0.023416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_117-3_0_3_line_53 |  | 48 | 57 | 0.018672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_117-3_0_3_line_54 |  | 48 | 52 | 0.003898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_117-3_0_3_line_55 |  | 49 | 65 | 0.0094923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_117-3_0_3_line_56 |  | 49 | 62 | 0.017659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_117-3_0_3_line_57 |  | 50 | 51 | 0.015134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_117-3_0_3_line_58 |  | 50 | 52 | 0.018689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_117-3_0_3_line_59 |  | 51 | 53 | 0.018851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_117-3_0_3_line_60 |  | 52 | 54 | 0.038219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_117-3_0_3_line_61 |  | 53 | 55 | 0.016151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_117-3_0_3_line_62 |  | 54 | 56 | 0.02984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_117-3_0_3_line_63 |  | 55 | 58 | 0.019519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_117-3_0_3_line_64 |  | 57 | 59 | 0.022449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_117-3_0_3_line_65 |  | 58 | 60 | 0.016058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_117-3_0_3_line_66 |  | 59 | 89 | 0.014994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_117-3_0_3_line_67 |  | 59 | 90 | 0.014501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_117-3_0_3_line_68 |  | 60 | 84 | 0.016999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_117-3_0_3_line_69 |  | 61 | 62 | 0.0042327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_117-3_0_3_line_70 |  | 61 | 63 | 0.01234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_117-3_0_3_line_71 |  | 63 | 64 | 0.014319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_117-3_0_3_line_72 |  | 64 | 66 | 0.012013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_117-3_0_3_line_73 |  | 64 | 67 | 0.015875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_117-3_0_3_line_74 |  | 65 | 70 | 0.023917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_117-3_0_3_line_75 |  | 66 | 71 | 0.025026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_117-3_0_3_line_76 |  | 67 | 72 | 0.0038286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_117-3_0_3_line_77 |  | 68 | 69 | 0.018312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_117-3_0_3_line_78 |  | 69 | 73 | 0.0055992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_117-3_0_3_line_79 |  | 71 | 129 | 0.014597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_117-3_0_3_line_80 |  | 72 | 128 | 0.015963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_117-3_0_3_line_81 |  | 73 | 127 | 0.0018301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_117-3_0_3_line_82 |  | 75 | 76 | 0.010734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_117-3_0_3_line_83 |  | 76 | 77 | 0.040151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_117-3_0_3_line_84 |  | 76 | 78 | 0.12273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_117-3_0_3_line_85 |  | 77 | 81 | 0.030312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_117-3_0_3_line_86 |  | 78 | 79 | 0.022601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_117-3_0_3_line_87 |  | 80 | 83 | 0.0056657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_117-3_0_3_line_88 |  | 82 | 83 | 0.020037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_117-3_0_3_line_89 |  | 85 | 88 | 0.019278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_117-3_0_3_line_90 |  | 85 | 86 | 0.029605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_117-3_0_3_line_91 |  | 86 | 87 | 0.0095477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_117-3_0_3_line_92 |  | 89 | 91 | 0.017044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_117-3_0_3_line_93 |  | 90 | 92 | 0.013598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_117-3_0_3_line_94 |  | 93 | 94 | 0.013051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_117-3_0_3_line_95 |  | 93 | 95 | 0.012639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_117-3_0_3_line_96 |  | 94 | 96 | 0.017447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_117-3_0_3_line_97 |  | 95 | 97 | 0.030801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_117-3_0_3_line_98 |  | 96 | 98 | 0.00080276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_117-3_0_3_line_99 |  | 97 | 99 | 0.017097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_117-3_0_3_line_100 |  | 97 | 100 | 0.024949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_117-3_0_3_line_101 |  | 99 | 101 | 0.0075486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_117-3_0_3_line_102 |  | 100 | 102 | 0.00024174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_117-3_0_3_line_103 |  | 101 | 105 | 0.012487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_117-3_0_3_line_104 |  | 102 | 106 | 0.016215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_117-3_0_3_line_105 |  | 103 | 104 | 0.0070101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_117-3_0_3_line_106 |  | 104 | 112 | 0.016631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_117-3_0_3_line_107 |  | 105 | 107 | 0.018739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_117-3_0_3_line_108 |  | 105 | 108 | 0.0091838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_117-3_0_3_line_109 |  | 107 | 109 | 0.022841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_117-3_0_3_line_110 |  | 107 | 110 | 0.016176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_117-3_0_3_line_111 |  | 108 | 111 | 0.0059696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_117-3_0_3_line_112 |  | 109 | 113 | 0.003808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_117-3_0_3_line_113 |  | 109 | 114 | 0.010859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_117-3_0_3_line_114 |  | 110 | 115 | 0.0043566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_117-3_0_3_line_115 |  | 111 | 116 | 0.011352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_117-3_0_3_line_116 |  | 112 | 128 | 0.0094925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_117-3_0_3_line_117 |  | 113 | 118 | 0.022172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_117-3_0_3_line_118 |  | 113 | 119 | 0.03061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_117-3_0_3_line_119 |  | 115 | 117 | 0.014885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_117-3_0_3_line_120 |  | 116 | 133 | 0.014066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_117-3_0_3_line_121 |  | 118 | 122 | 0.0026794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_117-3_0_3_line_122 |  | 119 | 121 | 0.0042749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_117-3_0_3_line_123 |  | 120 | 121 | 0.022495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_117-3_0_3_line_124 |  | 122 | 123 | 0.017924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_117-3_0_3_line_125 |  | 123 | 125 | 0.015865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_117-3_0_3_line_126 |  | 123 | 124 | 0.0063937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_117-3_0_3_line_127 |  | 125 | 126 | 0.025157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_117-3_0_3_line_128 |  | 126 | 127 | 0.021147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_117-3_0_3_line_129 |  | 129 | 130 | 0.0070066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_117-3_0_3_line_130 |  | 130 | 131 | 0.014954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_117-3_0_3_line_131 |  | 131 | 132 | 0.00069372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_117-3_0_3_line_132 |  | 132 | 133 | 0.0060791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_117-3_0_3_line_133 |  | 132 | 134 | 0.0090076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_117-3_0_3_trafo_67 | 0.63 MVA 20/0.4 kV | 135 | 37 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2707548.1846 | 1238366.3736 | 2707554.0333 | 1238358.0796 | 2707555.1155 | 1238347.4296
1 | 2707553.5669 | 1238337.8888 | 2707555.5435 | 1238343.2176 | 2707555.1155 | 1238347.4296
2 | 2707553.5669 | 1238337.8888 | 2707569.8938 | 1238337.9401 | 2707579.7937 | 1238326.4883 | 2707587.628 | 1238330.8442
3 | 2707553.5669 | 1238337.8888 | 2707551.5544 | 1238332.4593
4 | 2707613.945 | 1238309.1046 | 2707599.0822 | 1238337.2127 | 2707587.628 | 1238330.8442
5 | 2707551.5544 | 1238332.4593 | 2707562.2636 | 1238330.6185 | 2707567.0799 | 1238327.8813 | 2707570.3876 | 1238324.0047
6 | 2707537.7085 | 1238317.8305 | 2707550.0829 | 1238328.4851 | 2707551.5544 | 1238332.4593
7 | 2707583.7888 | 1238306.3344 | 2707576.9674 | 1238314.1942 | 2707574.648 | 1238319.0115 | 2707570.3876 | 1238324.0047
8 | 2707537.7085 | 1238317.8305 | 2707521.9907 | 1238338.4601
9 | 2707537.7085 | 1238317.8305 | 2707516.5009 | 1238306.5266 | 2707505.1864 | 1238304.2574
10 | 2707732.0337 | 1238278.1215 | 2707732.0337 | 1238278.1215 | 2707721.6528 | 1238308.9683 | 2707720.8612 | 1238310.0773
11 | 2707728.0887 | 1238269.1207 | 2707732.0337 | 1238278.1215
12 | 2707728.0887 | 1238269.1207 | 2707721.6298 | 1238268.1361 | 2707719.6553 | 1238269.1876
13 | 2707402.2191 | 1238082.9408 | 2707426.402 | 1237984.3183
14 | 2707402.2191 | 1238082.9408 | 2707395.2245 | 1238104.0196 | 2707386.2204 | 1238118.657 | 2707390.385 | 1238123.5027
15 | 2707390.385 | 1238123.5027 | 2707378.1885 | 1238139.2538
16 | 2707390.385 | 1238123.5027 | 2707395.5294 | 1238116.8573 | 2707413.1022 | 1238132.5539 | 2707418.1727 | 1238144.6217 | 2707419.4323 | 1238157.7991
17 | 2707419.4323 | 1238157.7991 | 2707427.5469 | 1238157.6124 | 2707434.6419 | 1238153.5598 | 2707448.7562 | 1238142.6236
18 | 2707419.4323 | 1238157.7991 | 2707417.3169 | 1238174.7629 | 2707408.0349 | 1238189.818
19 | 2707464.049 | 1238130.7742 | 2707448.7562 | 1238142.6236
20 | 2707405.967 | 1238193.1719 | 2707408.0349 | 1238189.818
21 | 2707397.3907 | 1238387.5238 | 2707409.1444 | 1238367.8257
22 | 2707414.2039 | 1238359.3465 | 2707409.1444 | 1238367.8257
23 | 2707414.2039 | 1238359.3465 | 2707425.6634 | 1238340.1418
24 | 2707328.1872 | 1238390.0854 | 2707330.5202 | 1238396.3816
25 | 2707327.1562 | 1238355.4732 | 2707326.0557 | 1238371.9772 | 2707328.1872 | 1238390.0854
26 | 2707327.1562 | 1238355.4732 | 2707327.6246 | 1238348.3984 | 2707333.5445 | 1238322.7077
27 | 2707333.5445 | 1238322.7077 | 2707343.3835 | 1238295.9072
28 | 2707333.5445 | 1238322.7077 | 2707318.8426 | 1238318.1495 | 2707309.9045 | 1238320.7901
29 | 2707347.0975 | 1238285.7906 | 2707343.3835 | 1238295.9072
30 | 2707309.9045 | 1238320.7901 | 2707280.6051 | 1238279.1062
31 | 2707298.1032 | 1238332.5447 | 2707309.9045 | 1238320.7901
32 | 2707368.2248 | 1238301.974 | 2707348.0919 | 1238328.2007
33 | 2707368.2248 | 1238301.974 | 2707371.1651 | 1238304.2289
34 | 2707347.0975 | 1238285.7906 | 2707368.2248 | 1238301.974
35 | 2707432.8049 | 1238328.1733 | 2707425.6634 | 1238340.1418
36 | 2707432.8049 | 1238328.1733 | 2707440.4751 | 1238315.3243 | 2707443.0629 | 1238311.9375
37 | 2707432.8049 | 1238328.1733 | 2707447.5776 | 1238337.1695
38 | 2707454.6883 | 1238296.7226 | 2707443.0629 | 1238311.9375
39 | 2707466.6984 | 1238348.8137 | 2707447.5776 | 1238337.1695
40 | 2707454.6883 | 1238296.7226 | 2707459.0268 | 1238289.6525
41 | 2707454.6883 | 1238296.7226 | 2707465.9304 | 1238301.3963 | 2707487.4676 | 1238301.4657
42 | 2707459.0268 | 1238289.6525 | 2707474.035 | 1238265.1948
43 | 2707487.4676 | 1238301.4657 | 2707491.3287 | 1238301.4782 | 2707505.1864 | 1238304.2574
44 | 2707474.035 | 1238265.1948 | 2707487.5266 | 1238243.2085 | 2707489.0143 | 1238239.4185
45 | 2707492.6555 | 1238211.5212 | 2707493.1348 | 1238228.9212 | 2707489.0143 | 1238239.4185
46 | 2707492.6555 | 1238211.5212 | 2707487.1488 | 1238211.7725
47 | 2707492.6555 | 1238211.5212 | 2707514.5012 | 1238206.0794
48 | 2707461.1338 | 1238211.9294 | 2707466.4921 | 1238212.7153 | 2707487.1488 | 1238211.7725
49 | 2707514.5012 | 1238206.0794 | 2707536.0444 | 1238200.7129
50 | 2707444.5248 | 1238209.4931 | 2707461.1338 | 1238211.9294
51 | 2707551.4542 | 1238196.8743 | 2707536.0444 | 1238200.7129
52 | 2707507.7993 | 1238357.0862 | 2707521.9907 | 1238338.4601
53 | 2707444.5248 | 1238209.4931 | 2707449.1684 | 1238191.4072
54 | 2707440.7527 | 1238208.4686 | 2707444.5248 | 1238209.4931
55 | 2707551.4542 | 1238196.8743 | 2707560.675 | 1238194.6204
56 | 2707551.4542 | 1238196.8743 | 2707551.7681 | 1238214.5303
57 | 2707429.2818 | 1238223.2232 | 2707419.9927 | 1238235.1715
58 | 2707440.7527 | 1238208.4686 | 2707429.2818 | 1238223.2232
59 | 2707408.4226 | 1238250.0538 | 2707419.9927 | 1238235.1715
60 | 2707440.7527 | 1238208.4686 | 2707424.9264 | 1238204.1456 | 2707405.967 | 1238193.1719
61 | 2707408.4226 | 1238250.0538 | 2707398.5099 | 1238262.8043
62 | 2707405.967 | 1238193.1719 | 2707388.9621 | 1238217.6926
63 | 2707390.9364 | 1238277.7365 | 2707394.1409 | 1238273.4426 | 2707391.7085 | 1238271.5527 | 2707398.5099 | 1238262.8043
64 | 2707465.4948 | 1238178.7932 | 2707454.6781 | 1238181.9555 | 2707450.1743 | 1238187.4894 | 2707449.1684 | 1238191.4072
65 | 2707390.9364 | 1238277.7365 | 2707381.3323 | 1238290.6054
66 | 2707465.4948 | 1238178.7932 | 2707462.2577 | 1238164.1527
67 | 2707465.4948 | 1238178.7932 | 2707479.6226 | 1238175.5256
68 | 2707381.3323 | 1238290.6054 | 2707371.1651 | 1238304.2289
69 | 2707551.7681 | 1238214.5303 | 2707551.8433 | 1238218.7624
70 | 2707555.9705 | 1238229.4814 | 2707551.96 | 1238225.3278 | 2707551.8433 | 1238218.7624
71 | 2707555.9705 | 1238229.4814 | 2707559.7692 | 1238224.8689 | 2707567.9084 | 1238222.9036
72 | 2707567.9084 | 1238222.9036 | 2707576.9282 | 1238230.8383
73 | 2707567.9084 | 1238222.9036 | 2707583.3429 | 1238219.1914
74 | 2707560.675 | 1238194.6204 | 2707583.9079 | 1238188.9413
75 | 2707576.9282 | 1238230.8383 | 2707580.0405 | 1238233.5761 | 2707589.4677 | 1238236.9384 | 2707591.2339 | 1238241.763 | 2707595.1709 | 1238245.9325
76 | 2707583.3429 | 1238219.1914 | 2707587.158 | 1238219.512
77 | 2707580.1337 | 1238263.9954 | 2707594.1164 | 1238275.8202
78 | 2707598.3918 | 1238279.4358 | 2707594.1164 | 1238275.8202
79 | 2707606.9164 | 1238252.0948 | 2707601.3822 | 1238252.5108 | 2707595.1709 | 1238245.9325
80 | 2707602.6159 | 1238223.2542 | 2707590.9355 | 1238219.8295 | 2707587.158 | 1238219.512
81 | 2707599.7892 | 1238280.6175 | 2707598.3918 | 1238279.4358
82 | 2707280.6051 | 1238279.1062 | 2707285.2577 | 1238269.4324
83 | 2707305.1372 | 1238234.626 | 2707292.2956 | 1238254.7985 | 2707285.2577 | 1238269.4324
84 | 2707285.2577 | 1238269.4324 | 2707172.6705 | 1238220.5676
85 | 2707305.1372 | 1238234.626 | 2707305.1372 | 1238234.626 | 2707323.2064 | 1238210.2879
86 | 2707152.1028 | 1238211.0669 | 2707172.6705 | 1238220.5676
87 | 2707347.0975 | 1238285.7906 | 2707349.744 | 1238280.781
88 | 2707349.744 | 1238280.781 | 2707359.1036 | 1238263.064
89 | 2707474.879 | 1238115.6028 | 2707470.8792 | 1238125.4714 | 2707464.049 | 1238130.7742
90 | 2707440.2398 | 1238113.0852 | 2707464.049 | 1238130.7742
91 | 2707440.2398 | 1238113.0852 | 2707445.8158 | 1238105.335
92 | 2707458.5781 | 1238147.5104 | 2707462.2577 | 1238164.1527
93 | 2707492.8712 | 1238172.4614 | 2707479.6226 | 1238175.5256
94 | 2707614.659 | 1238186.7002 | 2707616.4204 | 1238173.7688
95 | 2707614.659 | 1238186.7002 | 2707626.4043 | 1238191.3672
96 | 2707618.7752 | 1238156.4814 | 2707616.4204 | 1238173.7688
97 | 2707652.5742 | 1238207.1366 | 2707637.1206 | 1238195.6253 | 2707626.4043 | 1238191.3672
98 | 2707618.8835 | 1238155.686 | 2707618.7752 | 1238156.4814
99 | 2707652.5742 | 1238207.1366 | 2707662.3524 | 1238221.1803
100 | 2707652.5742 | 1238207.1366 | 2707666.0726 | 1238194.2045 | 2707667.2843 | 1238188.0673
101 | 2707662.3524 | 1238221.1803 | 2707666.2984 | 1238227.6154
102 | 2707667.3312 | 1238187.8302 | 2707667.2843 | 1238188.0673
103 | 2707671.2937 | 1238238.8116 | 2707670.7301 | 1238234.8428 | 2707666.2984 | 1238227.6154
104 | 2707670.4719 | 1238171.9225 | 2707667.3312 | 1238187.8302
105 | 2707628.5838 | 1238224.131 | 2707635.5936 | 1238224.0673
106 | 2707628.5838 | 1238224.131 | 2707611.9531 | 1238224.2821
107 | 2707671.2937 | 1238238.8116 | 2707673.9307 | 1238257.3628
108 | 2707671.2937 | 1238238.8116 | 2707664.8199 | 1238245.3255
109 | 2707668.8003 | 1238279.4869 | 2707671.8257 | 1238271.6246 | 2707673.9307 | 1238257.3628
110 | 2707673.9307 | 1238257.3628 | 2707688.8737 | 1238251.1688
111 | 2707660.6118 | 1238249.5597 | 2707664.8199 | 1238245.3255
112 | 2707668.8003 | 1238279.4869 | 2707667.4344 | 1238283.0427
113 | 2707668.8003 | 1238279.4869 | 2707658.9824 | 1238276.3954 | 2707658.6027 | 1238275.9754
114 | 2707692.8983 | 1238249.5006 | 2707688.8737 | 1238251.1688
115 | 2707660.6118 | 1238249.5597 | 2707649.3065 | 1238248.5357
116 | 2707602.6159 | 1238223.2542 | 2707606.2967 | 1238224.3335 | 2707611.9531 | 1238224.2821
117 | 2707667.4344 | 1238283.0427 | 2707656.977 | 1238302.594
118 | 2707667.4344 | 1238283.0427 | 2707680.7116 | 1238287.7204 | 2707689.2204 | 1238285.3951 | 2707696.0273 | 1238281.7702
119 | 2707692.8983 | 1238249.5006 | 2707696.6299 | 1238246.0878 | 2707705.5038 | 1238241.8628
120 | 2707649.3065 | 1238248.5357 | 2707644.9526 | 1238248.1414 | 2707642.2203 | 1238249.4373 | 2707635.5685 | 1238249.9392
121 | 2707655.7133 | 1238304.9567 | 2707656.977 | 1238302.594
122 | 2707696.0273 | 1238281.7702 | 2707699.8005 | 1238279.7609
123 | 2707719.6553 | 1238269.1876 | 2707699.8005 | 1238279.7609
124 | 2707647.2595 | 1238320.7619 | 2707655.7133 | 1238304.9567
125 | 2707647.2595 | 1238320.7619 | 2707635.1454 | 1238310.5173
126 | 2707647.2595 | 1238320.7619 | 2707644.2055 | 1238326.3791
127 | 2707615.9362 | 1238294.2727 | 2707635.1454 | 1238310.5173
128 | 2707599.7892 | 1238280.6175 | 2707615.9362 | 1238294.2727
129 | 2707606.9164 | 1238252.0948 | 2707613.9034 | 1238251.5695
130 | 2707628.8149 | 1238250.4486 | 2707613.9034 | 1238251.5695
131 | 2707628.8149 | 1238250.4486 | 2707629.5067 | 1238250.3966
132 | 2707629.5067 | 1238250.3966 | 2707635.5685 | 1238249.9392
133 | 2707629.5067 | 1238250.3966 | 2707636.4238 | 1238256.1664

## bus_geodata
| x | y | coords
0 | 2707548.1846 | 1238366.3736
1 | 2707555.1155 | 1238347.4296
2 | 2707553.5669 | 1238337.8888
3 | 2707587.628 | 1238330.8442
4 | 2707551.5544 | 1238332.4593
5 | 2707613.945 | 1238309.1046
6 | 2707570.3876 | 1238324.0047
7 | 2707537.7085 | 1238317.8305
8 | 2707732.0337 | 1238278.1215
9 | 2707720.8612 | 1238310.0773
10 | 2707728.0887 | 1238269.1207
11 | 2707426.402 | 1237984.3183
12 | 2707402.2191 | 1238082.9408
13 | 2707390.385 | 1238123.5027
14 | 2707378.1885 | 1238139.2538
15 | 2707419.4323 | 1238157.7991
16 | 2707448.7562 | 1238142.6236
17 | 2707408.0349 | 1238189.818
18 | 2707397.3907 | 1238387.5238
19 | 2707409.1444 | 1238367.8257
20 | 2707414.2039 | 1238359.3465
21 | 2707330.5202 | 1238396.3816
22 | 2707328.1872 | 1238390.0854
23 | 2707327.1562 | 1238355.4732
24 | 2707333.5445 | 1238322.7077
25 | 2707343.3835 | 1238295.9072
26 | 2707309.9045 | 1238320.7901
27 | 2707348.0919 | 1238328.2007
28 | 2707368.2248 | 1238301.974
29 | 2707425.6634 | 1238340.1418
30 | 2707432.8049 | 1238328.1733
31 | 2707443.0629 | 1238311.9375
32 | 2707447.5776 | 1238337.1695
33 | 2707454.6883 | 1238296.7225
34 | 2707466.6984 | 1238348.8137
35 | 2707459.0268 | 1238289.6525
36 | 2707487.4676 | 1238301.4657
37 | 2707474.035 | 1238265.1948
38 | 2707505.1864 | 1238304.2574
39 | 2707489.0143 | 1238239.4185
40 | 2707492.6555 | 1238211.5212
41 | 2707487.1488 | 1238211.7725
42 | 2707514.5012 | 1238206.0794
43 | 2707461.1338 | 1238211.9294
44 | 2707536.0444 | 1238200.7129
45 | 2707521.9907 | 1238338.4601
46 | 2707507.7993 | 1238357.0862
47 | 2707583.7888 | 1238306.3344
48 | 2707444.5248 | 1238209.4931
49 | 2707551.4542 | 1238196.8743
50 | 2707429.2818 | 1238223.2232
51 | 2707419.9927 | 1238235.1715
52 | 2707440.7527 | 1238208.4686
53 | 2707408.4226 | 1238250.0538
54 | 2707405.967 | 1238193.1719
55 | 2707398.5099 | 1238262.8043
56 | 2707388.9621 | 1238217.6926
57 | 2707449.1684 | 1238191.4072
58 | 2707390.9364 | 1238277.7365
59 | 2707465.4948 | 1238178.7932
60 | 2707381.3323 | 1238290.6054
61 | 2707551.8433 | 1238218.7624
62 | 2707551.7681 | 1238214.5303
63 | 2707555.9705 | 1238229.4814
64 | 2707567.9084 | 1238222.9036
65 | 2707560.675 | 1238194.6204
66 | 2707576.9282 | 1238230.8383
67 | 2707583.3429 | 1238219.1914
68 | 2707580.1337 | 1238263.9954
69 | 2707594.1164 | 1238275.8202
70 | 2707583.9079 | 1238188.9413
71 | 2707595.1709 | 1238245.9325
72 | 2707587.158 | 1238219.512
73 | 2707598.3918 | 1238279.4358
74 | 2707298.1032 | 1238332.5447
75 | 2707280.6051 | 1238279.1062
76 | 2707285.2577 | 1238269.4324
77 | 2707305.1372 | 1238234.626
78 | 2707172.6705 | 1238220.5676
79 | 2707152.1028 | 1238211.0669
80 | 2707347.0975 | 1238285.7906
81 | 2707323.2064 | 1238210.2879
82 | 2707359.1036 | 1238263.064
83 | 2707349.744 | 1238280.781
84 | 2707371.1651 | 1238304.2289
85 | 2707464.049 | 1238130.7742
86 | 2707440.2398 | 1238113.0852
87 | 2707445.8158 | 1238105.335
88 | 2707474.879 | 1238115.6028
89 | 2707462.2577 | 1238164.1527
90 | 2707479.6226 | 1238175.5256
91 | 2707458.5781 | 1238147.5104
92 | 2707492.8712 | 1238172.4614
93 | 2707614.659 | 1238186.7002
94 | 2707616.4204 | 1238173.7688
95 | 2707626.4043 | 1238191.3672
96 | 2707618.7752 | 1238156.4814
97 | 2707652.5742 | 1238207.1366
98 | 2707618.8835 | 1238155.686
99 | 2707662.3524 | 1238221.1803
100 | 2707667.2843 | 1238188.0673
101 | 2707666.2984 | 1238227.6154
102 | 2707667.3312 | 1238187.8302
103 | 2707635.5936 | 1238224.0673
104 | 2707628.5838 | 1238224.131
105 | 2707671.2937 | 1238238.8116
106 | 2707670.4719 | 1238171.9225
107 | 2707673.9307 | 1238257.3628
108 | 2707664.8199 | 1238245.3255
109 | 2707668.8003 | 1238279.4869
110 | 2707688.8737 | 1238251.1688
111 | 2707660.6118 | 1238249.5597
112 | 2707611.9531 | 1238224.2821
113 | 2707667.4344 | 1238283.0427
114 | 2707658.6027 | 1238275.9754
115 | 2707692.8983 | 1238249.5006
116 | 2707649.3065 | 1238248.5357
117 | 2707705.5038 | 1238241.8628
118 | 2707656.977 | 1238302.594
119 | 2707696.0273 | 1238281.7702
120 | 2707719.6553 | 1238269.1876
121 | 2707699.8005 | 1238279.7609
122 | 2707655.7133 | 1238304.9567
123 | 2707647.2595 | 1238320.7619
124 | 2707644.2055 | 1238326.3791
125 | 2707635.1454 | 1238310.5173
126 | 2707615.9362 | 1238294.2727
127 | 2707599.7892 | 1238280.6175
128 | 2707602.6159 | 1238223.2542
129 | 2707606.9164 | 1238252.0948
130 | 2707613.9034 | 1238251.5695
131 | 2707628.8149 | 1238250.4486
132 | 2707629.5067 | 1238250.3966
133 | 2707635.5685 | 1238249.9392
134 | 2707636.4238 | 1238256.1664
135 | 2707454.6883 | 1238296.7225

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99668 | -0.06383 | 0.0021477 | 0.00053826
1 | 0.99672 | -0.063044 | 0.0012889 | 0.00032302
2 | 0.99675 | -0.062446 | 0 | 0
3 | 0.99658 | -0.065784 | 0.0015525 | 0.00038911
4 | 0.9968 | -0.061619 | 0 | 0
5 | 0.99645 | -0.068267 | 0.0031499 | 0.00078945
6 | 0.99672 | -0.063076 | 0.0015292 | 0.00038326
7 | 0.99702 | -0.057295 | 0 | 0
8 | 0.97451 | -0.491 | 0.0019016 | 0.0004766
9 | 0.97445 | -0.4922 | 0.0019164 | 0.0004803
10 | 0.97455 | -0.49031 | 0 | 0
11 | 0.98696 | -0.24919 | 0.0019077 | 0.00047812
12 | 0.98714 | -0.24572 | 0 | 0
13 | 0.98722 | -0.24416 | 0 | 0
14 | 0.98719 | -0.2447 | 0.0015107 | 0.00037862
15 | 0.9874 | -0.24059 | 0 | 0
16 | 0.98718 | -0.24486 | 0.0023412 | 0.00058675
17 | 0.98774 | -0.23411 | 0.0010726 | 0.00026883
18 | 0.99717 | -0.054417 | 0.0057339 | 0.0014371
19 | 0.99729 | -0.052112 | 0.0027466 | 0.00068836
20 | 0.99737 | -0.050644 | 0.0021394 | 0.0005362
21 | 0.97798 | -0.42417 | 0.002664 | 0.00066765
22 | 0.97799 | -0.42384 | 0 | 0
23 | 0.97808 | -0.42215 | 0 | 0
24 | 0.97816 | -0.42053 | 0 | 0
25 | 0.97884 | -0.40722 | 0.0027146 | 0.00068034
26 | 0.97764 | -0.43086 | 0.0036735 | 0.00092068
27 | 0.97976 | -0.38915 | 0.0074398 | 0.0018646
28 | 0.97999 | -0.38469 | 0 | 0
29 | 0.99758 | -0.046483 | 0.0042289 | 0.0010599
30 | 0.99777 | -0.042859 | 0 | 0
31 | 0.99809 | -0.036694 | 0.0019533 | 0.00048954
32 | 0.99772 | -0.043909 | 0.0017829 | 0.00044684
33 | 0.99844 | -0.029903 | 0 | 0
34 | 0.99768 | -0.04457 | 0.0016859 | 0.00042252
35 | 0.99875 | -0.024036 | 0.0075323 | 0.0018878
36 | 0.99782 | -0.04181 | 0.0024911 | 0.00062432
37 | 1 | 0 | -0.27457 | -0.069961
38 | 0.99754 | -0.047387 | 0.0018025 | 0.00045174
39 | 0.99695 | -0.057675 | 0.0032329 | 0.00081025
40 | 0.99405 | -0.11258 | 0 | 0
41 | 0.99344 | -0.12438 | 0.0011547 | 0.00028938
42 | 0.99204 | -0.15094 | 0.0023391 | 0.00058624
43 | 0.99054 | -0.17989 | 0.0011282 | 0.00028275
44 | 0.9901 | -0.188 | 0.0025116 | 0.00062948
45 | 0.99693 | -0.059062 | 0.001453 | 0.00036415
46 | 0.99688 | -0.060061 | 0.0024325 | 0.00060964
47 | 0.99667 | -0.063989 | 0.0023317 | 0.00058437
48 | 0.9887 | -0.21544 | 0 | 0
49 | 0.98875 | -0.21388 | 0 | 0
50 | 0.98664 | -0.25513 | 0.0069169 | 0.0017335
51 | 0.9854 | -0.27924 | 0.0097115 | 0.0024339
52 | 0.9883 | -0.22313 | 0 | 0
53 | 0.98402 | -0.30606 | 0.0072496 | 0.0018169
54 | 0.98778 | -0.2333 | 0 | 0
55 | 0.98294 | -0.32698 | 0.0069786 | 0.001749
56 | 0.98768 | -0.23512 | 0.0034109 | 0.00085485
57 | 0.98856 | -0.2182 | 0.0020867 | 0.00052299
58 | 0.98177 | -0.34987 | 0.0079417 | 0.0019904
59 | 0.98843 | -0.22068 | 0 | 0
60 | 0.98092 | -0.36643 | 0.0070461 | 0.0017659
61 | 0.98696 | -0.24828 | 0.0017588 | 0.0004408
62 | 0.98731 | -0.24166 | 0.0006531 | 0.00016368
63 | 0.98598 | -0.26722 | 0 | 0
64 | 0.98484 | -0.28925 | 0.00068963 | 0.00017284
65 | 0.98872 | -0.21447 | 0.0016444 | 0.00041213
66 | 0.98397 | -0.30601 | 0.00093147 | 0.00023345
67 | 0.98473 | -0.29136 | 0.0007217 | 0.00018087
68 | 0.97396 | -0.50184 | 0.00059306 | 0.00014864
69 | 0.97397 | -0.50164 | 0.0012897 | 0.00032323
70 | 0.98868 | -0.21524 | 0.0018014 | 0.00045146
71 | 0.98219 | -0.34061 | 0.000711 | 0.00017819
72 | 0.98471 | -0.29182 | 0.00073274 | 0.00018364
73 | 0.97398 | -0.50145 | 0.0016331 | 0.00040929
74 | 0.97757 | -0.43211 | 0.0041366 | 0.0010367
75 | 0.97692 | -0.44492 | 0 | 0
76 | 0.97677 | -0.44789 | 0.0013144 | 0.00032941
77 | 0.97645 | -0.45424 | 0.0047231 | 0.0011837
78 | 0.97618 | -0.45944 | 0 | 0
79 | 0.97608 | -0.46157 | 0.0051451 | 0.0012895
80 | 0.97912 | -0.40167 | 0 | 0
81 | 0.97634 | -0.45643 | 0.0039366 | 0.0009866
82 | 0.97901 | -0.40397 | 0.0043725 | 0.0010958
83 | 0.97909 | -0.40238 | 0.0024981 | 0.00062608
84 | 0.98014 | -0.38182 | 0.0072983 | 0.0018291
85 | 0.9871 | -0.24647 | 0 | 0
86 | 0.98704 | -0.2477 | 0 | 0
87 | 0.98702 | -0.2481 | 0.002326 | 0.00058295
88 | 0.98706 | -0.24727 | 0.0023219 | 0.00058193
89 | 0.98839 | -0.22146 | 0.0016532 | 0.00041433
90 | 0.98838 | -0.22153 | 0.0010659 | 0.00026713
91 | 0.98837 | -0.22185 | 0.0012601 | 0.00031581
92 | 0.98836 | -0.22207 | 0.0022249 | 0.0005576
93 | 0.97565 | -0.46867 | 0 | 0
94 | 0.97556 | -0.4703 | 0.0018879 | 0.00047315
95 | 0.97573 | -0.4671 | 0.0014604 | 0.00036601
96 | 0.97548 | -0.47186 | 0.0021683 | 0.00054344
97 | 0.97596 | -0.46244 | 0 | 0
98 | 0.97548 | -0.4719 | 0.0027404 | 0.00068681
99 | 0.97628 | -0.45618 | 0 | 0
100 | 0.97569 | -0.46782 | 0.0017058 | 0.0004275
101 | 0.97642 | -0.45341 | 0.0041516 | 0.0010405
102 | 0.97569 | -0.46786 | 0.00239 | 0.00059899
103 | 0.98453 | -0.29535 | 0.0015056 | 0.00037733
104 | 0.98454 | -0.29516 | 0.0013776 | 0.00034527
105 | 0.9767 | -0.44789 | 0 | 0
106 | 0.97557 | -0.47014 | 0.0076769 | 0.001924
107 | 0.97599 | -0.46194 | 0 | 0
108 | 0.97726 | -0.43696 | 0.0013779 | 0.00034534
109 | 0.97519 | -0.47757 | 0 | 0
110 | 0.97593 | -0.463 | 0.0017658 | 0.00044254
111 | 0.97763 | -0.42971 | 0 | 0
112 | 0.98458 | -0.2943 | 0.0016176 | 0.00040541
113 | 0.97507 | -0.48005 | 0 | 0
114 | 0.97517 | -0.47795 | 0.0019143 | 0.00047978
115 | 0.97593 | -0.46315 | 0 | 0
116 | 0.97833 | -0.41595 | 0.0016224 | 0.00040662
117 | 0.9759 | -0.46365 | 0.0018429 | 0.00046187
118 | 0.97458 | -0.48968 | 0.010496 | 0.0026306
119 | 0.97473 | -0.48665 | 0.0037917 | 0.00095028
120 | 0.97458 | -0.4897 | 0.0020511 | 0.00051406
121 | 0.9747 | -0.48728 | 0.0021026 | 0.00052696
122 | 0.97455 | -0.49033 | 0.001468 | 0.00036792
123 | 0.97435 | -0.49419 | 0 | 0
124 | 0.97432 | -0.49468 | 0.0041507 | 0.0010403
125 | 0.97424 | -0.4964 | 0.00089667 | 0.00022473
126 | 0.97408 | -0.49949 | 0.0019371 | 0.00048548
127 | 0.97399 | -0.50133 | 0.0012276 | 0.00030766
128 | 0.98462 | -0.29353 | 0.0014513 | 0.00036373
129 | 0.98116 | -0.36066 | 0.0015264 | 0.00038254
130 | 0.98068 | -0.37011 | 0.0014388 | 0.0003606
131 | 0.97966 | -0.38991 | 0.0014479 | 0.00036288
132 | 0.97961 | -0.39081 | 0 | 0
133 | 0.97922 | -0.3985 | 0.0014219 | 0.00035636
134 | 0.9796 | -0.39113 | 0.0019365 | 0.00048534
135 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0021477 | -0.00053826 | 0.0021478 | 0.00053804 | 8.0397e-08 | -2.2033e-07 | 0.0032064 | 0.0032063 | 0.0032064 | 0.99668 | -0.06383 | 0.99672 | -0.063044 | 0.88088
1 | -0.0034366 | -0.00086106 | 0.0034367 | 0.00086099 | 9.7889e-08 | -6.6611e-08 | 0.0051305 | 0.0051304 | 0.0051305 | 0.99672 | -0.063044 | 0.99675 | -0.062446 | 1.4095
2 | 0.0047036 | 0.0011782 | -0.0047029 | -0.0011782 | 7.4749e-07 | -4.8475e-08 | 0.0070216 | 0.0070218 | 0.0070218 | 0.99675 | -0.062446 | 0.99658 | -0.065784 | 1.9291
3 | -0.0081403 | -0.0020392 | 0.0081406 | 0.0020393 | 3.2058e-07 | 1.2971e-07 | 0.012152 | 0.012152 | 0.012152 | 0.99675 | -0.062446 | 0.9968 | -0.061619 | 3.3385
4 | 0.0031503 | 0.0007891 | -0.0031499 | -0.00078945 | 3.7254e-07 | -3.4655e-07 | 0.0047036 | 0.0047038 | 0.0047038 | 0.99658 | -0.065784 | 0.99645 | -0.068267 | 1.2923
5 | 0.0038613 | 0.0009673 | -0.003861 | -0.0009674 | 2.6789e-07 | -1.0882e-07 | 0.0057639 | 0.005764 | 0.005764 | 0.9968 | -0.061619 | 0.99672 | -0.063076 | 1.5835
6 | -0.012002 | -0.0030066 | 0.012004 | 0.0030079 | 2.4722e-06 | 1.3144e-06 | 0.017916 | 0.017916 | 0.017916 | 0.9968 | -0.061619 | 0.99702 | -0.057295 | 4.922
7 | 0.0023318 | 0.00058415 | -0.0023317 | -0.00058437 | 1.0142e-07 | -2.2595e-07 | 0.003481 | 0.0034811 | 0.0034811 | 0.99672 | -0.063076 | 0.99667 | -0.063989 | 0.95636
8 | 0.0038859 | 0.00097343 | -0.0038856 | -0.00097356 | 3.2711e-07 | -1.2885e-07 | 0.0057994 | 0.0057995 | 0.0057995 | 0.99702 | -0.057295 | 0.99693 | -0.059062 | 1.5933
9 | -0.01589 | -0.0039813 | 0.015898 | 0.0039857 | 7.5022e-06 | 4.3373e-06 | 0.023715 | 0.023715 | 0.023715 | 0.99702 | -0.057295 | 0.99754 | -0.047387 | 6.5152
10 | 0.0019165 | 0.00047995 | -0.0019164 | -0.0004803 | 1.0889e-07 | -3.5276e-07 | 0.0029263 | 0.0029264 | 0.0029264 | 0.97451 | -0.491 | 0.97445 | -0.4922 | 0.80396
11 | -0.0038182 | -0.00095654 | 0.0038183 | 0.0009565 | 1.2526e-07 | -4.228e-08 | 0.00583 | 0.0058299 | 0.00583 | 0.97451 | -0.491 | 0.97455 | -0.49031 | 1.6016
12 | -0.0038183 | -0.0009565 | 0.0038184 | 0.00095646 | 1.1178e-07 | -3.7742e-08 | 0.0058299 | 0.0058299 | 0.0058299 | 0.97455 | -0.49031 | 0.97458 | -0.4897 | 1.6016
13 | -0.0019077 | -0.00047812 | 0.001908 | 0.00047703 | 3.1497e-07 | -1.0963e-06 | 0.0028762 | 0.0028758 | 0.0028762 | 0.98696 | -0.24919 | 0.98714 | -0.24572 | 0.79017
14 | -0.001908 | -0.00047703 | 0.0019082 | 0.00047653 | 1.4191e-07 | -4.9425e-07 | 0.0028758 | 0.0028756 | 0.0028758 | 0.98714 | -0.24572 | 0.98722 | -0.24416 | 0.79005
15 | 0.0015108 | 0.00037839 | -0.0015107 | -0.00037862 | 3.8735e-08 | -2.2992e-07 | 0.002277 | 0.0022771 | 0.0022771 | 0.98722 | -0.24416 | 0.98719 | -0.2447 | 0.62559
16 | -0.0034189 | -0.00085492 | 0.0034195 | 0.00085455 | 5.8034e-07 | -3.7407e-07 | 0.0051526 | 0.0051524 | 0.0051526 | 0.98722 | -0.24416 | 0.9874 | -0.24059 | 1.4156
17 | 0.0069911 | 0.0017515 | -0.0069897 | -0.001751 | 1.4211e-06 | 4.7291e-07 | 0.010535 | 0.010536 | 0.010536 | 0.9874 | -0.24059 | 0.98718 | -0.24486 | 2.8944
18 | -0.010411 | -0.0026061 | 0.010414 | 0.0026077 | 3.2099e-06 | 1.6093e-06 | 0.015688 | 0.015688 | 0.015688 | 0.9874 | -0.24059 | 0.98774 | -0.23411 | 4.3098
19 | 0.0046485 | 0.0011643 | -0.0046482 | -0.0011643 | 3.5617e-07 | -1.9379e-08 | 0.0070066 | 0.0070067 | 0.0070067 | 0.98718 | -0.24486 | 0.9871 | -0.24647 | 1.9249
20 | -0.011486 | -0.0028765 | 0.011487 | 0.0028767 | 4.4239e-07 | 2.327e-07 | 0.017303 | 0.017303 | 0.017303 | 0.98774 | -0.23411 | 0.98778 | -0.2333 | 4.7537
21 | -0.0057339 | -0.0014371 | 0.0057346 | 0.0014372 | 6.2975e-07 | 1.0377e-07 | 0.0085564 | 0.0085563 | 0.0085564 | 0.99717 | -0.054417 | 0.99729 | -0.052112 | 2.3507
22 | -0.0084812 | -0.0021255 | 0.0084818 | 0.0021258 | 5.9293e-07 | 2.5063e-07 | 0.012654 | 0.012654 | 0.012654 | 0.99729 | -0.052112 | 0.99737 | -0.050644 | 3.4765
23 | -0.010621 | -0.002662 | 0.010623 | 0.002663 | 2.1059e-06 | 1.0558e-06 | 0.015846 | 0.015846 | 0.015846 | 0.99737 | -0.050644 | 0.99758 | -0.046483 | 4.3534
24 | -0.002664 | -0.00066765 | 0.002664 | 0.00066759 | 4.1367e-08 | -5.7779e-08 | 0.0040533 | 0.0040533 | 0.0040533 | 0.97798 | -0.42417 | 0.97799 | -0.42384 | 1.1135
25 | -0.002664 | -0.00066759 | 0.0026642 | 0.00066729 | 2.1425e-07 | -2.9932e-07 | 0.0040533 | 0.0040531 | 0.0040533 | 0.97799 | -0.42384 | 0.97808 | -0.42215 | 1.1135
26 | -0.0026642 | -0.00066729 | 0.0026644 | 0.00066701 | 2.0609e-07 | -2.8801e-07 | 0.0040531 | 0.0040529 | 0.0040531 | 0.97808 | -0.42215 | 0.97816 | -0.42053 | 1.1135
27 | -0.025624 | -0.006429 | 0.02564 | 0.0064391 | 1.6269e-05 | 1.0054e-05 | 0.038983 | 0.038983 | 0.038983 | 0.97816 | -0.42053 | 0.97884 | -0.40722 | 10.7095
28 | 0.02296 | 0.005762 | -0.022948 | -0.0057551 | 1.1307e-05 | 6.9263e-06 | 0.03493 | 0.03493 | 0.03493 | 0.97816 | -0.42053 | 0.97764 | -0.43086 | 9.5961
29 | -0.028355 | -0.0071194 | 0.028362 | 0.0071241 | 7.5104e-06 | 4.6711e-06 | 0.043109 | 0.043109 | 0.043109 | 0.97884 | -0.40722 | 0.97912 | -0.40167 | 11.8432
30 | 0.015138 | 0.0037977 | -0.015128 | -0.0037919 | 1.0144e-05 | 5.8541e-06 | 0.023042 | 0.023042 | 0.023042 | 0.97764 | -0.43086 | 0.97692 | -0.44492 | 6.3303
31 | 0.0041369 | 0.0010367 | -0.0041366 | -0.0010367 | 2.4764e-07 | -5.0355e-08 | 0.0062965 | 0.0062966 | 0.0062966 | 0.97764 | -0.43086 | 0.97757 | -0.43211 | 1.7298
32 | -0.0074398 | -0.0018646 | 0.0074414 | 0.0018652 | 1.583e-06 | 5.9661e-07 | 0.011299 | 0.011299 | 0.011299 | 0.97976 | -0.38915 | 0.97999 | -0.38469 | 3.1042
33 | -0.042703 | -0.010729 | 0.042709 | 0.010733 | 5.8437e-06 | 3.6933e-06 | 0.06485 | 0.06485 | 0.06485 | 0.97999 | -0.38469 | 0.98014 | -0.38182 | 17.8161
34 | 0.035262 | 0.008864 | -0.035233 | -0.008846 | 2.8567e-05 | 1.7949e-05 | 0.053551 | 0.053551 | 0.053551 | 0.97999 | -0.38469 | 0.97912 | -0.40167 | 14.7119
35 | -0.014852 | -0.0037229 | 0.014855 | 0.0037244 | 2.5652e-06 | 1.4597e-06 | 0.022154 | 0.022154 | 0.022154 | 0.99758 | -0.046483 | 0.99777 | -0.042859 | 6.0863
36 | -0.018324 | -0.0045933 | 0.018329 | 0.0045965 | 5.3843e-06 | 3.1947e-06 | 0.027327 | 0.027327 | 0.027327 | 0.99777 | -0.042859 | 0.99809 | -0.036694 | 7.5075
37 | 0.003469 | 0.00086899 | -0.0034688 | -0.0008691 | 1.7359e-07 | -1.1479e-07 | 0.0051733 | 0.0051734 | 0.0051734 | 0.99777 | -0.042859 | 0.99772 | -0.043909 | 1.4213
38 | -0.020283 | -0.0050861 | 0.020289 | 0.00509 | 6.566e-06 | 3.9519e-06 | 0.030239 | 0.030239 | 0.030239 | 0.99809 | -0.036694 | 0.99844 | -0.029903 | 8.3075
39 | 0.0016859 | 0.00042226 | -0.0016859 | -0.00042252 | 5.3075e-08 | -2.5839e-07 | 0.0025143 | 0.0025144 | 0.0025144 | 0.99772 | -0.043909 | 0.99768 | -0.04457 | 0.69077
40 | -0.040497 | -0.010161 | 0.040508 | 0.010169 | 1.1332e-05 | 7.1441e-06 | 0.060358 | 0.060358 | 0.060358 | 0.99844 | -0.029903 | 0.99875 | -0.024036 | 16.5818
41 | 0.020208 | 0.0050714 | -0.020196 | -0.0050645 | 1.1468e-05 | 6.8988e-06 | 0.030118 | 0.030119 | 0.030119 | 0.99844 | -0.029903 | 0.99782 | -0.04181 | 8.2743
42 | -0.04804 | -0.012056 | 0.048095 | 0.012091 | 5.5135e-05 | 3.491e-05 | 0.07158 | 0.07158 | 0.07158 | 0.99875 | -0.024036 | 1 | 0 | 19.6648
43 | 0.017705 | 0.0044402 | -0.0177 | -0.0044374 | 4.7044e-06 | 2.7759e-06 | 0.026404 | 0.026404 | 0.026404 | 0.99782 | -0.04181 | 0.99754 | -0.047387 | 7.2538
44 | 0.22482 | 0.05787 | -0.22419 | -0.057468 | 0.00062878 | 0.00040164 | 0.33508 | 0.33508 | 0.33508 | 1 | 0 | 0.99695 | -0.057675 | 46.0277
45 | 0.22096 | 0.056658 | -0.22037 | -0.056283 | 0.00058659 | 0.00037467 | 0.33026 | 0.33026 | 0.33026 | 0.99695 | -0.057675 | 0.99405 | -0.11258 | 45.3649
46 | 0.12255 | 0.031214 | -0.12248 | -0.03117 | 6.9702e-05 | 4.4538e-05 | 0.18363 | 0.18363 | 0.18363 | 0.99405 | -0.11258 | 0.99344 | -0.12438 | 50.4467
47 | 0.097824 | 0.025069 | -0.097642 | -0.024953 | 0.00018152 | 0.00011588 | 0.14663 | 0.14663 | 0.14663 | 0.99405 | -0.11258 | 0.99204 | -0.15094 | 40.2831
48 | 0.12133 | 0.03088 | -0.121 | -0.030674 | 0.00032376 | 0.00020687 | 0.1819 | 0.1819 | 0.1819 | 0.99344 | -0.12438 | 0.99054 | -0.17989 | 49.9716
49 | 0.095303 | 0.024367 | -0.095132 | -0.024258 | 0.00017054 | 0.00010886 | 0.14312 | 0.14312 | 0.14312 | 0.99204 | -0.15094 | 0.9901 | -0.188 | 39.3193
50 | 0.11987 | 0.030391 | -0.11967 | -0.03026 | 0.00020442 | 0.00013061 | 0.1802 | 0.1802 | 0.1802 | 0.99054 | -0.17989 | 0.9887 | -0.21544 | 49.506
51 | 0.092621 | 0.023629 | -0.092505 | -0.023555 | 0.00011564 | 7.3804e-05 | 0.13935 | 0.13935 | 0.13935 | 0.9901 | -0.188 | 0.98875 | -0.21388 | 38.2823
52 | 0.0024326 | 0.00060941 | -0.0024325 | -0.00060964 | 1.1576e-07 | -2.3122e-07 | 0.0036308 | 0.0036309 | 0.0036309 | 0.99693 | -0.059062 | 0.99688 | -0.060061 | 0.9975
53 | 0.0082929 | 0.0020779 | -0.0082918 | -0.0020775 | 1.0908e-06 | 4.5865e-07 | 0.012481 | 0.012481 | 0.012481 | 0.9887 | -0.21544 | 0.98856 | -0.2182 | 3.4288
54 | 0.11138 | 0.028182 | -0.11134 | -0.028156 | 4.112e-05 | 2.6267e-05 | 0.16772 | 0.16772 | 0.16772 | 0.9887 | -0.21544 | 0.9883 | -0.22313 | 46.0772
55 | 0.0034459 | 0.00086327 | -0.0034458 | -0.00086333 | 9.5728e-08 | -6.0477e-08 | 0.0051858 | 0.0051858 | 0.0051858 | 0.98875 | -0.21388 | 0.98872 | -0.21447 | 1.4247
56 | 0.089059 | 0.022691 | -0.08894 | -0.022615 | 0.00011919 | 7.6057e-05 | 0.13416 | 0.13416 | 0.13416 | 0.98875 | -0.21388 | 0.98731 | -0.24166 | 36.8577
57 | 0.089366 | 0.022593 | -0.089263 | -0.022527 | 0.0001032 | 6.5855e-05 | 0.13485 | 0.13485 | 0.13485 | 0.98664 | -0.25513 | 0.9854 | -0.27924 | 37.0461
58 | -0.096283 | -0.024326 | 0.096431 | 0.02442 | 0.00014792 | 9.443e-05 | 0.14528 | 0.14528 | 0.14528 | 0.98664 | -0.25513 | 0.9883 | -0.22313 | 39.9119
59 | 0.079551 | 0.020093 | -0.079449 | -0.020028 | 0.0001021 | 6.5107e-05 | 0.12018 | 0.12018 | 0.12018 | 0.9854 | -0.27924 | 0.98402 | -0.30606 | 33.0173
60 | 0.014905 | 0.0037355 | -0.014898 | -0.0037314 | 7.2183e-06 | 4.1302e-06 | 0.022442 | 0.022442 | 0.022442 | 0.9883 | -0.22313 | 0.98778 | -0.2333 | 6.1654
61 | 0.072199 | 0.018211 | -0.072127 | -0.018165 | 7.2248e-05 | 4.6033e-05 | 0.10922 | 0.10922 | 0.10922 | 0.98402 | -0.30606 | 0.98294 | -0.32698 | 30.0055
62 | 0.0034112 | 0.00085466 | -0.0034109 | -0.00085485 | 2.9549e-07 | -1.9282e-07 | 0.0051386 | 0.0051388 | 0.0051388 | 0.98778 | -0.2333 | 0.98768 | -0.23512 | 1.4117
63 | 0.065149 | 0.016416 | -0.065077 | -0.01637 | 7.1243e-05 | 4.5348e-05 | 0.098656 | 0.098656 | 0.098656 | 0.98294 | -0.32698 | 0.98177 | -0.34987 | 27.1033
64 | 0.0062051 | 0.0015545 | -0.0062043 | -0.0015543 | 7.3439e-07 | 1.8223e-07 | 0.0093399 | 0.00934 | 0.00934 | 0.98856 | -0.2182 | 0.98843 | -0.22068 | 2.5659
65 | 0.057136 | 0.01438 | -0.05709 | -0.014351 | 4.5179e-05 | 2.8712e-05 | 0.086619 | 0.086619 | 0.086619 | 0.98177 | -0.34987 | 0.98092 | -0.36643 | 23.7965
66 | 0.0029134 | 0.00072981 | -0.0029133 | -0.00072993 | 1.0816e-07 | -1.2296e-07 | 0.0043858 | 0.0043859 | 0.0043859 | 0.98843 | -0.22068 | 0.98839 | -0.22146 | 1.2049
67 | 0.0032909 | 0.0008245 | -0.0032908 | -0.0008246 | 1.3347e-07 | -1.0044e-07 | 0.0049542 | 0.0049542 | 0.0049542 | 0.98843 | -0.22068 | 0.98838 | -0.22153 | 1.3611
68 | 0.050044 | 0.012585 | -0.050008 | -0.012562 | 3.6753e-05 | 2.3308e-05 | 0.07593 | 0.075931 | 0.075931 | 0.98092 | -0.36643 | 0.98014 | -0.38182 | 20.86
69 | -0.088259 | -0.022434 | 0.088287 | 0.022452 | 2.8152e-05 | 1.7963e-05 | 0.13318 | 0.13318 | 0.13318 | 0.98696 | -0.24828 | 0.98731 | -0.24166 | 36.5872
70 | 0.0865 | 0.021993 | -0.086421 | -0.021943 | 7.8841e-05 | 5.0301e-05 | 0.13053 | 0.13053 | 0.13053 | 0.98696 | -0.24828 | 0.98598 | -0.26722 | 35.8588
71 | 0.086421 | 0.021943 | -0.08633 | -0.021884 | 9.1482e-05 | 5.8366e-05 | 0.13053 | 0.13053 | 0.13053 | 0.98598 | -0.26722 | 0.98484 | -0.28925 | 35.8588
72 | 0.078232 | 0.019855 | -0.078169 | -0.019815 | 6.3037e-05 | 4.0191e-05 | 0.11829 | 0.11829 | 0.11829 | 0.98484 | -0.28925 | 0.98397 | -0.30601 | 32.4975
73 | 0.0074082 | 0.0018565 | -0.0074075 | -0.0018562 | 7.4584e-07 | 2.7536e-07 | 0.011193 | 0.011193 | 0.011193 | 0.98484 | -0.28925 | 0.98473 | -0.29136 | 3.0751
74 | 0.0018014 | 0.0004512 | -0.0018014 | -0.00045146 | 6.5921e-08 | -2.6453e-07 | 0.002711 | 0.0027111 | 0.0027111 | 0.98872 | -0.21447 | 0.98868 | -0.21524 | 0.74482
75 | 0.077237 | 0.019581 | -0.077109 | -0.0195 | 0.00012821 | 8.1737e-05 | 0.11688 | 0.11688 | 0.11688 | 0.98397 | -0.30601 | 0.98219 | -0.34061 | 32.1106
76 | 0.0066858 | 0.0016753 | -0.0066856 | -0.0016753 | 1.4654e-07 | 4.5078e-08 | 0.010103 | 0.010103 | 0.010103 | 0.98473 | -0.29136 | 0.98471 | -0.29182 | 2.7755
77 | -0.00059306 | -0.00014864 | 0.00059307 | 0.00014841 | 5.6372e-09 | -2.2429e-07 | 0.00090608 | 0.000906 | 0.00090608 | 0.97396 | -0.50184 | 0.97397 | -0.50164 | 0.24892
78 | -0.0018828 | -0.00047164 | 0.0018828 | 0.00047158 | 1.7372e-08 | -5.8567e-08 | 0.0028764 | 0.0028763 | 0.0028764 | 0.97397 | -0.50164 | 0.97398 | -0.50145 | 0.79021
79 | 0.076398 | 0.019321 | -0.076325 | -0.019275 | 7.341e-05 | 4.6798e-05 | 0.11581 | 0.11581 | 0.11581 | 0.98219 | -0.34061 | 0.98116 | -0.36066 | 31.8147
80 | 0.0059529 | 0.0014916 | -0.0059524 | -0.0014915 | 4.8439e-07 | 1.0696e-07 | 0.0089954 | 0.0089955 | 0.0089955 | 0.98471 | -0.29182 | 0.98462 | -0.29353 | 2.4713
81 | -0.0035159 | -0.00088087 | 0.0035159 | 0.00088086 | 1.98e-08 | -1.0104e-08 | 0.0053713 | 0.0053713 | 0.0053713 | 0.97398 | -0.50145 | 0.97399 | -0.50133 | 1.4756
82 | 0.015128 | 0.0037919 | -0.015126 | -0.0037906 | 2.1373e-06 | 1.2335e-06 | 0.023042 | 0.023042 | 0.023042 | 0.97692 | -0.44492 | 0.97677 | -0.44789 | 6.3303
83 | 0.0086627 | 0.0021714 | -0.0086601 | -0.0021702 | 2.6223e-06 | 1.1759e-06 | 0.013197 | 0.013197 | 0.013197 | 0.97677 | -0.44789 | 0.97645 | -0.45424 | 3.6256
84 | 0.0051485 | 0.0012898 | -0.0051456 | -0.0012895 | 2.8313e-06 | 2.7674e-07 | 0.007843 | 0.0078436 | 0.0078436 | 0.97677 | -0.44789 | 0.97618 | -0.45944 | 2.1548
85 | 0.003937 | 0.00098648 | -0.0039366 | -0.0009866 | 4.0916e-07 | -1.1726e-07 | 0.0059995 | 0.0059997 | 0.0059997 | 0.97645 | -0.45424 | 0.97634 | -0.45643 | 1.6483
86 | 0.0051456 | 0.0012895 | -0.0051451 | -0.0012895 | 5.2143e-07 | 5.119e-08 | 0.0078436 | 0.0078437 | 0.0078437 | 0.97618 | -0.45944 | 0.97608 | -0.46157 | 2.1549
87 | 0.0068711 | 0.001722 | -0.0068709 | -0.0017219 | 2.3167e-07 | 7.7015e-08 | 0.010442 | 0.010442 | 0.010442 | 0.97912 | -0.40167 | 0.97909 | -0.40238 | 2.8688
88 | -0.0043725 | -0.0010958 | 0.0043728 | 0.0010958 | 3.3187e-07 | -3.9581e-08 | 0.0066458 | 0.0066457 | 0.0066458 | 0.97901 | -0.40397 | 0.97909 | -0.40238 | 1.8258
89 | 0.002322 | 0.00058174 | -0.0023219 | -0.00058193 | 8.8574e-08 | -1.8973e-07 | 0.0035003 | 0.0035004 | 0.0035004 | 0.9871 | -0.24647 | 0.98706 | -0.24727 | 0.96164
90 | 0.0023262 | 0.00058256 | -0.002326 | -0.00058285 | 1.365e-07 | -2.9105e-07 | 0.0035064 | 0.0035066 | 0.0035066 | 0.9871 | -0.24647 | 0.98704 | -0.2477 | 0.96335
91 | 0.002326 | 0.00058285 | -0.002326 | -0.00058295 | 4.4025e-08 | -9.3854e-08 | 0.0035066 | 0.0035066 | 0.0035066 | 0.98704 | -0.2477 | 0.98702 | -0.2481 | 0.96336
92 | 0.0012601 | 0.00031561 | -0.0012601 | -0.00031581 | 2.3003e-08 | -2.0372e-07 | 0.001897 | 0.0018971 | 0.0018971 | 0.98839 | -0.22146 | 0.98837 | -0.22185 | 0.52119
93 | 0.0022249 | 0.00055747 | -0.0022249 | -0.0005576 | 5.7214e-08 | -1.3766e-07 | 0.0033496 | 0.0033496 | 0.0033496 | 0.98838 | -0.22153 | 0.98836 | -0.22207 | 0.92023
94 | 0.0067976 | 0.0017036 | -0.006797 | -0.0017034 | 5.2603e-07 | 1.7369e-07 | 0.010367 | 0.010367 | 0.010367 | 0.97565 | -0.46867 | 0.97556 | -0.4703 | 2.8482
95 | -0.0067976 | -0.0017036 | 0.0067981 | 0.0017038 | 5.0941e-07 | 1.6818e-07 | 0.010367 | 0.010367 | 0.010367 | 0.97565 | -0.46867 | 0.97573 | -0.4671 | 2.8482
96 | 0.0049091 | 0.0012303 | -0.0049088 | -0.0012302 | 3.6683e-07 | 1.6948e-08 | 0.0074878 | 0.0074879 | 0.0074879 | 0.97556 | -0.4703 | 0.97548 | -0.47186 | 2.0571
97 | -0.0082585 | -0.0020698 | 0.0082603 | 0.0020706 | 1.8321e-06 | 7.8775e-07 | 0.012594 | 0.012594 | 0.012594 | 0.97573 | -0.4671 | 0.97596 | -0.46244 | 3.46
98 | 0.0027404 | 0.00068681 | -0.0027404 | -0.00068681 | 5.2604e-09 | -6.6547e-09 | 0.0041803 | 0.0041803 | 0.0041803 | 0.97548 | -0.47186 | 0.97548 | -0.4719 | 1.1484
99 | -0.020037 | -0.005023 | 0.020043 | 0.0050266 | 5.9837e-06 | 3.6159e-06 | 0.03055 | 0.03055 | 0.03055 | 0.97596 | -0.46244 | 0.97628 | -0.45618 | 8.3929
100 | 0.011777 | 0.0029525 | -0.011774 | -0.0029508 | 3.0164e-06 | 1.6188e-06 | 0.017956 | 0.017956 | 0.017956 | 0.97596 | -0.46244 | 0.97569 | -0.46782 | 4.9329
101 | -0.020043 | -0.0050266 | 0.020045 | 0.0050282 | 2.6419e-06 | 1.5964e-06 | 0.03055 | 0.03055 | 0.03055 | 0.97628 | -0.45618 | 0.97642 | -0.45341 | 8.3928
102 | 0.010068 | 0.0025233 | -0.010068 | -0.0025233 | 2.1371e-08 | 1.0659e-08 | 0.015354 | 0.015354 | 0.015354 | 0.97569 | -0.46782 | 0.97569 | -0.46786 | 4.2182
103 | -0.024197 | -0.0060687 | 0.024203 | 0.0060726 | 6.3676e-06 | 3.9191e-06 | 0.036877 | 0.036877 | 0.036877 | 0.97642 | -0.45341 | 0.9767 | -0.44789 | 10.131
104 | 0.0076777 | 0.0019243 | -0.0076769 | -0.001924 | 8.337e-07 | 3.3108e-07 | 0.011709 | 0.011709 | 0.011709 | 0.97569 | -0.46786 | 0.97557 | -0.47014 | 3.2169
105 | -0.0015056 | -0.00037733 | 0.0015056 | 0.00037725 | 1.3612e-08 | -8.0433e-08 | 0.0022755 | 0.0022755 | 0.0022755 | 0.98453 | -0.29535 | 0.98454 | -0.29516 | 0.62514
106 | -0.0028832 | -0.00072252 | 0.0028833 | 0.00072238 | 1.1843e-07 | -1.3571e-07 | 0.0043576 | 0.0043575 | 0.0043576 | 0.98454 | -0.29516 | 0.98458 | -0.2943 | 1.1971
107 | 0.041059 | 0.010318 | -0.041032 | -0.0103 | 2.7506e-05 | 1.7369e-05 | 0.062564 | 0.062564 | 0.062564 | 0.9767 | -0.44789 | 0.97599 | -0.46194 | 17.1879
108 | -0.065262 | -0.01639 | 0.065297 | 0.016412 | 3.4055e-05 | 2.168e-05 | 0.09944 | 0.09944 | 0.09944 | 0.9767 | -0.44789 | 0.97726 | -0.43696 | 27.3188
109 | 0.037423 | 0.009396 | -0.037395 | -0.0093785 | 2.7889e-05 | 1.7564e-05 | 0.057062 | 0.057062 | 0.057062 | 0.97599 | -0.46194 | 0.97519 | -0.47757 | 15.6763
110 | 0.0036089 | 0.00090412 | -0.0036087 | -0.00090421 | 1.8364e-07 | -8.4609e-08 | 0.0055021 | 0.0055021 | 0.0055021 | 0.97599 | -0.46194 | 0.97593 | -0.463 | 1.5116
111 | -0.066674 | -0.016757 | 0.066698 | 0.016772 | 2.308e-05 | 1.4696e-05 | 0.10154 | 0.10154 | 0.10154 | 0.97726 | -0.43696 | 0.97763 | -0.42971 | 27.8952
112 | 0.03548 | 0.0088988 | -0.035476 | -0.0088962 | 4.1858e-06 | 2.6314e-06 | 0.054141 | 0.054141 | 0.054141 | 0.97519 | -0.47757 | 0.97507 | -0.48005 | 14.8739
113 | 0.0019144 | 0.00047966 | -0.0019143 | -0.00047978 | 3.4747e-08 | -1.1325e-07 | 0.002921 | 0.0029211 | 0.0029211 | 0.97519 | -0.47757 | 0.97517 | -0.47795 | 0.80249
114 | 0.0018429 | 0.00046166 | -0.0018429 | -0.00046171 | 1.2899e-08 | -4.6182e-08 | 0.0028099 | 0.0028099 | 0.0028099 | 0.97593 | -0.463 | 0.97593 | -0.46315 | 0.77195
115 | -0.066698 | -0.016772 | 0.066741 | 0.0168 | 4.3888e-05 | 2.7946e-05 | 0.10154 | 0.10154 | 0.10154 | 0.97763 | -0.42971 | 0.97833 | -0.41595 | 27.8952
116 | -0.0045009 | -0.0011278 | 0.0045011 | 0.0011278 | 1.6471e-07 | -1.5316e-08 | 0.0068023 | 0.0068022 | 0.0068023 | 0.98458 | -0.2943 | 0.98462 | -0.29353 | 1.8688
117 | 0.023708 | 0.0059462 | -0.023697 | -0.0059395 | 1.0885e-05 | 6.6897e-06 | 0.036181 | 0.036181 | 0.036181 | 0.97507 | -0.48005 | 0.97458 | -0.48968 | 9.9399
118 | 0.011768 | 0.00295 | -0.011765 | -0.002948 | 3.7024e-06 | 1.9879e-06 | 0.01796 | 0.01796 | 0.01796 | 0.97507 | -0.48005 | 0.97473 | -0.48665 | 4.934
119 | 0.0018429 | 0.00046171 | -0.0018429 | -0.00046187 | 4.4073e-08 | -1.5778e-07 | 0.0028099 | 0.00281 | 0.00281 | 0.97593 | -0.46315 | 0.9759 | -0.46365 | 0.77196
120 | -0.068364 | -0.017206 | 0.068421 | 0.017243 | 5.706e-05 | 3.6342e-05 | 0.10401 | 0.10401 | 0.10401 | 0.97833 | -0.41595 | 0.97922 | -0.3985 | 28.5731
121 | 0.013201 | 0.0033089 | -0.0132 | -0.0033087 | 4.082e-07 | 2.2786e-07 | 0.020156 | 0.020156 | 0.020156 | 0.97458 | -0.48968 | 0.97455 | -0.49033 | 5.5373
122 | 0.0079731 | 0.0019977 | -0.0079728 | -0.0019976 | 2.3749e-07 | 9.8708e-08 | 0.012171 | 0.012171 | 0.012171 | 0.97473 | -0.48665 | 0.9747 | -0.48728 | 3.3438
123 | -0.0058695 | -0.0014705 | 0.0058702 | 0.0014707 | 6.7745e-07 | 1.5323e-07 | 0.0089616 | 0.0089615 | 0.0089616 | 0.97458 | -0.4897 | 0.9747 | -0.48728 | 2.462
124 | 0.011732 | 0.0029408 | -0.01173 | -0.0029396 | 2.157e-06 | 1.1572e-06 | 0.017914 | 0.017914 | 0.017914 | 0.97455 | -0.49033 | 0.97435 | -0.49419 | 4.9215
125 | 0.0075794 | 0.0018994 | -0.0075786 | -0.001899 | 7.9714e-07 | 3.1259e-07 | 0.011575 | 0.011575 | 0.011575 | 0.97435 | -0.49419 | 0.97424 | -0.4964 | 3.18
126 | 0.0041508 | 0.0010402 | -0.0041507 | -0.0010403 | 9.6346e-08 | -1.7969e-08 | 0.0063391 | 0.0063391 | 0.0063391 | 0.97435 | -0.49419 | 0.97432 | -0.49468 | 1.7415
127 | 0.006682 | 0.0016743 | -0.006681 | -0.001674 | 9.826e-07 | 3.1566e-07 | 0.010206 | 0.010206 | 0.010206 | 0.97424 | -0.4964 | 0.97408 | -0.49949 | 2.8038
128 | 0.0047439 | 0.0011885 | -0.0047435 | -0.0011885 | 4.1645e-07 | 3.3139e-09 | 0.0072467 | 0.0072468 | 0.0072468 | 0.97408 | -0.49949 | 0.97399 | -0.50133 | 1.9909
129 | 0.074798 | 0.018892 | -0.074764 | -0.018871 | 3.3842e-05 | 2.1571e-05 | 0.11349 | 0.11349 | 0.11349 | 0.98116 | -0.36066 | 0.98068 | -0.37011 | 31.1787
130 | 0.073326 | 0.01851 | -0.073256 | -0.018466 | 6.9475e-05 | 4.4275e-05 | 0.11131 | 0.11131 | 0.11131 | 0.98068 | -0.37011 | 0.97966 | -0.38991 | 30.579
131 | 0.071808 | 0.018103 | -0.071805 | -0.018101 | 3.0969e-06 | 1.9733e-06 | 0.10911 | 0.10911 | 0.10911 | 0.97966 | -0.38991 | 0.97961 | -0.39081 | 29.9748
132 | 0.069868 | 0.017616 | -0.069843 | -0.017599 | 2.5695e-05 | 1.6368e-05 | 0.10617 | 0.10617 | 0.10617 | 0.97961 | -0.39081 | 0.97922 | -0.3985 | 29.1667
133 | 0.0019366 | 0.00048525 | -0.0019365 | -0.00048534 | 2.9229e-08 | -9.4696e-08 | 0.0029416 | 0.0029416 | 0.0029416 | 0.97961 | -0.39081 | 0.9796 | -0.39113 | 0.80814

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28137 | 0.071666

## res_load
| p_mw | q_mvar
0 | 0.0021477 | 0.00053826
1 | 0.0012889 | 0.00032302
2 | 0.0015525 | 0.00038911
3 | 0.0031499 | 0.00078945
4 | 0.0015292 | 0.00038326
5 | 0.0019016 | 0.0004766
6 | 0.0019164 | 0.0004803
7 | 0.0019077 | 0.00047812
8 | 0.0015107 | 0.00037862
9 | 0.0023412 | 0.00058675
10 | 0.0010726 | 0.00026883
11 | 0.0057339 | 0.0014371
12 | 0.0027466 | 0.00068836
13 | 0.0021394 | 0.0005362
14 | 0.002664 | 0.00066765
15 | 0.0027146 | 0.00068034
16 | 0.0036735 | 0.00092068
17 | 0.0074398 | 0.0018646
18 | 0.0042289 | 0.0010599
19 | 0.0019533 | 0.00048954
20 | 0.0017829 | 0.00044684
21 | 0.0016859 | 0.00042252
22 | 0.0075323 | 0.0018878
23 | 0.0024911 | 0.00062432
24 | 0.0068016 | 0.0017046
25 | 0.0018025 | 0.00045174
26 | 0.0032329 | 0.00081025
27 | 0.0011547 | 0.00028938
28 | 0.0023391 | 0.00058624
29 | 0.0011282 | 0.00028275
30 | 0.0025116 | 0.00062948
31 | 0.001453 | 0.00036415
32 | 0.0024325 | 0.00060964
33 | 0.0023317 | 0.00058437
34 | 0.0069169 | 0.0017335
35 | 0.0097115 | 0.0024339
36 | 0.0072496 | 0.0018169
37 | 0.0069786 | 0.001749
38 | 0.0034109 | 0.00085485
39 | 0.0020867 | 0.00052299
40 | 0.0079417 | 0.0019904
41 | 0.0070461 | 0.0017659
42 | 0.0017588 | 0.0004408
43 | 0.0006531 | 0.00016368
44 | 0.00068963 | 0.00017284
45 | 0.0016444 | 0.00041213
46 | 0.00093147 | 0.00023345
47 | 0.0007217 | 0.00018087
48 | 0.00059306 | 0.00014864
49 | 0.0012897 | 0.00032323
50 | 0.0018014 | 0.00045146
51 | 0.000711 | 0.00017819
52 | 0.00073274 | 0.00018364
53 | 0.0016331 | 0.00040929
54 | 0.0041366 | 0.0010367
55 | 0.0013144 | 0.00032941
56 | 0.0047231 | 0.0011837
57 | 0.0051451 | 0.0012895
58 | 0.0039366 | 0.0009866
59 | 0.0043725 | 0.0010958
60 | 0.0024981 | 0.00062608
61 | 0.0072983 | 0.0018291
62 | 0.002326 | 0.00058295
63 | 0.0023219 | 0.00058193
64 | 0.0016532 | 0.00041433
65 | 0.0010659 | 0.00026713
66 | 0.0012601 | 0.00031581
67 | 0.0022249 | 0.0005576
68 | 0.0018879 | 0.00047315
69 | 0.0014604 | 0.00036601
70 | 0.0021683 | 0.00054344
71 | 0.0027404 | 0.00068681
72 | 0.0017058 | 0.0004275
73 | 0.0041516 | 0.0010405
74 | 0.00239 | 0.00059899
75 | 0.0015056 | 0.00037733
76 | 0.0013776 | 0.00034527
77 | 0.0076769 | 0.001924
78 | 0.0013779 | 0.00034534
79 | 0.0017658 | 0.00044254
80 | 0.0016176 | 0.00040541
81 | 0.0019143 | 0.00047978
82 | 0.0016224 | 0.00040662
83 | 0.0018429 | 0.00046187
84 | 0.010496 | 0.0026306
85 | 0.0037917 | 0.00095028
86 | 0.0020511 | 0.00051406
87 | 0.0021026 | 0.00052696
88 | 0.001468 | 0.00036792
89 | 0.0041507 | 0.0010403
90 | 0.00089667 | 0.00022473
91 | 0.0019371 | 0.00048548
92 | 0.0012276 | 0.00030766
93 | 0.0014513 | 0.00036373
94 | 0.0015264 | 0.00038254
95 | 0.0014388 | 0.0003606
96 | 0.0014479 | 0.00036288
97 | 0.0014219 | 0.00035636
98 | 0.0019365 | 0.00048534

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1