## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_117-5_2_2_node_8 | 0.4 | n |  | TRUE
1 | bus_LV_117-5_2_2_node_9 | 0.4 | n |  | TRUE
2 | bus_LV_117-5_2_2_node_10 | 0.4 | n |  | TRUE
3 | bus_LV_117-5_2_2_node_11 | 0.4 | n |  | TRUE
4 | bus_LV_117-5_2_2_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_117-5_2_2_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_117-5_2_2_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_117-5_2_2_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_117-5_2_2_node_145 | 0.4 | n |  | TRUE
9 | bus_LV_117-5_2_2_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_117-5_2_2_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_117-5_2_2_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_117-5_2_2_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_117-5_2_2_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_117-5_2_2_node_196 | 0.4 | n |  | TRUE
15 | bus_LV_117-5_2_2_node_201 | 0.4 | n |  | TRUE
16 | bus_LV_117-5_2_2_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_117-5_2_2_node_58 | 0.4 | n |  | TRUE
18 | bus_LV_117-5_2_2_node_56 | 0.4 | n |  | TRUE
19 | bus_LV_117-5_2_2_node_57 | 0.4 | n |  | TRUE
20 | bus_LV_117-5_2_2_node_170 | 0.4 | n |  | TRUE
21 | bus_LV_117-5_2_2_node_89 | 0.4 | n |  | TRUE
22 | bus_LV_117-5_2_2_node_92 | 0.4 | n |  | TRUE
23 | bus_LV_117-5_2_2_node_93 | 0.4 | n |  | TRUE
24 | bus_LV_117-5_2_2_node_90 | 0.4 | n |  | TRUE
25 | bus_LV_117-5_2_2_node_212 | 0.4 | n |  | TRUE
26 | bus_LV_117-5_2_2_node_91 | 0.4 | n |  | TRUE
27 | bus_LV_117-5_2_2_node_211 | 0.4 | n |  | TRUE
28 | bus_LV_117-5_2_2_node_123 | 0.4 | n |  | TRUE
29 | bus_LV_117-5_2_2_node_105 | 0.4 | n |  | TRUE
30 | bus_LV_117-5_2_2_node_106 | 0.4 | n |  | TRUE
31 | bus_LV_117-5_2_2_node_108 | 0.4 | n |  | TRUE
32 | bus_LV_117-5_2_2_node_124 | 0.4 | n |  | TRUE
33 | bus_LV_117-5_2_2_node_112 | 0.4 | n |  | TRUE
34 | bus_LV_117-5_2_2_node_118 | 0.4 | n |  | TRUE
35 | bus_LV_117-5_2_2_node_120 | 0.4 | n |  | TRUE
36 | bus_LV_117-5_2_2_node_119 | 0.4 | n |  | TRUE
37 | bus_LV_117-5_2_2_node_121 | 0.4 | n |  | TRUE
38 | bus_LV_117-5_2_2_node_227 | 0.4 | n |  | TRUE
39 | bus_LV_117-5_2_2_node_122 | 0.4 | n |  | TRUE
40 | bus_LV_117-5_2_2_node_163 | 0.4 | n |  | TRUE
41 | bus_LV_117-5_2_2_node_125 | 0.4 | n |  | TRUE
42 | bus_LV_117-5_2_2_node_127 | 0.4 | n |  | TRUE
43 | bus_LV_117-5_2_2_node_130 | 0.4 | n |  | TRUE
44 | bus_LV_117-5_2_2_node_128 | 0.4 | n |  | TRUE
45 | bus_LV_117-5_2_2_node_129 | 0.4 | n |  | TRUE
46 | bus_LV_117-5_2_2_node_140 | 0.4 | n |  | TRUE
47 | bus_LV_117-5_2_2_node_134 | 0.4 | n |  | TRUE
48 | bus_LV_117-5_2_2_node_135 | 0.4 | n |  | TRUE
49 | bus_LV_117-5_2_2_node_132 | 0.4 | n |  | TRUE
50 | bus_LV_117-5_2_2_node_131 | 0.4 | n |  | TRUE
51 | bus_LV_117-5_2_2_node_204 | 0.4 | n |  | TRUE
52 | bus_LV_117-5_2_2_node_133 | 0.4 | n |  | TRUE
53 | bus_LV_117-5_2_2_node_136 | 0.4 | n |  | TRUE
54 | bus_LV_117-5_2_2_node_144 | 0.4 | n |  | TRUE
55 | bus_LV_117-5_2_2_node_137 | 0.4 | n |  | TRUE
56 | bus_LV_117-5_2_2_node_138 | 0.4 | n |  | TRUE
57 | bus_LV_117-5_2_2_node_141 | 0.4 | n |  | TRUE
58 | bus_LV_117-5_2_2_node_143 | 0.4 | n |  | TRUE
59 | bus_LV_117-5_2_2_node_152 | 0.4 | n |  | TRUE
60 | bus_LV_117-5_2_2_node_154 | 0.4 | n |  | TRUE
61 | bus_LV_117-5_2_2_node_156 | 0.4 | n |  | TRUE
62 | bus_LV_117-5_2_2_node_155 | 0.4 | n |  | TRUE
63 | bus_LV_117-5_2_2_node_157 | 0.4 | n |  | TRUE
64 | bus_LV_117-5_2_2_node_158 | 0.4 | n |  | TRUE
65 | bus_LV_117-5_2_2_node_161 | 0.4 | n |  | TRUE
66 | bus_LV_117-5_2_2_node_159 | 0.4 | n |  | TRUE
67 | bus_LV_117-5_2_2_node_160 | 0.4 | n |  | TRUE
68 | bus_LV_117-5_2_2_node_162 | 0.4 | n |  | TRUE
69 | bus_LV_117-5_2_2_node_169 | 0.4 | n |  | TRUE
70 | bus_LV_117-5_2_2_node_171 | 0.4 | n |  | TRUE
71 | bus_LV_117-5_2_2_node_172 | 0.4 | n |  | TRUE
72 | bus_LV_117-5_2_2_node_173 | 0.4 | n |  | TRUE
73 | bus_LV_117-5_2_2_node_175 | 0.4 | n |  | TRUE
74 | bus_LV_117-5_2_2_node_176 | 0.4 | n |  | TRUE
75 | bus_LV_117-5_2_2_node_174 | 0.4 | n |  | TRUE
76 | bus_LV_117-5_2_2_node_207 | 0.4 | n |  | TRUE
77 | bus_LV_117-5_2_2_node_183 | 0.4 | n |  | TRUE
78 | bus_LV_117-5_2_2_node_206 | 0.4 | n |  | TRUE
79 | bus_LV_117-5_2_2_node_190 | 0.4 | n |  | TRUE
80 | bus_LV_117-5_2_2_node_177 | 0.4 | n |  | TRUE
81 | bus_LV_117-5_2_2_node_178 | 0.4 | n |  | TRUE
82 | bus_LV_117-5_2_2_node_179 | 0.4 | n |  | TRUE
83 | bus_LV_117-5_2_2_node_180 | 0.4 | n |  | TRUE
84 | bus_LV_117-5_2_2_node_181 | 0.4 | n |  | TRUE
85 | bus_LV_117-5_2_2_node_182 | 0.4 | n |  | TRUE
86 | bus_LV_117-5_2_2_node_184 | 0.4 | n |  | TRUE
87 | bus_LV_117-5_2_2_node_185 | 0.4 | n |  | TRUE
88 | bus_LV_117-5_2_2_node_186 | 0.4 | n |  | TRUE
89 | bus_LV_117-5_2_2_node_187 | 0.4 | n |  | TRUE
90 | bus_LV_117-5_2_2_node_188 | 0.4 | n |  | TRUE
91 | bus_LV_117-5_2_2_node_189 | 0.4 | n |  | TRUE
92 | bus_LV_117-5_2_2_node_205 | 0.4 | n |  | TRUE
93 | bus_LV_117-5_2_2_node_222 | 0.4 | n |  | TRUE
94 | bus_LV_117-5_2_2_node_209 | 0.4 | n |  | TRUE
95 | bus_LV_117-5_2_2_node_208 | 0.4 | n |  | TRUE
96 | bus_LV_117-5_2_2_node_218 | 0.4 | n |  | TRUE
97 | bus_LV_117-5_2_2_node_191 | 0.4 | n |  | TRUE
98 | bus_LV_117-5_2_2_node_192 | 0.4 | n |  | TRUE
99 | bus_LV_117-5_2_2_node_193 | 0.4 | n |  | TRUE
100 | bus_LV_117-5_2_2_node_194 | 0.4 | n |  | TRUE
101 | bus_LV_117-5_2_2_node_195 | 0.4 | n |  | TRUE
102 | bus_LV_117-5_2_2_node_197 | 0.4 | n |  | TRUE
103 | bus_LV_117-5_2_2_node_198 | 0.4 | n |  | TRUE
104 | bus_LV_117-5_2_2_node_223 | 0.4 | n |  | TRUE
105 | bus_LV_117-5_2_2_node_199 | 0.4 | n |  | TRUE
106 | bus_LV_117-5_2_2_node_200 | 0.4 | n |  | TRUE
107 | bus_LV_117-5_2_2_node_202 | 0.4 | n |  | TRUE
108 | bus_LV_117-5_2_2_node_203 | 0.4 | n |  | TRUE
109 | bus_LV_117-5_2_2_node_210 | 0.4 | n |  | TRUE
110 | bus_LV_117-5_2_2_node_233 | 0.4 | n |  | TRUE
111 | bus_LV_117-5_2_2_node_230 | 0.4 | n |  | TRUE
112 | bus_LV_117-5_2_2_node_221 | 0.4 | n |  | TRUE
113 | bus_LV_117-5_2_2_node_216 | 0.4 | n |  | TRUE
114 | bus_LV_117-5_2_2_node_213 | 0.4 | n |  | TRUE
115 | bus_LV_117-5_2_2_node_214 | 0.4 | n |  | TRUE
116 | bus_LV_117-5_2_2_node_215 | 0.4 | n |  | TRUE
117 | bus_LV_117-5_2_2_node_217 | 0.4 | n |  | TRUE
118 | bus_LV_117-5_2_2_node_219 | 0.4 | n |  | TRUE
119 | bus_LV_117-5_2_2_node_220 | 0.4 | n |  | TRUE
120 | bus_LV_117-5_2_2_node_224 | 0.4 | n |  | TRUE
121 | bus_LV_117-5_2_2_node_225 | 0.4 | n |  | TRUE
122 | bus_LV_117-5_2_2_node_226 | 0.4 | n |  | TRUE
123 | bus_LV_117-5_2_2_node_228 | 0.4 | n |  | TRUE
124 | bus_LV_117-5_2_2_node_437 | 0.4 | n |  | TRUE
125 | bus_LV_117-5_2_2_node_229 | 0.4 | n |  | TRUE
126 | bus_LV_117-5_2_2_node_235 | 0.4 | n |  | TRUE
127 | bus_LV_117-5_2_2_node_231 | 0.4 | n |  | TRUE
128 | bus_LV_117-5_2_2_node_232 | 0.4 | n |  | TRUE
129 | bus_LV_117-5_2_2_node_234 | 0.4 | n |  | TRUE
130 | bus_LV_117-5_2_2_node_236 | 0.4 | n |  | TRUE
131 | bus_LV_117-5_2_2_node_237 | 0.4 | n |  | TRUE
132 | bus_LV_117-5_2_2_node_436 | 0.4 | n |  | TRUE
133 | bus_MV_6_0_node_18 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_117-5_2_2_load_8 | 0 | 0.0022608 | 0.00056661 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_117-5_2_2_load_9 | 1 | 0.00080298 | 0.00020125 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_117-5_2_2_load_11 | 3 | 0.00078294 | 0.00019622 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_117-5_2_2_load_12 | 4 | 0.00070144 | 0.0001758 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_117-5_2_2_load_13 | 5 | 0.0022217 | 0.0005568 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_117-5_2_2_load_14 | 6 | 0.00057176 | 0.0001433 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_117-5_2_2_load_15 | 7 | 0.0027319 | 0.00068469 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_117-5_2_2_load_19 | 11 | 0.00078923 | 0.0001978 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_117-5_2_2_load_22 | 13 | 0.00060469 | 0.00015155 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_117-5_2_2_load_196 | 14 | 0.00083006 | 0.00020803 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_117-5_2_2_load_201 | 15 | 0.0010988 | 0.00027539 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_117-5_2_2_load_21 | 16 | 0.0012611 | 0.00031605 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_117-5_2_2_load_58 | 17 | 0.0013452 | 0.00033714 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_117-5_2_2_load_170 | 20 | 0.0005599 | 0.00014033 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_117-5_2_2_load_92 | 22 | 0.0017395 | 0.00043596 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_117-5_2_2_load_93 | 23 | 0.00050375 | 0.00012625 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_117-5_2_2_load_211 | 27 | 0.00016886 | 4.2319e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_117-5_2_2_load_123 | 28 | 0.00034402 | 8.6219e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_117-5_2_2_load_105 | 29 | 0.00044153 | 0.00011066 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_117-5_2_2_load_112 | 33 | 0.00030776 | 7.7133e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_117-5_2_2_load_118 | 34 | 7.7951e-05 | 1.9536e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_117-5_2_2_load_120 | 35 | 8.7616e-05 | 2.1959e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_117-5_2_2_load_119 | 36 | 0.0016975 | 0.00042544 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_117-5_2_2_load_227 | 38 | 0.0012459 | 0.00031224 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_117-5_2_2_load_122 | 39 | 8.8391e-05 | 2.2153e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_117-5_2_2_load_163 | 40 | 0.00039011 | 9.7771e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_117-5_2_2_load_125 | 41 | 0.00069592 | 0.00017441 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_117-5_2_2_load_130 | 43 | 0.00076138 | 0.00019082 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_117-5_2_2_load_134 | 47 | 0.0004263 | 0.00010684 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_117-5_2_2_load_135 | 48 | 0.0001491 | 3.7368e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_117-5_2_2_load_132 | 49 | 0.00066049 | 0.00016553 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_117-5_2_2_load_131 | 50 | 0.0011494 | 0.00028808 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_117-5_2_2_load_204 | 51 | 0.00048685 | 0.00012202 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_117-5_2_2_load_133 | 52 | 0.00018644 | 4.6727e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_117-5_2_2_load_144 | 54 | 0.00022447 | 5.6257e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_117-5_2_2_load_137 | 55 | 0.00053819 | 0.00013488 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_117-5_2_2_load_141 | 57 | 0.0016344 | 0.00040962 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_117-5_2_2_load_143 | 58 | 0.00030043 | 7.5295e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_117-5_2_2_load_152 | 59 | 0.00022047 | 5.5254e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_117-5_2_2_load_156 | 61 | 0.00011253 | 2.8203e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_117-5_2_2_load_157 | 63 | 0.00040552 | 0.00010163 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_117-5_2_2_load_159 | 66 | 0.00020389 | 5.11e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_117-5_2_2_load_160 | 67 | 0.0001455 | 3.6466e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_117-5_2_2_load_162 | 68 | 0.00014811 | 3.7121e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_117-5_2_2_load_169 | 69 | 0.0026318 | 0.00065959 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_117-5_2_2_load_172 | 71 | 0.001276 | 0.00031979 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_117-5_2_2_load_173 | 72 | 0.00099323 | 0.00024893 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_117-5_2_2_load_175 | 73 | 0.0034179 | 0.00085661 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_117-5_2_2_load_176 | 74 | 0.0018798 | 0.00047113 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_117-5_2_2_load_207 | 76 | 0.015573 | 0.0039029 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_117-5_2_2_load_206 | 78 | 0.001288 | 0.00032281 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_117-5_2_2_load_190 | 79 | 0.00076844 | 0.00019259 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_117-5_2_2_load_177 | 80 | 0.0062364 | 0.001563 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_117-5_2_2_load_178 | 81 | 0.0021587 | 0.00054101 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_117-5_2_2_load_180 | 83 | 0.0021424 | 0.00053695 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_117-5_2_2_load_182 | 85 | 0.013068 | 0.0032752 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_117-5_2_2_load_184 | 86 | 0.036419 | 0.0091276 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_117-5_2_2_load_185 | 87 | 0.0051391 | 0.001288 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_117-5_2_2_load_187 | 89 | 0.0024838 | 0.0006225 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_117-5_2_2_load_189 | 91 | 0.013485 | 0.0033796 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_117-5_2_2_load_205 | 92 | 0.0014029 | 0.00035161 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_117-5_2_2_load_222 | 93 | 0.0087614 | 0.0021958 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_117-5_2_2_load_209 | 94 | 0.0019386 | 0.00048585 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_117-5_2_2_load_208 | 95 | 0.0043606 | 0.0010929 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_117-5_2_2_load_191 | 97 | 0.0011616 | 0.00029112 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_117-5_2_2_load_192 | 98 | 0.0013607 | 0.00034102 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_117-5_2_2_load_193 | 99 | 0.00098171 | 0.00024604 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_117-5_2_2_load_194 | 100 | 0.00091306 | 0.00022884 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_117-5_2_2_load_197 | 102 | 0.0017041 | 0.00042708 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_117-5_2_2_load_198 | 103 | 0.00068948 | 0.0001728 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_117-5_2_2_load_223 | 104 | 0.00075277 | 0.00018866 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_117-5_2_2_load_199 | 105 | 0.0012387 | 0.00031045 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_117-5_2_2_load_200 | 106 | 0.00098954 | 0.000248 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_117-5_2_2_load_202 | 107 | 0.00077728 | 0.00019481 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_117-5_2_2_load_203 | 108 | 0.00043046 | 0.00010788 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_117-5_2_2_load_230 | 111 | 0.007277 | 0.0018238 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_117-5_2_2_load_221 | 112 | 0.0002493 | 6.2482e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_117-5_2_2_load_213 | 114 | 0.00025147 | 6.3023e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_117-5_2_2_load_214 | 115 | 0.00030705 | 7.6954e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_117-5_2_2_load_215 | 116 | 9.1788e-05 | 2.3004e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_117-5_2_2_load_217 | 117 | 0.00010746 | 2.6932e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_117-5_2_2_load_219 | 118 | 0.00010737 | 2.6911e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_117-5_2_2_load_220 | 119 | 0.00015612 | 3.9128e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_117-5_2_2_load_224 | 120 | 0.00089983 | 0.00022552 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_117-5_2_2_load_225 | 121 | 0.00053761 | 0.00013474 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_117-5_2_2_load_229 | 125 | 0.00053112 | 0.00013311 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_117-5_2_2_load_235 | 126 | 0.00036723 | 9.2038e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_117-5_2_2_load_231 | 127 | 0.00021058 | 5.2775e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_117-5_2_2_load_232 | 128 | 0.00038106 | 9.5502e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_117-5_2_2_load_234 | 129 | 0.00023311 | 5.8424e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_117-5_2_2_load_236 | 130 | 0.00057633 | 0.00014444 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_117-5_2_2_load_237 | 131 | 0.0011797 | 0.00029567 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_117-5_2_2_load_436 | 132 | 0.00018791 | 4.7095e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 78 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_117-5_2_2_line_0 |  | 0 | 1 | 0.10948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_117-5_2_2_line_1 |  | 0 | 2 | 0.019363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_117-5_2_2_line_2 |  | 1 | 3 | 0.025399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_117-5_2_2_line_3 |  | 2 | 4 | 0.027496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_117-5_2_2_line_4 |  | 2 | 5 | 0.016663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_117-5_2_2_line_5 |  | 3 | 6 | 0.01063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_117-5_2_2_line_6 |  | 4 | 7 | 0.0078195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_117-5_2_2_line_7 |  | 6 | 8 | 0.18971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_117-5_2_2_line_8 |  | 8 | 54 | 0.18344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_117-5_2_2_line_9 |  | 9 | 10 | 0.019398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_117-5_2_2_line_10 |  | 9 | 11 | 0.0019935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_117-5_2_2_line_11 |  | 10 | 12 | 0.032729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_117-5_2_2_line_12 |  | 11 | 13 | 0.020314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_117-5_2_2_line_13 |  | 12 | 14 | 0.0025032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_117-5_2_2_line_14 |  | 12 | 15 | 0.019978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_117-5_2_2_line_15 |  | 14 | 101 | 0.025397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_117-5_2_2_line_16 |  | 15 | 105 | 0.0064259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_117-5_2_2_line_17 |  | 16 | 17 | 0.023376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_117-5_2_2_line_18 |  | 17 | 18 | 0.01418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_117-5_2_2_line_19 |  | 18 | 19 | 0.011444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_117-5_2_2_line_20 |  | 19 | 20 | 0.010765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_117-5_2_2_line_21 |  | 20 | 69 | 0.012854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_117-5_2_2_line_22 |  | 21 | 22 | 0.0098049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_117-5_2_2_line_23 |  | 21 | 23 | 0.019129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_117-5_2_2_line_24 |  | 23 | 27 | 0.0012059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_117-5_2_2_line_25 |  | 24 | 25 | 0.050619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_117-5_2_2_line_26 |  | 24 | 26 | 0.039451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_117-5_2_2_line_27 |  | 24 | 27 | 0.017898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_117-5_2_2_line_28 |  | 25 | 112 | 0.024828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_117-5_2_2_line_29 |  | 25 | 113 | 0.018644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_117-5_2_2_line_30 |  | 26 | 28 | 0.02092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_117-5_2_2_line_31 |  | 29 | 30 | 0.023021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_117-5_2_2_line_32 |  | 30 | 31 | 0.015998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_117-5_2_2_line_33 |  | 30 | 32 | 0.23942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_117-5_2_2_line_34 |  | 31 | 33 | 0.028276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_117-5_2_2_line_35 |  | 32 | 40 | 0.2522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_117-5_2_2_line_36 |  | 32 | 39 | 0.020931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_117-5_2_2_line_37 |  | 34 | 35 | 0.0065108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_117-5_2_2_line_38 |  | 35 | 37 | 0.01164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_117-5_2_2_line_39 |  | 36 | 37 | 0.042583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_117-5_2_2_line_40 |  | 36 | 38 | 0.22197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_117-5_2_2_line_41 |  | 37 | 39 | 0.006621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_117-5_2_2_line_42 |  | 38 | 124 | 0.08603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_117-5_2_2_line_43 |  | 38 | 122 | 0.051217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_117-5_2_2_line_44 |  | 40 | 65 | 0.002891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_117-5_2_2_line_45 |  | 41 | 42 | 0.021516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_117-5_2_2_line_46 |  | 41 | 43 | 0.26721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_117-5_2_2_line_47 |  | 42 | 44 | 0.042075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_117-5_2_2_line_48 |  | 43 | 50 | 0.0031187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_117-5_2_2_line_49 |  | 44 | 45 | 0.057042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_117-5_2_2_line_50 |  | 44 | 46 | 0.19944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_117-5_2_2_line_51 |  | 45 | 47 | 0.013794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_117-5_2_2_line_52 |  | 45 | 48 | 0.012276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_117-5_2_2_line_53 |  | 45 | 49 | 0.026573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_117-5_2_2_line_54 |  | 46 | 58 | 0.033568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_117-5_2_2_line_55 |  | 46 | 56 | 0.053814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_117-5_2_2_line_56 |  | 48 | 53 | 0.11438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_117-5_2_2_line_57 |  | 49 | 52 | 0.010223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_117-5_2_2_line_58 |  | 50 | 51 | 0.0031946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_117-5_2_2_line_59 |  | 51 | 108 | 0.0053222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_117-5_2_2_line_60 |  | 53 | 54 | 0.027568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_117-5_2_2_line_61 |  | 55 | 56 | 0.019365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_117-5_2_2_line_62 |  | 56 | 57 | 0.0041526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_117-5_2_2_line_63 |  | 59 | 60 | 0.032422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_117-5_2_2_line_64 |  | 60 | 61 | 0.01067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_117-5_2_2_line_65 |  | 60 | 62 | 0.021297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_117-5_2_2_line_66 |  | 61 | 64 | 0.0026076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_117-5_2_2_line_67 |  | 62 | 63 | 0.012911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_117-5_2_2_line_68 |  | 63 | 65 | 0.017243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_117-5_2_2_line_69 |  | 64 | 66 | 0.026105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_117-5_2_2_line_70 |  | 64 | 67 | 0.029303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_117-5_2_2_line_71 |  | 67 | 68 | 0.00069016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_117-5_2_2_line_72 |  | 69 | 70 | 0.021997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_117-5_2_2_line_73 |  | 70 | 71 | 0.013295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_117-5_2_2_line_74 |  | 70 | 72 | 0.0013039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_117-5_2_2_line_75 |  | 71 | 73 | 0.025828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_117-5_2_2_line_76 |  | 72 | 74 | 0.0012999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_117-5_2_2_line_77 |  | 73 | 78 | 0.004163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_117-5_2_2_line_78 |  | 74 | 79 | 0.015756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_117-5_2_2_line_79 |  | 75 | 76 | 0.017614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_117-5_2_2_line_80 |  | 75 | 77 | 0.022969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_117-5_2_2_line_81 |  | 77 | 91 | 0.023521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_117-5_2_2_line_82 |  | 78 | 92 | 0.0047706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_117-5_2_2_line_83 |  | 79 | 97 | 0.015518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_117-5_2_2_line_84 |  | 80 | 81 | 0.032659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_117-5_2_2_line_85 |  | 80 | 82 | 0.025347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_117-5_2_2_line_86 |  | 81 | 83 | 0.00479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_117-5_2_2_line_87 |  | 82 | 84 | 0.01079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_117-5_2_2_line_88 |  | 82 | 85 | 0.014464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_117-5_2_2_line_89 |  | 83 | 86 | 0.004839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_117-5_2_2_line_90 |  | 84 | 87 | 0.023922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_117-5_2_2_line_91 |  | 84 | 88 | 0.050581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_117-5_2_2_line_92 |  | 84 | 89 | 0.016472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_117-5_2_2_line_93 |  | 85 | 90 | 0.0088563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_117-5_2_2_line_94 |  | 86 | 92 | 0.00056199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_117-5_2_2_line_95 |  | 87 | 93 | 0.00098184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_117-5_2_2_line_96 |  | 88 | 94 | 0.048331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_117-5_2_2_line_97 |  | 88 | 95 | 0.01657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_117-5_2_2_line_98 |  | 89 | 96 | 0.017254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_117-5_2_2_line_99 |  | 90 | 91 | 0.0066966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_117-5_2_2_line_100 |  | 94 | 109 | 0.036613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_117-5_2_2_line_101 |  | 96 | 113 | 0.016095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_117-5_2_2_line_102 |  | 97 | 98 | 0.0064147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_117-5_2_2_line_103 |  | 98 | 99 | 0.0035833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_117-5_2_2_line_104 |  | 99 | 100 | 0.0074859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_117-5_2_2_line_105 |  | 100 | 101 | 0.0096236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_117-5_2_2_line_106 |  | 101 | 102 | 0.026122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_117-5_2_2_line_107 |  | 102 | 103 | 0.0075027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_117-5_2_2_line_108 |  | 103 | 104 | 0.00089452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_117-5_2_2_line_109 |  | 105 | 106 | 0.014913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_117-5_2_2_line_110 |  | 106 | 107 | 0.0023618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_117-5_2_2_line_111 |  | 107 | 108 | 0.0046223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_117-5_2_2_line_112 |  | 109 | 110 | 0.14219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_117-5_2_2_line_113 |  | 109 | 111 | 0.029001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_117-5_2_2_line_114 |  | 110 | 126 | 0.017067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_117-5_2_2_line_115 |  | 110 | 130 | 0.030778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_117-5_2_2_line_116 |  | 111 | 127 | 0.063894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_117-5_2_2_line_117 |  | 113 | 115 | 0.010255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_117-5_2_2_line_118 |  | 114 | 115 | 0.0017024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_117-5_2_2_line_119 |  | 114 | 116 | 0.0087384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_117-5_2_2_line_120 |  | 116 | 117 | 0.00066898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_117-5_2_2_line_121 |  | 117 | 118 | 0.0039894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_117-5_2_2_line_122 |  | 118 | 119 | 0.007991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_117-5_2_2_line_123 |  | 120 | 121 | 0.023519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_117-5_2_2_line_124 |  | 120 | 122 | 0.0070868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_117-5_2_2_line_125 |  | 122 | 123 | 0.10303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_117-5_2_2_line_126 |  | 123 | 125 | 0.096527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_117-5_2_2_line_127 |  | 124 | 132 | 0.035358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_117-5_2_2_line_128 |  | 125 | 126 | 0.051004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_117-5_2_2_line_129 |  | 127 | 128 | 0.012778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_117-5_2_2_line_130 |  | 128 | 129 | 0.008624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_117-5_2_2_line_131 |  | 129 | 131 | 0.003406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_117-5_2_2_trafo_206 | 0.63 MVA 20/0.4 kV | 133 | 78 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2708615.1769 | 1241356.3629 | 2708609.4743 | 1241359.386 | 2708591.6581 | 1241372.9707 | 2708587.3785 | 1241376.2394 | 2708562.652 | 1241390.5651 | 2708532.3194 | 1241407.5127 | 2708521.9221 | 1241413.324
1 | 2708632.2846 | 1241347.2938 | 2708615.1769 | 1241356.3629
2 | 2708498.9785 | 1241420.5573 | 2708506.1967 | 1241422.1133 | 2708521.9221 | 1241413.324
3 | 2708632.2846 | 1241347.2938 | 2708623.6893 | 1241329.7783 | 2708621.1886 | 1241322.195
4 | 2708632.2846 | 1241347.2938 | 2708647.5095 | 1241340.5224
5 | 2708491.082 | 1241413.7193 | 2708497.6849 | 1241420.2785 | 2708498.9785 | 1241420.5573
6 | 2708618.7397 | 1241314.7689 | 2708621.1886 | 1241322.195
7 | 2708491.082 | 1241413.7193 | 2708333.6522 | 1241519.583
8 | 2708333.6522 | 1241519.583 | 2708309.5009 | 1241506.6209 | 2708277.5764 | 1241487.8126 | 2708264.2605 | 1241470.7674 | 2708258.7706 | 1241457.0787 | 2708254.2311 | 1241450.5685 | 2708240.1381 | 1241436.7229 | 2708230.3988 | 1241420.0988 | 2708220.9505 | 1241407.4166 | 2708203.4868 | 1241401.7382 | 2708202.0777 | 1241401.3664
9 | 2708468.325 | 1241049.0829 | 2708461.9398 | 1241067.4029
10 | 2708461.9398 | 1241067.4029 | 2708461.2739 | 1241069.2819
11 | 2708468.325 | 1241049.0829 | 2708462.9311 | 1241047.105 | 2708456.797 | 1241042.178 | 2708449.9469 | 1241024.2943
12 | 2708454.4892 | 1241088.4293 | 2708461.2739 | 1241069.2819
13 | 2708449.9469 | 1241024.2943 | 2708449.3072 | 1241021.8742
14 | 2708449.9469 | 1241024.2943 | 2708441.0922 | 1241026.7011 | 2708431.5783 | 1241031.8159
15 | 2708442.8167 | 1240997.3206 | 2708449.3072 | 1241021.8742
16 | 2708431.5783 | 1241031.8159 | 2708425.9185 | 1241034.8587
17 | 2708481.9156 | 1240996.249 | 2708482.6352 | 1240991.5213 | 2708483.9914 | 1240976.501 | 2708483.9791 | 1240972.9883
18 | 2708483.9293 | 1240958.8081 | 2708483.9791 | 1240972.9883
19 | 2708482.8823 | 1240947.4134 | 2708483.9293 | 1240958.8081
20 | 2708482.8823 | 1240947.4134 | 2708479.2531 | 1240947.7695 | 2708474.4097 | 1240947.1139 | 2708472.3027 | 1240946.381
21 | 2708460.0452 | 1240942.628 | 2708462.7012 | 1240943.0412 | 2708472.3027 | 1240946.381
22 | 2708435.893 | 1240716.1953 | 2708435.393 | 1240725.9874
23 | 2708435.893 | 1240716.1953 | 2708416.7913 | 1240717.2092
24 | 2708416.7913 | 1240717.2092 | 2708415.5871 | 1240717.2731
25 | 2708378.4806 | 1240765.0519 | 2708388.8375 | 1240740.8776 | 2708397.7147 | 1240718.2218
26 | 2708395.0673 | 1240679.3318 | 2708398.3465 | 1240691.9238 | 2708398.9437 | 1240698.1507 | 2708399.3494 | 1240704.919 | 2708397.7147 | 1240718.2218
27 | 2708397.7147 | 1240718.2218 | 2708415.5871 | 1240717.2731
28 | 2708378.4806 | 1240765.0519 | 2708395.2606 | 1240774.7103 | 2708396.5771 | 1240780.0608
29 | 2708378.4806 | 1240765.0519 | 2708373.501 | 1240783.0196
30 | 2708395.0673 | 1240679.3318 | 2708375.5704 | 1240686.9153
31 | 2708356.9891 | 1240423.7026 | 2708365.1347 | 1240426.6202 | 2708379.1831 | 1240423.6056
32 | 2708356.9891 | 1240423.7026 | 2708363.0082 | 1240418.8197 | 2708369.4267 | 1240413.5995
33 | 2708356.9891 | 1240423.7026 | 2708165.1667 | 1240566.9726
34 | 2708369.4267 | 1240413.5995 | 2708367.868 | 1240409.0786 | 2708370.8508 | 1240396.0895 | 2708370.2319 | 1240385.9412
35 | 2708165.1667 | 1240566.9726 | 2708141.2121 | 1240549.6226 | 2708131.2514 | 1240545.4601 | 2708120.1703 | 1240543.8348 | 2708110.0807 | 1240545.0854 | 2708098.1496 | 1240547.3588 | 2708085.7694 | 1240552.2817 | 2708064.6175 | 1240564.1615 | 2708059.7988 | 1240565.864 | 2708055.6924 | 1240565.4223 | 2708051.5674 | 1240562.6784 | 2708048.5043 | 1240559.3534 | 2708046.0535 | 1240554.3826 | 2708042.3626 | 1240534.0328 | 2708038.6802 | 1240521.5227 | 2708033.8993 | 1240511.1831 | 2708027.1497 | 1240499.718 | 2708019.7507 | 1240491.5214 | 2708005.2502 | 1240481.205 | 2707984.2383 | 1240469.1912 | 2707979.2995 | 1240468.3539
36 | 2708165.1667 | 1240566.9726 | 2708152.9344 | 1240583.9574
37 | 2708137.467 | 1240588.3382 | 2708130.9799 | 1240587.7834
38 | 2708149.0651 | 1240589.3302 | 2708137.467 | 1240588.3382
39 | 2708149.0651 | 1240589.3302 | 2708146.5155 | 1240605.9634 | 2708133.3396 | 1240628.094
40 | 2708134.0411 | 1240850.0612 | 2708133.3396 | 1240628.094
41 | 2708149.0651 | 1240589.3302 | 2708152.9344 | 1240583.9574
42 | 2708134.0411 | 1240850.0612 | 2708114.3076 | 1240766.3249
43 | 2708084.782 | 1240863.408 | 2708099.2357 | 1240859.2123 | 2708114.0114 | 1240854.7779 | 2708117.3122 | 1240852.9365 | 2708126.1925 | 1240850.374 | 2708134.0411 | 1240850.0612
44 | 2707976.4492 | 1240467.8707 | 2707979.2995 | 1240468.3539
45 | 2708161.3013 | 1241200.7668 | 2708163.8199 | 1241204.4823 | 2708174.6906 | 1241207.2047 | 2708180.4383 | 1241208.125
46 | 2708396.3834 | 1241050.7373 | 2708180.4383 | 1241208.125
47 | 2708139.9606 | 1241232.6586 | 2708151.449 | 1241228.8761 | 2708154.9172 | 1241223.2348 | 2708159.7149 | 1241206.4757 | 2708161.3013 | 1241200.7668
48 | 2708399.1303 | 1241049.2605 | 2708396.3834 | 1241050.7373
49 | 2708139.9606 | 1241232.6586 | 2708151.449 | 1241228.8761 | 2708151.4302 | 1241240.2736 | 2708151.4808 | 1241252.4285 | 2708150.3568 | 1241267.2086 | 2708149.3008 | 1241273.6944
50 | 2708139.9606 | 1241232.6586 | 2708132.792 | 1241225.5669 | 2708080.2446 | 1241219.9166 | 2708066.1407 | 1241221.1497 | 2708053.7143 | 1241225.7827 | 2708027.824 | 1241239.6891 | 2707990.215 | 1241254.2607 | 2707974.3724 | 1241258.7871 | 2707951.1213 | 1241261.4997
51 | 2708149.3008 | 1241273.6944 | 2708163.0797 | 1241274.9353
52 | 2708149.3008 | 1241273.6944 | 2708150.0793 | 1241278.2789 | 2708153.0445 | 1241284.0486 | 2708152.9782 | 1241285.1853
53 | 2708149.3008 | 1241273.6944 | 2708139 | 1241279.1221 | 2708130.3421 | 1241291.2854
54 | 2707951.1213 | 1241261.4997 | 2707935.2054 | 1241254.6827 | 2707922.7432 | 1241244.2479
55 | 2707951.1213 | 1241261.4997 | 2707938.3429 | 1241266.7826 | 2707901.7878 | 1241283.3088
56 | 2708175.422 | 1241394.332 | 2708173.9538 | 1241361.635 | 2708172.2195 | 1241348.5042 | 2708165.7357 | 1241334.9754 | 2708153.736 | 1241314.1404 | 2708151.3546 | 1241305.8015 | 2708152.3181 | 1241296.5118 | 2708152.6483 | 1241290.8467 | 2708152.9782 | 1241285.1853
57 | 2708130.3421 | 1241291.2854 | 2708124.4138 | 1241299.6139
58 | 2708399.1303 | 1241049.2605 | 2708401.944 | 1241047.7478
59 | 2708406.6317 | 1241045.2277 | 2708401.944 | 1241047.7478
60 | 2708175.422 | 1241394.332 | 2708202.0777 | 1241401.3664
61 | 2707901.7878 | 1241283.3088 | 2707908.3984 | 1241301.5103
62 | 2707901.7878 | 1241283.3088 | 2707900.9797 | 1241279.2356
63 | 2707939.8943 | 1240458.7543 | 2707918.2692 | 1240482.9109
64 | 2707939.8943 | 1240458.7543 | 2707934.9485 | 1240449.2994
65 | 2707948.2435 | 1240478.3437 | 2707942.1919 | 1240463.422 | 2707939.8943 | 1240458.7543
66 | 2707933.7399 | 1240446.9888 | 2707934.9485 | 1240449.2994
67 | 2707948.2435 | 1240478.3437 | 2707960.2014 | 1240473.4743
68 | 2707976.4492 | 1240467.8707 | 2707971.1414 | 1240469.0195 | 2707960.2014 | 1240473.4743
69 | 2707933.7399 | 1240446.9888 | 2707950.9634 | 1240446.913 | 2707958.0592 | 1240446.4305 | 2707959.791 | 1240446.7925
70 | 2707933.7399 | 1240446.9888 | 2707931.2912 | 1240437.3256 | 2707931.8497 | 1240428.6623 | 2707934.2793 | 1240421.5008 | 2707935.3029 | 1240418.5848
71 | 2707935.5314 | 1240417.9335 | 2707935.3029 | 1240418.5848
72 | 2708438.3546 | 1240938.9932 | 2708444.8807 | 1240940.269 | 2708460.0452 | 1240942.628
73 | 2708438.3546 | 1240938.9932 | 2708439.6809 | 1240933.0461 | 2708439.492 | 1240927.6606 | 2708438.8835 | 1240925.9533
74 | 2708438.3546 | 1240938.9932 | 2708438.0827 | 1240940.2684
75 | 2708438.8835 | 1240925.9533 | 2708437.3698 | 1240921.706 | 2708428.7669 | 1240910.3289 | 2708425.0114 | 1240904.3556 | 2708425.0114 | 1240904.3556
76 | 2708437.8116 | 1240941.5398 | 2708438.0827 | 1240940.2684
77 | 2708425.0114 | 1240904.3556 | 2708424.0638 | 1240900.3018
78 | 2708437.8116 | 1240941.5398 | 2708434.5258 | 1240956.9495
79 | 2708448.0819 | 1240862.7998 | 2708457.5323 | 1240847.9359
80 | 2708430.7287 | 1240847.6932 | 2708448.0819 | 1240862.7998
81 | 2708430.7287 | 1240847.6932 | 2708439.0051 | 1240834.7342 | 2708438.2956 | 1240828.8611 | 2708436.1216 | 1240828.3715
82 | 2708422.9779 | 1240895.6564 | 2708424.0638 | 1240900.3018
83 | 2708432.8388 | 1240972.2242 | 2708432.3437 | 1240969.5185 | 2708433.1349 | 1240963.4727 | 2708434.5258 | 1240956.9495
84 | 2708411.2111 | 1240854.4805 | 2708419.7225 | 1240881.7301 | 2708420.6582 | 1240885.7329
85 | 2708406.8383 | 1240829.8317 | 2708406.6473 | 1240839.8695 | 2708411.2111 | 1240854.4805
86 | 2708420.6582 | 1240885.7329 | 2708421.7485 | 1240890.3972
87 | 2708398.075 | 1240823.5001 | 2708406.8383 | 1240829.8317
88 | 2708406.8383 | 1240829.8317 | 2708414.7673 | 1240826.7741 | 2708420.7326 | 1240826.825
89 | 2708422.85 | 1240895.1092 | 2708421.7485 | 1240890.3972
90 | 2708398.075 | 1240823.5001 | 2708406.3207 | 1240818.8359 | 2708412.6128 | 1240805.8296
91 | 2708398.075 | 1240823.5001 | 2708394.2649 | 1240827.9562 | 2708390.9636 | 1240831.4765 | 2708385.9119 | 1240834.3532 | 2708377.8479 | 1240838.1756 | 2708367.0744 | 1240842.1043 | 2708357.5299 | 1240842.5193 | 2708353.279 | 1240842.5417
92 | 2708398.075 | 1240823.5001 | 2708385.775 | 1240812.544
93 | 2708429.5886 | 1240826.9005 | 2708420.7326 | 1240826.825
94 | 2708422.9779 | 1240895.6564 | 2708422.85 | 1240895.1092
95 | 2708413.0404 | 1240804.9458 | 2708412.6128 | 1240805.8296
96 | 2708353.279 | 1240842.5417 | 2708321.0235 | 1240842.4975 | 2708304.9493 | 1240842.3341
97 | 2708353.279 | 1240842.5417 | 2708354.3996 | 1240859.0734
98 | 2708375.7225 | 1240798.8615 | 2708377.9968 | 1240804.3629 | 2708383.7492 | 1240810.7396 | 2708385.775 | 1240812.544
99 | 2708429.5886 | 1240826.9005 | 2708436.1216 | 1240828.3715
100 | 2708268.3498 | 1240841.5136 | 2708275.2637 | 1240841.8622 | 2708282.5651 | 1240842.1066 | 2708304.9493 | 1240842.3341
101 | 2708373.501 | 1240783.0196 | 2708373.6857 | 1240790.7068 | 2708375.7225 | 1240798.8615
102 | 2708432.8388 | 1240972.2242 | 2708433.4645 | 1240975.6438 | 2708434.6931 | 1240978.3129
103 | 2708436.1913 | 1240981.568 | 2708434.6931 | 1240978.3129
104 | 2708436.1913 | 1240981.568 | 2708439.3214 | 1240988.3681
105 | 2708442.8167 | 1240997.3206 | 2708441.073 | 1240992.1736 | 2708439.3214 | 1240988.3681
106 | 2708442.8167 | 1240997.3206 | 2708418.8915 | 1241007.8057
107 | 2708418.8915 | 1241007.8057 | 2708412.0197 | 1241010.8172
108 | 2708411.2004 | 1241011.1762 | 2708412.0197 | 1241010.8172
109 | 2708425.9185 | 1241034.8587 | 2708412.7831 | 1241041.9205
110 | 2708410.7029 | 1241043.0389 | 2708412.7831 | 1241041.9205
111 | 2708406.6317 | 1241045.2277 | 2708410.7029 | 1241043.0389
112 | 2708147.8154 | 1240911.338 | 2708171.9446 | 1240893.7305 | 2708200.0675 | 1240873.2047 | 2708213.7343 | 1240862.4008 | 2708230.624 | 1240849.0538 | 2708243.0056 | 1240844.0312 | 2708258.9473 | 1240842.0203 | 2708268.3498 | 1240841.5136
113 | 2708268.3498 | 1240841.5136 | 2708265.1007 | 1240851.2953 | 2708255.4293 | 1240867.2924
114 | 2708147.8154 | 1240911.338 | 2708132.7886 | 1240916.2793 | 2708131.5476 | 1240916.4212
115 | 2708147.8154 | 1240911.338 | 2708142.2091 | 1240903.1628 | 2708146.1211 | 1240882.6673
116 | 2708255.4293 | 1240867.2924 | 2708254.721 | 1240868.464 | 2708240.6028 | 1240883.6963 | 2708211.4331 | 1240904.8033 | 2708206.979 | 1240908.4405
117 | 2708373.501 | 1240783.0196 | 2708363.4039 | 1240781.2262
118 | 2708361.7277 | 1240780.9285 | 2708363.4039 | 1240781.2262
119 | 2708361.7277 | 1240780.9285 | 2708353.124 | 1240779.4003 | 2708353.124 | 1240779.4003
120 | 2708352.5179 | 1240779.6834 | 2708353.124 | 1240779.4003
121 | 2708352.5179 | 1240779.6834 | 2708348.9033 | 1240781.3716
122 | 2708347.2292 | 1240788.1506 | 2708347.0062 | 1240782.2576 | 2708348.9033 | 1240781.3716
123 | 2708090.8841 | 1240866.8306 | 2708100.9048 | 1240868.8836 | 2708110.9222 | 1240869.0773 | 2708114.1924 | 1240869.116
124 | 2708084.782 | 1240863.408 | 2708089.4066 | 1240866.5279 | 2708090.8841 | 1240866.8306
125 | 2707987.0722 | 1240893.0975 | 2707998.516 | 1240888.4687 | 2708016.9872 | 1240886.2586 | 2708035.0713 | 1240881.2171 | 2708054.2923 | 1240869.8135 | 2708065.829 | 1240866.3208 | 2708084.782 | 1240863.408
126 | 2707987.0722 | 1240893.0975 | 2708031.2216 | 1240902.8195 | 2708058.6303 | 1240909.0121 | 2708080.9286 | 1240915.4898
127 | 2708114.3076 | 1240766.3249 | 2708118.4894 | 1240765.1112 | 2708125.3874 | 1240758.8653 | 2708137.5084 | 1240740.8679
128 | 2708080.9286 | 1240915.4898 | 2708087.504 | 1240917.3999 | 2708115.9259 | 1240918.207 | 2708131.5476 | 1240916.4212
129 | 2708197.0818 | 1240916.5226 | 2708206.979 | 1240908.4405
130 | 2708197.0818 | 1240916.5226 | 2708190.4021 | 1240921.9773
131 | 2708187.764 | 1240924.1316 | 2708190.4021 | 1240921.9773

## bus_geodata
| x | y | coords
0 | 2708615.1769 | 1241356.3629
1 | 2708521.9221 | 1241413.324
2 | 2708632.2846 | 1241347.2938
3 | 2708498.9785 | 1241420.5573
4 | 2708621.1886 | 1241322.195
5 | 2708647.5095 | 1241340.5224
6 | 2708491.082 | 1241413.7193
7 | 2708618.7397 | 1241314.7689
8 | 2708333.6522 | 1241519.583
9 | 2708461.9398 | 1241067.4029
10 | 2708468.325 | 1241049.0829
11 | 2708461.2739 | 1241069.2819
12 | 2708449.9469 | 1241024.2943
13 | 2708454.4892 | 1241088.4293
14 | 2708449.3072 | 1241021.8742
15 | 2708431.5783 | 1241031.8159
16 | 2708481.9156 | 1240996.249
17 | 2708483.9791 | 1240972.9883
18 | 2708483.9293 | 1240958.8081
19 | 2708482.8823 | 1240947.4134
20 | 2708472.3027 | 1240946.381
21 | 2708435.893 | 1240716.1953
22 | 2708435.393 | 1240725.9874
23 | 2708416.7913 | 1240717.2092
24 | 2708397.7147 | 1240718.2218
25 | 2708378.4806 | 1240765.0519
26 | 2708395.0673 | 1240679.3318
27 | 2708415.5871 | 1240717.2731
28 | 2708375.5704 | 1240686.9153
29 | 2708379.1831 | 1240423.6056
30 | 2708356.9891 | 1240423.7026
31 | 2708369.4267 | 1240413.5995
32 | 2708165.1667 | 1240566.9726
33 | 2708370.2319 | 1240385.9412
34 | 2708130.9799 | 1240587.7834
35 | 2708137.467 | 1240588.3382
36 | 2708133.3396 | 1240628.094
37 | 2708149.0651 | 1240589.3302
38 | 2708134.0411 | 1240850.0612
39 | 2708152.9344 | 1240583.9574
40 | 2707979.2995 | 1240468.3539
41 | 2708180.4383 | 1241208.125
42 | 2708161.3013 | 1241200.7668
43 | 2708396.3834 | 1241050.7373
44 | 2708139.9606 | 1241232.6586
45 | 2708149.3008 | 1241273.6944
46 | 2707951.1213 | 1241261.4997
47 | 2708163.0797 | 1241274.9353
48 | 2708152.9782 | 1241285.1853
49 | 2708130.3421 | 1241291.2854
50 | 2708399.1303 | 1241049.2605
51 | 2708401.944 | 1241047.7478
52 | 2708124.4138 | 1241299.6139
53 | 2708175.422 | 1241394.332
54 | 2708202.0777 | 1241401.3664
55 | 2707908.3984 | 1241301.5103
56 | 2707901.7878 | 1241283.3088
57 | 2707900.9797 | 1241279.2356
58 | 2707922.7432 | 1241244.2479
59 | 2707918.2692 | 1240482.9109
60 | 2707939.8943 | 1240458.7543
61 | 2707934.9485 | 1240449.2994
62 | 2707948.2435 | 1240478.3437
63 | 2707960.2014 | 1240473.4743
64 | 2707933.7399 | 1240446.9888
65 | 2707976.4492 | 1240467.8707
66 | 2707959.791 | 1240446.7925
67 | 2707935.3029 | 1240418.5848
68 | 2707935.5314 | 1240417.9335
69 | 2708460.0452 | 1240942.628
70 | 2708438.3546 | 1240938.9932
71 | 2708438.8835 | 1240925.9533
72 | 2708438.0827 | 1240940.2684
73 | 2708425.0114 | 1240904.3556
74 | 2708437.8116 | 1240941.5398
75 | 2708448.0819 | 1240862.7998
76 | 2708457.5323 | 1240847.9359
77 | 2708430.7287 | 1240847.6932
78 | 2708424.0638 | 1240900.3019
79 | 2708434.5258 | 1240956.9495
80 | 2708411.2111 | 1240854.4805
81 | 2708420.6582 | 1240885.7329
82 | 2708406.8383 | 1240829.8317
83 | 2708421.7485 | 1240890.3972
84 | 2708398.075 | 1240823.5001
85 | 2708420.7326 | 1240826.825
86 | 2708422.85 | 1240895.1092
87 | 2708412.6128 | 1240805.8296
88 | 2708353.279 | 1240842.5417
89 | 2708385.775 | 1240812.544
90 | 2708429.5886 | 1240826.9005
91 | 2708436.1216 | 1240828.3715
92 | 2708422.9779 | 1240895.6565
93 | 2708413.0404 | 1240804.9458
94 | 2708304.9493 | 1240842.3341
95 | 2708354.3996 | 1240859.0734
96 | 2708375.7225 | 1240798.8615
97 | 2708432.8388 | 1240972.2242
98 | 2708434.6931 | 1240978.3129
99 | 2708436.1913 | 1240981.568
100 | 2708439.3214 | 1240988.3681
101 | 2708442.8167 | 1240997.3206
102 | 2708418.8915 | 1241007.8057
103 | 2708412.0197 | 1241010.8172
104 | 2708411.2004 | 1241011.1762
105 | 2708425.9185 | 1241034.8587
106 | 2708412.7831 | 1241041.9205
107 | 2708410.7029 | 1241043.0389
108 | 2708406.6317 | 1241045.2277
109 | 2708268.3498 | 1240841.5136
110 | 2708147.8154 | 1240911.338
111 | 2708255.4293 | 1240867.2924
112 | 2708396.5771 | 1240780.0608
113 | 2708373.501 | 1240783.0196
114 | 2708361.7277 | 1240780.9285
115 | 2708363.4039 | 1240781.2262
116 | 2708353.124 | 1240779.4003
117 | 2708352.5179 | 1240779.6834
118 | 2708348.9033 | 1240781.3716
119 | 2708347.2292 | 1240788.1506
120 | 2708090.8841 | 1240866.8306
121 | 2708114.1924 | 1240869.116
122 | 2708084.782 | 1240863.408
123 | 2707987.0722 | 1240893.0975
124 | 2708114.3076 | 1240766.3249
125 | 2708080.9286 | 1240915.4898
126 | 2708131.5476 | 1240916.4212
127 | 2708206.979 | 1240908.4405
128 | 2708197.0818 | 1240916.5225
129 | 2708190.4021 | 1240921.9773
130 | 2708146.1211 | 1240882.6673
131 | 2708187.764 | 1240924.1316
132 | 2708137.5084 | 1240740.8679
133 | 2708438.3546 | 1240938.9932

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9838 | -0.31293 | 0.0022608 | 0.00056661
1 | 0.9846 | -0.29733 | 0.00080298 | 0.00020125
2 | 0.9837 | -0.31491 | 0 | 0
3 | 0.9848 | -0.29335 | 0.00078294 | 0.00019622
4 | 0.98361 | -0.31661 | 0.00070144 | 0.0001758
5 | 0.98366 | -0.31557 | 0.0022217 | 0.0005568
6 | 0.9849 | -0.29153 | 0.00057176 | 0.0001433
7 | 0.98359 | -0.31699 | 0.0027319 | 0.00068469
8 | 0.98666 | -0.25722 | 0 | 0
9 | 0.99595 | -0.077724 | 0 | 0
10 | 0.99597 | -0.077248 | 0 | 0
11 | 0.99594 | -0.077772 | 0.00078923 | 0.0001978
12 | 0.99601 | -0.076445 | 0 | 0
13 | 0.99593 | -0.077988 | 0.00060469 | 0.00015155
14 | 0.99607 | -0.075422 | 0.00083006 | 0.00020803
15 | 0.99561 | -0.084126 | 0.0010988 | 0.00027539
16 | 0.99806 | -0.037104 | 0.0012611 | 0.00031605
17 | 0.99809 | -0.036588 | 0.0013452 | 0.00033714
18 | 0.99812 | -0.035941 | 0 | 0
19 | 0.99815 | -0.035419 | 0 | 0
20 | 0.99818 | -0.034928 | 0.0005599 | 0.00014033
21 | 0.9928 | -0.13852 | 0 | 0
22 | 0.99278 | -0.13882 | 0.0017395 | 0.00043596
23 | 0.99283 | -0.13793 | 0.00050375 | 0.00012625
24 | 0.99287 | -0.13712 | 0 | 0
25 | 0.993 | -0.13465 | 0 | 0
26 | 0.99286 | -0.13736 | 0 | 0
27 | 0.99283 | -0.13788 | 0.00016886 | 4.2319e-05
28 | 0.99285 | -0.13749 | 0.00034402 | 8.6219e-05
29 | 0.98623 | -0.26657 | 0.00044153 | 0.00011066
30 | 0.98624 | -0.26638 | 0 | 0
31 | 0.98624 | -0.26647 | 0 | 0
32 | 0.98641 | -0.26314 | 0 | 0
33 | 0.98623 | -0.26663 | 0.00030776 | 7.7133e-05
34 | 0.98646 | -0.26199 | 7.7951e-05 | 1.9536e-05
35 | 0.98647 | -0.26198 | 8.7616e-05 | 2.1959e-05
36 | 0.98657 | -0.25992 | 0.0016975 | 0.00042544
37 | 0.98647 | -0.26195 | 0 | 0
38 | 0.98745 | -0.24262 | 0.0012459 | 0.00031224
39 | 0.98645 | -0.26224 | 8.8391e-05 | 2.2153e-05
40 | 0.98603 | -0.27054 | 0.00039011 | 9.7771e-05
41 | 0.99127 | -0.16777 | 0.00069592 | 0.00017441
42 | 0.99099 | -0.17321 | 0 | 0
43 | 0.99493 | -0.097248 | 0.00076138 | 0.00019082
44 | 0.99044 | -0.18384 | 0 | 0
45 | 0.98982 | -0.19575 | 0 | 0
46 | 0.98999 | -0.19263 | 0 | 0
47 | 0.98982 | -0.19586 | 0.0004263 | 0.00010684
48 | 0.98971 | -0.19804 | 0.0001491 | 3.7368e-05
49 | 0.9898 | -0.19615 | 0.00066049 | 0.00016553
50 | 0.99497 | -0.096386 | 0.0011494 | 0.00028808
51 | 0.99502 | -0.095438 | 0.00048685 | 0.00012202
52 | 0.9898 | -0.19619 | 0.00018644 | 4.6727e-05
53 | 0.98862 | -0.21907 | 0 | 0
54 | 0.98836 | -0.22414 | 0.00022447 | 5.6257e-05
55 | 0.98987 | -0.1949 | 0.00053819 | 0.00013488
56 | 0.98988 | -0.19471 | 0 | 0
57 | 0.98987 | -0.19483 | 0.0016344 | 0.00040962
58 | 0.98998 | -0.19281 | 0.00030043 | 7.5295e-05
59 | 0.98597 | -0.27162 | 0.00022047 | 5.5254e-05
60 | 0.98598 | -0.27149 | 0 | 0
61 | 0.98597 | -0.27161 | 0.00011253 | 2.8203e-05
62 | 0.986 | -0.27118 | 0 | 0
63 | 0.98601 | -0.27098 | 0.00040552 | 0.00010163
64 | 0.98597 | -0.27164 | 0 | 0
65 | 0.98603 | -0.2706 | 0 | 0
66 | 0.98597 | -0.27173 | 0.00020389 | 5.11e-05
67 | 0.98597 | -0.27179 | 0.0001455 | 3.6466e-05
68 | 0.98597 | -0.27179 | 0.00014811 | 3.7121e-05
69 | 0.99821 | -0.034216 | 0.0026318 | 0.00065959
70 | 0.99833 | -0.031984 | 0 | 0
71 | 0.99883 | -0.022431 | 0.001276 | 0.00031979
72 | 0.99829 | -0.032789 | 0.00099323 | 0.00024893
73 | 0.99983 | -0.0033241 | 0.0034179 | 0.00085661
74 | 0.99825 | -0.033569 | 0.0018798 | 0.00047113
75 | 0.99208 | -0.15242 | 0 | 0
76 | 0.99183 | -0.15728 | 0.015573 | 0.0039029
77 | 0.9924 | -0.14609 | 0 | 0
78 | 1 | 0 | -0.18352 | -0.045909
79 | 0.99778 | -0.042512 | 0.00076844 | 0.00019259
80 | 0.99572 | -0.082073 | 0.0062364 | 0.001563
81 | 0.9985 | -0.028767 | 0.0021587 | 0.00054101
82 | 0.99371 | -0.12086 | 0 | 0
83 | 0.99891 | -0.020793 | 0.0021424 | 0.00053695
84 | 0.99327 | -0.12938 | 0 | 0
85 | 0.99315 | -0.13162 | 0.013068 | 0.0032752
86 | 0.99934 | -0.012563 | 0.036419 | 0.0091276
87 | 0.99296 | -0.13526 | 0.0051391 | 0.001288
88 | 0.99214 | -0.15114 | 0 | 0
89 | 0.99317 | -0.13128 | 0.0024838 | 0.0006225
90 | 0.99292 | -0.13617 | 0 | 0
91 | 0.99274 | -0.13961 | 0.013485 | 0.0033796
92 | 0.99941 | -0.011251 | 0.0014029 | 0.00035161
93 | 0.99296 | -0.13541 | 0.0087614 | 0.0021958
94 | 0.99126 | -0.16823 | 0.0019386 | 0.00048585
95 | 0.99208 | -0.15242 | 0.0043606 | 0.0010929
96 | 0.99311 | -0.13251 | 0 | 0
97 | 0.99733 | -0.051119 | 0.0011616 | 0.00029112
98 | 0.99715 | -0.054548 | 0.0013607 | 0.00034102
99 | 0.99706 | -0.056379 | 0.00098171 | 0.00024604
100 | 0.99686 | -0.060076 | 0.00091306 | 0.00022884
101 | 0.99662 | -0.064676 | 0 | 0
102 | 0.99655 | -0.066118 | 0.0017041 | 0.00042708
103 | 0.99654 | -0.066308 | 0.00068948 | 0.0001728
104 | 0.99654 | -0.06632 | 0.00075277 | 0.00018866
105 | 0.99549 | -0.086473 | 0.0012387 | 0.00031045
106 | 0.99522 | -0.091598 | 0.00098954 | 0.000248
107 | 0.99518 | -0.092369 | 0.00077728 | 0.00019481
108 | 0.99511 | -0.093814 | 0.00043046 | 0.00010788
109 | 0.99066 | -0.17993 | 0 | 0
110 | 0.98953 | -0.20199 | 0 | 0
111 | 0.99041 | -0.18472 | 0.007277 | 0.0018238
112 | 0.99299 | -0.13476 | 0.0002493 | 6.2482e-05
113 | 0.99305 | -0.13366 | 0 | 0
114 | 0.99304 | -0.13386 | 0.00025147 | 6.3023e-05
115 | 0.99304 | -0.13384 | 0.00030705 | 7.6954e-05
116 | 0.99303 | -0.13394 | 9.1788e-05 | 2.3004e-05
117 | 0.99303 | -0.13394 | 0.00010746 | 2.6932e-05
118 | 0.99303 | -0.13396 | 0.00010737 | 2.6911e-05
119 | 0.99303 | -0.13398 | 0.00015612 | 3.9128e-05
120 | 0.98771 | -0.2375 | 0.00089983 | 0.00022552
121 | 0.9877 | -0.23772 | 0.00053761 | 0.00013474
122 | 0.98772 | -0.23731 | 0 | 0
123 | 0.9884 | -0.224 | 0 | 0
124 | 0.98744 | -0.24292 | 0 | 0
125 | 0.98904 | -0.21153 | 0.00053112 | 0.00013311
126 | 0.9894 | -0.20447 | 0.00036723 | 9.2038e-05
127 | 0.9903 | -0.18699 | 0.00021058 | 5.2775e-05
128 | 0.99028 | -0.1874 | 0.00038106 | 9.5502e-05
129 | 0.99026 | -0.18762 | 0.00023311 | 5.8424e-05
130 | 0.98951 | -0.20231 | 0.00057633 | 0.00014444
131 | 0.99026 | -0.18769 | 0.0011797 | 0.00029567
132 | 0.98743 | -0.24303 | 0.00018791 | 4.7095e-05
133 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0079168 | -0.0019836 | 0.0079227 | 0.001986 | 5.8861e-06 | 2.3758e-06 | 0.011974 | 0.011974 | 0.011974 | 0.9838 | -0.31293 | 0.9846 | -0.29733 | 3.2896
1 | 0.005656 | 0.001417 | -0.0056555 | -0.0014169 | 5.3138e-07 | 9.4244e-08 | 0.0085546 | 0.0085547 | 0.0085547 | 0.9838 | -0.31293 | 0.9837 | -0.31491 | 2.3502
2 | -0.0087257 | -0.0021872 | 0.0087273 | 0.0021879 | 1.6563e-06 | 7.3695e-07 | 0.013187 | 0.013187 | 0.013187 | 0.9846 | -0.29733 | 0.9848 | -0.29335 | 3.6228
3 | 0.0034337 | 0.00086025 | -0.0034334 | -0.00086042 | 2.7817e-07 | -1.71e-07 | 0.005194 | 0.0051941 | 0.0051941 | 0.9837 | -0.31491 | 0.98361 | -0.31661 | 1.4269
4 | 0.0022217 | 0.00055664 | -0.0022217 | -0.0005568 | 7.0575e-08 | -1.6636e-07 | 0.0033607 | 0.0033608 | 0.0033608 | 0.9837 | -0.31491 | 0.98366 | -0.31557 | 0.92329
5 | -0.0095103 | -0.0023842 | 0.0095111 | 0.0023846 | 8.2318e-07 | 3.9156e-07 | 0.01437 | 0.01437 | 0.01437 | 0.9848 | -0.29335 | 0.9849 | -0.29153 | 3.9478
6 | 0.002732 | 0.00068462 | -0.0027319 | -0.00068469 | 5.0088e-08 | -6.7193e-08 | 0.004133 | 0.004133 | 0.004133 | 0.98361 | -0.31661 | 0.98359 | -0.31699 | 1.1354
7 | -0.010083 | -0.0025279 | 0.010099 | 0.002536 | 1.6509e-05 | 8.1472e-06 | 0.015234 | 0.015233 | 0.015234 | 0.9849 | -0.29153 | 0.98666 | -0.25722 | 4.1851
8 | -0.010099 | -0.002536 | 0.010115 | 0.0025439 | 1.5961e-05 | 7.8683e-06 | 0.015233 | 0.015232 | 0.015233 | 0.98666 | -0.25722 | 0.98836 | -0.22414 | 4.1849
9 | -0.0013939 | -0.00034906 | 0.001394 | 0.00034883 | 3.1546e-08 | -2.3225e-07 | 0.0020825 | 0.0020824 | 0.0020825 | 0.99595 | -0.077724 | 0.99597 | -0.077248 | 0.57212
10 | 0.0013939 | 0.00034906 | -0.0013939 | -0.00034909 | 3.2422e-09 | -2.3867e-08 | 0.0020825 | 0.0020825 | 0.0020825 | 0.99595 | -0.077724 | 0.99594 | -0.077772 | 0.57212
11 | -0.001394 | -0.00034883 | 0.001394 | 0.00034844 | 5.322e-08 | -3.9188e-07 | 0.0020824 | 0.0020823 | 0.0020824 | 0.99597 | -0.077248 | 0.99601 | -0.076445 | 0.5721
12 | 0.00060469 | 0.00015129 | -0.00060469 | -0.00015155 | 6.2172e-09 | -2.6036e-07 | 0.00090336 | 0.00090346 | 0.00090346 | 0.99594 | -0.077772 | 0.99593 | -0.077988 | 0.2482
13 | -0.023361 | -0.0058905 | 0.023362 | 0.0058912 | 1.1442e-06 | 6.9973e-07 | 0.034913 | 0.034913 | 0.034913 | 0.99601 | -0.076445 | 0.99607 | -0.075422 | 9.5916
14 | 0.021967 | 0.0055421 | -0.021959 | -0.0055372 | 8.0751e-06 | 4.9082e-06 | 0.032831 | 0.032831 | 0.032831 | 0.99601 | -0.076445 | 0.99561 | -0.084126 | 9.0196
15 | -0.024192 | -0.0060993 | 0.024205 | 0.0061069 | 1.2448e-05 | 7.6362e-06 | 0.036153 | 0.036153 | 0.036153 | 0.99607 | -0.075422 | 0.99662 | -0.064676 | 9.9323
16 | 0.02086 | 0.0052618 | -0.020858 | -0.0052604 | 2.344e-06 | 1.4166e-06 | 0.031189 | 0.031189 | 0.031189 | 0.99561 | -0.084126 | 0.99549 | -0.086473 | 8.5684
17 | -0.0012611 | -0.00031605 | 0.0012611 | 0.00031577 | 3.0986e-08 | -2.8567e-07 | 0.0018801 | 0.00188 | 0.0018801 | 0.99806 | -0.037104 | 0.99809 | -0.036588 | 0.51652
18 | -0.0026063 | -0.00065291 | 0.0026064 | 0.00065278 | 8.0282e-08 | -1.3395e-07 | 0.0038856 | 0.0038855 | 0.0038856 | 0.99809 | -0.036588 | 0.99812 | -0.035941 | 1.0675
19 | -0.0026064 | -0.00065278 | 0.0026065 | 0.00065267 | 6.4789e-08 | -1.0811e-07 | 0.0038855 | 0.0038855 | 0.0038855 | 0.99812 | -0.035941 | 0.99815 | -0.035419 | 1.0674
20 | -0.0026065 | -0.00065267 | 0.0026065 | 0.00065257 | 6.0943e-08 | -1.0171e-07 | 0.0038855 | 0.0038854 | 0.0038855 | 0.99815 | -0.035419 | 0.99818 | -0.034928 | 1.0674
21 | -0.0031664 | -0.0007929 | 0.0031665 | 0.0007928 | 1.0739e-07 | -9.9296e-08 | 0.0047201 | 0.00472 | 0.0047201 | 0.99818 | -0.034928 | 0.99821 | -0.034216 | 1.2967
22 | 0.0017395 | 0.00043585 | -0.0017395 | -0.00043596 | 2.4994e-08 | -1.1079e-07 | 0.0026072 | 0.0026072 | 0.0026072 | 0.9928 | -0.13852 | 0.99278 | -0.13882 | 0.71627
23 | -0.0017395 | -0.00043585 | 0.0017396 | 0.00043563 | 4.8758e-08 | -2.1615e-07 | 0.0026072 | 0.0026071 | 0.0026072 | 0.9928 | -0.13852 | 0.99283 | -0.13793 | 0.71626
24 | -0.0022433 | -0.00056188 | 0.0022433 | 0.00056187 | 5.1118e-09 | -1.2323e-08 | 0.0033621 | 0.0033621 | 0.0033621 | 0.99283 | -0.13793 | 0.99283 | -0.13788 | 0.92365
25 | -0.0027563 | -0.00068946 | 0.0027566 | 0.00068901 | 3.2382e-07 | -4.4748e-07 | 0.0041304 | 0.0041302 | 0.0041304 | 0.99287 | -0.13712 | 0.993 | -0.13465 | 1.1347
26 | 0.00034402 | 8.5442e-05 | -0.00034402 | -8.595e-05 | 3.93e-09 | -5.0769e-07 | 0.00051532 | 0.0005155 | 0.0005155 | 0.99287 | -0.13712 | 0.99286 | -0.13736 | 0.14162
27 | 0.0024123 | 0.00060402 | -0.0024122 | -0.00060419 | 8.7715e-08 | -1.7532e-07 | 0.0036151 | 0.0036152 | 0.0036152 | 0.99287 | -0.13712 | 0.99283 | -0.13788 | 0.99318
28 | 0.00024931 | 6.2161e-05 | -0.0002493 | -6.2482e-05 | 1.2991e-09 | -3.2035e-07 | 0.00037347 | 0.00037359 | 0.00037359 | 0.993 | -0.13465 | 0.99299 | -0.13476 | 0.10263
29 | -0.0030059 | -0.00075117 | 0.0030061 | 0.00075102 | 1.4181e-07 | -1.5044e-07 | 0.0045037 | 0.0045036 | 0.0045037 | 0.993 | -0.13465 | 0.99305 | -0.13366 | 1.2373
30 | 0.00034402 | 8.595e-05 | -0.00034402 | -8.6219e-05 | 2.0851e-09 | -2.6921e-07 | 0.0005155 | 0.00051559 | 0.00051559 | 0.99286 | -0.13736 | 0.99285 | -0.13749 | 0.14165
31 | -0.00044153 | -0.00011066 | 0.00044153 | 0.00011037 | 3.8305e-09 | -2.9131e-07 | 0.00066618 | 0.00066607 | 0.00066618 | 0.98623 | -0.26657 | 0.98624 | -0.26638 | 0.18302
32 | 0.00030777 | 7.657e-05 | -0.00030777 | -7.6774e-05 | 1.2927e-09 | -2.0332e-07 | 0.00046415 | 0.00046422 | 0.00046422 | 0.98624 | -0.26638 | 0.98624 | -0.26647 | 0.12753
33 | -0.0007493 | -0.00018694 | 0.00074942 | 0.00018395 | 1.1458e-07 | -2.9824e-06 | 0.0011302 | 0.0011291 | 0.0011302 | 0.98624 | -0.26638 | 0.98641 | -0.26314 | 0.3105
34 | 0.00030777 | 7.6774e-05 | -0.00030776 | -7.7133e-05 | 2.2858e-09 | -3.5936e-07 | 0.00046422 | 0.00046435 | 0.00046435 | 0.98624 | -0.26647 | 0.98623 | -0.26663 | 0.12757
35 | 0.0016268 | 0.00040274 | -0.0016262 | -0.00040559 | 5.6898e-07 | -2.8539e-06 | 0.0024522 | 0.0024534 | 0.0024534 | 0.98641 | -0.26314 | 0.98603 | -0.27054 | 0.674
36 | -0.0023762 | -0.00058669 | 0.0023763 | 0.00058649 | 1.0067e-07 | -2.0277e-07 | 0.0035814 | 0.0035813 | 0.0035814 | 0.98641 | -0.26314 | 0.98645 | -0.26224 | 0.9839
37 | -7.7951e-05 | -1.9536e-05 | 7.7951e-05 | 1.9453e-05 | 3.3746e-11 | -8.3099e-08 | 0.00011758 | 0.00011755 | 0.00011758 | 0.98646 | -0.26199 | 0.98647 | -0.26198 | 0.032303
38 | -0.00016557 | -4.1412e-05 | 0.00016557 | 4.1263e-05 | 2.7216e-10 | -1.4843e-07 | 0.00024972 | 0.00024966 | 0.00024972 | 0.98647 | -0.26198 | 0.98647 | -0.26195 | 0.068604
39 | 0.0026305 | 0.00064946 | -0.0026303 | -0.00064984 | 2.5094e-07 | -3.831e-07 | 0.0039641 | 0.0039643 | 0.0039643 | 0.98657 | -0.25992 | 0.98647 | -0.26195 | 1.0891
40 | -0.004328 | -0.0010749 | 0.0043316 | 0.0010743 | 3.5427e-06 | -5.6958e-07 | 0.0065244 | 0.0065234 | 0.0065244 | 0.98657 | -0.25992 | 0.98745 | -0.24262 | 1.7924
41 | 0.0024647 | 0.00060858 | -0.0024647 | -0.00060864 | 3.426e-08 | -6.2601e-08 | 0.0037146 | 0.0037146 | 0.0037146 | 0.98647 | -0.26195 | 0.98645 | -0.26224 | 1.0205
42 | 0.00018791 | 4.5544e-05 | -0.00018791 | -4.6643e-05 | 2.5805e-09 | -1.0988e-06 | 0.00028263 | 0.00028301 | 0.00028301 | 0.98745 | -0.24262 | 0.98744 | -0.24292 | 0.077751
43 | -0.0057654 | -0.0014321 | 0.0057668 | 0.0014324 | 1.4482e-06 | 2.7147e-07 | 0.0086834 | 0.0086832 | 0.0086834 | 0.98745 | -0.24262 | 0.98772 | -0.23731 | 2.3856
44 | 0.0012361 | 0.00030782 | -0.0012361 | -0.00030785 | 3.7695e-09 | -3.4463e-08 | 0.0018647 | 0.0018647 | 0.0018647 | 0.98603 | -0.27054 | 0.98603 | -0.2706 | 0.51227
45 | 0.014268 | 0.0035893 | -0.014264 | -0.0035872 | 3.703e-06 | 2.0926e-06 | 0.021423 | 0.021423 | 0.021423 | 0.99127 | -0.16777 | 0.99099 | -0.17321 | 5.8854
46 | -0.014964 | -0.0037638 | 0.015015 | 0.0037927 | 5.058e-05 | 2.8914e-05 | 0.022468 | 0.022466 | 0.022468 | 0.99127 | -0.16777 | 0.99493 | -0.097248 | 6.1724
47 | 0.014264 | 0.0035872 | -0.014257 | -0.0035832 | 7.2413e-06 | 4.0927e-06 | 0.021423 | 0.021423 | 0.021423 | 0.99099 | -0.17321 | 0.99044 | -0.18384 | 5.8855
48 | -0.015776 | -0.0039835 | 0.015777 | 0.0039839 | 6.5165e-07 | 3.7655e-07 | 0.023605 | 0.023605 | 0.023605 | 0.99493 | -0.097248 | 0.99497 | -0.096386 | 6.4849
49 | 0.011783 | 0.0029665 | -0.011776 | -0.002963 | 6.707e-06 | 3.5588e-06 | 0.017707 | 0.017707 | 0.017707 | 0.99044 | -0.18384 | 0.98982 | -0.19575 | 4.8647
50 | 0.0024743 | 0.00061661 | -0.0024732 | -0.00061852 | 1.033e-06 | -1.9044e-06 | 0.0037161 | 0.003717 | 0.003717 | 0.99044 | -0.18384 | 0.98999 | -0.19263 | 1.0211
51 | 0.0004263 | 0.00010666 | -0.0004263 | -0.00010684 | 2.1243e-09 | -1.7594e-07 | 0.0006408 | 0.00064086 | 0.00064086 | 0.98982 | -0.19575 | 0.98982 | -0.19586 | 0.17606
52 | 0.010503 | 0.0026445 | -0.010502 | -0.0026439 | 1.1483e-06 | 5.7712e-07 | 0.015794 | 0.015794 | 0.015794 | 0.98982 | -0.19575 | 0.98971 | -0.19804 | 4.3389
53 | 0.00084695 | 0.0002118 | -0.00084693 | -0.00021213 | 1.6152e-08 | -3.3122e-07 | 0.0012731 | 0.0012732 | 0.0012732 | 0.98982 | -0.19575 | 0.9898 | -0.19615 | 0.34978
54 | 0.00030043 | 7.4865e-05 | -0.00030043 | -7.5295e-05 | 2.5661e-09 | -4.2997e-07 | 0.00045142 | 0.00045157 | 0.00045157 | 0.98999 | -0.19263 | 0.98998 | -0.19281 | 0.12406
55 | 0.0021728 | 0.00054365 | -0.0021726 | -0.00054421 | 2.1522e-07 | -5.5412e-07 | 0.0032656 | 0.0032658 | 0.0032658 | 0.98999 | -0.19263 | 0.98988 | -0.19471 | 0.8972
56 | 0.010353 | 0.0026066 | -0.010342 | -0.0026014 | 1.0398e-05 | 5.1863e-06 | 0.015569 | 0.01557 | 0.01557 | 0.98971 | -0.19804 | 0.98862 | -0.21907 | 4.2775
57 | 0.00018644 | 4.6595e-05 | -0.00018644 | -4.6727e-05 | 3.0113e-10 | -1.312e-07 | 0.00028024 | 0.00028029 | 0.00028029 | 0.9898 | -0.19615 | 0.9898 | -0.19619 | 0.077002
58 | -0.016926 | -0.0042719 | 0.016927 | 0.0042724 | 7.6826e-07 | 4.502e-07 | 0.025324 | 0.025324 | 0.025324 | 0.99497 | -0.096386 | 0.99502 | -0.095438 | 6.9572
59 | -0.017414 | -0.0043944 | 0.017415 | 0.0043952 | 1.3546e-06 | 7.978e-07 | 0.026052 | 0.026052 | 0.026052 | 0.99502 | -0.095438 | 0.99511 | -0.093814 | 7.1572
60 | 0.010342 | 0.0026014 | -0.01034 | -0.0026001 | 2.5062e-06 | 1.2506e-06 | 0.01557 | 0.01557 | 0.01557 | 0.98862 | -0.21907 | 0.98836 | -0.22414 | 4.2775
61 | -0.00053819 | -0.00013488 | 0.00053819 | 0.00013464 | 4.7525e-09 | -2.4589e-07 | 0.00080903 | 0.00080894 | 0.00080903 | 0.98987 | -0.1949 | 0.98988 | -0.19471 | 0.22226
62 | 0.0016344 | 0.00040957 | -0.0016344 | -0.00040962 | 9.3997e-09 | -4.7366e-08 | 0.0024569 | 0.0024569 | 0.0024569 | 0.98988 | -0.19471 | 0.98987 | -0.19483 | 0.67497
63 | -0.00022047 | -5.5254e-05 | 0.00022047 | 5.4842e-05 | 1.3454e-09 | -4.1265e-07 | 0.00033272 | 0.00033258 | 0.00033272 | 0.98597 | -0.27162 | 0.98598 | -0.27149 | 0.091408
64 | 0.00061004 | 0.00015201 | -0.00061004 | -0.00015214 | 3.3895e-09 | -1.3392e-07 | 0.00092035 | 0.0009204 | 0.0009204 | 0.98598 | -0.27149 | 0.98597 | -0.27161 | 0.25286
65 | -0.00083051 | -0.00020685 | 0.00083052 | 0.00020659 | 1.2536e-08 | -2.636e-07 | 0.0012529 | 0.0012528 | 0.0012529 | 0.98598 | -0.27149 | 0.986 | -0.27118 | 0.34421
66 | 0.00049751 | 0.00012394 | -0.00049751 | -0.00012397 | 5.5082e-10 | -3.2904e-08 | 0.00075057 | 0.00075058 | 0.00075058 | 0.98597 | -0.27161 | 0.98597 | -0.27164 | 0.2062
67 | -0.00083052 | -0.00020659 | 0.00083053 | 0.00020643 | 7.5992e-09 | -1.5982e-07 | 0.0012528 | 0.0012528 | 0.0012528 | 0.986 | -0.27118 | 0.98601 | -0.27098 | 0.34418
68 | -0.0012361 | -0.00030806 | 0.0012361 | 0.00030785 | 2.2484e-08 | -2.0554e-07 | 0.0018648 | 0.0018647 | 0.0018648 | 0.98601 | -0.27098 | 0.98603 | -0.2706 | 0.51229
69 | 0.00020389 | 5.0768e-05 | -0.00020389 | -5.11e-05 | 9.2657e-10 | -3.3234e-07 | 0.00030759 | 0.00030771 | 0.00030771 | 0.98597 | -0.27164 | 0.98597 | -0.27173 | 0.084536
70 | 0.00029362 | 7.3205e-05 | -0.00029361 | -7.3578e-05 | 2.157e-09 | -3.7234e-07 | 0.00044299 | 0.00044312 | 0.00044312 | 0.98597 | -0.27164 | 0.98597 | -0.27179 | 0.12174
71 | 0.00014811 | 3.7112e-05 | -0.00014811 | -3.7121e-05 | 1.2877e-11 | -8.7937e-09 | 0.00022353 | 0.00022353 | 0.00022353 | 0.98597 | -0.27179 | 0.98597 | -0.27179 | 0.06141
72 | -0.0057983 | -0.0014524 | 0.0057989 | 0.0014525 | 6.1621e-07 | 1.0679e-07 | 0.0086432 | 0.0086431 | 0.0086432 | 0.99821 | -0.034216 | 0.99833 | -0.031984 | 2.3745
73 | -0.041257 | -0.010397 | 0.041276 | 0.010409 | 1.8865e-05 | 1.19e-05 | 0.061514 | 0.061514 | 0.061514 | 0.99833 | -0.031984 | 0.99883 | -0.022431 | 16.8995
74 | 0.035458 | 0.0089449 | -0.035457 | -0.0089441 | 1.3668e-06 | 8.5772e-07 | 0.052871 | 0.052871 | 0.052871 | 0.99833 | -0.031984 | 0.99829 | -0.032789 | 14.525
75 | -0.042552 | -0.010729 | 0.042591 | 0.010754 | 3.895e-05 | 2.459e-05 | 0.063415 | 0.063415 | 0.063415 | 0.99883 | -0.022431 | 0.99983 | -0.0033241 | 17.4217
76 | 0.034464 | 0.0086951 | -0.034462 | -0.0086943 | 1.2874e-06 | 8.0695e-07 | 0.051391 | 0.051391 | 0.051391 | 0.99829 | -0.032789 | 0.99825 | -0.033569 | 14.1183
77 | -0.046009 | -0.01161 | 0.046016 | 0.011615 | 7.3255e-06 | 4.6337e-06 | 0.068502 | 0.068502 | 0.068502 | 0.99983 | -0.0033241 | 1 | 0 | 18.8191
78 | 0.032582 | 0.0082232 | -0.032568 | -0.0082145 | 1.3949e-05 | 8.7216e-06 | 0.048588 | 0.048589 | 0.048589 | 0.99825 | -0.033569 | 0.99778 | -0.042512 | 13.3485
79 | 0.015576 | 0.0039049 | -0.015573 | -0.0039029 | 3.6054e-06 | 2.0801e-06 | 0.023363 | 0.023363 | 0.023363 | 0.99208 | -0.15242 | 0.99183 | -0.15728 | 6.4185
80 | -0.015576 | -0.0039049 | 0.015581 | 0.0039076 | 4.7015e-06 | 2.7123e-06 | 0.023363 | 0.023363 | 0.023363 | 0.99208 | -0.15242 | 0.9924 | -0.14609 | 6.4184
81 | -0.015581 | -0.0039076 | 0.015586 | 0.0039104 | 4.8144e-06 | 2.7772e-06 | 0.023363 | 0.023363 | 0.023363 | 0.9924 | -0.14609 | 0.99274 | -0.13961 | 6.4184
82 | 0.13586 | 0.034294 | -0.13578 | -0.034247 | 7.3175e-05 | 4.6769e-05 | 0.20224 | 0.20224 | 0.20224 | 1 | 0 | 0.99941 | -0.011251 | 55.5617
83 | 0.0318 | 0.0080219 | -0.031787 | -0.0080137 | 1.3098e-05 | 8.18e-06 | 0.047443 | 0.047443 | 0.047443 | 0.99778 | -0.042512 | 0.99733 | -0.051119 | 13.0337
84 | -0.093339 | -0.023484 | 0.093577 | 0.023636 | 0.0002384 | 0.00015215 | 0.13952 | 0.13952 | 0.13952 | 0.99572 | -0.082073 | 0.9985 | -0.028767 | 38.3295
85 | 0.087103 | 0.021921 | -0.086941 | -0.021818 | 0.00016113 | 0.00010279 | 0.1302 | 0.1302 | 0.1302 | 0.99572 | -0.082073 | 0.99371 | -0.12086 | 35.7691
86 | -0.095736 | -0.024177 | 0.095773 | 0.024201 | 3.6596e-05 | 2.3359e-05 | 0.14274 | 0.14274 | 0.14274 | 0.9985 | -0.028767 | 0.99891 | -0.020793 | 39.2132
87 | 0.04477 | 0.011233 | -0.044752 | -0.011221 | 1.8188e-05 | 1.15e-05 | 0.067045 | 0.067045 | 0.067045 | 0.99371 | -0.12086 | 0.99327 | -0.12938 | 18.4188
88 | 0.042171 | 0.010586 | -0.04215 | -0.010572 | 2.1633e-05 | 1.3658e-05 | 0.063155 | 0.063155 | 0.063155 | 0.99371 | -0.12086 | 0.99315 | -0.13162 | 17.3503
89 | -0.097915 | -0.024738 | 0.097954 | 0.024762 | 3.8642e-05 | 2.4668e-05 | 0.14593 | 0.14593 | 0.14593 | 0.99891 | -0.020793 | 0.99934 | -0.012563 | 40.09
90 | 0.013904 | 0.003486 | -0.013901 | -0.0034838 | 3.8926e-06 | 2.1817e-06 | 0.020831 | 0.020831 | 0.020831 | 0.99327 | -0.12938 | 0.99296 | -0.13526 | 5.7228
91 | 0.024335 | 0.0061059 | -0.02431 | -0.0060905 | 2.5213e-05 | 1.5483e-05 | 0.036459 | 0.036459 | 0.036459 | 0.99327 | -0.12938 | 0.99214 | -0.15114 | 10.0163
92 | 0.0065122 | 0.0016291 | -0.0065116 | -0.0016289 | 5.8779e-07 | 1.6301e-07 | 0.0097548 | 0.0097549 | 0.0097549 | 0.99327 | -0.12938 | 0.99317 | -0.13128 | 2.6799
93 | 0.029081 | 0.0072969 | -0.029075 | -0.007293 | 6.3061e-06 | 3.9213e-06 | 0.043575 | 0.043575 | 0.043575 | 0.99315 | -0.13162 | 0.99292 | -0.13617 | 11.9712
94 | -0.13437 | -0.03389 | 0.13438 | 0.033895 | 8.443e-06 | 5.3962e-06 | 0.20016 | 0.20016 | 0.20016 | 0.99934 | -0.012563 | 0.99941 | -0.011251 | 54.9878
95 | 0.0087615 | 0.0021958 | -0.0087614 | -0.0021958 | 6.3471e-08 | 2.7921e-08 | 0.01313 | 0.01313 | 0.01313 | 0.99296 | -0.13526 | 0.99296 | -0.13541 | 3.607
96 | 0.019949 | 0.0049976 | -0.019933 | -0.0049879 | 1.6224e-05 | 9.7595e-06 | 0.029919 | 0.029919 | 0.029919 | 0.99214 | -0.15114 | 0.99126 | -0.16823 | 8.2195
97 | 0.0043608 | 0.0010928 | -0.0043606 | -0.0010929 | 2.6579e-07 | -4.3856e-08 | 0.0065403 | 0.0065404 | 0.0065404 | 0.99214 | -0.15114 | 0.99208 | -0.15242 | 1.7968
98 | 0.0040278 | 0.0010064 | -0.0040276 | -0.0010065 | 2.3554e-07 | -7.2513e-08 | 0.0060336 | 0.0060337 | 0.0060337 | 0.99317 | -0.13128 | 0.99311 | -0.13251 | 1.6576
99 | 0.029075 | 0.007293 | -0.02907 | -0.00729 | 4.7683e-06 | 2.9651e-06 | 0.043575 | 0.043575 | 0.043575 | 0.99292 | -0.13617 | 0.99274 | -0.13961 | 11.9712
100 | 0.017994 | 0.004502 | -0.017984 | -0.0044961 | 1.0016e-05 | 5.9385e-06 | 0.027009 | 0.027009 | 0.027009 | 0.99126 | -0.16823 | 0.99066 | -0.17993 | 7.4201
101 | 0.0040276 | 0.0010065 | -0.0040273 | -0.0010066 | 2.1973e-07 | -6.7614e-08 | 0.0060337 | 0.0060337 | 0.0060337 | 0.99311 | -0.13251 | 0.99305 | -0.13366 | 1.6576
102 | 0.030625 | 0.0077226 | -0.03062 | -0.0077195 | 5.026e-06 | 3.1329e-06 | 0.04571 | 0.04571 | 0.04571 | 0.99733 | -0.051119 | 0.99715 | -0.054548 | 12.5576
103 | 0.02926 | 0.0073784 | -0.029257 | -0.0073768 | 2.5637e-06 | 1.594e-06 | 0.043679 | 0.043679 | 0.043679 | 0.99715 | -0.054548 | 0.99706 | -0.056379 | 11.9998
104 | 0.028275 | 0.0071308 | -0.02827 | -0.0071277 | 5.0025e-06 | 3.104e-06 | 0.042214 | 0.042214 | 0.042214 | 0.99706 | -0.056379 | 0.99686 | -0.060076 | 11.5973
105 | 0.027357 | 0.0068989 | -0.027351 | -0.0068951 | 6.0225e-06 | 3.729e-06 | 0.040851 | 0.040851 | 0.040851 | 0.99686 | -0.060076 | 0.99662 | -0.064676 | 11.2228
106 | 0.0031466 | 0.00078824 | -0.0031463 | -0.00078844 | 2.1619e-07 | -2.02e-07 | 0.0046978 | 0.004698 | 0.004698 | 0.99662 | -0.064676 | 0.99655 | -0.066118 | 1.2907
107 | 0.0014423 | 0.00036136 | -0.0014423 | -0.00036145 | 1.3048e-08 | -8.9401e-08 | 0.0021535 | 0.0021536 | 0.0021536 | 0.99655 | -0.066118 | 0.99654 | -0.066308 | 0.59164
108 | 0.00075277 | 0.00018865 | -0.00075277 | -0.00018866 | 4.2381e-10 | -1.1383e-08 | 0.001124 | 0.001124 | 0.001124 | 0.99654 | -0.066308 | 0.99654 | -0.06632 | 0.3088
109 | 0.019619 | 0.0049499 | -0.019614 | -0.004947 | 4.8134e-06 | 2.8867e-06 | 0.029337 | 0.029337 | 0.029337 | 0.99549 | -0.086473 | 0.99522 | -0.091598 | 8.0597
110 | 0.018625 | 0.004699 | -0.018624 | -0.0046986 | 6.8733e-07 | 4.0921e-07 | 0.027858 | 0.027858 | 0.027858 | 0.99522 | -0.091598 | 0.99518 | -0.092369 | 7.6533
111 | 0.017847 | 0.0045038 | -0.017846 | -0.0045031 | 1.2353e-06 | 7.3055e-07 | 0.026696 | 0.026696 | 0.026696 | 0.99518 | -0.092369 | 0.99511 | -0.093814 | 7.334
112 | 0.0087004 | 0.0021699 | -0.0086913 | -0.0021659 | 9.1016e-06 | 3.9964e-06 | 0.013065 | 0.013065 | 0.013065 | 0.99066 | -0.17993 | 0.98953 | -0.20199 | 3.5894
113 | 0.0092838 | 0.0023262 | -0.0092817 | -0.0023252 | 2.1147e-06 | 9.8011e-07 | 0.013945 | 0.013945 | 0.013945 | 0.99066 | -0.17993 | 0.99041 | -0.18472 | 3.8309
114 | 0.008115 | 0.0020219 | -0.008114 | -0.0020215 | 9.5244e-07 | 3.9034e-07 | 0.012199 | 0.012199 | 0.012199 | 0.98953 | -0.20199 | 0.9894 | -0.20447 | 3.3513
115 | 0.00057634 | 0.00014405 | -0.00057633 | -0.00014444 | 8.6682e-09 | -3.8982e-07 | 0.00086654 | 0.00086668 | 0.00086668 | 0.98953 | -0.20199 | 0.98951 | -0.20231 | 0.2381
116 | 0.0020048 | 0.0005014 | -0.0020045 | -0.00050209 | 2.1733e-07 | -6.8305e-07 | 0.0030116 | 0.0030119 | 0.0030119 | 0.99041 | -0.18472 | 0.9903 | -0.18699 | 0.82744
117 | 0.0010213 | 0.00025553 | -0.0010213 | -0.00025566 | 9.0045e-09 | -1.2691e-07 | 0.0015302 | 0.0015302 | 0.0015302 | 0.99305 | -0.13366 | 0.99304 | -0.13384 | 0.42039
118 | -0.00071422 | -0.00017872 | 0.00071422 | 0.0001787 | 7.3109e-10 | -2.1556e-08 | 0.0010701 | 0.0010701 | 0.0010701 | 0.99304 | -0.13386 | 0.99304 | -0.13384 | 0.29399
119 | 0.00046275 | 0.0001157 | -0.00046275 | -0.00011581 | 1.5752e-09 | -1.1204e-07 | 0.00069331 | 0.00069335 | 0.00069335 | 0.99304 | -0.13386 | 0.99303 | -0.13394 | 0.19048
120 | 0.00037096 | 9.2808e-05 | -0.00037096 | -9.2816e-05 | 7.7589e-11 | -8.6049e-09 | 0.00055581 | 0.00055581 | 0.00055581 | 0.99303 | -0.13394 | 0.99303 | -0.13394 | 0.1527
121 | 0.0002635 | 6.5884e-05 | -0.0002635 | -6.5936e-05 | 2.3317e-10 | -5.1461e-08 | 0.00039479 | 0.0003948 | 0.0003948 | 0.99303 | -0.13394 | 0.99303 | -0.13396 | 0.10846
122 | 0.00015612 | 3.9025e-05 | -0.00015612 | -3.9128e-05 | 1.6399e-10 | -1.0328e-07 | 0.00023391 | 0.00023394 | 0.00023394 | 0.99303 | -0.13396 | 0.99303 | -0.13398 | 0.064271
123 | 0.00053762 | 0.00013444 | -0.00053761 | -0.00013474 | 5.7848e-09 | -2.9731e-07 | 0.00080983 | 0.00080994 | 0.00080994 | 0.98771 | -0.2375 | 0.9877 | -0.23772 | 0.22251
124 | -0.0014375 | -0.00035996 | 0.0014375 | 0.00035988 | 1.2462e-08 | -8.2728e-08 | 0.0021655 | 0.0021654 | 0.0021655 | 0.98771 | -0.2375 | 0.98772 | -0.23731 | 0.5949
125 | -0.0072043 | -0.0017923 | 0.0072088 | 0.0017939 | 4.547e-06 | 1.5905e-06 | 0.010849 | 0.010848 | 0.010849 | 0.98772 | -0.23731 | 0.9884 | -0.224 | 2.9804
126 | -0.0072088 | -0.0017939 | 0.0072131 | 0.0017953 | 4.2597e-06 | 1.4882e-06 | 0.010848 | 0.010848 | 0.010848 | 0.9884 | -0.224 | 0.98904 | -0.21153 | 2.9803
127 | 0.00018791 | 4.6643e-05 | -0.00018791 | -4.7095e-05 | 1.0626e-09 | -4.5161e-07 | 0.00028301 | 0.00028317 | 0.00028317 | 0.98744 | -0.24292 | 0.98743 | -0.24303 | 0.077795
128 | -0.0077442 | -0.0019285 | 0.0077468 | 0.0019295 | 2.5944e-06 | 1.0056e-06 | 0.011647 | 0.011647 | 0.011647 | 0.98904 | -0.21153 | 0.9894 | -0.20447 | 3.1997
129 | 0.001794 | 0.00044931 | -0.0017939 | -0.00044945 | 3.4816e-08 | -1.4211e-07 | 0.0026955 | 0.0026955 | 0.0026955 | 0.9903 | -0.18699 | 0.99028 | -0.1874 | 0.74054
130 | 0.0014129 | 0.00035395 | -0.0014129 | -0.00035405 | 1.4576e-08 | -1.0162e-07 | 0.002123 | 0.002123 | 0.002123 | 0.99028 | -0.1874 | 0.99026 | -0.18762 | 0.58324
131 | 0.0011797 | 0.00029563 | -0.0011797 | -0.00029567 | 4.0138e-09 | -4.1249e-08 | 0.0017727 | 0.0017727 | 0.0017727 | 0.99026 | -0.18762 | 0.99026 | -0.18769 | 0.48701

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.18481 | 0.046231

## res_load
| p_mw | q_mvar
0 | 0.0022608 | 0.00056661
1 | 0.00080298 | 0.00020125
2 | 0.00078294 | 0.00019622
3 | 0.00070144 | 0.0001758
4 | 0.0022217 | 0.0005568
5 | 0.00057176 | 0.0001433
6 | 0.0027319 | 0.00068469
7 | 0.00078923 | 0.0001978
8 | 0.00060469 | 0.00015155
9 | 0.00083006 | 0.00020803
10 | 0.0010988 | 0.00027539
11 | 0.0012611 | 0.00031605
12 | 0.0013452 | 0.00033714
13 | 0.0005599 | 0.00014033
14 | 0.0017395 | 0.00043596
15 | 0.00050375 | 0.00012625
16 | 0.00016886 | 4.2319e-05
17 | 0.00034402 | 8.6219e-05
18 | 0.00044153 | 0.00011066
19 | 0.00030776 | 7.7133e-05
20 | 7.7951e-05 | 1.9536e-05
21 | 8.7616e-05 | 2.1959e-05
22 | 0.0016975 | 0.00042544
23 | 0.0012459 | 0.00031224
24 | 8.8391e-05 | 2.2153e-05
25 | 0.00039011 | 9.7771e-05
26 | 0.00069592 | 0.00017441
27 | 0.00076138 | 0.00019082
28 | 0.0004263 | 0.00010684
29 | 0.0001491 | 3.7368e-05
30 | 0.00066049 | 0.00016553
31 | 0.0011494 | 0.00028808
32 | 0.00048685 | 0.00012202
33 | 0.00018644 | 4.6727e-05
34 | 0.00022447 | 5.6257e-05
35 | 0.00053819 | 0.00013488
36 | 0.0016344 | 0.00040962
37 | 0.00030043 | 7.5295e-05
38 | 0.00022047 | 5.5254e-05
39 | 0.00011253 | 2.8203e-05
40 | 0.00040552 | 0.00010163
41 | 0.00020389 | 5.11e-05
42 | 0.0001455 | 3.6466e-05
43 | 0.00014811 | 3.7121e-05
44 | 0.0026318 | 0.00065959
45 | 0.001276 | 0.00031979
46 | 0.00099323 | 0.00024893
47 | 0.0034179 | 0.00085661
48 | 0.0018798 | 0.00047113
49 | 0.015573 | 0.0039029
50 | 0.001288 | 0.00032281
51 | 0.00076844 | 0.00019259
52 | 0.0062364 | 0.001563
53 | 0.0021587 | 0.00054101
54 | 0.0021424 | 0.00053695
55 | 0.013068 | 0.0032752
56 | 0.036419 | 0.0091276
57 | 0.0051391 | 0.001288
58 | 0.0024838 | 0.0006225
59 | 0.013485 | 0.0033796
60 | 0.0014029 | 0.00035161
61 | 0.0087614 | 0.0021958
62 | 0.0019386 | 0.00048585
63 | 0.0043606 | 0.0010929
64 | 0.0011616 | 0.00029112
65 | 0.0013607 | 0.00034102
66 | 0.00098171 | 0.00024604
67 | 0.00091306 | 0.00022884
68 | 0.0017041 | 0.00042708
69 | 0.00068948 | 0.0001728
70 | 0.00075277 | 0.00018866
71 | 0.0012387 | 0.00031045
72 | 0.00098954 | 0.000248
73 | 0.00077728 | 0.00019481
74 | 0.00043046 | 0.00010788
75 | 0.007277 | 0.0018238
76 | 0.0002493 | 6.2482e-05
77 | 0.00025147 | 6.3023e-05
78 | 0.00030705 | 7.6954e-05
79 | 9.1788e-05 | 2.3004e-05
80 | 0.00010746 | 2.6932e-05
81 | 0.00010737 | 2.6911e-05
82 | 0.00015612 | 3.9128e-05
83 | 0.00089983 | 0.00022552
84 | 0.00053761 | 0.00013474
85 | 0.00053112 | 0.00013311
86 | 0.00036723 | 9.2038e-05
87 | 0.00021058 | 5.2775e-05
88 | 0.00038106 | 9.5502e-05
89 | 0.00023311 | 5.8424e-05
90 | 0.00057633 | 0.00014444
91 | 0.0011797 | 0.00029567
92 | 0.00018791 | 4.7095e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1