## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_120-15_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_120-15_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_120-15_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_120-15_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_120-15_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_120-15_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_120-15_0_2_node_33 | 0.4 | n |  | TRUE
7 | bus_LV_120-15_0_2_node_42 | 0.4 | n |  | TRUE
8 | bus_LV_120-15_0_2_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_120-15_0_2_node_41 | 0.4 | n |  | TRUE
10 | bus_LV_120-15_0_2_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_120-15_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_120-15_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_120-15_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_120-15_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_120-15_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_120-15_0_2_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_120-15_0_2_node_37 | 0.4 | n |  | TRUE
18 | bus_LV_120-15_0_2_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_120-15_0_2_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_120-15_0_2_node_44 | 0.4 | n |  | TRUE
21 | bus_LV_120-15_0_2_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_120-15_0_2_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_120-15_0_2_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_120-15_0_2_node_45 | 0.4 | n |  | TRUE
25 | bus_LV_120-15_0_2_node_46 | 0.4 | n |  | TRUE
26 | bus_LV_120-15_0_2_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_120-15_0_2_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_120-15_0_2_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_120-15_0_2_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_120-15_0_2_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_120-15_0_2_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_120-15_0_2_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_120-15_0_2_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_120-15_0_2_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_120-15_0_2_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_120-15_0_2_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_120-15_0_2_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_120-15_0_2_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_120-15_0_2_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_120-15_0_2_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_120-15_0_2_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_120-15_0_2_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_120-15_0_2_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_120-15_0_2_node_38 | 0.4 | n |  | TRUE
45 | bus_MV_10_0_node_19 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_120-15_0_2_load_0 | 0 | 0.0038188 | 0.00095708 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_120-15_0_2_load_3 | 3 | 0.00085138 | 0.00021338 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_120-15_0_2_load_4 | 4 | 0.0020098 | 0.0005037 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_120-15_0_2_load_5 | 5 | 0.0064857 | 0.0016255 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_120-15_0_2_load_33 | 6 | 0.0044273 | 0.0011096 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_120-15_0_2_load_42 | 7 | 0.0036356 | 0.00091118 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_120-15_0_2_load_36 | 8 | 0.0035739 | 0.00089571 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_120-15_0_2_load_41 | 9 | 0.0013179 | 0.00033029 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_120-15_0_2_load_35 | 10 | 0.00086047 | 0.00021565 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_120-15_0_2_load_6 | 11 | 0.0046689 | 0.0011701 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_120-15_0_2_load_7 | 12 | 0.0023238 | 0.00058241 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_120-15_0_2_load_10 | 15 | 0.025139 | 0.0063005 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_120-15_0_2_load_37 | 17 | 0.0038275 | 0.00095925 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_120-15_0_2_load_34 | 19 | 0.0025843 | 0.00064768 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_120-15_0_2_load_44 | 20 | 0.00041174 | 0.00010319 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_120-15_0_2_load_32 | 21 | 0.014334 | 0.0035923 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_120-15_0_2_load_29 | 22 | 0.01189 | 0.0029799 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_120-15_0_2_load_12 | 23 | 0.00048131 | 0.00012063 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_120-15_0_2_load_45 | 24 | 0.0036523 | 0.00091536 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_120-15_0_2_load_46 | 25 | 0.010555 | 0.0026453 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_120-15_0_2_load_30 | 26 | 0.0069937 | 0.0017528 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_120-15_0_2_load_13 | 27 | 0.0011172 | 0.00027999 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_120-15_0_2_load_16 | 28 | 0.00914 | 0.0022907 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_120-15_0_2_load_17 | 29 | 0.0035649 | 0.00089345 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_120-15_0_2_load_19 | 31 | 0.0020111 | 0.00050402 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_120-15_0_2_load_20 | 32 | 0.0041479 | 0.0010396 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_120-15_0_2_load_26 | 33 | 0.002419 | 0.00060625 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_120-15_0_2_load_27 | 35 | 0.001075 | 0.00026942 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_120-15_0_2_load_43 | 38 | 0.0024599 | 0.00061652 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_120-15_0_2_load_25 | 39 | 0.0011606 | 0.00029088 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_120-15_0_2_load_23 | 40 | 0.010447 | 0.0026184 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_120-15_0_2_load_28 | 41 | 0.0013249 | 0.00033205 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_120-15_0_2_load_40 | 42 | 0.0041353 | 0.0010364 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_120-15_0_2_load_31 | 43 | 0.0025727 | 0.00064478 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_120-15_0_2_load_38 | 44 | 0.0015116 | 0.00037883 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_120-15_0_2_line_0 |  | 0 | 1 | 0.0097395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_120-15_0_2_line_1 |  | 0 | 2 | 0.012679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_120-15_0_2_line_2 |  | 1 | 3 | 0.012869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_120-15_0_2_line_3 |  | 2 | 4 | 0.018048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_120-15_0_2_line_4 |  | 2 | 5 | 0.015563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_120-15_0_2_line_5 |  | 3 | 6 | 0.024058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_120-15_0_2_line_6 |  | 4 | 7 | 0.0013826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_120-15_0_2_line_7 |  | 5 | 8 | 0.0047179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_120-15_0_2_line_8 |  | 7 | 9 | 0.013362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_120-15_0_2_line_9 |  | 8 | 10 | 0.022424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_120-15_0_2_line_10 |  | 9 | 42 | 0.015354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_120-15_0_2_line_11 |  | 10 | 19 | 0.013138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_120-15_0_2_line_12 |  | 11 | 12 | 0.013139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_120-15_0_2_line_13 |  | 11 | 13 | 0.02692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_120-15_0_2_line_14 |  | 12 | 14 | 0.044591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_120-15_0_2_line_15 |  | 13 | 15 | 0.065617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_120-15_0_2_line_16 |  | 13 | 16 | 0.092577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_120-15_0_2_line_17 |  | 14 | 17 | 0.0293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_120-15_0_2_line_18 |  | 14 | 18 | 0.076817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_120-15_0_2_line_19 |  | 14 | 19 | 0.012851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_120-15_0_2_line_20 |  | 15 | 20 | 0.0050243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_120-15_0_2_line_21 |  | 16 | 21 | 0.026646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_120-15_0_2_line_22 |  | 16 | 22 | 0.013882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_120-15_0_2_line_23 |  | 18 | 23 | 0.041652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_120-15_0_2_line_24 |  | 20 | 24 | 0.01271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_120-15_0_2_line_25 |  | 21 | 25 | 0.06045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_120-15_0_2_line_26 |  | 22 | 26 | 0.036503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_120-15_0_2_line_27 |  | 23 | 27 | 0.030144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_120-15_0_2_line_28 |  | 26 | 43 | 0.02114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_120-15_0_2_line_29 |  | 28 | 29 | 0.0071391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_120-15_0_2_line_30 |  | 28 | 30 | 0.048453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_120-15_0_2_line_31 |  | 29 | 31 | 0.017883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_120-15_0_2_line_32 |  | 30 | 32 | 0.017014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_120-15_0_2_line_33 |  | 31 | 33 | 0.0049832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_120-15_0_2_line_34 |  | 32 | 34 | 0.14785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_120-15_0_2_line_35 |  | 33 | 35 | 0.017095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_120-15_0_2_line_36 |  | 34 | 36 | 0.065849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_120-15_0_2_line_37 |  | 35 | 41 | 0.0079616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_120-15_0_2_line_38 |  | 36 | 37 | 0.017451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_120-15_0_2_line_39 |  | 36 | 38 | 0.01255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_120-15_0_2_line_40 |  | 37 | 39 | 0.011948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_120-15_0_2_line_41 |  | 37 | 40 | 0.024173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_120-15_0_2_line_42 |  | 41 | 42 | 0.0017581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_120-15_0_2_line_43 |  | 43 | 44 | 0.011354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_120-15_0_2_trafo_45 | 0.63 MVA 20/0.4 kV | 45 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2711356.5537 | 1237319.9207 | 2711363.9934 | 1237313.6352
1 | 2711373.6783 | 1237305.4526 | 2711363.9934 | 1237313.6352
2 | 2711356.5537 | 1237319.9207 | 2711344.0503 | 1237322.9657
3 | 2711373.6783 | 1237305.4526 | 2711380.7888 | 1237322.0412
4 | 2711373.6783 | 1237305.4526 | 2711380.1313 | 1237298.3125 | 2711382.8199 | 1237293.0168
5 | 2711344.0503 | 1237322.9657 | 2711320.6757 | 1237328.658
6 | 2711380.7888 | 1237322.0412 | 2711381.3335 | 1237323.312
7 | 2711384.9557 | 1237288.81 | 2711382.8199 | 1237293.0168
8 | 2711386.5976 | 1237335.5931 | 2711381.3335 | 1237323.312
9 | 2711384.9557 | 1237288.81 | 2711386.4729 | 1237285.8216 | 2711392.1542 | 1237267.6147
10 | 2711392.6465 | 1237349.7052 | 2711386.5976 | 1237335.5931
11 | 2711392.1542 | 1237267.6147 | 2711396.0676 | 1237255.0736
12 | 2711457.6217 | 1237243.3934 | 2711444.4836 | 1237243.257
13 | 2711484.54 | 1237243.6726 | 2711457.6217 | 1237243.3934
14 | 2711399.8956 | 1237242.8061 | 2711404.7545 | 1237242.7861 | 2711421.0209 | 1237243.0136 | 2711444.4836 | 1237243.257
15 | 2711484.54 | 1237243.6726 | 2711483.9028 | 1237257.049 | 2711483.4561 | 1237266.3257 | 2711483.0557 | 1237274.747 | 2711457.9495 | 1237289.8766 | 2711454.154 | 1237293.4229
16 | 2711484.54 | 1237243.6726 | 2711536.6782 | 1237244.2741 | 2711535.9468 | 1237264.265 | 2711534.0189 | 1237272.6243 | 2711531.3499 | 1237284.1721
17 | 2711399.8956 | 1237242.8061 | 2711370.6006 | 1237242.2507
18 | 2711399.8956 | 1237242.8061 | 2711397.9996 | 1237229.7158 | 2711389.515 | 1237198.3209 | 2711395.198 | 1237195.5253 | 2711406.1288 | 1237177.227 | 2711407.3016 | 1237174.0132
19 | 2711399.8956 | 1237242.8061 | 2711396.0676 | 1237255.0736
20 | 2711454.154 | 1237293.4229 | 2711450.4827 | 1237296.853
21 | 2711531.3499 | 1237284.1721 | 2711531.2302 | 1237295.3787 | 2711526.3473 | 1237310.0252
22 | 2711531.3499 | 1237284.1721 | 2711517.8422 | 1237280.9719
23 | 2711407.3016 | 1237174.0132 | 2711408.3095 | 1237172.7311 | 2711411.3636 | 1237172.099 | 2711415.9927 | 1237172.2303 | 2711424.672 | 1237171.8817 | 2711437.4687 | 1237171.5104 | 2711447.8489 | 1237168.5895
24 | 2711441.1958 | 1237305.5302 | 2711450.4827 | 1237296.853
25 | 2711532.3638 | 1237354.6577 | 2711513.4987 | 1237348.5654 | 2711526.3473 | 1237310.0252
26 | 2711506.3358 | 1237315.1577 | 2711517.3816 | 1237280.8628 | 2711517.8422 | 1237280.9719
27 | 2711447.8489 | 1237168.5895 | 2711457.8811 | 1237165.7666 | 2711468.2057 | 1237162.4355 | 2711476.9894 | 1237161.1759
28 | 2711499.855 | 1237335.2795 | 2711506.3358 | 1237315.1577
29 | 2711412.2193 | 1237395.3687 | 2711415.0319 | 1237401.9304
30 | 2711446.6898 | 1237437.3258 | 2711425.9685 | 1237421.28 | 2711416.1353 | 1237404.5046 | 2711415.0319 | 1237401.9304
31 | 2711412.2193 | 1237395.3687 | 2711405.1739 | 1237378.9317
32 | 2711446.6898 | 1237437.3258 | 2711459.8432 | 1237448.1172
33 | 2711405.1739 | 1237378.9317 | 2711403.2107 | 1237374.3515
34 | 2711595.7268 | 1237483.894 | 2711535.8954 | 1237488.0846 | 2711520.0728 | 1237486.0192 | 2711507.5112 | 1237481.9691 | 2711497.3122 | 1237477.0293 | 2711486.6808 | 1237470.1354 | 2711459.8432 | 1237448.1172
35 | 2711396.4757 | 1237358.6389 | 2711403.2107 | 1237374.3515
36 | 2711595.7268 | 1237483.894 | 2711590.3511 | 1237444.1951 | 2711587.9054 | 1237428.1699 | 2711589.7997 | 1237418.7869
37 | 2711396.4757 | 1237358.6389 | 2711393.3391 | 1237351.3211
38 | 2711589.7997 | 1237418.7869 | 2711572.6071 | 1237415.517
39 | 2711589.7997 | 1237418.7869 | 2711592.2116 | 1237406.8228 | 2711592.342 | 1237406.5037
40 | 2711572.6071 | 1237415.517 | 2711570.9943 | 1237427.3551
41 | 2711572.6071 | 1237415.517 | 2711558.2498 | 1237412.7896 | 2711552.6565 | 1237405.0376
42 | 2711392.6465 | 1237349.7052 | 2711393.3391 | 1237351.3211
43 | 2711496.3743 | 1237346.0864 | 2711499.855 | 1237335.2795

## bus_geodata
| x | y | coords
0 | 2711363.9934 | 1237313.6352
1 | 2711356.5537 | 1237319.9207
2 | 2711373.6783 | 1237305.4526
3 | 2711344.0503 | 1237322.9657
4 | 2711380.7888 | 1237322.0412
5 | 2711382.8199 | 1237293.0168
6 | 2711320.6757 | 1237328.658
7 | 2711381.3335 | 1237323.312
8 | 2711384.9557 | 1237288.81
9 | 2711386.5976 | 1237335.5931
10 | 2711392.1542 | 1237267.6147
11 | 2711457.6217 | 1237243.3934
12 | 2711444.4836 | 1237243.2571
13 | 2711484.54 | 1237243.6726
14 | 2711399.8956 | 1237242.8061
15 | 2711454.154 | 1237293.4229
16 | 2711531.3499 | 1237284.1721
17 | 2711370.6006 | 1237242.2507
18 | 2711407.3016 | 1237174.0132
19 | 2711396.0676 | 1237255.0736
20 | 2711450.4827 | 1237296.853
21 | 2711526.3473 | 1237310.0252
22 | 2711517.8422 | 1237280.9719
23 | 2711447.8489 | 1237168.5895
24 | 2711441.1958 | 1237305.5302
25 | 2711532.3638 | 1237354.6577
26 | 2711506.3358 | 1237315.1577
27 | 2711476.9894 | 1237161.1759
28 | 2711415.0319 | 1237401.9304
29 | 2711412.2193 | 1237395.3687
30 | 2711446.6898 | 1237437.3258
31 | 2711405.1739 | 1237378.9317
32 | 2711459.8432 | 1237448.1172
33 | 2711403.2107 | 1237374.3515
34 | 2711595.7268 | 1237483.894
35 | 2711396.4757 | 1237358.6389
36 | 2711589.7997 | 1237418.7869
37 | 2711572.6071 | 1237415.517
38 | 2711592.342 | 1237406.5037
39 | 2711570.9943 | 1237427.3551
40 | 2711552.6565 | 1237405.0376
41 | 2711393.3391 | 1237351.3211
42 | 2711392.6465 | 1237349.7052
43 | 2711499.855 | 1237335.2795
44 | 2711496.3743 | 1237346.0864
45 | 2711484.54 | 1237243.6726

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98015 | -0.38122 | 0.0038188 | 0.00095708
1 | 0.9801 | -0.38216 | 0 | 0
2 | 0.98025 | -0.37913 | 0 | 0
3 | 0.98004 | -0.38339 | 0.00085138 | 0.00021338
4 | 0.97943 | -0.39514 | 0.0020098 | 0.0005037
5 | 0.98109 | -0.36278 | 0.0064857 | 0.0016255
6 | 0.97994 | -0.38532 | 0.0044273 | 0.0011096
7 | 0.97937 | -0.39632 | 0.0036356 | 0.00091118
8 | 0.98137 | -0.35728 | 0.0035739 | 0.00089571
9 | 0.97884 | -0.40682 | 0.0013179 | 0.00033029
10 | 0.98279 | -0.32971 | 0.00086047 | 0.00021565
11 | 0.98863 | -0.21682 | 0.0046689 | 0.0011701
12 | 0.98766 | -0.2354 | 0.0023238 | 0.00058241
13 | 0.99072 | -0.17663 | 0 | 0
14 | 0.98448 | -0.29687 | 0 | 0
15 | 0.99871 | -0.024326 | 0.025139 | 0.0063005
16 | 0.98664 | -0.25564 | 0 | 0
17 | 0.98438 | -0.29888 | 0.0038275 | 0.00095925
18 | 0.98437 | -0.29908 | 0 | 0
19 | 0.98363 | -0.3134 | 0.0025843 | 0.00064768
20 | 0.99908 | -0.017441 | 0.00041174 | 0.00010319
21 | 0.98603 | -0.26752 | 0.014334 | 0.0035923
22 | 0.98635 | -0.26135 | 0.01189 | 0.0029799
23 | 0.98431 | -0.30028 | 0.00048131 | 0.00012063
24 | 1 | 0 | -0.16124 | -0.040882
25 | 0.98545 | -0.27896 | 0.010555 | 0.0026453
26 | 0.98598 | -0.26859 | 0.0069937 | 0.0017528
27 | 0.98427 | -0.30088 | 0.0011172 | 0.00027999
28 | 0.9765 | -0.45272 | 0.00914 | 0.0022907
29 | 0.97668 | -0.44914 | 0.0035649 | 0.00089345
30 | 0.97567 | -0.46887 | 0 | 0
31 | 0.97719 | -0.43904 | 0.0020111 | 0.00050402
32 | 0.97538 | -0.47455 | 0.0041479 | 0.0010396
33 | 0.97734 | -0.43605 | 0.002419 | 0.00060625
34 | 0.97344 | -0.51275 | 0 | 0
35 | 0.97791 | -0.42502 | 0.001075 | 0.00026942
36 | 0.97258 | -0.52981 | 0 | 0
37 | 0.97239 | -0.53354 | 0 | 0
38 | 0.97255 | -0.53038 | 0.0024599 | 0.00061652
39 | 0.97238 | -0.5338 | 0.0011606 | 0.00029088
40 | 0.97216 | -0.5382 | 0.010447 | 0.0026184
41 | 0.97818 | -0.41974 | 0.0013249 | 0.00033205
42 | 0.97824 | -0.41853 | 0.0041353 | 0.0010364
43 | 0.9859 | -0.27014 | 0.0025727 | 0.00064478
44 | 0.98588 | -0.27045 | 0.0015116 | 0.00037883
45 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0052796 | 0.001323 | -0.0052794 | -0.0013229 | 2.3464e-07 | 2.7422e-08 | 0.0080152 | 0.0080152 | 0.0080152 | 0.98015 | -0.38122 | 0.9801 | -0.38216 | 2.202
1 | -0.0090984 | -0.0022801 | 0.0090993 | 0.0022805 | 9.0712e-07 | 4.2074e-07 | 0.013813 | 0.013813 | 0.013813 | 0.98015 | -0.38122 | 0.98025 | -0.37913 | 3.7947
2 | 0.0052794 | 0.0013229 | -0.005279 | -0.0013229 | 3.1003e-07 | 3.6253e-08 | 0.0080152 | 0.0080153 | 0.0080153 | 0.9801 | -0.38216 | 0.98004 | -0.38339 | 2.202
3 | 0.04905 | 0.012366 | -0.049012 | -0.012342 | 3.7548e-05 | 2.3803e-05 | 0.074483 | 0.074483 | 0.074483 | 0.98025 | -0.37913 | 0.97943 | -0.39514 | 20.4624
4 | -0.058149 | -0.014646 | 0.058195 | 0.014675 | 4.55e-05 | 2.8923e-05 | 0.088296 | 0.088296 | 0.088296 | 0.98025 | -0.37913 | 0.98109 | -0.36278 | 24.2571
5 | 0.0044277 | 0.0011095 | -0.0044273 | -0.0011096 | 4.0773e-07 | -4.2168e-08 | 0.0067226 | 0.0067227 | 0.0067227 | 0.98004 | -0.38339 | 0.97994 | -0.38532 | 1.8469
6 | 0.047002 | 0.011838 | -0.047 | -0.011836 | 2.6454e-06 | 1.6757e-06 | 0.07143 | 0.07143 | 0.07143 | 0.97943 | -0.39514 | 0.97937 | -0.39632 | 19.6236
7 | -0.06468 | -0.0163 | 0.064697 | 0.016311 | 1.7038e-05 | 1.0844e-05 | 0.098133 | 0.098133 | 0.098133 | 0.98109 | -0.36278 | 0.98137 | -0.35728 | 26.9595
8 | 0.043364 | 0.010925 | -0.043342 | -0.010911 | 2.1764e-05 | 1.3761e-05 | 0.065906 | 0.065906 | 0.065906 | 0.97937 | -0.39632 | 0.97884 | -0.40682 | 18.1061
9 | -0.068271 | -0.017207 | 0.068361 | 0.017264 | 9.017e-05 | 5.7425e-05 | 0.10355 | 0.10355 | 0.10355 | 0.98137 | -0.35728 | 0.98279 | -0.32971 | 28.4482
10 | 0.042025 | 0.010581 | -0.042001 | -0.010566 | 2.3512e-05 | 1.4855e-05 | 0.063903 | 0.063903 | 0.063903 | 0.97884 | -0.40682 | 0.97824 | -0.41853 | 17.5557
11 | -0.069222 | -0.01748 | 0.069276 | 0.017515 | 5.4165e-05 | 3.4499e-05 | 0.10485 | 0.10485 | 0.10485 | 0.98279 | -0.32971 | 0.98363 | -0.3134 | 28.8061
12 | 0.079968 | 0.02033 | -0.079896 | -0.020285 | 7.1501e-05 | 4.5592e-05 | 0.12047 | 0.12047 | 0.12047 | 0.98863 | -0.21682 | 0.98766 | -0.2354 | 33.095
13 | -0.084637 | -0.021501 | 0.084801 | 0.021605 | 0.00016409 | 0.00010467 | 0.12749 | 0.12749 | 0.12749 | 0.98863 | -0.21682 | 0.99072 | -0.17663 | 35.0256
14 | 0.077573 | 0.019702 | -0.077344 | -0.019557 | 0.00022876 | 0.00014584 | 0.11696 | 0.11697 | 0.11697 | 0.98766 | -0.2354 | 0.98448 | -0.29687 | 32.1333
15 | -0.13287 | -0.033731 | 0.13385 | 0.034358 | 0.00098146 | 0.00062728 | 0.19972 | 0.19972 | 0.19972 | 0.99072 | -0.17663 | 0.99871 | -0.024326 | 54.8672
16 | 0.048068 | 0.012126 | -0.047887 | -0.012011 | 0.00018109 | 0.00011471 | 0.072224 | 0.072224 | 0.072224 | 0.99072 | -0.17663 | 0.98664 | -0.25564 | 19.8418
17 | 0.0038278 | 0.00095911 | -0.0038275 | -0.00095925 | 3.678e-07 | -1.3713e-07 | 0.0057856 | 0.0057857 | 0.0057857 | 0.98448 | -0.29687 | 0.98438 | -0.29888 | 1.5895
18 | 0.0015988 | 0.00039892 | -0.0015986 | -0.00039979 | 1.6815e-07 | -8.6902e-07 | 0.0024159 | 0.0024162 | 0.0024162 | 0.98448 | -0.29687 | 0.98437 | -0.29908 | 0.6638
19 | 0.071917 | 0.018199 | -0.07186 | -0.018162 | 5.7007e-05 | 3.6321e-05 | 0.10876 | 0.10876 | 0.10876 | 0.98448 | -0.29687 | 0.98363 | -0.3134 | 29.8801
20 | -0.15899 | -0.040659 | 0.15904 | 0.040693 | 5.2991e-05 | 3.3783e-05 | 0.23717 | 0.23717 | 0.23717 | 0.99871 | -0.024326 | 0.99908 | -0.017441 | 32.5785
21 | 0.024908 | 0.0062493 | -0.024894 | -0.0062406 | 1.4103e-05 | 8.6859e-06 | 0.037568 | 0.037568 | 0.037568 | 0.98664 | -0.25564 | 0.98603 | -0.26752 | 10.321
22 | 0.022978 | 0.0057618 | -0.022972 | -0.005758 | 6.2521e-06 | 3.8241e-06 | 0.034656 | 0.034656 | 0.034656 | 0.98664 | -0.25564 | 0.98635 | -0.26135 | 9.5208
23 | 0.0015986 | 0.00039979 | -0.0015985 | -0.00040026 | 9.1197e-08 | -4.711e-07 | 0.0024162 | 0.0024164 | 0.0024164 | 0.98437 | -0.29908 | 0.98431 | -0.30028 | 0.66385
24 | -0.15945 | -0.040796 | 0.15959 | 0.040882 | 0.00013474 | 8.5903e-05 | 0.23778 | 0.23778 | 0.23778 | 0.99908 | -0.017441 | 1 | 0 | 32.6628
25 | 0.010561 | 0.0026483 | -0.010555 | -0.0026453 | 5.7582e-06 | 2.9146e-06 | 0.015938 | 0.015938 | 0.015938 | 0.98603 | -0.26752 | 0.98545 | -0.27896 | 4.3786
26 | 0.011082 | 0.0027782 | -0.011078 | -0.0027762 | 3.8263e-06 | 1.9831e-06 | 0.016719 | 0.016719 | 0.016719 | 0.98635 | -0.26135 | 0.98598 | -0.26859 | 4.5931
27 | 0.0011172 | 0.00027963 | -0.0011172 | -0.00027999 | 3.2242e-08 | -3.625e-07 | 0.0016888 | 0.0016889 | 0.0016889 | 0.98431 | -0.30028 | 0.98427 | -0.30088 | 0.46399
28 | 0.0040846 | 0.0010234 | -0.0040843 | -0.0010235 | 3.0123e-07 | -7.6806e-08 | 0.0061643 | 0.0061644 | 0.0061644 | 0.98598 | -0.26859 | 0.9859 | -0.27014 | 1.6935
29 | -0.027416 | -0.0068905 | 0.027421 | 0.0068934 | 4.6743e-06 | 2.9022e-06 | 0.041785 | 0.041785 | 0.041785 | 0.9765 | -0.45272 | 0.97668 | -0.44914 | 11.4794
30 | 0.018276 | 0.0045998 | -0.018262 | -0.0045914 | 1.41e-05 | 8.4187e-06 | 0.027857 | 0.027857 | 0.027857 | 0.9765 | -0.45272 | 0.97567 | -0.46887 | 7.6531
31 | -0.030986 | -0.0077869 | 0.031001 | 0.0077962 | 1.4951e-05 | 9.3446e-06 | 0.047216 | 0.047216 | 0.047216 | 0.97668 | -0.44914 | 0.97719 | -0.43904 | 12.9715
32 | 0.018262 | 0.0045914 | -0.018257 | -0.0045885 | 4.9512e-06 | 2.9564e-06 | 0.027857 | 0.027858 | 0.027858 | 0.97567 | -0.46887 | 0.97538 | -0.47455 | 7.6532
33 | -0.033012 | -0.0083003 | 0.033017 | 0.0083032 | 4.7239e-06 | 2.9609e-06 | 0.050279 | 0.050279 | 0.050279 | 0.97719 | -0.43904 | 0.97734 | -0.43605 | 13.8128
34 | 0.01411 | 0.0035489 | -0.014084 | -0.0035343 | 2.57e-05 | 1.4607e-05 | 0.02153 | 0.02153 | 0.02153 | 0.97538 | -0.47455 | 0.97344 | -0.51275 | 5.9149
35 | -0.035436 | -0.0089095 | 0.035454 | 0.0089212 | 1.8667e-05 | 1.1732e-05 | 0.053961 | 0.053961 | 0.053961 | 0.97734 | -0.43605 | 0.97791 | -0.42502 | 14.8246
36 | 0.014084 | 0.0035343 | -0.014072 | -0.0035278 | 1.1447e-05 | 6.5081e-06 | 0.02153 | 0.021531 | 0.021531 | 0.97344 | -0.51275 | 0.97258 | -0.52981 | 5.915
37 | -0.036529 | -0.0091906 | 0.036539 | 0.0091964 | 9.2287e-06 | 5.8064e-06 | 0.055597 | 0.055597 | 0.055597 | 0.97791 | -0.42502 | 0.97818 | -0.41974 | 15.2739
38 | 0.011612 | 0.0029114 | -0.01161 | -0.0029103 | 2.0658e-06 | 1.1056e-06 | 0.017767 | 0.017767 | 0.017767 | 0.97258 | -0.52981 | 0.97239 | -0.53354 | 4.881
39 | 0.00246 | 0.0006164 | -0.0024599 | -0.00061652 | 6.6664e-08 | -1.1307e-07 | 0.0037637 | 0.0037637 | 0.0037637 | 0.97258 | -0.52981 | 0.97255 | -0.53038 | 1.034
40 | 0.0011606 | 0.00029074 | -0.0011606 | -0.00029088 | 1.4132e-08 | -1.3916e-07 | 0.001776 | 0.0017761 | 0.0017761 | 0.97239 | -0.53354 | 0.97238 | -0.5338 | 0.48793
41 | 0.01045 | 0.0026195 | -0.010447 | -0.0026184 | 2.318e-06 | 1.1838e-06 | 0.015991 | 0.015991 | 0.015991 | 0.97239 | -0.53354 | 0.97216 | -0.5382 | 4.3932
42 | -0.037864 | -0.0095285 | 0.037866 | 0.0095298 | 2.1883e-06 | 1.3784e-06 | 0.057613 | 0.057613 | 0.057613 | 0.97818 | -0.41974 | 0.97824 | -0.41853 | 15.8276
43 | 0.0015116 | 0.0003787 | -0.0015116 | -0.00037883 | 2.216e-08 | -1.306e-07 | 0.0022814 | 0.0022814 | 0.0022814 | 0.9859 | -0.27014 | 0.98588 | -0.27045 | 0.62677

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.16489 | 0.041797

## res_load
| p_mw | q_mvar
0 | 0.0038188 | 0.00095708
1 | 0.00085138 | 0.00021338
2 | 0.0020098 | 0.0005037
3 | 0.0064857 | 0.0016255
4 | 0.0044273 | 0.0011096
5 | 0.0036356 | 0.00091118
6 | 0.0035739 | 0.00089571
7 | 0.0013179 | 0.00033029
8 | 0.00086047 | 0.00021565
9 | 0.0046689 | 0.0011701
10 | 0.0023238 | 0.00058241
11 | 0.025139 | 0.0063005
12 | 0.0038275 | 0.00095925
13 | 0.0025843 | 0.00064768
14 | 0.00041174 | 0.00010319
15 | 0.014334 | 0.0035923
16 | 0.01189 | 0.0029799
17 | 0.00048131 | 0.00012063
18 | 0.0036523 | 0.00091536
19 | 0.010555 | 0.0026453
20 | 0.0069937 | 0.0017528
21 | 0.0011172 | 0.00027999
22 | 0.00914 | 0.0022907
23 | 0.0035649 | 0.00089345
24 | 0.0020111 | 0.00050402
25 | 0.0041479 | 0.0010396
26 | 0.002419 | 0.00060625
27 | 0.001075 | 0.00026942
28 | 0.0024599 | 0.00061652
29 | 0.0011606 | 0.00029088
30 | 0.010447 | 0.0026184
31 | 0.0013249 | 0.00033205
32 | 0.0041353 | 0.0010364
33 | 0.0025727 | 0.00064478
34 | 0.0015116 | 0.00037883

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1