## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_120-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_120-1_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_120-1_0_6_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_120-1_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_120-1_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_120-1_0_6_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_120-1_0_6_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_120-1_0_6_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_120-1_0_6_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_120-1_0_6_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_120-1_0_6_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_120-1_0_6_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_120-1_0_6_node_38 | 0.4 | n |  | TRUE
13 | bus_LV_120-1_0_6_node_124 | 0.4 | n |  | TRUE
14 | bus_LV_120-1_0_6_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_120-1_0_6_node_40 | 0.4 | n |  | TRUE
16 | bus_LV_120-1_0_6_node_41 | 0.4 | n |  | TRUE
17 | bus_LV_120-1_0_6_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_120-1_0_6_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_120-1_0_6_node_123 | 0.4 | n |  | TRUE
20 | bus_LV_120-1_0_6_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_120-1_0_6_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_120-1_0_6_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_120-1_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_120-1_0_6_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_120-1_0_6_node_121 | 0.4 | n |  | TRUE
26 | bus_LV_120-1_0_6_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_120-1_0_6_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_120-1_0_6_node_120 | 0.4 | n |  | TRUE
29 | bus_LV_120-1_0_6_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_120-1_0_6_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_120-1_0_6_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_120-1_0_6_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_120-1_0_6_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_120-1_0_6_node_75 | 0.4 | n |  | TRUE
35 | bus_LV_120-1_0_6_node_74 | 0.4 | n |  | TRUE
36 | bus_LV_120-1_0_6_node_164 | 0.4 | n |  | TRUE
37 | bus_LV_120-1_0_6_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_120-1_0_6_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_120-1_0_6_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_120-1_0_6_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_120-1_0_6_node_166 | 0.4 | n |  | TRUE
42 | bus_LV_120-1_0_6_node_165 | 0.4 | n |  | TRUE
43 | bus_LV_120-1_0_6_node_72 | 0.4 | n |  | TRUE
44 | bus_LV_120-1_0_6_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_120-1_0_6_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_120-1_0_6_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_120-1_0_6_node_31 | 0.4 | n |  | TRUE
48 | bus_LV_120-1_0_6_node_32 | 0.4 | n |  | TRUE
49 | bus_LV_120-1_0_6_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_120-1_0_6_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_120-1_0_6_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_120-1_0_6_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_120-1_0_6_node_105 | 0.4 | n |  | TRUE
54 | bus_LV_120-1_0_6_node_106 | 0.4 | n |  | TRUE
55 | bus_LV_120-1_0_6_node_118 | 0.4 | n |  | TRUE
56 | bus_LV_120-1_0_6_node_112 | 0.4 | n |  | TRUE
57 | bus_LV_120-1_0_6_node_119 | 0.4 | n |  | TRUE
58 | bus_LV_120-1_0_6_node_117 | 0.4 | n |  | TRUE
59 | bus_LV_120-1_0_6_node_109 | 0.4 | n |  | TRUE
60 | bus_LV_120-1_0_6_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_120-1_0_6_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_120-1_0_6_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_120-1_0_6_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_120-1_0_6_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_120-1_0_6_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_120-1_0_6_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_120-1_0_6_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_120-1_0_6_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_120-1_0_6_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_120-1_0_6_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_120-1_0_6_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_120-1_0_6_node_59 | 0.4 | n |  | TRUE
73 | bus_LV_120-1_0_6_node_58 | 0.4 | n |  | TRUE
74 | bus_LV_120-1_0_6_node_161 | 0.4 | n |  | TRUE
75 | bus_LV_120-1_0_6_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_120-1_0_6_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_120-1_0_6_node_162 | 0.4 | n |  | TRUE
78 | bus_LV_120-1_0_6_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_120-1_0_6_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_120-1_0_6_node_68 | 0.4 | n |  | TRUE
81 | bus_LV_120-1_0_6_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_120-1_0_6_node_77 | 0.4 | n |  | TRUE
83 | bus_LV_120-1_0_6_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_120-1_0_6_node_73 | 0.4 | n |  | TRUE
85 | bus_LV_120-1_0_6_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_120-1_0_6_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_120-1_0_6_node_67 | 0.4 | n |  | TRUE
88 | bus_LV_120-1_0_6_node_78 | 0.4 | n |  | TRUE
89 | bus_LV_120-1_0_6_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_120-1_0_6_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_120-1_0_6_node_104 | 0.4 | n |  | TRUE
92 | bus_LV_120-1_0_6_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_120-1_0_6_node_83 | 0.4 | n |  | TRUE
94 | bus_LV_120-1_0_6_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_120-1_0_6_node_80 | 0.4 | n |  | TRUE
96 | bus_LV_120-1_0_6_node_82 | 0.4 | n |  | TRUE
97 | bus_LV_120-1_0_6_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_120-1_0_6_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_120-1_0_6_node_86 | 0.4 | n |  | TRUE
100 | bus_LV_120-1_0_6_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_120-1_0_6_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_120-1_0_6_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_120-1_0_6_node_85 | 0.4 | n |  | TRUE
104 | bus_LV_120-1_0_6_node_89 | 0.4 | n |  | TRUE
105 | bus_LV_120-1_0_6_node_97 | 0.4 | n |  | TRUE
106 | bus_LV_120-1_0_6_node_101 | 0.4 | n |  | TRUE
107 | bus_LV_120-1_0_6_node_129 | 0.4 | n |  | TRUE
108 | bus_LV_120-1_0_6_node_141 | 0.4 | n |  | TRUE
109 | bus_LV_120-1_0_6_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_120-1_0_6_node_144 | 0.4 | n |  | TRUE
111 | bus_LV_120-1_0_6_node_131 | 0.4 | n |  | TRUE
112 | bus_LV_120-1_0_6_node_132 | 0.4 | n |  | TRUE
113 | bus_LV_120-1_0_6_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_120-1_0_6_node_136 | 0.4 | n |  | TRUE
115 | bus_LV_120-1_0_6_node_133 | 0.4 | n |  | TRUE
116 | bus_LV_120-1_0_6_node_94 | 0.4 | n |  | TRUE
117 | bus_LV_120-1_0_6_node_96 | 0.4 | n |  | TRUE
118 | bus_LV_120-1_0_6_node_92 | 0.4 | n |  | TRUE
119 | bus_LV_120-1_0_6_node_130 | 0.4 | n |  | TRUE
120 | bus_LV_120-1_0_6_node_142 | 0.4 | n |  | TRUE
121 | bus_LV_120-1_0_6_node_93 | 0.4 | n |  | TRUE
122 | bus_LV_120-1_0_6_node_95 | 0.4 | n |  | TRUE
123 | bus_LV_120-1_0_6_node_99 | 0.4 | n |  | TRUE
124 | bus_LV_120-1_0_6_node_100 | 0.4 | n |  | TRUE
125 | bus_LV_120-1_0_6_node_116 | 0.4 | n |  | TRUE
126 | bus_LV_120-1_0_6_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_120-1_0_6_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_120-1_0_6_node_145 | 0.4 | n |  | TRUE
129 | bus_LV_120-1_0_6_node_134 | 0.4 | n |  | TRUE
130 | bus_LV_120-1_0_6_node_122 | 0.4 | n |  | TRUE
131 | bus_LV_120-1_0_6_node_107 | 0.4 | n |  | TRUE
132 | bus_LV_120-1_0_6_node_108 | 0.4 | n |  | TRUE
133 | bus_LV_120-1_0_6_node_111 | 0.4 | n |  | TRUE
134 | bus_LV_120-1_0_6_node_110 | 0.4 | n |  | TRUE
135 | bus_LV_120-1_0_6_node_113 | 0.4 | n |  | TRUE
136 | bus_LV_120-1_0_6_node_138 | 0.4 | n |  | TRUE
137 | bus_LV_120-1_0_6_node_139 | 0.4 | n |  | TRUE
138 | bus_LV_120-1_0_6_node_137 | 0.4 | n |  | TRUE
139 | bus_LV_120-1_0_6_node_140 | 0.4 | n |  | TRUE
140 | bus_LV_120-1_0_6_node_146 | 0.4 | n |  | TRUE
141 | bus_LV_120-1_0_6_node_128 | 0.4 | n |  | TRUE
142 | bus_LV_120-1_0_6_node_126 | 0.4 | n |  | TRUE
143 | bus_LV_120-1_0_6_node_153 | 0.4 | n |  | TRUE
144 | bus_LV_120-1_0_6_node_151 | 0.4 | n |  | TRUE
145 | bus_LV_120-1_0_6_node_135 | 0.4 | n |  | TRUE
146 | bus_LV_120-1_0_6_node_147 | 0.4 | n |  | TRUE
147 | bus_LV_120-1_0_6_node_148 | 0.4 | n |  | TRUE
148 | bus_LV_120-1_0_6_node_150 | 0.4 | n |  | TRUE
149 | bus_LV_120-1_0_6_node_159 | 0.4 | n |  | TRUE
150 | bus_LV_120-1_0_6_node_158 | 0.4 | n |  | TRUE
151 | bus_LV_120-1_0_6_node_154 | 0.4 | n |  | TRUE
152 | bus_LV_120-1_0_6_node_152 | 0.4 | n |  | TRUE
153 | bus_LV_120-1_0_6_node_167 | 0.4 | n |  | TRUE
154 | bus_LV_120-1_0_6_node_160 | 0.4 | n |  | TRUE
155 | bus_LV_120-1_0_6_node_156 | 0.4 | n |  | TRUE
156 | bus_LV_120-1_0_6_node_155 | 0.4 | n |  | TRUE
157 | bus_MV_10_0_node_38 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_120-1_0_6_load_0 | 0 | 0.0036245 | 0.00090838 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_120-1_0_6_load_5 | 4 | 0.0016818 | 0.0004215 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_120-1_0_6_load_7 | 7 | 0.0095722 | 0.002399 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_120-1_0_6_load_13 | 11 | 0.0010748 | 0.00026936 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_120-1_0_6_load_38 | 12 | 0.0073507 | 0.0018423 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_120-1_0_6_load_10 | 14 | 0.00051497 | 0.00012906 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_120-1_0_6_load_40 | 15 | 0.00078968 | 0.00019791 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_120-1_0_6_load_41 | 16 | 0.002683 | 0.00067242 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_120-1_0_6_load_35 | 18 | 0.0039355 | 0.00098633 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_120-1_0_6_load_123 | 19 | 0.0070712 | 0.0017722 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_120-1_0_6_load_12 | 20 | 0.0019053 | 0.00047753 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_120-1_0_6_load_14 | 21 | 0.00045914 | 0.00011507 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_120-1_0_6_load_15 | 22 | 0.013418 | 0.0033629 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_120-1_0_6_load_16 | 23 | 0.0002782 | 6.9724e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_120-1_0_6_load_121 | 25 | 0.0017418 | 0.00043654 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_120-1_0_6_load_120 | 28 | 0.0033334 | 0.00083544 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_120-1_0_6_load_17 | 29 | 0.01672 | 0.0041904 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_120-1_0_6_load_26 | 31 | 0.0026899 | 0.00067415 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_120-1_0_6_load_75 | 34 | 0.020424 | 0.0051188 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_120-1_0_6_load_74 | 35 | 0.0043921 | 0.0011008 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_120-1_0_6_load_164 | 36 | 0.0021181 | 0.00053086 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_120-1_0_6_load_29 | 39 | 0.00085936 | 0.00021538 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_120-1_0_6_load_166 | 41 | 0.0044005 | 0.0011029 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_120-1_0_6_load_165 | 42 | 0.00262 | 0.00065663 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_120-1_0_6_load_72 | 43 | 0.0020764 | 0.0005204 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_120-1_0_6_load_44 | 44 | 0.00085901 | 0.00021529 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_120-1_0_6_load_30 | 46 | 0.016671 | 0.0041783 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_120-1_0_6_load_31 | 47 | 0.0038194 | 0.00095724 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_120-1_0_6_load_33 | 49 | 0.00287 | 0.00071928 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_120-1_0_6_load_34 | 51 | 0.0029316 | 0.00073472 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_120-1_0_6_load_105 | 53 | 0.0039737 | 0.00099591 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_120-1_0_6_load_118 | 55 | 0.0036572 | 0.00091658 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_120-1_0_6_load_112 | 56 | 0.0081736 | 0.0020485 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_120-1_0_6_load_119 | 57 | 0.019535 | 0.004896 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_120-1_0_6_load_47 | 60 | 0.0034081 | 0.00085416 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_120-1_0_6_load_48 | 61 | 0.0031928 | 0.00080019 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_120-1_0_6_load_49 | 62 | 0.013667 | 0.0034253 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_120-1_0_6_load_53 | 64 | 0.0061523 | 0.0015419 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_120-1_0_6_load_55 | 66 | 0.0017513 | 0.00043893 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_120-1_0_6_load_52 | 67 | 0.0010226 | 0.00025629 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_120-1_0_6_load_59 | 72 | 0.00094192 | 0.00023607 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_120-1_0_6_load_58 | 73 | 0.0010766 | 0.00026982 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_120-1_0_6_load_161 | 74 | 0.0020598 | 0.00051622 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_120-1_0_6_load_61 | 75 | 0.005753 | 0.0014418 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_120-1_0_6_load_162 | 77 | 0.0059142 | 0.0014822 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_120-1_0_6_load_65 | 78 | 0.0012023 | 0.00030132 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_120-1_0_6_load_68 | 80 | 0.0045843 | 0.0011489 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_120-1_0_6_load_66 | 81 | 0.0038337 | 0.00096081 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_120-1_0_6_load_77 | 82 | 0.0032467 | 0.0008137 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_120-1_0_6_load_76 | 85 | 0.0018632 | 0.00046696 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_120-1_0_6_load_71 | 86 | 0.0028994 | 0.00072665 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_120-1_0_6_load_78 | 88 | 0.0027403 | 0.00068677 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_120-1_0_6_load_70 | 89 | 0.0039404 | 0.00098756 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_120-1_0_6_load_69 | 90 | 0.0054848 | 0.0013746 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_120-1_0_6_load_104 | 91 | 0.0015726 | 0.00039412 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_120-1_0_6_load_83 | 93 | 0.0027642 | 0.00069276 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_120-1_0_6_load_79 | 94 | 0.0026406 | 0.00066181 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_120-1_0_6_load_80 | 95 | 0.0049828 | 0.0012488 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_120-1_0_6_load_82 | 96 | 0.0053456 | 0.0013397 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_120-1_0_6_load_91 | 101 | 0.0023834 | 0.00059733 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_120-1_0_6_load_87 | 102 | 0.015555 | 0.0038984 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_120-1_0_6_load_85 | 103 | 0.008449 | 0.0021175 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_120-1_0_6_load_129 | 107 | 0.0016974 | 0.00042541 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_120-1_0_6_load_141 | 108 | 0.0028349 | 0.00071049 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_120-1_0_6_load_103 | 109 | 0.0018531 | 0.00046443 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_120-1_0_6_load_144 | 110 | 0.0073114 | 0.0018324 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_120-1_0_6_load_131 | 111 | 0.0018783 | 0.00047076 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_120-1_0_6_load_132 | 112 | 0.0046398 | 0.0011628 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_120-1_0_6_load_136 | 114 | 0.033475 | 0.0083896 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_120-1_0_6_load_133 | 115 | 0.0046433 | 0.0011637 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_120-1_0_6_load_96 | 117 | 0.002136 | 0.00053534 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_120-1_0_6_load_92 | 118 | 0.0044583 | 0.0011174 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_120-1_0_6_load_130 | 119 | 0.0011468 | 0.00028742 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_120-1_0_6_load_142 | 120 | 0.0033039 | 0.00082803 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_120-1_0_6_load_93 | 121 | 0.0019668 | 0.00049292 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_120-1_0_6_load_95 | 122 | 0.0010363 | 0.00025973 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_120-1_0_6_load_99 | 123 | 0.00034105 | 8.5475e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_120-1_0_6_load_100 | 124 | 0.0014671 | 0.00036769 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_120-1_0_6_load_114 | 126 | 0.0031609 | 0.00079219 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_120-1_0_6_load_115 | 127 | 0.010428 | 0.0026136 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_120-1_0_6_load_145 | 128 | 0.002916 | 0.00073081 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_120-1_0_6_load_134 | 129 | 0.0040247 | 0.0010087 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_120-1_0_6_load_122 | 130 | 0.0022719 | 0.0005694 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_120-1_0_6_load_107 | 131 | 0.0028694 | 0.00071913 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_120-1_0_6_load_108 | 132 | 0.0056147 | 0.0014072 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_120-1_0_6_load_111 | 133 | 0.0075887 | 0.0019019 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_120-1_0_6_load_110 | 134 | 0.0082018 | 0.0020556 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_120-1_0_6_load_139 | 137 | 0.0030839 | 0.00077291 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_120-1_0_6_load_137 | 138 | 0.0046688 | 0.0011701 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_120-1_0_6_load_128 | 141 | 0.0049742 | 0.0012466 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_120-1_0_6_load_126 | 142 | 0.0055294 | 0.0013858 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_120-1_0_6_load_153 | 143 | 0.0086985 | 0.00218 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_120-1_0_6_load_135 | 145 | 0.015252 | 0.0038226 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_120-1_0_6_load_148 | 147 | 0.0014347 | 0.00035957 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_120-1_0_6_load_158 | 150 | 0.0016045 | 0.00040213 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_120-1_0_6_load_154 | 151 | 0.0015816 | 0.00039638 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_120-1_0_6_load_167 | 153 | 0.0064076 | 0.0016059 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_120-1_0_6_load_160 | 154 | 0.0084553 | 0.0021191 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_120-1_0_6_load_155 | 156 | 0.0087193 | 0.0021853 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 118 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_120-1_0_6_line_0 |  | 0 | 1 | 0.025414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_120-1_0_6_line_1 |  | 1 | 5 | 0.049557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_120-1_0_6_line_2 |  | 2 | 3 | 0.016776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_120-1_0_6_line_3 |  | 2 | 4 | 0.0081427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_120-1_0_6_line_4 |  | 3 | 7 | 0.013297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_120-1_0_6_line_5 |  | 4 | 9 | 0.0097145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_120-1_0_6_line_6 |  | 5 | 10 | 0.007098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_120-1_0_6_line_7 |  | 5 | 11 | 0.0043124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_120-1_0_6_line_8 |  | 6 | 7 | 0.046572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_120-1_0_6_line_9 |  | 6 | 8 | 0.012728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_120-1_0_6_line_10 |  | 8 | 12 | 0.013422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_120-1_0_6_line_11 |  | 8 | 13 | 0.032967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_120-1_0_6_line_12 |  | 9 | 14 | 0.03318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_120-1_0_6_line_13 |  | 10 | 15 | 0.018483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_120-1_0_6_line_14 |  | 10 | 16 | 0.035425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_120-1_0_6_line_15 |  | 11 | 17 | 0.02823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_120-1_0_6_line_16 |  | 12 | 18 | 0.014822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_120-1_0_6_line_17 |  | 13 | 19 | 0.016882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_120-1_0_6_line_18 |  | 15 | 38 | 0.0015059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_120-1_0_6_line_19 |  | 17 | 20 | 0.021258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_120-1_0_6_line_20 |  | 17 | 21 | 0.036315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_120-1_0_6_line_21 |  | 18 | 48 | 0.017596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_120-1_0_6_line_22 |  | 20 | 22 | 0.032901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_120-1_0_6_line_23 |  | 21 | 23 | 0.0076336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_120-1_0_6_line_24 |  | 22 | 24 | 0.0058158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_120-1_0_6_line_25 |  | 23 | 25 | 0.0082297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_120-1_0_6_line_26 |  | 24 | 26 | 0.010527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_120-1_0_6_line_27 |  | 24 | 27 | 0.043836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_120-1_0_6_line_28 |  | 25 | 28 | 0.0097612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_120-1_0_6_line_29 |  | 26 | 29 | 0.039174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_120-1_0_6_line_30 |  | 27 | 36 | 0.026334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_120-1_0_6_line_31 |  | 28 | 53 | 0.0061238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_120-1_0_6_line_32 |  | 30 | 31 | 0.0044784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_120-1_0_6_line_33 |  | 30 | 32 | 0.017012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_120-1_0_6_line_34 |  | 31 | 40 | 0.027589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_120-1_0_6_line_35 |  | 32 | 41 | 0.011573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_120-1_0_6_line_36 |  | 32 | 42 | 0.033025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_120-1_0_6_line_37 |  | 33 | 34 | 0.067235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_120-1_0_6_line_38 |  | 33 | 35 | 0.013183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_120-1_0_6_line_39 |  | 35 | 43 | 0.012544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_120-1_0_6_line_40 |  | 37 | 38 | 0.01074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_120-1_0_6_line_41 |  | 37 | 39 | 0.013938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_120-1_0_6_line_42 |  | 38 | 44 | 0.017818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_120-1_0_6_line_43 |  | 39 | 40 | 0.04328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_120-1_0_6_line_44 |  | 40 | 45 | 0.029781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_120-1_0_6_line_45 |  | 43 | 90 | 0.016266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_120-1_0_6_line_46 |  | 45 | 60 | 0.007744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_120-1_0_6_line_47 |  | 45 | 61 | 0.010831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_120-1_0_6_line_48 |  | 46 | 47 | 0.010941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_120-1_0_6_line_49 |  | 46 | 48 | 0.029003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_120-1_0_6_line_50 |  | 47 | 49 | 0.032176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_120-1_0_6_line_51 |  | 49 | 50 | 0.015362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_120-1_0_6_line_52 |  | 50 | 53 | 0.026861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_120-1_0_6_line_53 |  | 50 | 54 | 0.016029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_120-1_0_6_line_54 |  | 51 | 52 | 0.011939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_120-1_0_6_line_55 |  | 52 | 54 | 0.017586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_120-1_0_6_line_56 |  | 52 | 55 | 0.039659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_120-1_0_6_line_57 |  | 52 | 56 | 0.016336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_120-1_0_6_line_58 |  | 54 | 57 | 0.036673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_120-1_0_6_line_59 |  | 55 | 58 | 0.023802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_120-1_0_6_line_60 |  | 56 | 59 | 0.008878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_120-1_0_6_line_61 |  | 57 | 130 | 0.010398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_120-1_0_6_line_62 |  | 58 | 125 | 0.004229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_120-1_0_6_line_63 |  | 59 | 133 | 0.022956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_120-1_0_6_line_64 |  | 59 | 131 | 0.027752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_120-1_0_6_line_65 |  | 62 | 63 | 0.059213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_120-1_0_6_line_66 |  | 63 | 64 | 0.021882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_120-1_0_6_line_67 |  | 63 | 65 | 0.039446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_120-1_0_6_line_68 |  | 64 | 66 | 0.040138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_120-1_0_6_line_69 |  | 65 | 67 | 0.0024551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_120-1_0_6_line_70 |  | 66 | 71 | 0.016155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_120-1_0_6_line_71 |  | 67 | 68 | 0.006533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_120-1_0_6_line_72 |  | 68 | 69 | 0.055421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_120-1_0_6_line_73 |  | 68 | 70 | 0.11058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_120-1_0_6_line_74 |  | 69 | 72 | 0.014006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_120-1_0_6_line_75 |  | 70 | 73 | 0.00063464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_120-1_0_6_line_76 |  | 71 | 75 | 0.035438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_120-1_0_6_line_77 |  | 71 | 76 | 0.061789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_120-1_0_6_line_78 |  | 72 | 77 | 0.038685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_120-1_0_6_line_79 |  | 73 | 74 | 0.13626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_120-1_0_6_line_80 |  | 75 | 78 | 0.018517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_120-1_0_6_line_81 |  | 76 | 82 | 0.032865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_120-1_0_6_line_82 |  | 79 | 80 | 0.057909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_120-1_0_6_line_83 |  | 79 | 81 | 0.015645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_120-1_0_6_line_84 |  | 80 | 86 | 0.0070554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_120-1_0_6_line_85 |  | 81 | 87 | 0.011737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_120-1_0_6_line_86 |  | 82 | 85 | 0.00098234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_120-1_0_6_line_87 |  | 83 | 84 | 0.023414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_120-1_0_6_line_88 |  | 83 | 85 | 0.0079995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_120-1_0_6_line_89 |  | 84 | 88 | 0.0095036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_120-1_0_6_line_90 |  | 84 | 89 | 0.013054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_120-1_0_6_line_91 |  | 86 | 91 | 0.037405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_120-1_0_6_line_92 |  | 87 | 90 | 0.022033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_120-1_0_6_line_93 |  | 87 | 89 | 0.0305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_120-1_0_6_line_94 |  | 88 | 92 | 0.0089664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_120-1_0_6_line_95 |  | 92 | 93 | 0.0030684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_120-1_0_6_line_96 |  | 92 | 94 | 0.01427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_120-1_0_6_line_97 |  | 93 | 97 | 0.02201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_120-1_0_6_line_98 |  | 94 | 95 | 0.0072676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_120-1_0_6_line_99 |  | 95 | 96 | 0.012635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_120-1_0_6_line_100 |  | 97 | 98 | 0.031515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_120-1_0_6_line_101 |  | 97 | 99 | 0.022471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_120-1_0_6_line_102 |  | 98 | 100 | 0.017504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_120-1_0_6_line_103 |  | 98 | 101 | 0.0075523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_120-1_0_6_line_104 |  | 99 | 102 | 0.02406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_120-1_0_6_line_105 |  | 99 | 103 | 0.022637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_120-1_0_6_line_106 |  | 100 | 107 | 0.019122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_120-1_0_6_line_107 |  | 101 | 108 | 0.0023376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_120-1_0_6_line_108 |  | 104 | 105 | 0.014382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_120-1_0_6_line_109 |  | 104 | 106 | 0.03602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_120-1_0_6_line_110 |  | 105 | 109 | 0.014582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_120-1_0_6_line_111 |  | 106 | 110 | 0.02661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_120-1_0_6_line_112 |  | 106 | 111 | 0.015629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_120-1_0_6_line_113 |  | 106 | 112 | 0.013047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_120-1_0_6_line_114 |  | 107 | 119 | 0.0065437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_120-1_0_6_line_115 |  | 108 | 120 | 0.021958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_120-1_0_6_line_116 |  | 109 | 123 | 0.033726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_120-1_0_6_line_117 |  | 110 | 128 | 0.0049841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_120-1_0_6_line_118 |  | 111 | 119 | 0.01001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_120-1_0_6_line_119 |  | 113 | 114 | 0.068258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_120-1_0_6_line_120 |  | 113 | 115 | 0.019437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_120-1_0_6_line_121 |  | 115 | 129 | 0.028562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_120-1_0_6_line_122 |  | 116 | 117 | 0.019697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_120-1_0_6_line_123 |  | 116 | 118 | 0.0087155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_120-1_0_6_line_124 |  | 117 | 124 | 0.021758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_120-1_0_6_line_125 |  | 118 | 121 | 0.017503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
126 | LV_120-1_0_6_line_126 |  | 121 | 122 | 0.038306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_120-1_0_6_line_127 |  | 122 | 123 | 0.0098824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
128 | LV_120-1_0_6_line_128 |  | 124 | 125 | 0.017912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
129 | LV_120-1_0_6_line_129 |  | 125 | 127 | 0.0009061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_120-1_0_6_line_130 |  | 126 | 127 | 0.020141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_120-1_0_6_line_131 |  | 128 | 146 | 0.0154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_120-1_0_6_line_132 |  | 129 | 145 | 0.0035106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_120-1_0_6_line_133 |  | 131 | 132 | 0.031242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_120-1_0_6_line_134 |  | 133 | 135 | 0.012404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_120-1_0_6_line_135 |  | 134 | 135 | 0.049047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_120-1_0_6_line_136 |  | 135 | 136 | 0.021406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_120-1_0_6_line_137 |  | 136 | 137 | 0.011982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_120-1_0_6_line_138 |  | 136 | 138 | 0.014266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_120-1_0_6_line_139 |  | 137 | 140 | 0.0055418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_120-1_0_6_line_140 |  | 138 | 145 | 0.011695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_120-1_0_6_line_141 |  | 139 | 140 | 0.005232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_120-1_0_6_line_142 |  | 139 | 141 | 0.021976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_120-1_0_6_line_143 |  | 140 | 144 | 0.030941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_120-1_0_6_line_144 |  | 141 | 142 | 0.034615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_120-1_0_6_line_145 |  | 143 | 144 | 0.017493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_120-1_0_6_line_146 |  | 144 | 151 | 0.0073757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_120-1_0_6_line_147 |  | 144 | 148 | 0.066066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_120-1_0_6_line_148 |  | 146 | 147 | 0.012653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_120-1_0_6_line_149 |  | 148 | 149 | 0.041718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_120-1_0_6_line_150 |  | 148 | 150 | 0.0054526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_120-1_0_6_line_151 |  | 149 | 154 | 0.004979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_120-1_0_6_line_152 |  | 149 | 152 | 0.036055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_120-1_0_6_line_153 |  | 150 | 155 | 0.016246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_120-1_0_6_line_154 |  | 152 | 153 | 0.004787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_120-1_0_6_line_155 |  | 155 | 156 | 0.033956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_120-1_0_6_trafo_92 | 0.63 MVA 20/0.4 kV | 157 | 118 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2711533.4721 | 1236751.9603 | 2711555.0055 | 1236765.4581
1 | 2711533.4721 | 1236751.9603 | 2711521.0099 | 1236742.5411 | 2711519.1598 | 1236744.33 | 2711517.8268 | 1236744.3828 | 2711508.9945 | 1236740.7586 | 2711501.5956 | 1236737.3726 | 2711497.1125 | 1236735.4981 | 2711490.1292 | 1236738.1914
2 | 2711598.391 | 1236810.481 | 2711612.5965 | 1236807.679 | 2711614.649 | 1236808.8074
3 | 2711598.391 | 1236810.481 | 2711591.4018 | 1236806.3033
4 | 2711614.649 | 1236808.8074 | 2711625.4986 | 1236816.4946
5 | 2711583.0633 | 1236801.3192 | 2711591.4018 | 1236806.3033
6 | 2711490.1292 | 1236738.1914 | 2711487.277 | 1236731.6883
7 | 2711490.1292 | 1236738.1914 | 2711491.9196 | 1236742.1146
8 | 2711654.7724 | 1236847.236 | 2711655.9786 | 1236841.8545 | 2711655.3706 | 1236837.1616 | 2711644.933 | 1236829.9709 | 2711630.6098 | 1236820.1162 | 2711625.4986 | 1236816.4946
9 | 2711654.7724 | 1236847.236 | 2711656.6399 | 1236850.1512 | 2711657.3509 | 1236854.6014 | 2711656.4004 | 1236859.265
10 | 2711656.4004 | 1236859.265 | 2711653.4213 | 1236862.3336 | 2711649.4855 | 1236864.3612 | 2711644.8776 | 1236865.3722
11 | 2711666.2587 | 1236890.0078 | 2711660.2686 | 1236863.2408 | 2711656.4004 | 1236859.265
12 | 2711583.0633 | 1236801.3192 | 2711554.7907 | 1236783.953
13 | 2711487.277 | 1236731.6883 | 2711483.4342 | 1236733.1952 | 2711477.9878 | 1236734.2493 | 2711475.2787 | 1236734.2318 | 2711469.3182 | 1236732.9427
14 | 2711487.277 | 1236731.6883 | 2711482.4371 | 1236720.5999 | 2711478.8472 | 1236711.0584 | 2711477.0447 | 1236705.0754 | 2711476.2578 | 1236700.6349 | 2711476.0656 | 1236698.2694
15 | 2711503.3146 | 1236767.94 | 2711497.3257 | 1236753.9611 | 2711491.9196 | 1236742.1146
16 | 2711644.8776 | 1236865.3722 | 2711630.4001 | 1236868.5484
17 | 2711666.2587 | 1236890.0078 | 2711669.7782 | 1236906.5193
18 | 2711467.8464 | 1236732.6244 | 2711469.3182 | 1236732.9427
19 | 2711503.3146 | 1236767.94 | 2711487.9057 | 1236773.5663 | 2711483.1298 | 1236774.4323
20 | 2711503.3146 | 1236767.94 | 2711518.7666 | 1236800.804
21 | 2711613.2126 | 1236872.3192 | 2711630.4001 | 1236868.5484
22 | 2711483.1298 | 1236774.4323 | 2711477.2358 | 1236775.5009 | 2711462.7312 | 1236776.0959 | 2711450.3962 | 1236774.888
23 | 2711518.7666 | 1236800.804 | 2711522.0147 | 1236807.7121
24 | 2711444.608 | 1236774.3212 | 2711450.3962 | 1236774.888
25 | 2711525.5164 | 1236815.1597 | 2711522.0147 | 1236807.7121
26 | 2711444.608 | 1236774.3212 | 2711444.1697 | 1236763.8047
27 | 2711444.608 | 1236774.3212 | 2711401.1289 | 1236767.8116
28 | 2711525.5164 | 1236815.1597 | 2711529.6698 | 1236823.9932
29 | 2711444.1697 | 1236763.8047 | 2711405.6114 | 1236756.8852
30 | 2711395.893 | 1236792.3327 | 2711397.7375 | 1236792.0448 | 2711401.1289 | 1236767.8116
31 | 2711529.6698 | 1236823.9932 | 2711532.2754 | 1236829.535
32 | 2711369.9488 | 1236712.8617 | 2711374.4144 | 1236713.2008
33 | 2711353.5126 | 1236708.2944 | 2711369.9488 | 1236712.8617
34 | 2711401.6239 | 1236717.2368 | 2711389.1982 | 1236714.3237 | 2711374.4144 | 1236713.2008
35 | 2711353.5126 | 1236708.2944 | 2711356.2449 | 1236697.0485
36 | 2711353.5126 | 1236708.2944 | 2711345.7976 | 1236740.4055
37 | 2711350.3381 | 1236810.5485 | 2711351.0607 | 1236815.5993 | 2711344.688 | 1236817.6259 | 2711342.9889 | 1236820.2517 | 2711344.1083 | 1236828.3568 | 2711345.1476 | 1236847.1911 | 2711367.0905 | 1236847.4582 | 2711370.3821 | 1236846.9673
38 | 2711350.3381 | 1236810.5485 | 2711344.6569 | 1236813.233 | 2711338.0008 | 1236815.048
39 | 2711338.0008 | 1236815.048 | 2711325.8984 | 1236818.348
40 | 2711457.3322 | 1236730.292 | 2711460.1428 | 1236730.9563 | 2711467.8464 | 1236732.6244
41 | 2711457.3322 | 1236730.292 | 2711443.7623 | 1236727.1119
42 | 2711467.8464 | 1236732.6244 | 2711463.4353 | 1236749.8885
43 | 2711401.6239 | 1236717.2368 | 2711443.7623 | 1236727.1119
44 | 2711401.6239 | 1236717.2368 | 2711409.3763 | 1236688.4818
45 | 2711310.2058 | 1236822.6271 | 2711325.8984 | 1236818.348
46 | 2711409.3763 | 1236688.4818 | 2711416.9113 | 1236690.269
47 | 2711409.3763 | 1236688.4818 | 2711398.9245 | 1236685.6398
48 | 2711590.4933 | 1236848.3838 | 2711601.4205 | 1236848.9377
49 | 2711613.2126 | 1236872.3192 | 2711609.3192 | 1236853.1754 | 2711604.8168 | 1236849.1099 | 2711601.4205 | 1236848.9377
50 | 2711590.4933 | 1236848.3838 | 2711571.6917 | 1236847.4307 | 2711558.6787 | 1236850.4125
51 | 2711543.7048 | 1236853.8435 | 2711558.6787 | 1236850.4125
52 | 2711543.7048 | 1236853.8435 | 2711532.2754 | 1236829.535
53 | 2711543.7048 | 1236853.8435 | 2711550.3327 | 1236868.4461
54 | 2711557.287 | 1236884.6005 | 2711568.9486 | 1236882.0396
55 | 2711557.287 | 1236884.6005 | 2711554.6276 | 1236877.912 | 2711550.3327 | 1236868.4461
56 | 2711557.287 | 1236884.6005 | 2711518.7619 | 1236894.0156
57 | 2711557.287 | 1236884.6005 | 2711563.1345 | 1236899.8543
58 | 2711550.3327 | 1236868.4461 | 2711525.8422 | 1236876.8818 | 2711518.7585 | 1236872.4453 | 2711516.3484 | 1236872.5539
59 | 2711495.6408 | 1236899.6661 | 2711518.7619 | 1236894.0156
60 | 2711566.3123 | 1236908.1441 | 2711563.1345 | 1236899.8543
61 | 2711516.3484 | 1236872.5539 | 2711505.9605 | 1236873.0218
62 | 2711495.6408 | 1236899.6661 | 2711491.52 | 1236900.6673
63 | 2711566.3123 | 1236908.1441 | 2711571.8753 | 1236925.0396 | 2711573.4297 | 1236929.9686
64 | 2711566.3123 | 1236908.1441 | 2711593.3785 | 1236902.0138
65 | 2711235.6238 | 1236733.4833 | 2711256.0044 | 1236728.6946 | 2711266.8851 | 1236722.7826 | 2711277.249 | 1236699.0531
66 | 2711235.6238 | 1236733.4833 | 2711235.3008 | 1236737.7918 | 2711234.8978 | 1236743.144 | 2711233.6106 | 1236748.0237 | 2711231.6991 | 1236754.9105
67 | 2711214.5991 | 1236701.5535 | 2711221.3057 | 1236706.3495 | 2711227.9478 | 1236714.18 | 2711233.3943 | 1236724.023 | 2711235.6238 | 1236733.4833
68 | 2711224.9983 | 1236794.3802 | 2711225.4195 | 1236784.4878 | 2711231.6302 | 1236755.1589 | 2711231.6991 | 1236754.9105
69 | 2711214.5991 | 1236701.5535 | 2711212.3042 | 1236700.6813
70 | 2711224.311 | 1236810.5208 | 2711224.9983 | 1236794.3802
71 | 2711206.1974 | 1236698.3604 | 2711212.3042 | 1236700.6813
72 | 2711221.4752 | 1236646.4057 | 2711222.1952 | 1236651.2007 | 2711222.7779 | 1236659.6849 | 2711206.1974 | 1236698.3604
73 | 2711206.1974 | 1236698.3604 | 2711097.6687 | 1236677.1798
74 | 2711221.4752 | 1236646.4057 | 2711233.496 | 1236639.2174
75 | 2711097.1701 | 1236676.7871 | 2711097.6687 | 1236677.1798
76 | 2711224.311 | 1236810.5208 | 2711207.8 | 1236808.3433 | 2711189.9691 | 1236802.437
77 | 2711224.311 | 1236810.5208 | 2711225.0432 | 1236850.2101 | 2711225.3576 | 1236855.2422 | 2711226.3199 | 1236864.4674 | 2711230.1513 | 1236871.2334
78 | 2711233.496 | 1236639.2174 | 2711236.5848 | 1236637.3704 | 2711266.2389 | 1236618.6176
79 | 2711097.1701 | 1236676.7871 | 2710988.3897 | 1236594.7272
80 | 2711189.9691 | 1236802.437 | 2711182.9635 | 1236800.1164 | 2711185.3145 | 1236789.2304
81 | 2711230.1513 | 1236871.2334 | 2711239.0474 | 1236875.4922 | 2711257.3695 | 1236873.1001 | 2711261.46 | 1236871.1668
82 | 2711262.7572 | 1236836.4055 | 2711255.9136 | 1236805.82 | 2711257.0654 | 1236800.0927 | 2711261.8505 | 1236796.7574 | 2711276.2222 | 1236792.8537
83 | 2711262.7572 | 1236836.4055 | 2711277.7226 | 1236831.8447
84 | 2711276.2222 | 1236792.8537 | 2711283.031 | 1236791.0043
85 | 2711288.9493 | 1236828.4232 | 2711277.7226 | 1236831.8447
86 | 2711261.46 | 1236871.1668 | 2711262.3481 | 1236870.7471 | 2711262.3481 | 1236870.7471
87 | 2711266.7345 | 1236864.0573 | 2711289.1011 | 1236871.193
88 | 2711266.7345 | 1236864.0573 | 2711262.3481 | 1236870.7471
89 | 2711289.1011 | 1236871.193 | 2711298.1554 | 1236874.0805
90 | 2711289.1011 | 1236871.193 | 2711291.5108 | 1236858.3634
91 | 2711283.031 | 1236791.0043 | 2711294.4012 | 1236787.9158 | 2711306.7262 | 1236788.9253 | 2711319.5776 | 1236785.6721
92 | 2711288.9493 | 1236828.4232 | 2711310.2058 | 1236822.6271
93 | 2711288.9493 | 1236828.4232 | 2711293.1367 | 1236849.7073 | 2711291.5108 | 1236858.3634
94 | 2711306.6979 | 1236876.8049 | 2711298.1554 | 1236874.0805
95 | 2711306.6979 | 1236876.8049 | 2711309.6164 | 1236877.7521
96 | 2711306.6979 | 1236876.8049 | 2711312.232 | 1236863.6512
97 | 2711330.5516 | 1236884.5468 | 2711309.6164 | 1236877.7521
98 | 2711312.232 | 1236863.6512 | 2711315.0504 | 1236856.9523
99 | 2711319.9503 | 1236845.3062 | 2711315.0504 | 1236856.9523
100 | 2711347.0314 | 1236907.7406 | 2711335.3748 | 1236898.9485 | 2711329.402 | 1236892.9764 | 2711330.5516 | 1236884.5468
101 | 2711330.5516 | 1236884.5468 | 2711351.9028 | 1236891.7416
102 | 2711347.0314 | 1236907.7406 | 2711362.3322 | 1236916.323
103 | 2711347.0314 | 1236907.7406 | 2711343.1458 | 1236914.2167
104 | 2711351.9028 | 1236891.7416 | 2711364.2816 | 1236895.9213 | 2711374.7363 | 1236899.3255
105 | 2711351.9028 | 1236891.7416 | 2711358.596 | 1236870.1167
106 | 2711362.3322 | 1236916.323 | 2711359.4041 | 1236927.577 | 2711360.5501 | 1236934.9818
107 | 2711341.9432 | 1236916.2211 | 2711343.1458 | 1236914.2167
108 | 2711416.6083 | 1236912.8492 | 2711418.5445 | 1236908.0817 | 2711416.3364 | 1236899.1111
109 | 2711416.6083 | 1236912.8492 | 2711411.7554 | 1236921.8096 | 2711405.4315 | 1236928.096 | 2711398.3075 | 1236931.8542 | 2711390.4725 | 1236935.9883
110 | 2711416.3364 | 1236899.1111 | 2711412.8555 | 1236884.9505
111 | 2711390.4725 | 1236935.9883 | 2711386.9699 | 1236939.1362 | 2711385.3336 | 1236942.8529 | 2711384.3291 | 1236947.5822 | 2711384.2295 | 1236960.5869
112 | 2711390.4725 | 1236935.9883 | 2711375.0389 | 1236938.454
113 | 2711390.4725 | 1236935.9883 | 2711383.7138 | 1236925.1197 | 2711383.4845 | 1236925.0254
114 | 2711360.5501 | 1236934.9818 | 2711360.7676 | 1236936.3872 | 2711365.0671 | 1236939.17 | 2711365.0671 | 1236939.17
115 | 2711341.9432 | 1236916.2211 | 2711341.5159 | 1236916.9333 | 2711332.0908 | 1236921.5158 | 2711321.9628 | 1236918.2318
116 | 2711405.7722 | 1236852.7962 | 2711404.9949 | 1236852.9732 | 2711412.8555 | 1236884.9505
117 | 2711384.1913 | 1236965.5708 | 2711384.2295 | 1236960.5869
118 | 2711375.0389 | 1236938.454 | 2711372.5959 | 1236938.8443 | 2711365.0671 | 1236939.17
119 | 2711490.261 | 1236936.672 | 2711479.3203 | 1236968.7585 | 2711469.217 | 1236971.5712 | 2711446.6311 | 1236963.8484
120 | 2711490.261 | 1236936.672 | 2711508.7863 | 1236942.5549
121 | 2711508.7863 | 1236942.5549 | 2711528.9682 | 1236948.9638 | 2711536.098 | 1236950.896
122 | 2711456.9206 | 1236875.9542 | 2711476.1189 | 1236871.5502
123 | 2711456.9206 | 1236875.9542 | 2711455.0754 | 1236867.4363
124 | 2711487.153 | 1236883.2958 | 2711483.7597 | 1236869.7974 | 2711476.1189 | 1236871.5502
125 | 2711455.0754 | 1236867.4363 | 2711451.3698 | 1236850.3299 | 2711451.3698 | 1236850.3299
126 | 2711451.3698 | 1236850.3299 | 2711442.0714 | 1236844.5287 | 2711415.4078 | 1236850.6016
127 | 2711405.7722 | 1236852.7962 | 2711415.4078 | 1236850.6016
128 | 2711491.52 | 1236900.6673 | 2711487.153 | 1236883.2958
129 | 2711491.52 | 1236900.6673 | 2711490.6399 | 1236900.8825
130 | 2711471.0745 | 1236905.6647 | 2711490.6399 | 1236900.8825
131 | 2711384.0734 | 1236980.9703 | 2711384.1913 | 1236965.5708
132 | 2711536.098 | 1236950.896 | 2711539.4864 | 1236951.8143
133 | 2711593.3785 | 1236902.0138 | 2711623.8491 | 1236895.1125
134 | 2711575.8006 | 1236942.0823 | 2711575.0608 | 1236935.1407 | 2711573.4297 | 1236929.9686
135 | 2711575.8006 | 1236942.0823 | 2711583.411 | 1236943.0594 | 2711623.9686 | 1236934.8776
136 | 2711564.8387 | 1236957.1549 | 2711565.7945 | 1236953.8147 | 2711568.0317 | 1236951.1546 | 2711571.1558 | 1236949.6232 | 2711574.6322 | 1236949.4884 | 2711575.8006 | 1236942.0823
137 | 2711564.8387 | 1236957.1549 | 2711565.0415 | 1236959.6496 | 2711565.9742 | 1236961.9689 | 2711567.5497 | 1236963.9112 | 2711569.6352 | 1236965.2959 | 2711571.5258 | 1236965.8656
138 | 2711564.8387 | 1236957.1549 | 2711553.8625 | 1236955.6699 | 2711550.7774 | 1236954.8598
139 | 2711576.9245 | 1236965.2327 | 2711574.5413 | 1236965.9997 | 2711572.0358 | 1236966.0193 | 2711571.5258 | 1236965.8656
140 | 2711539.4864 | 1236951.8143 | 2711549.0728 | 1236954.4123 | 2711550.7774 | 1236954.8598
141 | 2711576.9245 | 1236965.2327 | 2711579.0719 | 1236963.7274 | 2711580.64 | 1236961.633
142 | 2711580.64 | 1236961.633 | 2711585.9352 | 1236965.7913 | 2711589.4518 | 1236967.1362 | 2711595.3345 | 1236966.2127 | 2711600.7083 | 1236964.9339
143 | 2711576.9245 | 1236965.2327 | 2711578.8872 | 1236967.9161 | 2711582.3881 | 1236973.7198 | 2711587.1963 | 1236981.2383 | 2711593.6452 | 1236991.2562
144 | 2711600.7083 | 1236964.9339 | 2711625.7355 | 1236958.9782 | 2711634.435 | 1236957.1525
145 | 2711593.6452 | 1236991.2562 | 2711611.0727 | 1236992.7631
146 | 2711593.6452 | 1236991.2562 | 2711596.5986 | 1236996.7938 | 2711597.0737 | 1236997.7855
147 | 2711542.7252 | 1237010.6817 | 2711559.5512 | 1237004.5262 | 2711568.458 | 1236998.5332 | 2711587.1963 | 1236981.2383 | 2711593.6452 | 1236991.2562
148 | 2711384.0734 | 1236980.9703 | 2711395.7444 | 1236985.8579
149 | 2711509.7223 | 1237010.6065 | 2711530.2346 | 1236998.3709 | 2711541.2254 | 1237007.1286 | 2711542.7252 | 1237010.6817
150 | 2711542.7252 | 1237010.6817 | 2711537.6047 | 1237012.5555
151 | 2711509.7223 | 1237010.6065 | 2711507.1078 | 1237006.3652
152 | 2711475.4413 | 1237021.3604 | 2711498.3566 | 1237016.1642 | 2711509.7223 | 1237010.6065
153 | 2711522.3481 | 1237018.1383 | 2711537.6047 | 1237012.5555
154 | 2711472.9909 | 1237017.2445 | 2711475.4413 | 1237021.3604
155 | 2711522.3481 | 1237018.1383 | 2711528.7463 | 1237036.4951 | 2711530.0781 | 1237046.1722 | 2711529.1958 | 1237050.837

## bus_geodata
| x | y | coords
0 | 2711555.0055 | 1236765.4581
1 | 2711533.4721 | 1236751.9603
2 | 2711598.391 | 1236810.481
3 | 2711614.649 | 1236808.8074
4 | 2711591.4018 | 1236806.3033
5 | 2711490.1292 | 1236738.1914
6 | 2711654.7724 | 1236847.236
7 | 2711625.4986 | 1236816.4946
8 | 2711656.4004 | 1236859.265
9 | 2711583.0633 | 1236801.3192
10 | 2711487.277 | 1236731.6883
11 | 2711491.9196 | 1236742.1146
12 | 2711644.8776 | 1236865.3722
13 | 2711666.2587 | 1236890.0078
14 | 2711554.7907 | 1236783.953
15 | 2711469.3182 | 1236732.9427
16 | 2711476.0656 | 1236698.2694
17 | 2711503.3146 | 1236767.94
18 | 2711630.4001 | 1236868.5484
19 | 2711669.7782 | 1236906.5193
20 | 2711483.1298 | 1236774.4323
21 | 2711518.7666 | 1236800.804
22 | 2711450.3962 | 1236774.888
23 | 2711522.0147 | 1236807.7121
24 | 2711444.608 | 1236774.3212
25 | 2711525.5164 | 1236815.1597
26 | 2711444.1697 | 1236763.8047
27 | 2711401.1289 | 1236767.8116
28 | 2711529.6698 | 1236823.9932
29 | 2711405.6114 | 1236756.8852
30 | 2711369.9488 | 1236712.8617
31 | 2711374.4144 | 1236713.2008
32 | 2711353.5126 | 1236708.2944
33 | 2711350.3381 | 1236810.5485
34 | 2711370.3821 | 1236846.9673
35 | 2711338.0008 | 1236815.048
36 | 2711395.893 | 1236792.3327
37 | 2711457.3322 | 1236730.292
38 | 2711467.8464 | 1236732.6244
39 | 2711443.7623 | 1236727.1119
40 | 2711401.6239 | 1236717.2368
41 | 2711356.2449 | 1236697.0485
42 | 2711345.7976 | 1236740.4055
43 | 2711325.8984 | 1236818.348
44 | 2711463.4353 | 1236749.8885
45 | 2711409.3763 | 1236688.4818
46 | 2711601.4205 | 1236848.9377
47 | 2711590.4933 | 1236848.3838
48 | 2711613.2126 | 1236872.3192
49 | 2711558.6787 | 1236850.4125
50 | 2711543.7048 | 1236853.8435
51 | 2711568.9486 | 1236882.0396
52 | 2711557.287 | 1236884.6005
53 | 2711532.2754 | 1236829.535
54 | 2711550.3327 | 1236868.4461
55 | 2711518.7619 | 1236894.0156
56 | 2711563.1345 | 1236899.8543
57 | 2711516.3484 | 1236872.5539
58 | 2711495.6408 | 1236899.6661
59 | 2711566.3123 | 1236908.1441
60 | 2711416.9113 | 1236690.269
61 | 2711398.9245 | 1236685.6398
62 | 2711277.249 | 1236699.0531
63 | 2711235.6238 | 1236733.4833
64 | 2711231.6991 | 1236754.9105
65 | 2711214.5991 | 1236701.5535
66 | 2711224.9983 | 1236794.3802
67 | 2711212.3042 | 1236700.6813
68 | 2711206.1974 | 1236698.3604
69 | 2711221.4752 | 1236646.4057
70 | 2711097.6687 | 1236677.1798
71 | 2711224.311 | 1236810.5208
72 | 2711233.496 | 1236639.2174
73 | 2711097.1701 | 1236676.7871
74 | 2710988.3897 | 1236594.7272
75 | 2711189.9691 | 1236802.437
76 | 2711230.1513 | 1236871.2334
77 | 2711266.2389 | 1236618.6176
78 | 2711185.3145 | 1236789.2304
79 | 2711262.7572 | 1236836.4055
80 | 2711276.2222 | 1236792.8537
81 | 2711277.7226 | 1236831.8447
82 | 2711261.46 | 1236871.1668
83 | 2711266.7345 | 1236864.0573
84 | 2711289.1011 | 1236871.193
85 | 2711262.3481 | 1236870.7471
86 | 2711283.0309 | 1236791.0043
87 | 2711288.9493 | 1236828.4232
88 | 2711298.1554 | 1236874.0805
89 | 2711291.5108 | 1236858.3634
90 | 2711310.2058 | 1236822.6271
91 | 2711319.5776 | 1236785.6721
92 | 2711306.6979 | 1236876.8049
93 | 2711309.6164 | 1236877.7521
94 | 2711312.232 | 1236863.6512
95 | 2711315.0504 | 1236856.9523
96 | 2711319.9503 | 1236845.3062
97 | 2711330.5516 | 1236884.5468
98 | 2711347.0314 | 1236907.7406
99 | 2711351.9028 | 1236891.7416
100 | 2711362.3322 | 1236916.323
101 | 2711343.1458 | 1236914.2167
102 | 2711374.7363 | 1236899.3255
103 | 2711358.596 | 1236870.1167
104 | 2711416.6083 | 1236912.8492
105 | 2711416.3364 | 1236899.1111
106 | 2711390.4725 | 1236935.9883
107 | 2711360.5501 | 1236934.9818
108 | 2711341.9432 | 1236916.2211
109 | 2711412.8555 | 1236884.9505
110 | 2711384.2295 | 1236960.5869
111 | 2711375.0389 | 1236938.454
112 | 2711383.4845 | 1236925.0254
113 | 2711490.261 | 1236936.672
114 | 2711446.6311 | 1236963.8484
115 | 2711508.7863 | 1236942.5549
116 | 2711456.9206 | 1236875.9542
117 | 2711476.1189 | 1236871.5502
118 | 2711455.0754 | 1236867.4363
119 | 2711365.0671 | 1236939.17
120 | 2711321.9628 | 1236918.2318
121 | 2711451.3698 | 1236850.3299
122 | 2711415.4078 | 1236850.6016
123 | 2711405.7722 | 1236852.7962
124 | 2711487.153 | 1236883.2958
125 | 2711491.52 | 1236900.6673
126 | 2711471.0745 | 1236905.6647
127 | 2711490.6399 | 1236900.8825
128 | 2711384.1913 | 1236965.5708
129 | 2711536.098 | 1236950.896
130 | 2711505.9605 | 1236873.0218
131 | 2711593.3785 | 1236902.0138
132 | 2711623.8491 | 1236895.1125
133 | 2711573.4297 | 1236929.9686
134 | 2711623.9686 | 1236934.8776
135 | 2711575.8006 | 1236942.0823
136 | 2711564.8387 | 1236957.1549
137 | 2711571.5258 | 1236965.8656
138 | 2711550.7774 | 1236954.8598
139 | 2711580.64 | 1236961.633
140 | 2711576.9245 | 1236965.2327
141 | 2711600.7083 | 1236964.9339
142 | 2711634.435 | 1236957.1525
143 | 2711611.0727 | 1236992.7631
144 | 2711593.6452 | 1236991.2562
145 | 2711539.4864 | 1236951.8143
146 | 2711384.0734 | 1236980.9703
147 | 2711395.7444 | 1236985.8579
148 | 2711542.7252 | 1237010.6817
149 | 2711509.7223 | 1237010.6065
150 | 2711537.6047 | 1237012.5555
151 | 2711597.0737 | 1236997.7855
152 | 2711475.4413 | 1237021.3604
153 | 2711472.9909 | 1237017.2445
154 | 2711507.1078 | 1237006.3652
155 | 2711522.3481 | 1237018.1383
156 | 2711529.1958 | 1237050.837
157 | 2711456.9206 | 1236875.9542

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97762 | -0.43022 | 0.0036245 | 0.00090838
1 | 0.97771 | -0.42854 | 0 | 0
2 | 0.97895 | -0.40451 | 0 | 0
3 | 0.97898 | -0.40384 | 0 | 0
4 | 0.97893 | -0.40484 | 0.0016818 | 0.0004215
5 | 0.97787 | -0.42527 | 0 | 0
6 | 0.97952 | -0.39334 | 0 | 0
7 | 0.97901 | -0.40331 | 0.0095722 | 0.002399
8 | 0.97966 | -0.39062 | 0 | 0
9 | 0.97893 | -0.40493 | 0 | 0
10 | 0.97773 | -0.42805 | 0 | 0
11 | 0.97798 | -0.42329 | 0.0010748 | 0.00026936
12 | 0.97989 | -0.38603 | 0.0073507 | 0.0018423
13 | 0.97944 | -0.39486 | 0 | 0
14 | 0.97891 | -0.40524 | 0.00051497 | 0.00012906
15 | 0.97741 | -0.4344 | 0.00078968 | 0.00019791
16 | 0.97764 | -0.42979 | 0.002683 | 0.00067242
17 | 0.97866 | -0.40982 | 0 | 0
18 | 0.98025 | -0.37898 | 0.0039355 | 0.00098633
19 | 0.97933 | -0.39703 | 0.0070712 | 0.0017722
20 | 0.97799 | -0.42304 | 0.0019053 | 0.00047753
21 | 0.9807 | -0.37 | 0.00045914 | 0.00011507
22 | 0.977 | -0.44241 | 0.013418 | 0.0033629
23 | 0.98113 | -0.36158 | 0.0002782 | 6.9724e-05
24 | 0.9769 | -0.44441 | 0 | 0
25 | 0.9816 | -0.35248 | 0.0017418 | 0.00043654
26 | 0.97674 | -0.44762 | 0 | 0
27 | 0.97681 | -0.4461 | 0 | 0
28 | 0.98217 | -0.34139 | 0.0033334 | 0.00083544
29 | 0.97613 | -0.4596 | 0.01672 | 0.0041904
30 | 0.97606 | -0.46101 | 0 | 0
31 | 0.97609 | -0.46044 | 0.0026899 | 0.00067415
32 | 0.97595 | -0.4632 | 0 | 0
33 | 0.97624 | -0.45701 | 0 | 0
34 | 0.97497 | -0.48216 | 0.020424 | 0.0051188
35 | 0.9765 | -0.45209 | 0.0043921 | 0.0011008
36 | 0.97676 | -0.44712 | 0.0021181 | 0.00053086
37 | 0.97721 | -0.43826 | 0 | 0
38 | 0.97738 | -0.43489 | 0 | 0
39 | 0.97699 | -0.44263 | 0.00085936 | 0.00021538
40 | 0.97634 | -0.45554 | 0 | 0
41 | 0.9759 | -0.46413 | 0.0044005 | 0.0011029
42 | 0.97587 | -0.46478 | 0.00262 | 0.00065663
43 | 0.97678 | -0.4464 | 0.0020764 | 0.0005204
44 | 0.97737 | -0.43517 | 0.00085901 | 0.00021529
45 | 0.97615 | -0.45913 | 0 | 0
46 | 0.98155 | -0.35355 | 0.016671 | 0.0041783
47 | 0.98202 | -0.34429 | 0.0038194 | 0.00095724
48 | 0.98074 | -0.36937 | 0 | 0
49 | 0.98353 | -0.31489 | 0.00287 | 0.00071928
50 | 0.98429 | -0.3001 | 0 | 0
51 | 0.98728 | -0.24223 | 0.0029316 | 0.00073472
52 | 0.98731 | -0.2416 | 0 | 0
53 | 0.98254 | -0.33406 | 0.0039737 | 0.00099591
54 | 0.98613 | -0.2645 | 0 | 0
55 | 0.99089 | -0.17283 | 0.0036572 | 0.00091658
56 | 0.98622 | -0.26259 | 0.0081736 | 0.0020485
57 | 0.98539 | -0.27885 | 0.019535 | 0.004896
58 | 0.99307 | -0.13128 | 0 | 0
59 | 0.98511 | -0.28416 | 0 | 0
60 | 0.97613 | -0.45961 | 0.0034081 | 0.00085416
61 | 0.97612 | -0.45976 | 0.0031928 | 0.00080019
62 | 0.97199 | -0.54058 | 0.013667 | 0.0034253
63 | 0.97275 | -0.52567 | 0 | 0
64 | 0.97325 | -0.51572 | 0.0061523 | 0.0015419
65 | 0.97234 | -0.53368 | 0 | 0
66 | 0.97441 | -0.49296 | 0.0017513 | 0.00043893
67 | 0.97232 | -0.53418 | 0.0010226 | 0.00025629
68 | 0.97226 | -0.53538 | 0 | 0
69 | 0.9719 | -0.5424 | 0 | 0
70 | 0.97193 | -0.54179 | 0 | 0
71 | 0.9749 | -0.48329 | 0 | 0
72 | 0.97181 | -0.54417 | 0.00094192 | 0.00023607
73 | 0.97193 | -0.54183 | 0.0010766 | 0.00026982
74 | 0.97167 | -0.54702 | 0.0020598 | 0.00051622
75 | 0.97467 | -0.48782 | 0.005753 | 0.0014418
76 | 0.97718 | -0.43857 | 0 | 0
77 | 0.9716 | -0.54839 | 0.0059142 | 0.0014822
78 | 0.97465 | -0.48822 | 0.0012023 | 0.00030132
79 | 0.97758 | -0.43074 | 0 | 0
80 | 0.9771 | -0.44031 | 0.0045843 | 0.0011489
81 | 0.97771 | -0.42816 | 0.0038337 | 0.00096081
82 | 0.97839 | -0.41487 | 0.0032467 | 0.0008137
83 | 0.97876 | -0.4076 | 0 | 0
84 | 0.97973 | -0.38859 | 0 | 0
85 | 0.97843 | -0.4141 | 0.0018632 | 0.00046696
86 | 0.97707 | -0.44089 | 0.0028994 | 0.00072665
87 | 0.97785 | -0.4254 | 0 | 0
88 | 0.98056 | -0.3724 | 0.0027403 | 0.00068677
89 | 0.97914 | -0.40026 | 0.0039404 | 0.00098756
90 | 0.97719 | -0.43841 | 0.0054848 | 0.0013746
91 | 0.97701 | -0.44196 | 0.0015726 | 0.00039412
92 | 0.98137 | -0.3567 | 0 | 0
93 | 0.98168 | -0.35062 | 0.0027642 | 0.00069276
94 | 0.9812 | -0.36005 | 0.0026406 | 0.00066181
95 | 0.98113 | -0.36141 | 0.0049828 | 0.0012488
96 | 0.98107 | -0.36264 | 0.0053456 | 0.0013397
97 | 0.98398 | -0.30599 | 0 | 0
98 | 0.98797 | -0.22894 | 0 | 0
99 | 0.98348 | -0.31571 | 0 | 0
100 | 0.98915 | -0.20632 | 0 | 0
101 | 0.98791 | -0.23009 | 0.0023834 | 0.00059733
102 | 0.98314 | -0.32246 | 0.015555 | 0.0038984
103 | 0.98331 | -0.31916 | 0.008449 | 0.0021175
104 | 0.99333 | -0.12635 | 0 | 0
105 | 0.99406 | -0.11231 | 0 | 0
106 | 0.99148 | -0.16161 | 0 | 0
107 | 0.99 | -0.18988 | 0.0016974 | 0.00042541
108 | 0.9879 | -0.23034 | 0.0028349 | 0.00071049
109 | 0.99481 | -0.098094 | 0.0018531 | 0.00046443
110 | 0.9912 | -0.16711 | 0.0073114 | 0.0018324
111 | 0.99076 | -0.17544 | 0.0018783 | 0.00047076
112 | 0.99143 | -0.16268 | 0.0046398 | 0.0011628
113 | 0.97561 | -0.46945 | 0 | 0
114 | 0.97348 | -0.51139 | 0.033475 | 0.0083896
115 | 0.97621 | -0.45754 | 0.0046433 | 0.0011637
116 | 0.99916 | -0.015855 | 0 | 0
117 | 0.99725 | -0.051787 | 0.002136 | 0.00053534
118 | 1 | 0 | -0.49467 | -0.12707
119 | 0.9903 | -0.1842 | 0.0011468 | 0.00028742
120 | 0.98783 | -0.23164 | 0.0033039 | 0.00082803
121 | 0.99907 | -0.01742 | 0.0019668 | 0.00049292
122 | 0.99707 | -0.055215 | 0.0010363 | 0.00025973
123 | 0.99656 | -0.06493 | 0.00034105 | 8.5475e-05
124 | 0.99516 | -0.091364 | 0.0014671 | 0.00036769
125 | 0.99345 | -0.12392 | 0 | 0
126 | 0.99338 | -0.12526 | 0.0031609 | 0.00079219
127 | 0.99344 | -0.12413 | 0.010428 | 0.0026136
128 | 0.99118 | -0.1675 | 0.002916 | 0.00073081
129 | 0.97723 | -0.43765 | 0.0040247 | 0.0010087
130 | 0.98537 | -0.27927 | 0.0022719 | 0.0005694
131 | 0.98489 | -0.28839 | 0.0028694 | 0.00071913
132 | 0.98473 | -0.29154 | 0.0056147 | 0.0014072
133 | 0.9824 | -0.33664 | 0.0075887 | 0.0019019
134 | 0.98065 | -0.3707 | 0.0082018 | 0.0020556
135 | 0.98102 | -0.36341 | 0 | 0
136 | 0.97881 | -0.40659 | 0 | 0
137 | 0.97827 | -0.41729 | 0.0030839 | 0.00077291
138 | 0.97799 | -0.42271 | 0.0046688 | 0.0011701
139 | 0.97798 | -0.42293 | 0 | 0
140 | 0.97803 | -0.42193 | 0 | 0
141 | 0.97776 | -0.42714 | 0.0049742 | 0.0012466
142 | 0.97759 | -0.43063 | 0.0055294 | 0.0013858
143 | 0.97687 | -0.44473 | 0.0086985 | 0.00218
144 | 0.97701 | -0.44195 | 0 | 0
145 | 0.97736 | -0.43495 | 0.015252 | 0.0038226
146 | 0.99116 | -0.16789 | 0 | 0
147 | 0.99114 | -0.16821 | 0.0014347 | 0.00035957
148 | 0.97546 | -0.47239 | 0 | 0
149 | 0.97488 | -0.48376 | 0 | 0
150 | 0.97541 | -0.47342 | 0.0016045 | 0.00040213
151 | 0.977 | -0.44217 | 0.0015816 | 0.00039638
152 | 0.97467 | -0.488 | 0 | 0
153 | 0.97464 | -0.48856 | 0.0064076 | 0.0016059
154 | 0.97485 | -0.48453 | 0.0084553 | 0.0021191
155 | 0.97528 | -0.47602 | 0 | 0
156 | 0.975 | -0.48145 | 0.0087193 | 0.0021853
157 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0036245 | -0.00090838 | 0.0036248 | 0.00090824 | 2.9004e-07 | -1.3306e-07 | 0.0055167 | 0.0055166 | 0.0055167 | 0.97762 | -0.43022 | 0.97771 | -0.42854 | 1.5156
1 | -0.0036248 | -0.00090824 | 0.0036253 | 0.00090798 | 5.6553e-07 | -2.5965e-07 | 0.0055166 | 0.0055164 | 0.0055166 | 0.97771 | -0.42854 | 0.97787 | -0.42527 | 1.5155
2 | -0.0021968 | -0.00054995 | 0.0021969 | 0.00054978 | 7.0134e-08 | -1.6604e-07 | 0.003339 | 0.0033389 | 0.003339 | 0.97895 | -0.40451 | 0.97898 | -0.40384 | 0.9173
3 | 0.0021968 | 0.00054995 | -0.0021968 | -0.00055003 | 3.4043e-08 | -8.0587e-08 | 0.003339 | 0.003339 | 0.003339 | 0.97895 | -0.40451 | 0.97893 | -0.40484 | 0.91731
4 | -0.0021969 | -0.00054978 | 0.0021969 | 0.00054965 | 5.5587e-08 | -1.3162e-07 | 0.0033389 | 0.0033388 | 0.0033389 | 0.97898 | -0.40384 | 0.97901 | -0.40331 | 0.91727
5 | 0.00051498 | 0.00012853 | -0.00051498 | -0.00012865 | 2.2313e-09 | -1.207e-07 | 0.0007826 | 0.00078265 | 0.00078265 | 0.97893 | -0.40484 | 0.97893 | -0.40493 | 0.21501
6 | 0.021533 | 0.0054049 | -0.02153 | -0.0054031 | 2.8582e-06 | 1.7402e-06 | 0.032769 | 0.032769 | 0.032769 | 0.97787 | -0.42527 | 0.97773 | -0.42805 | 9.0025
7 | -0.025158 | -0.0063129 | 0.025161 | 0.0063143 | 2.3704e-06 | 1.463e-06 | 0.038286 | 0.038285 | 0.038286 | 0.97787 | -0.42527 | 0.97798 | -0.42329 | 10.518
8 | 0.011775 | 0.0029517 | -0.011769 | -0.0029487 | 5.5881e-06 | 2.9905e-06 | 0.017888 | 0.017888 | 0.017888 | 0.97952 | -0.39334 | 0.97901 | -0.40331 | 4.9142
9 | -0.011775 | -0.0029517 | 0.011776 | 0.0029525 | 1.5272e-06 | 8.1717e-07 | 0.017888 | 0.017888 | 0.017888 | 0.97952 | -0.39334 | 0.97966 | -0.39062 | 4.9142
10 | -0.01885 | -0.0047254 | 0.018854 | 0.0047279 | 4.126e-06 | 2.4716e-06 | 0.028631 | 0.028631 | 0.028631 | 0.97966 | -0.39062 | 0.97989 | -0.38603 | 7.8658
11 | 0.0070734 | 0.001773 | -0.0070719 | -0.0017725 | 1.4271e-06 | 4.9832e-07 | 0.010744 | 0.010744 | 0.010744 | 0.97966 | -0.39062 | 0.97944 | -0.39486 | 2.9517
12 | 0.00051498 | 0.00012865 | -0.00051497 | -0.00012906 | 7.623e-09 | -4.1226e-07 | 0.00078265 | 0.0007828 | 0.0007828 | 0.97893 | -0.40493 | 0.97891 | -0.40524 | 0.21505
13 | 0.018847 | 0.004731 | -0.018841 | -0.0047276 | 5.7033e-06 | 3.4184e-06 | 0.028686 | 0.028686 | 0.028686 | 0.97773 | -0.42805 | 0.97741 | -0.4344 | 7.8807
14 | 0.0026832 | 0.00067211 | -0.002683 | -0.00067242 | 2.2152e-07 | -3.0247e-07 | 0.0040834 | 0.0040836 | 0.0040836 | 0.97773 | -0.42805 | 0.97764 | -0.42979 | 1.1219
15 | -0.026235 | -0.0065837 | 0.026252 | 0.0065941 | 1.6871e-05 | 1.0443e-05 | 0.039921 | 0.039921 | 0.039921 | 0.97798 | -0.42329 | 0.97866 | -0.40982 | 10.9672
16 | -0.026204 | -0.0065702 | 0.026213 | 0.0065756 | 8.8016e-06 | 5.4463e-06 | 0.039794 | 0.039794 | 0.039794 | 0.97989 | -0.38603 | 0.98025 | -0.37898 | 10.9324
17 | 0.0070719 | 0.0017725 | -0.0070712 | -0.0017722 | 7.3081e-07 | 2.5527e-07 | 0.010744 | 0.010744 | 0.010744 | 0.97944 | -0.39486 | 0.97933 | -0.39703 | 2.9517
18 | 0.018051 | 0.0045297 | -0.018051 | -0.0045294 | 4.2655e-07 | 2.5412e-07 | 0.027484 | 0.027484 | 0.027484 | 0.97741 | -0.4344 | 0.97738 | -0.43489 | 7.5504
19 | 0.034227 | 0.0086014 | -0.034206 | -0.0085878 | 2.1596e-05 | 1.3555e-05 | 0.052049 | 0.052049 | 0.052049 | 0.97866 | -0.40982 | 0.97799 | -0.42304 | 14.2993
20 | -0.060479 | -0.015196 | 0.060594 | 0.015269 | 0.00011519 | 7.3264e-05 | 0.09197 | 0.09197 | 0.09197 | 0.97866 | -0.40982 | 0.9807 | -0.37 | 25.2665
21 | -0.030149 | -0.007562 | 0.030163 | 0.0075706 | 1.3822e-05 | 8.6242e-06 | 0.045768 | 0.045768 | 0.045768 | 0.98025 | -0.37898 | 0.98074 | -0.36937 | 12.5736
22 | 0.0323 | 0.0081103 | -0.03227 | -0.0080917 | 2.9805e-05 | 1.8663e-05 | 0.04915 | 0.049151 | 0.049151 | 0.97799 | -0.42304 | 0.977 | -0.44241 | 13.5029
23 | -0.061054 | -0.015384 | 0.061078 | 0.0154 | 2.4581e-05 | 1.5636e-05 | 0.092666 | 0.092666 | 0.092666 | 0.9807 | -0.37 | 0.98113 | -0.36158 | 25.4578
24 | 0.018852 | 0.0047288 | -0.01885 | -0.0047277 | 1.7982e-06 | 1.078e-06 | 0.028714 | 0.028714 | 0.028714 | 0.977 | -0.44241 | 0.9769 | -0.44441 | 7.8885
25 | -0.061356 | -0.015469 | 0.061383 | 0.015486 | 2.6743e-05 | 1.7011e-05 | 0.093088 | 0.093088 | 0.093088 | 0.98113 | -0.36158 | 0.9816 | -0.35248 | 25.5737
26 | 0.016732 | 0.0041975 | -0.01673 | -0.004196 | 2.5645e-06 | 1.5095e-06 | 0.025488 | 0.025488 | 0.025488 | 0.9769 | -0.44441 | 0.97674 | -0.44762 | 7.0022
27 | 0.0021184 | 0.00053015 | -0.0021182 | -0.00053059 | 1.7114e-07 | -4.3926e-07 | 0.0032265 | 0.0032267 | 0.0032267 | 0.9769 | -0.44441 | 0.97681 | -0.4461 | 0.88646
28 | -0.063125 | -0.015923 | 0.063158 | 0.015944 | 3.3544e-05 | 2.1345e-05 | 0.095729 | 0.095729 | 0.095729 | 0.9816 | -0.35248 | 0.98217 | -0.34139 | 26.2991
29 | 0.01673 | 0.004196 | -0.01672 | -0.0041904 | 9.5434e-06 | 5.6177e-06 | 0.025488 | 0.025488 | 0.025488 | 0.97674 | -0.44762 | 0.97613 | -0.4596 | 7.0022
30 | 0.0021182 | 0.00053059 | -0.0021181 | -0.00053086 | 1.0282e-07 | -2.6383e-07 | 0.0032267 | 0.0032268 | 0.0032268 | 0.97681 | -0.4461 | 0.97676 | -0.44712 | 0.88649
31 | -0.066492 | -0.01678 | 0.066515 | 0.016794 | 2.3323e-05 | 1.4849e-05 | 0.10078 | 0.10078 | 0.10078 | 0.98217 | -0.34139 | 0.98254 | -0.33406 | 27.6865
32 | -0.0070216 | -0.0017595 | 0.0070218 | 0.0017595 | 1.9244e-07 | 6.7183e-08 | 0.010705 | 0.010704 | 0.010705 | 0.97606 | -0.46101 | 0.97609 | -0.46044 | 2.9408
33 | 0.0070216 | 0.0017595 | -0.0070209 | -0.0017592 | 7.3101e-07 | 2.5524e-07 | 0.010705 | 0.010705 | 0.010705 | 0.97606 | -0.46101 | 0.97595 | -0.4632 | 2.9408
34 | -0.0097117 | -0.0024337 | 0.009714 | 0.0024348 | 2.2677e-06 | 1.1064e-06 | 0.014805 | 0.014805 | 0.014805 | 0.97609 | -0.46044 | 0.97634 | -0.45554 | 4.0673
35 | 0.0044007 | 0.0011029 | -0.0044005 | -0.0011029 | 1.9539e-07 | -1.956e-08 | 0.0067097 | 0.0067098 | 0.0067098 | 0.97595 | -0.4632 | 0.9759 | -0.46413 | 1.8433
36 | 0.0026202 | 0.00065634 | -0.00262 | -0.00065663 | 1.9765e-07 | -2.8614e-07 | 0.0039949 | 0.003995 | 0.003995 | 0.97595 | -0.4632 | 0.97587 | -0.46478 | 1.0975
37 | 0.020449 | 0.0051336 | -0.020424 | -0.0051188 | 2.4499e-05 | 1.484e-05 | 0.031171 | 0.031172 | 0.031172 | 0.97624 | -0.45701 | 0.97497 | -0.48216 | 8.5637
38 | -0.020449 | -0.0051336 | 0.020453 | 0.0051365 | 4.8033e-06 | 2.9093e-06 | 0.031171 | 0.031171 | 0.031171 | 0.97624 | -0.45701 | 0.9765 | -0.45209 | 8.5636
39 | -0.024845 | -0.0062373 | 0.024852 | 0.0062414 | 6.7442e-06 | 4.1593e-06 | 0.037864 | 0.037864 | 0.037864 | 0.9765 | -0.45209 | 0.97678 | -0.4464 | 10.4022
40 | -0.017189 | -0.0043127 | 0.017192 | 0.0043144 | 2.7596e-06 | 1.6315e-06 | 0.026176 | 0.026176 | 0.026176 | 0.97721 | -0.43826 | 0.97738 | -0.43489 | 7.1912
41 | 0.017189 | 0.0043127 | -0.017186 | -0.0043106 | 3.5811e-06 | 2.1174e-06 | 0.026176 | 0.026176 | 0.026176 | 0.97721 | -0.43826 | 0.97699 | -0.44263 | 7.1912
42 | 0.00085902 | 0.00021507 | -0.00085901 | -0.00021529 | 1.1428e-08 | -2.1599e-07 | 0.0013077 | 0.0013078 | 0.0013078 | 0.97738 | -0.43489 | 0.97737 | -0.43517 | 0.35929
43 | 0.016326 | 0.0040952 | -0.016316 | -0.0040894 | 1.0036e-05 | 5.8816e-06 | 0.024867 | 0.024867 | 0.024867 | 0.97699 | -0.44263 | 0.97634 | -0.45554 | 6.8317
44 | 0.0066022 | 0.0016546 | -0.0066011 | -0.0016542 | 1.1308e-06 | 3.5132e-07 | 0.010062 | 0.010062 | 0.010062 | 0.97634 | -0.45554 | 0.97615 | -0.45913 | 2.7644
45 | -0.026929 | -0.0067618 | 0.026939 | 0.0067682 | 1.0267e-05 | 6.3672e-06 | 0.041027 | 0.041027 | 0.041027 | 0.97678 | -0.4464 | 0.97719 | -0.43841 | 11.2712
46 | 0.0034082 | 0.00085411 | -0.0034081 | -0.00085416 | 7.8384e-08 | -4.6639e-08 | 0.0051954 | 0.0051954 | 0.0051954 | 0.97615 | -0.45913 | 0.97613 | -0.45961 | 1.4273
47 | 0.0031929 | 0.00080011 | -0.0031928 | -0.00080019 | 9.6218e-08 | -7.3819e-08 | 0.0048671 | 0.0048671 | 0.0048671 | 0.97615 | -0.45913 | 0.97612 | -0.45976 | 1.3371
48 | -0.046857 | -0.011763 | 0.046878 | 0.011776 | 2.0707e-05 | 1.3114e-05 | 0.071041 | 0.071041 | 0.071041 | 0.98155 | -0.35355 | 0.98202 | -0.34429 | 19.5169
49 | 0.030185 | 0.0075848 | -0.030163 | -0.0075706 | 2.2782e-05 | 1.4214e-05 | 0.045768 | 0.045768 | 0.045768 | 0.98155 | -0.35355 | 0.98074 | -0.36937 | 12.5736
50 | -0.050697 | -0.012733 | 0.050768 | 0.012779 | 7.1221e-05 | 4.5174e-05 | 0.076829 | 0.076829 | 0.076829 | 0.98202 | -0.34429 | 0.98353 | -0.31489 | 21.1068
51 | -0.053638 | -0.013498 | 0.053676 | 0.013522 | 3.7956e-05 | 2.4096e-05 | 0.081171 | 0.081171 | 0.081171 | 0.98353 | -0.31489 | 0.98429 | -0.3001 | 22.2996
52 | 0.070604 | 0.017864 | -0.070489 | -0.01779 | 0.00011489 | 7.3188e-05 | 0.1068 | 0.1068 | 0.1068 | 0.98429 | -0.3001 | 0.98254 | -0.33406 | 29.3398
53 | -0.12428 | -0.031385 | 0.12449 | 0.031521 | 0.00021237 | 0.00013572 | 0.18797 | 0.18797 | 0.18797 | 0.98429 | -0.3001 | 0.98613 | -0.2645 | 51.6394
54 | -0.0029316 | -0.00073472 | 0.0029317 | 0.00073463 | 8.7408e-08 | -9.6742e-08 | 0.0044185 | 0.0044184 | 0.0044185 | 0.98728 | -0.24223 | 0.98731 | -0.2416 | 1.2139
55 | 0.14648 | 0.037098 | -0.14631 | -0.036996 | 0.0001609 | 0.00010253 | 0.2209 | 0.2209 | 0.2209 | 0.98731 | -0.2416 | 0.98613 | -0.2645 | 30.3431
56 | -0.29431 | -0.074659 | 0.29528 | 0.075282 | 0.00097676 | 0.0006236 | 0.44388 | 0.44388 | 0.44388 | 0.98731 | -0.2416 | 0.99089 | -0.17283 | 40.6487
57 | 0.1449 | 0.036826 | -0.14475 | -0.036733 | 0.00014633 | 9.3232e-05 | 0.21857 | 0.21857 | 0.21857 | 0.98731 | -0.2416 | 0.98622 | -0.26259 | 30.023
58 | 0.021822 | 0.0054744 | -0.021807 | -0.0054653 | 1.4914e-05 | 9.0772e-06 | 0.032931 | 0.032931 | 0.032931 | 0.98613 | -0.2645 | 0.98539 | -0.27885 | 9.0469
59 | -0.29894 | -0.076199 | 0.29954 | 0.076582 | 0.0006008 | 0.00038359 | 0.44937 | 0.44937 | 0.44937 | 0.99089 | -0.17283 | 0.99307 | -0.13128 | 41.1515
60 | 0.13658 | 0.034684 | -0.13644 | -0.034594 | 0.0001416 | 9.0513e-05 | 0.20624 | 0.20624 | 0.20624 | 0.98622 | -0.26259 | 0.98511 | -0.28416 | 56.6581
61 | 0.002272 | 0.0005693 | -0.0022719 | -0.0005694 | 4.5899e-08 | -1.0308e-07 | 0.0034308 | 0.0034309 | 0.0034309 | 0.98539 | -0.27885 | 0.98537 | -0.27927 | 0.94255
62 | -0.29954 | -0.076582 | 0.29965 | 0.076651 | 0.00010675 | 6.8155e-05 | 0.44937 | 0.44937 | 0.44937 | 0.99307 | -0.13128 | 0.99345 | -0.12392 | 41.1515
63 | 0.12795 | 0.032467 | -0.12763 | -0.032261 | 0.00032204 | 0.00020582 | 0.19342 | 0.19342 | 0.19342 | 0.98511 | -0.28416 | 0.9824 | -0.33664 | 53.1363
64 | 0.0084866 | 0.0021272 | -0.0084849 | -0.0021265 | 1.7102e-06 | 7.413e-07 | 0.012819 | 0.012819 | 0.012819 | 0.98511 | -0.28416 | 0.98489 | -0.28839 | 3.5218
65 | -0.013667 | -0.0034253 | 0.013677 | 0.0034307 | 9.7201e-06 | 5.4864e-06 | 0.020923 | 0.020922 | 0.020923 | 0.97199 | -0.54058 | 0.97275 | -0.52567 | 5.748
66 | -0.024702 | -0.0061932 | 0.024714 | 0.0062004 | 1.1717e-05 | 7.2272e-06 | 0.037788 | 0.037788 | 0.037788 | 0.97275 | -0.52567 | 0.97325 | -0.51572 | 10.3813
67 | 0.011026 | 0.0027624 | -0.011021 | -0.0027602 | 4.2077e-06 | 2.2035e-06 | 0.016866 | 0.016866 | 0.016866 | 0.97275 | -0.52567 | 0.97234 | -0.53368 | 4.6335
68 | -0.030866 | -0.0077423 | 0.0309 | 0.0077633 | 3.3525e-05 | 2.0957e-05 | 0.047194 | 0.047194 | 0.047194 | 0.97325 | -0.51572 | 0.97441 | -0.49296 | 12.9655
69 | 0.011021 | 0.0027602 | -0.011021 | -0.0027601 | 2.6188e-07 | 1.3716e-07 | 0.016866 | 0.016866 | 0.016866 | 0.97234 | -0.53368 | 0.97232 | -0.53418 | 4.6335
70 | -0.032651 | -0.0082022 | 0.032666 | 0.0082116 | 1.5066e-05 | 9.4409e-06 | 0.049869 | 0.049869 | 0.049869 | 0.97441 | -0.49296 | 0.9749 | -0.48329 | 13.7002
71 | 0.0099986 | 0.0025038 | -0.009998 | -0.0025035 | 5.7356e-07 | 2.8605e-07 | 0.015301 | 0.015301 | 0.015301 | 0.97232 | -0.53418 | 0.97226 | -0.53538 | 4.2036
72 | 0.0068602 | 0.0017196 | -0.0068579 | -0.0017188 | 2.2911e-06 | 7.7928e-07 | 0.010499 | 0.0105 | 0.0105 | 0.97226 | -0.53538 | 0.9719 | -0.5424 | 2.8845
73 | 0.0031378 | 0.00078392 | -0.0031369 | -0.00078468 | 9.5606e-07 | -7.5897e-07 | 0.0048015 | 0.0048019 | 0.0048019 | 0.97226 | -0.53538 | 0.97193 | -0.54179 | 1.3192
74 | 0.0068579 | 0.0017188 | -0.0068574 | -0.0017186 | 5.7904e-07 | 1.9703e-07 | 0.0105 | 0.0105 | 0.0105 | 0.9719 | -0.5424 | 0.97181 | -0.54417 | 2.8846
75 | 0.0031369 | 0.00078468 | -0.0031369 | -0.00078468 | 5.4876e-09 | -4.3531e-09 | 0.0048019 | 0.004802 | 0.004802 | 0.97193 | -0.54179 | 0.97193 | -0.54183 | 1.3192
76 | 0.0069568 | 0.0017435 | -0.0069553 | -0.0017429 | 1.4984e-06 | 5.1719e-07 | 0.010618 | 0.010619 | 0.010619 | 0.9749 | -0.48329 | 0.97467 | -0.48782 | 2.9172
77 | -0.039623 | -0.0099551 | 0.039708 | 0.010009 | 8.4774e-05 | 5.3483e-05 | 0.060487 | 0.060487 | 0.060487 | 0.9749 | -0.48329 | 0.97718 | -0.43857 | 16.6173
78 | 0.0059154 | 0.0014825 | -0.0059142 | -0.0014822 | 1.1902e-06 | 2.8249e-07 | 0.0090576 | 0.0090577 | 0.0090577 | 0.97181 | -0.54417 | 0.9716 | -0.54839 | 2.4884
79 | 0.0020603 | 0.00051486 | -0.0020598 | -0.00051622 | 5.0831e-07 | -1.3629e-06 | 0.0031537 | 0.0031543 | 0.0031543 | 0.97193 | -0.54183 | 0.97167 | -0.54702 | 0.86657
80 | 0.0012023 | 0.0003011 | -0.0012023 | -0.00030132 | 2.3394e-08 | -2.158e-07 | 0.0018354 | 0.0018355 | 0.0018355 | 0.97467 | -0.48782 | 0.97465 | -0.48822 | 0.50427
81 | -0.039708 | -0.010009 | 0.039753 | 0.010037 | 4.509e-05 | 2.8445e-05 | 0.060487 | 0.060486 | 0.060487 | 0.97718 | -0.43857 | 0.97839 | -0.41487 | 16.6172
82 | 0.0090605 | 0.0022712 | -0.0090564 | -0.0022693 | 4.1306e-06 | 1.9179e-06 | 0.013792 | 0.013792 | 0.013792 | 0.97758 | -0.43074 | 0.9771 | -0.44031 | 3.7889
83 | -0.0090605 | -0.0022712 | 0.0090616 | 0.0022717 | 1.1159e-06 | 5.18e-07 | 0.013792 | 0.013791 | 0.013792 | 0.97758 | -0.43074 | 0.97771 | -0.42816 | 3.7889
84 | 0.0044721 | 0.0011203 | -0.004472 | -0.0011204 | 1.2272e-07 | -9.8295e-09 | 0.0068104 | 0.0068104 | 0.0068104 | 0.9771 | -0.44031 | 0.97707 | -0.44089 | 1.871
85 | -0.012895 | -0.0032325 | 0.012897 | 0.0032335 | 1.6953e-06 | 9.3776e-07 | 0.019626 | 0.019626 | 0.019626 | 0.97771 | -0.42816 | 0.97785 | -0.4254 | 5.3918
86 | -0.043 | -0.010851 | 0.043001 | 0.010852 | 1.5768e-06 | 9.9681e-07 | 0.065424 | 0.065424 | 0.065424 | 0.97839 | -0.41487 | 0.97843 | -0.4141 | 17.9737
87 | -0.044878 | -0.011328 | 0.044919 | 0.011353 | 4.0908e-05 | 2.5887e-05 | 0.068258 | 0.068258 | 0.068258 | 0.97876 | -0.4076 | 0.97973 | -0.38859 | 18.7522
88 | 0.044878 | 0.011328 | -0.044865 | -0.011319 | 1.3977e-05 | 8.8445e-06 | 0.068258 | 0.068258 | 0.068258 | 0.97876 | -0.4076 | 0.97843 | -0.4141 | 18.7522
89 | -0.094283 | -0.023782 | 0.094356 | 0.023828 | 7.3133e-05 | 4.6686e-05 | 0.14325 | 0.14325 | 0.14325 | 0.97973 | -0.38859 | 0.98056 | -0.3724 | 39.3547
90 | 0.049363 | 0.012428 | -0.049336 | -0.012411 | 2.7531e-05 | 1.7455e-05 | 0.074993 | 0.074993 | 0.074993 | 0.97973 | -0.38859 | 0.97914 | -0.40026 | 20.6025
91 | 0.0015726 | 0.0003937 | -0.0015726 | -0.00039412 | 8.0457e-08 | -4.1696e-07 | 0.0023949 | 0.0023951 | 0.0023951 | 0.97707 | -0.44089 | 0.97701 | -0.44196 | 0.65798
92 | 0.032444 | 0.0081554 | -0.032424 | -0.0081428 | 2.0146e-05 | 1.2617e-05 | 0.049379 | 0.049379 | 0.049379 | 0.97785 | -0.4254 | 0.97719 | -0.43841 | 13.5657
93 | -0.045341 | -0.011389 | 0.045395 | 0.011423 | 5.4461e-05 | 3.4472e-05 | 0.069005 | 0.069005 | 0.069005 | 0.97785 | -0.4254 | 0.97914 | -0.40026 | 18.9574
94 | -0.097096 | -0.024515 | 0.097169 | 0.024562 | 7.3063e-05 | 4.6647e-05 | 0.14741 | 0.14741 | 0.14741 | 0.98056 | -0.3724 | 0.98137 | -0.3567 | 40.497
95 | -0.11014 | -0.027814 | 0.11017 | 0.027834 | 3.2121e-05 | 2.0518e-05 | 0.16708 | 0.16708 | 0.16708 | 0.98137 | -0.3567 | 0.98168 | -0.35062 | 45.9007
96 | 0.012972 | 0.0032519 | -0.01297 | -0.0032507 | 2.0704e-06 | 1.1448e-06 | 0.019669 | 0.01967 | 0.01967 | 0.98137 | -0.3567 | 0.9812 | -0.36005 | 5.4037
97 | -0.11294 | -0.028527 | 0.11318 | 0.028682 | 0.00024211 | 0.00015467 | 0.17127 | 0.17127 | 0.17127 | 0.98168 | -0.35062 | 0.98398 | -0.30599 | 47.0518
98 | 0.010329 | 0.0025889 | -0.010329 | -0.0025886 | 6.6877e-07 | 3.3623e-07 | 0.015665 | 0.015665 | 0.015665 | 0.9812 | -0.36005 | 0.98113 | -0.36141 | 4.3036
99 | 0.0053459 | 0.0013398 | -0.0053456 | -0.0013397 | 3.1147e-07 | 3.9785e-08 | 0.0081078 | 0.0081079 | 0.0081079 | 0.98113 | -0.36141 | 0.98107 | -0.36264 | 2.2274
100 | -0.1372 | -0.034708 | 0.13771 | 0.035034 | 0.00050932 | 0.00032556 | 0.2076 | 0.2076 | 0.2076 | 0.98398 | -0.30599 | 0.98797 | -0.22894 | 57.032
101 | 0.024021 | 0.0060263 | -0.02401 | -0.0060194 | 1.1121e-05 | 6.8321e-06 | 0.036328 | 0.036328 | 0.036328 | 0.98398 | -0.30599 | 0.98348 | -0.31571 | 9.9803
102 | -0.14623 | -0.037169 | 0.14639 | 0.037271 | 0.00015947 | 0.00010161 | 0.22043 | 0.22043 | 0.22043 | 0.98797 | -0.22894 | 0.98915 | -0.20632 | 30.2792
103 | 0.0085229 | 0.0021359 | -0.0085224 | -0.0021357 | 4.6667e-07 | 2.0196e-07 | 0.012837 | 0.012837 | 0.012837 | 0.98797 | -0.22894 | 0.98791 | -0.23009 | 3.5265
104 | 0.01556 | 0.0039013 | -0.015555 | -0.0038984 | 5.0009e-06 | 2.8954e-06 | 0.023543 | 0.023543 | 0.023543 | 0.98348 | -0.31571 | 0.98314 | -0.32246 | 6.4678
105 | 0.0084504 | 0.0021181 | -0.008449 | -0.0021175 | 1.3877e-06 | 6.0093e-07 | 0.012786 | 0.012786 | 0.012786 | 0.98348 | -0.31571 | 0.98331 | -0.31916 | 3.5125
106 | -0.14639 | -0.037271 | 0.14651 | 0.037345 | 0.00011614 | 7.3593e-05 | 0.22043 | 0.22043 | 0.22043 | 0.98915 | -0.20632 | 0.99 | -0.18988 | 20.1861
107 | 0.006139 | 0.0015384 | -0.0061389 | -0.0015384 | 7.495e-08 | 1.8038e-08 | 0.0092467 | 0.0092467 | 0.0092467 | 0.98791 | -0.23009 | 0.9879 | -0.23034 | 2.5403
108 | -0.16803 | -0.042927 | 0.16814 | 0.042999 | 0.00011416 | 7.2505e-05 | 0.252 | 0.252 | 0.252 | 0.99333 | -0.12635 | 0.99406 | -0.11231 | 23.0767
109 | 0.16803 | 0.042927 | -0.16774 | -0.042745 | 0.00028593 | 0.0001816 | 0.252 | 0.252 | 0.252 | 0.99333 | -0.12635 | 0.99148 | -0.16161 | 23.0768
110 | -0.16814 | -0.042999 | 0.16826 | 0.043073 | 0.00011575 | 7.3513e-05 | 0.252 | 0.252 | 0.252 | 0.99406 | -0.11231 | 0.99481 | -0.098094 | 23.0767
111 | 0.011665 | 0.0029241 | -0.011662 | -0.0029224 | 3.0586e-06 | 1.6144e-06 | 0.017507 | 0.017507 | 0.017507 | 0.99148 | -0.16161 | 0.9912 | -0.16711 | 4.8098
112 | 0.15144 | 0.038658 | -0.15134 | -0.038594 | 0.00010114 | 6.4125e-05 | 0.22753 | 0.22753 | 0.22753 | 0.99148 | -0.16161 | 0.99076 | -0.17544 | 20.8359
113 | 0.00464 | 0.0011628 | -0.0046398 | -0.0011628 | 2.3726e-07 | -1.6406e-08 | 0.0069637 | 0.0069638 | 0.0069638 | 0.99148 | -0.16161 | 0.99143 | -0.16268 | 1.9131
114 | -0.14821 | -0.03777 | 0.14825 | 0.037796 | 4.067e-05 | 2.5776e-05 | 0.22298 | 0.22298 | 0.22298 | 0.99 | -0.18988 | 0.9903 | -0.1842 | 20.4198
115 | 0.0033041 | 0.00082788 | -0.0033039 | -0.00082803 | 2.0394e-07 | -1.506e-07 | 0.0049767 | 0.0049768 | 0.0049768 | 0.9879 | -0.23034 | 0.98783 | -0.23164 | 1.3672
116 | -0.17011 | -0.043537 | 0.17038 | 0.043711 | 0.00027364 | 0.00017381 | 0.25477 | 0.25477 | 0.25477 | 0.99481 | -0.098094 | 0.99656 | -0.06493 | 23.3305
117 | 0.0043508 | 0.00109 | -0.0043507 | -0.0010901 | 7.9733e-08 | -1.3211e-08 | 0.0065314 | 0.0065315 | 0.0065315 | 0.9912 | -0.16711 | 0.99118 | -0.1675 | 1.7944
118 | 0.14946 | 0.038123 | -0.14939 | -0.038083 | 6.3178e-05 | 4.0048e-05 | 0.22471 | 0.22471 | 0.22471 | 0.99076 | -0.17544 | 0.9903 | -0.1842 | 20.5775
119 | 0.033542 | 0.0084316 | -0.033475 | -0.0083896 | 6.7016e-05 | 4.204e-05 | 0.051168 | 0.051168 | 0.051168 | 0.97561 | -0.46945 | 0.97348 | -0.51139 | 14.0572
120 | -0.033542 | -0.0084316 | 0.033561 | 0.0084436 | 1.9083e-05 | 1.197e-05 | 0.051168 | 0.051168 | 0.051168 | 0.97561 | -0.46945 | 0.97621 | -0.45754 | 14.0571
121 | -0.038204 | -0.0096073 | 0.038241 | 0.0096302 | 3.6336e-05 | 2.2898e-05 | 0.058245 | 0.058245 | 0.058245 | 0.97621 | -0.45754 | 0.97723 | -0.43765 | 16.0015
122 | 0.3185 | 0.082017 | -0.31794 | -0.081662 | 0.00055577 | 0.00035492 | 0.47511 | 0.47511 | 0.47511 | 0.99916 | -0.015855 | 0.99725 | -0.051787 | 43.5082
123 | -0.3185 | -0.082017 | 0.31874 | 0.082174 | 0.00024592 | 0.00015704 | 0.47511 | 0.47511 | 0.47511 | 0.99916 | -0.015855 | 1 | 0 | 43.5081
124 | 0.31581 | 0.081126 | -0.3152 | -0.08074 | 0.0006057 | 0.0003868 | 0.47192 | 0.47192 | 0.47192 | 0.99725 | -0.051787 | 0.99516 | -0.091364 | 43.2163
125 | 0.17427 | 0.044895 | -0.17412 | -0.044801 | 0.00014762 | 9.3789e-05 | 0.25975 | 0.25975 | 0.25975 | 1 | 0 | 0.99907 | -0.01742 | 23.7869
126 | 0.17216 | 0.044308 | -0.17184 | -0.044107 | 0.00031583 | 0.00020063 | 0.25682 | 0.25682 | 0.25682 | 0.99907 | -0.01742 | 0.99707 | -0.055215 | 23.5187
127 | 0.17081 | 0.043848 | -0.17073 | -0.043796 | 8.05e-05 | 5.1134e-05 | 0.25528 | 0.25528 | 0.25528 | 0.99707 | -0.055215 | 0.99656 | -0.06493 | 23.3771
128 | 0.31373 | 0.080372 | -0.31324 | -0.080056 | 0.00049403 | 0.00031548 | 0.46973 | 0.46973 | 0.46973 | 0.99516 | -0.091364 | 0.99345 | -0.12392 | 43.0155
129 | 0.01359 | 0.0034057 | -0.013589 | -0.0034056 | 1.4078e-07 | 7.8367e-08 | 0.020355 | 0.020355 | 0.020355 | 0.99345 | -0.12392 | 0.99344 | -0.12413 | 5.592
130 | -0.0031609 | -0.00079219 | 0.003161 | 0.00079204 | 1.6932e-07 | -1.5241e-07 | 0.0047348 | 0.0047347 | 0.0047348 | 0.99338 | -0.12526 | 0.99344 | -0.12413 | 1.3008
131 | 0.0014348 | 0.00035924 | -0.0014347 | -0.00035942 | 2.6791e-08 | -1.8134e-07 | 0.0021538 | 0.0021539 | 0.0021539 | 0.99118 | -0.1675 | 0.99116 | -0.16789 | 0.59173
132 | -0.042265 | -0.010639 | 0.042271 | 0.010642 | 5.4554e-06 | 3.4475e-06 | 0.064374 | 0.064374 | 0.064374 | 0.97723 | -0.43765 | 0.97736 | -0.43495 | 17.6851
133 | 0.0056155 | 0.0014073 | -0.0056147 | -0.0014072 | 8.4334e-07 | 1.4222e-07 | 0.0084842 | 0.0084843 | 0.0084843 | 0.98489 | -0.28839 | 0.98473 | -0.29154 | 2.3309
134 | 0.12004 | 0.030359 | -0.11989 | -0.03026 | 0.00015395 | 9.8369e-05 | 0.18192 | 0.18192 | 0.18192 | 0.9824 | -0.33664 | 0.98102 | -0.36341 | 49.9785
135 | -0.0082018 | -0.0020556 | 0.0082046 | 0.0020568 | 2.8487e-06 | 1.2041e-06 | 0.012445 | 0.012445 | 0.012445 | 0.98065 | -0.3707 | 0.98102 | -0.36341 | 3.419
136 | 0.11168 | 0.028204 | -0.11145 | -0.028056 | 0.00023056 | 0.00014729 | 0.16948 | 0.16948 | 0.16948 | 0.98102 | -0.36341 | 0.97881 | -0.40659 | 46.5596
137 | 0.049179 | 0.012369 | -0.049153 | -0.012353 | 2.5124e-05 | 1.5929e-05 | 0.074778 | 0.074778 | 0.074778 | 0.97881 | -0.40659 | 0.97827 | -0.41729 | 20.5435
138 | 0.062274 | 0.015687 | -0.062226 | -0.015656 | 4.7975e-05 | 3.0525e-05 | 0.094699 | 0.094699 | 0.094699 | 0.97881 | -0.40659 | 0.97799 | -0.42271 | 26.0161
139 | 0.046069 | 0.011581 | -0.046059 | -0.011574 | 1.0209e-05 | 6.4639e-06 | 0.070087 | 0.070088 | 0.070088 | 0.97827 | -0.41729 | 0.97803 | -0.42193 | 19.2548
140 | 0.057557 | 0.014486 | -0.057523 | -0.014465 | 3.3649e-05 | 2.1389e-05 | 0.087595 | 0.087595 | 0.087595 | 0.97799 | -0.42271 | 0.97736 | -0.43495 | 24.0646
141 | -0.010507 | -0.0026337 | 0.010507 | 0.0026339 | 5.014e-07 | 2.5524e-07 | 0.015986 | 0.015986 | 0.015986 | 0.97798 | -0.42293 | 0.97803 | -0.42193 | 4.3918
142 | 0.010507 | 0.0026337 | -0.010504 | -0.0026326 | 2.1061e-06 | 1.0722e-06 | 0.015986 | 0.015986 | 0.015986 | 0.97798 | -0.42293 | 0.97776 | -0.42714 | 4.3918
143 | 0.035552 | 0.0089402 | -0.035518 | -0.0089188 | 3.3961e-05 | 2.1347e-05 | 0.054101 | 0.054102 | 0.054102 | 0.97803 | -0.42193 | 0.97701 | -0.44195 | 14.8631
144 | 0.0055303 | 0.0013859 | -0.0055294 | -0.0013858 | 9.1948e-07 | 1.5439e-07 | 0.0084163 | 0.0084164 | 0.0084164 | 0.97776 | -0.42714 | 0.97759 | -0.43063 | 2.3122
145 | -0.0086985 | -0.00218 | 0.0086996 | 0.0021806 | 1.1516e-06 | 5.1802e-07 | 0.01325 | 0.01325 | 0.01325 | 0.97687 | -0.44473 | 0.97701 | -0.44195 | 3.6401
146 | 0.0015816 | 0.0003963 | -0.0015816 | -0.00039638 | 1.6049e-08 | -8.2093e-08 | 0.0024088 | 0.0024088 | 0.0024088 | 0.97701 | -0.44195 | 0.977 | -0.44217 | 0.66177
147 | 0.025237 | 0.006342 | -0.0252 | -0.0063193 | 3.6614e-05 | 2.2607e-05 | 0.038443 | 0.038443 | 0.038443 | 0.97701 | -0.44195 | 0.97546 | -0.47239 | 10.5613
148 | 0.0014347 | 0.00035942 | -0.0014347 | -0.00035957 | 2.2013e-08 | -1.4899e-07 | 0.0021539 | 0.0021539 | 0.0021539 | 0.99116 | -0.16789 | 0.99114 | -0.16821 | 0.59174
149 | 0.014873 | 0.0037302 | -0.014865 | -0.0037256 | 8.0533e-06 | 4.6336e-06 | 0.022689 | 0.022689 | 0.022689 | 0.97546 | -0.47239 | 0.97488 | -0.48376 | 6.2332
150 | 0.010328 | 0.0025892 | -0.010327 | -0.0025889 | 5.0752e-07 | 2.5675e-07 | 0.015755 | 0.015755 | 0.015755 | 0.97546 | -0.47239 | 0.97541 | -0.47342 | 4.3282
151 | 0.0084556 | 0.0021192 | -0.0084553 | -0.0021191 | 3.1101e-07 | 1.3697e-07 | 0.012906 | 0.012906 | 0.012906 | 0.97488 | -0.48376 | 0.97485 | -0.48453 | 3.5457
152 | 0.0064091 | 0.0016063 | -0.0064078 | -0.0016059 | 1.2939e-06 | 3.7865e-07 | 0.0097825 | 0.0097827 | 0.0097827 | 0.97488 | -0.48376 | 0.97467 | -0.488 | 2.6876
153 | 0.0087226 | 0.0021868 | -0.0087216 | -0.0021863 | 1.0788e-06 | 4.8766e-07 | 0.013307 | 0.013307 | 0.013307 | 0.97541 | -0.47342 | 0.97528 | -0.47602 | 3.6558
154 | 0.0064078 | 0.0016059 | -0.0064076 | -0.0016059 | 1.718e-07 | 5.029e-08 | 0.0097827 | 0.0097827 | 0.0097827 | 0.97467 | -0.488 | 0.97464 | -0.48856 | 2.6876
155 | 0.0087216 | 0.0021863 | -0.0087193 | -0.0021853 | 2.2548e-06 | 1.0195e-06 | 0.013307 | 0.013307 | 0.013307 | 0.97528 | -0.47602 | 0.975 | -0.48145 | 3.6558

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.49912 | 0.12819

## res_load
| p_mw | q_mvar
0 | 0.0036245 | 0.00090838
1 | 0.0016818 | 0.0004215
2 | 0.0095722 | 0.002399
3 | 0.0010748 | 0.00026936
4 | 0.0073507 | 0.0018423
5 | 0.00051497 | 0.00012906
6 | 0.00078968 | 0.00019791
7 | 0.002683 | 0.00067242
8 | 0.0039355 | 0.00098633
9 | 0.0070712 | 0.0017722
10 | 0.0019053 | 0.00047753
11 | 0.00045914 | 0.00011507
12 | 0.013418 | 0.0033629
13 | 0.0002782 | 6.9724e-05
14 | 0.0017418 | 0.00043654
15 | 0.0033334 | 0.00083544
16 | 0.01672 | 0.0041904
17 | 0.0026899 | 0.00067415
18 | 0.020424 | 0.0051188
19 | 0.0043921 | 0.0011008
20 | 0.0021181 | 0.00053086
21 | 0.00085936 | 0.00021538
22 | 0.0044005 | 0.0011029
23 | 0.00262 | 0.00065663
24 | 0.0020764 | 0.0005204
25 | 0.00085901 | 0.00021529
26 | 0.016671 | 0.0041783
27 | 0.0038194 | 0.00095724
28 | 0.00287 | 0.00071928
29 | 0.0029316 | 0.00073472
30 | 0.0039737 | 0.00099591
31 | 0.0036572 | 0.00091658
32 | 0.0081736 | 0.0020485
33 | 0.019535 | 0.004896
34 | 0.0034081 | 0.00085416
35 | 0.0031928 | 0.00080019
36 | 0.013667 | 0.0034253
37 | 0.0061523 | 0.0015419
38 | 0.0017513 | 0.00043893
39 | 0.0010226 | 0.00025629
40 | 0.00094192 | 0.00023607
41 | 0.0010766 | 0.00026982
42 | 0.0020598 | 0.00051622
43 | 0.005753 | 0.0014418
44 | 0.0059142 | 0.0014822
45 | 0.0012023 | 0.00030132
46 | 0.0045843 | 0.0011489
47 | 0.0038337 | 0.00096081
48 | 0.0032467 | 0.0008137
49 | 0.0018632 | 0.00046696
50 | 0.0028994 | 0.00072665
51 | 0.0027403 | 0.00068677
52 | 0.0039404 | 0.00098756
53 | 0.0054848 | 0.0013746
54 | 0.0015726 | 0.00039412
55 | 0.0027642 | 0.00069276
56 | 0.0026406 | 0.00066181
57 | 0.0049828 | 0.0012488
58 | 0.0053456 | 0.0013397
59 | 0.0023834 | 0.00059733
60 | 0.015555 | 0.0038984
61 | 0.008449 | 0.0021175
62 | 0.0016974 | 0.00042541
63 | 0.0028349 | 0.00071049
64 | 0.0018531 | 0.00046443
65 | 0.0073114 | 0.0018324
66 | 0.0018783 | 0.00047076
67 | 0.0046398 | 0.0011628
68 | 0.033475 | 0.0083896
69 | 0.0046433 | 0.0011637
70 | 0.002136 | 0.00053534
71 | 0.0044583 | 0.0011174
72 | 0.0011468 | 0.00028742
73 | 0.0033039 | 0.00082803
74 | 0.0019668 | 0.00049292
75 | 0.0010363 | 0.00025973
76 | 0.00034105 | 8.5475e-05
77 | 0.0014671 | 0.00036769
78 | 0.0031609 | 0.00079219
79 | 0.010428 | 0.0026136
80 | 0.002916 | 0.00073081
81 | 0.0040247 | 0.0010087
82 | 0.0022719 | 0.0005694
83 | 0.0028694 | 0.00071913
84 | 0.0056147 | 0.0014072
85 | 0.0075887 | 0.0019019
86 | 0.0082018 | 0.0020556
87 | 0.0030839 | 0.00077291
88 | 0.0046688 | 0.0011701
89 | 0.0049742 | 0.0012466
90 | 0.0055294 | 0.0013858
91 | 0.0086985 | 0.00218
92 | 0.015252 | 0.0038226
93 | 0.0014347 | 0.00035957
94 | 0.0016045 | 0.00040213
95 | 0.0015816 | 0.00039638
96 | 0.0064076 | 0.0016059
97 | 0.0084553 | 0.0021191
98 | 0.0087193 | 0.0021853

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1