## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_120-7_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_120-7_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_120-7_0_5_node_185 | 0.4 | n |  | TRUE
3 | bus_LV_120-7_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_120-7_0_5_node_186 | 0.4 | n |  | TRUE
5 | bus_LV_120-7_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_120-7_0_5_node_240 | 0.4 | n |  | TRUE
7 | bus_LV_120-7_0_5_node_2 | 0.4 | n |  | TRUE
8 | bus_LV_120-7_0_5_node_188 | 0.4 | n |  | TRUE
9 | bus_LV_120-7_0_5_node_56 | 0.4 | n |  | TRUE
10 | bus_LV_120-7_0_5_node_255 | 0.4 | n |  | TRUE
11 | bus_LV_120-7_0_5_node_238 | 0.4 | n |  | TRUE
12 | bus_LV_120-7_0_5_node_239 | 0.4 | n |  | TRUE
13 | bus_LV_120-7_0_5_node_180 | 0.4 | n |  | TRUE
14 | bus_LV_120-7_0_5_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_120-7_0_5_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_120-7_0_5_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_120-7_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_120-7_0_5_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_120-7_0_5_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_120-7_0_5_node_179 | 0.4 | n |  | TRUE
21 | bus_LV_120-7_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_120-7_0_5_node_177 | 0.4 | n |  | TRUE
23 | bus_LV_120-7_0_5_node_172 | 0.4 | n |  | TRUE
24 | bus_LV_120-7_0_5_node_170 | 0.4 | n |  | TRUE
25 | bus_LV_120-7_0_5_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_120-7_0_5_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_120-7_0_5_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_120-7_0_5_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_120-7_0_5_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_120-7_0_5_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_120-7_0_5_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_120-7_0_5_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_120-7_0_5_node_168 | 0.4 | n |  | TRUE
34 | bus_LV_120-7_0_5_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_120-7_0_5_node_199 | 0.4 | n |  | TRUE
36 | bus_LV_120-7_0_5_node_231 | 0.4 | n |  | TRUE
37 | bus_LV_120-7_0_5_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_120-7_0_5_node_198 | 0.4 | n |  | TRUE
39 | bus_LV_120-7_0_5_node_220 | 0.4 | n |  | TRUE
40 | bus_LV_120-7_0_5_node_229 | 0.4 | n |  | TRUE
41 | bus_LV_120-7_0_5_node_59 | 0.4 | n |  | TRUE
42 | bus_LV_120-7_0_5_node_197 | 0.4 | n |  | TRUE
43 | bus_LV_120-7_0_5_node_221 | 0.4 | n |  | TRUE
44 | bus_LV_120-7_0_5_node_196 | 0.4 | n |  | TRUE
45 | bus_LV_120-7_0_5_node_241 | 0.4 | n |  | TRUE
46 | bus_LV_120-7_0_5_node_218 | 0.4 | n |  | TRUE
47 | bus_LV_120-7_0_5_node_21 | 0.4 | n |  | TRUE
48 | bus_LV_120-7_0_5_node_22 | 0.4 | n |  | TRUE
49 | bus_LV_120-7_0_5_node_23 | 0.4 | n |  | TRUE
50 | bus_LV_120-7_0_5_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_120-7_0_5_node_202 | 0.4 | n |  | TRUE
52 | bus_LV_120-7_0_5_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_120-7_0_5_node_244 | 0.4 | n |  | TRUE
54 | bus_LV_120-7_0_5_node_204 | 0.4 | n |  | TRUE
55 | bus_LV_120-7_0_5_node_200 | 0.4 | n |  | TRUE
56 | bus_LV_120-7_0_5_node_26 | 0.4 | n |  | TRUE
57 | bus_LV_120-7_0_5_node_27 | 0.4 | n |  | TRUE
58 | bus_LV_120-7_0_5_node_28 | 0.4 | n |  | TRUE
59 | bus_LV_120-7_0_5_node_242 | 0.4 | n |  | TRUE
60 | bus_LV_120-7_0_5_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_120-7_0_5_node_249 | 0.4 | n |  | TRUE
62 | bus_LV_120-7_0_5_node_248 | 0.4 | n |  | TRUE
63 | bus_LV_120-7_0_5_node_247 | 0.4 | n |  | TRUE
64 | bus_LV_120-7_0_5_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_120-7_0_5_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_120-7_0_5_node_87 | 0.4 | n |  | TRUE
67 | bus_LV_120-7_0_5_node_88 | 0.4 | n |  | TRUE
68 | bus_LV_120-7_0_5_node_89 | 0.4 | n |  | TRUE
69 | bus_LV_120-7_0_5_node_90 | 0.4 | n |  | TRUE
70 | bus_LV_120-7_0_5_node_91 | 0.4 | n |  | TRUE
71 | bus_LV_120-7_0_5_node_151 | 0.4 | n |  | TRUE
72 | bus_LV_120-7_0_5_node_98 | 0.4 | n |  | TRUE
73 | bus_LV_120-7_0_5_node_162 | 0.4 | n |  | TRUE
74 | bus_LV_120-7_0_5_node_99 | 0.4 | n |  | TRUE
75 | bus_LV_120-7_0_5_node_100 | 0.4 | n |  | TRUE
76 | bus_LV_120-7_0_5_node_145 | 0.4 | n |  | TRUE
77 | bus_LV_120-7_0_5_node_173 | 0.4 | n |  | TRUE
78 | bus_LV_120-7_0_5_node_181 | 0.4 | n |  | TRUE
79 | bus_LV_120-7_0_5_node_171 | 0.4 | n |  | TRUE
80 | bus_LV_120-7_0_5_node_182 | 0.4 | n |  | TRUE
81 | bus_LV_120-7_0_5_node_157 | 0.4 | n |  | TRUE
82 | bus_LV_120-7_0_5_node_155 | 0.4 | n |  | TRUE
83 | bus_LV_120-7_0_5_node_156 | 0.4 | n |  | TRUE
84 | bus_LV_120-7_0_5_node_158 | 0.4 | n |  | TRUE
85 | bus_LV_120-7_0_5_node_159 | 0.4 | n |  | TRUE
86 | bus_LV_120-7_0_5_node_160 | 0.4 | n |  | TRUE
87 | bus_LV_120-7_0_5_node_161 | 0.4 | n |  | TRUE
88 | bus_LV_120-7_0_5_node_174 | 0.4 | n |  | TRUE
89 | bus_LV_120-7_0_5_node_222 | 0.4 | n |  | TRUE
90 | bus_LV_120-7_0_5_node_243 | 0.4 | n |  | TRUE
91 | bus_LV_120-7_0_5_node_232 | 0.4 | n |  | TRUE
92 | bus_LV_120-7_0_5_node_175 | 0.4 | n |  | TRUE
93 | bus_LV_120-7_0_5_node_223 | 0.4 | n |  | TRUE
94 | bus_LV_120-7_0_5_node_233 | 0.4 | n |  | TRUE
95 | bus_LV_120-7_0_5_node_163 | 0.4 | n |  | TRUE
96 | bus_LV_120-7_0_5_node_164 | 0.4 | n |  | TRUE
97 | bus_LV_120-7_0_5_node_165 | 0.4 | n |  | TRUE
98 | bus_LV_120-7_0_5_node_166 | 0.4 | n |  | TRUE
99 | bus_LV_120-7_0_5_node_167 | 0.4 | n |  | TRUE
100 | bus_LV_120-7_0_5_node_189 | 0.4 | n |  | TRUE
101 | bus_LV_120-7_0_5_node_225 | 0.4 | n |  | TRUE
102 | bus_LV_120-7_0_5_node_184 | 0.4 | n |  | TRUE
103 | bus_LV_120-7_0_5_node_224 | 0.4 | n |  | TRUE
104 | bus_LV_120-7_0_5_node_169 | 0.4 | n |  | TRUE
105 | bus_LV_120-7_0_5_node_176 | 0.4 | n |  | TRUE
106 | bus_LV_120-7_0_5_node_178 | 0.4 | n |  | TRUE
107 | bus_LV_120-7_0_5_node_183 | 0.4 | n |  | TRUE
108 | bus_LV_120-7_0_5_node_237 | 0.4 | n |  | TRUE
109 | bus_LV_120-7_0_5_node_235 | 0.4 | n |  | TRUE
110 | bus_LV_120-7_0_5_node_187 | 0.4 | n |  | TRUE
111 | bus_LV_120-7_0_5_node_190 | 0.4 | n |  | TRUE
112 | bus_LV_120-7_0_5_node_191 | 0.4 | n |  | TRUE
113 | bus_LV_120-7_0_5_node_193 | 0.4 | n |  | TRUE
114 | bus_LV_120-7_0_5_node_209 | 0.4 | n |  | TRUE
115 | bus_LV_120-7_0_5_node_194 | 0.4 | n |  | TRUE
116 | bus_LV_120-7_0_5_node_205 | 0.4 | n |  | TRUE
117 | bus_LV_120-7_0_5_node_211 | 0.4 | n |  | TRUE
118 | bus_LV_120-7_0_5_node_207 | 0.4 | n |  | TRUE
119 | bus_LV_120-7_0_5_node_206 | 0.4 | n |  | TRUE
120 | bus_LV_120-7_0_5_node_195 | 0.4 | n |  | TRUE
121 | bus_LV_120-7_0_5_node_219 | 0.4 | n |  | TRUE
122 | bus_LV_120-7_0_5_node_201 | 0.4 | n |  | TRUE
123 | bus_LV_120-7_0_5_node_203 | 0.4 | n |  | TRUE
124 | bus_LV_120-7_0_5_node_245 | 0.4 | n |  | TRUE
125 | bus_LV_120-7_0_5_node_208 | 0.4 | n |  | TRUE
126 | bus_LV_120-7_0_5_node_210 | 0.4 | n |  | TRUE
127 | bus_LV_120-7_0_5_node_226 | 0.4 | n |  | TRUE
128 | bus_LV_120-7_0_5_node_227 | 0.4 | n |  | TRUE
129 | bus_LV_120-7_0_5_node_246 | 0.4 | n |  | TRUE
130 | bus_LV_120-7_0_5_node_212 | 0.4 | n |  | TRUE
131 | bus_LV_120-7_0_5_node_213 | 0.4 | n |  | TRUE
132 | bus_LV_120-7_0_5_node_214 | 0.4 | n |  | TRUE
133 | bus_LV_120-7_0_5_node_215 | 0.4 | n |  | TRUE
134 | bus_LV_120-7_0_5_node_216 | 0.4 | n |  | TRUE
135 | bus_LV_120-7_0_5_node_250 | 0.4 | n |  | TRUE
136 | bus_LV_120-7_0_5_node_251 | 0.4 | n |  | TRUE
137 | bus_LV_120-7_0_5_node_217 | 0.4 | n |  | TRUE
138 | bus_LV_120-7_0_5_node_228 | 0.4 | n |  | TRUE
139 | bus_LV_120-7_0_5_node_234 | 0.4 | n |  | TRUE
140 | bus_LV_120-7_0_5_node_236 | 0.4 | n |  | TRUE
141 | bus_MV_10_0_node_284 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_120-7_0_5_load_0 | 0 | 0.001881 | 0.00047143 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_120-7_0_5_load_185 | 2 | 0.00049135 | 0.00012314 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_120-7_0_5_load_5 | 5 | 0.0018946 | 0.00047483 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_120-7_0_5_load_240 | 6 | 0.0015913 | 0.00039883 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_120-7_0_5_load_56 | 9 | 0.001527 | 0.00038269 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_120-7_0_5_load_255 | 10 | 0.00084404 | 0.00021154 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_120-7_0_5_load_238 | 11 | 0.0013931 | 0.00034913 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_120-7_0_5_load_239 | 12 | 0.0051838 | 0.0012992 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_120-7_0_5_load_180 | 13 | 0.00080734 | 0.00020234 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_120-7_0_5_load_6 | 14 | 0.0010774 | 0.00027002 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_120-7_0_5_load_7 | 15 | 0.0026965 | 0.0006758 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_120-7_0_5_load_8 | 16 | 0.00077525 | 0.0001943 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_120-7_0_5_load_9 | 17 | 0.00087868 | 0.00022022 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_120-7_0_5_load_10 | 18 | 0.00088619 | 0.0002221 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_120-7_0_5_load_11 | 19 | 0.00079518 | 0.00019929 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_120-7_0_5_load_179 | 20 | 0.00064609 | 0.00016193 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_120-7_0_5_load_12 | 21 | 0.0013661 | 0.00034237 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_120-7_0_5_load_177 | 22 | 0.00053579 | 0.00013428 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_120-7_0_5_load_172 | 23 | 0.0020783 | 0.00052087 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_120-7_0_5_load_170 | 24 | 0.0014623 | 0.0003665 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_120-7_0_5_load_13 | 25 | 0.076186 | 0.019094 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_120-7_0_5_load_20 | 30 | 0.0022835 | 0.00057231 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_120-7_0_5_load_31 | 31 | 0.0016407 | 0.0004112 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_120-7_0_5_load_29 | 32 | 0.0044101 | 0.0011053 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_120-7_0_5_load_199 | 35 | 0.0045976 | 0.0011523 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_120-7_0_5_load_231 | 36 | 0.0024238 | 0.00060745 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_120-7_0_5_load_19 | 37 | 0.0026675 | 0.00066854 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_120-7_0_5_load_229 | 40 | 0.0014781 | 0.00037045 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_120-7_0_5_load_59 | 41 | 0.0025203 | 0.00063164 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_120-7_0_5_load_197 | 42 | 0.0045429 | 0.0011386 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_120-7_0_5_load_196 | 44 | 0.0042227 | 0.0010583 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_120-7_0_5_load_241 | 45 | 0.0018833 | 0.00047201 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_120-7_0_5_load_218 | 46 | 0.0029623 | 0.00074242 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_120-7_0_5_load_21 | 47 | 0.0093194 | 0.0023357 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_120-7_0_5_load_22 | 48 | 0.0032348 | 0.0008107 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_120-7_0_5_load_23 | 49 | 0.002603 | 0.00065237 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_120-7_0_5_load_25 | 50 | 0.011636 | 0.0029164 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_120-7_0_5_load_35 | 52 | 0.0022821 | 0.00057195 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_120-7_0_5_load_204 | 54 | 0.0036349 | 0.00091099 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_120-7_0_5_load_200 | 55 | 0.0019484 | 0.00048832 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_120-7_0_5_load_26 | 56 | 0.025037 | 0.006275 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_120-7_0_5_load_27 | 57 | 0.011983 | 0.0030031 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_120-7_0_5_load_242 | 59 | 0.003516 | 0.00088119 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_120-7_0_5_load_41 | 60 | 0.00012424 | 3.1138e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_120-7_0_5_load_249 | 61 | 0.00029386 | 7.3649e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_120-7_0_5_load_247 | 63 | 0.00034416 | 8.6256e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_120-7_0_5_load_57 | 64 | 0.0068048 | 0.0017055 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_120-7_0_5_load_58 | 65 | 0.0015951 | 0.00039977 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_120-7_0_5_load_87 | 66 | 0.017387 | 0.0043575 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_120-7_0_5_load_88 | 67 | 0.0050569 | 0.0012674 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_120-7_0_5_load_89 | 68 | 0.0029458 | 0.00073828 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_120-7_0_5_load_90 | 69 | 0.0036762 | 0.00092134 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_120-7_0_5_load_91 | 70 | 0.0051424 | 0.0012888 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_120-7_0_5_load_151 | 71 | 0.0037716 | 0.00094526 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_120-7_0_5_load_162 | 73 | 0.0075738 | 0.0018982 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_120-7_0_5_load_100 | 75 | 0.0021867 | 0.00054804 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_120-7_0_5_load_145 | 76 | 0.0017031 | 0.00042683 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_120-7_0_5_load_173 | 77 | 0.0074227 | 0.0018603 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_120-7_0_5_load_181 | 78 | 0.004043 | 0.0010133 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_120-7_0_5_load_171 | 79 | 0.0013373 | 0.00033516 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_120-7_0_5_load_182 | 80 | 0.0011281 | 0.00028273 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_120-7_0_5_load_155 | 82 | 0.0018253 | 0.00045746 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_120-7_0_5_load_158 | 84 | 0.0021118 | 0.00052926 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_120-7_0_5_load_159 | 85 | 0.0040279 | 0.0010095 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_120-7_0_5_load_160 | 86 | 0.0028568 | 0.00071597 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_120-7_0_5_load_161 | 87 | 0.0019951 | 0.00050003 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_120-7_0_5_load_174 | 88 | 0.0010413 | 0.00026097 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_120-7_0_5_load_222 | 89 | 0.0039506 | 0.00099011 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_120-7_0_5_load_243 | 90 | 0.0037532 | 0.00094064 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_120-7_0_5_load_232 | 91 | 0.0022597 | 0.00056632 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_120-7_0_5_load_175 | 92 | 0.0013635 | 0.00034173 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_120-7_0_5_load_223 | 93 | 0.0033754 | 0.00084596 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_120-7_0_5_load_233 | 94 | 0.0034684 | 0.00086927 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_120-7_0_5_load_163 | 95 | 0.0016134 | 0.00040436 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_120-7_0_5_load_164 | 96 | 0.001421 | 0.00035613 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_120-7_0_5_load_165 | 97 | 0.0012522 | 0.00031382 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_120-7_0_5_load_166 | 98 | 0.0021835 | 0.00054724 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_120-7_0_5_load_167 | 99 | 0.00046125 | 0.0001156 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_120-7_0_5_load_189 | 100 | 0.0062993 | 0.0015788 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_120-7_0_5_load_225 | 101 | 0.0012913 | 0.00032363 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_120-7_0_5_load_184 | 102 | 0.001469 | 0.00036816 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_120-7_0_5_load_224 | 103 | 0.0011929 | 0.00029897 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_120-7_0_5_load_169 | 104 | 0.0016694 | 0.00041839 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_120-7_0_5_load_176 | 105 | 0.00066272 | 0.00016609 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_120-7_0_5_load_178 | 106 | 0.0010662 | 0.00026721 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_120-7_0_5_load_183 | 107 | 0.0011697 | 0.00029314 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_120-7_0_5_load_237 | 108 | 0.0014884 | 0.00037302 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_120-7_0_5_load_235 | 109 | 0.0013071 | 0.0003276 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_120-7_0_5_load_187 | 110 | 0.00034083 | 8.5421e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_120-7_0_5_load_190 | 111 | 0.0027066 | 0.00067835 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_120-7_0_5_load_191 | 112 | 0.0030813 | 0.00077224 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_120-7_0_5_load_193 | 113 | 0.0028733 | 0.00072011 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_120-7_0_5_load_209 | 114 | 0.0021994 | 0.00055122 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_120-7_0_5_load_194 | 115 | 0.0019671 | 0.00049299 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_120-7_0_5_load_205 | 116 | 0.004048 | 0.0010145 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_120-7_0_5_load_207 | 118 | 0.0018389 | 0.00046088 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_120-7_0_5_load_206 | 119 | 0.002734 | 0.00068522 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_120-7_0_5_load_195 | 120 | 0.0034759 | 0.00087114 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_120-7_0_5_load_219 | 121 | 0.0027351 | 0.00068548 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_120-7_0_5_load_201 | 122 | 0.0008965 | 0.00022468 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_120-7_0_5_load_203 | 123 | 0.0016436 | 0.00041194 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_120-7_0_5_load_245 | 124 | 0.0016603 | 0.00041612 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_120-7_0_5_load_208 | 125 | 0.0015789 | 0.00039571 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_120-7_0_5_load_210 | 126 | 0.0014971 | 0.00037521 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_120-7_0_5_load_226 | 127 | 0.0014642 | 0.00036696 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_120-7_0_5_load_227 | 128 | 0.0010831 | 0.00027144 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_120-7_0_5_load_246 | 129 | 0.0032325 | 0.00081014 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_120-7_0_5_load_212 | 130 | 0.0015668 | 0.00039267 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_120-7_0_5_load_213 | 131 | 0.0015212 | 0.00038124 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_120-7_0_5_load_214 | 132 | 0.001813 | 0.00045438 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_120-7_0_5_load_215 | 133 | 0.0038915 | 0.0009753 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_120-7_0_5_load_216 | 134 | 0.0019191 | 0.00048097 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_120-7_0_5_load_251 | 136 | 0.0042131 | 0.0010559 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_120-7_0_5_load_217 | 137 | 0.0028751 | 0.00072056 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_120-7_0_5_load_228 | 138 | 0.0015231 | 0.00038172 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_120-7_0_5_load_234 | 139 | 0.010804 | 0.0027076 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_120-7_0_5_load_236 | 140 | 0.0011861 | 0.00029727 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_120-7_0_5_line_0 |  | 0 | 1 | 0.017105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_120-7_0_5_line_1 |  | 0 | 2 | 0.182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_120-7_0_5_line_2 |  | 1 | 3 | 0.069495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_120-7_0_5_line_3 |  | 2 | 4 | 0.0075374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_120-7_0_5_line_4 |  | 3 | 5 | 0.10942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_120-7_0_5_line_5 |  | 3 | 6 | 0.1333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_120-7_0_5_line_6 |  | 4 | 110 | 0.048402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_120-7_0_5_line_7 |  | 4 | 8 | 0.019316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_120-7_0_5_line_8 |  | 6 | 11 | 0.0071599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_120-7_0_5_line_9 |  | 7 | 8 | 0.20545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_120-7_0_5_line_10 |  | 7 | 9 | 0.091239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_120-7_0_5_line_11 |  | 8 | 10 | 0.011984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_120-7_0_5_line_12 |  | 11 | 140 | 0.0086094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_120-7_0_5_line_13 |  | 12 | 13 | 0.0048203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_120-7_0_5_line_14 |  | 13 | 106 | 0.026247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_120-7_0_5_line_15 |  | 14 | 15 | 0.001753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_120-7_0_5_line_16 |  | 14 | 16 | 0.017516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_120-7_0_5_line_17 |  | 15 | 17 | 0.0053152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_120-7_0_5_line_18 |  | 16 | 18 | 0.00087415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_120-7_0_5_line_19 |  | 17 | 19 | 0.01726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_120-7_0_5_line_20 |  | 18 | 20 | 0.0027551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_120-7_0_5_line_21 |  | 19 | 21 | 0.020212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_120-7_0_5_line_22 |  | 20 | 22 | 0.017236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_120-7_0_5_line_23 |  | 21 | 23 | 0.017355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_120-7_0_5_line_24 |  | 22 | 105 | 0.0059222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_120-7_0_5_line_25 |  | 23 | 24 | 0.017393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_120-7_0_5_line_26 |  | 24 | 104 | 0.023365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_120-7_0_5_line_27 |  | 25 | 26 | 0.011972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_120-7_0_5_line_28 |  | 25 | 27 | 0.062594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_120-7_0_5_line_29 |  | 26 | 28 | 0.073991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_120-7_0_5_line_30 |  | 26 | 29 | 0.07919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_120-7_0_5_line_31 |  | 27 | 30 | 0.012585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_120-7_0_5_line_32 |  | 28 | 31 | 0.032187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_120-7_0_5_line_33 |  | 28 | 32 | 0.10078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_120-7_0_5_line_34 |  | 29 | 33 | 0.11778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_120-7_0_5_line_35 |  | 30 | 39 | 0.015275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_120-7_0_5_line_36 |  | 31 | 40 | 0.0080644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_120-7_0_5_line_37 |  | 32 | 58 | 0.051428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_120-7_0_5_line_38 |  | 33 | 41 | 0.021833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_120-7_0_5_line_39 |  | 34 | 35 | 0.033688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_120-7_0_5_line_40 |  | 34 | 36 | 0.031724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_120-7_0_5_line_41 |  | 35 | 42 | 0.01269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_120-7_0_5_line_42 |  | 37 | 38 | 0.025636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_120-7_0_5_line_43 |  | 38 | 43 | 0.010317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_120-7_0_5_line_44 |  | 38 | 44 | 0.02922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_120-7_0_5_line_45 |  | 39 | 45 | 0.023507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_120-7_0_5_line_46 |  | 39 | 46 | 0.034333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_120-7_0_5_line_47 |  | 41 | 65 | 0.03772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_120-7_0_5_line_48 |  | 42 | 120 | 0.0094581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_120-7_0_5_line_49 |  | 43 | 119 | 0.027816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_120-7_0_5_line_50 |  | 43 | 121 | 0.028459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_120-7_0_5_line_51 |  | 44 | 120 | 0.031424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_120-7_0_5_line_52 |  | 45 | 129 | 0.044159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_120-7_0_5_line_53 |  | 46 | 137 | 0.0044326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_120-7_0_5_line_54 |  | 47 | 48 | 0.017393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_120-7_0_5_line_55 |  | 47 | 49 | 0.020221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_120-7_0_5_line_56 |  | 49 | 50 | 0.022511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_120-7_0_5_line_57 |  | 50 | 51 | 0.018938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_120-7_0_5_line_58 |  | 51 | 54 | 0.022401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_120-7_0_5_line_59 |  | 51 | 55 | 0.0078739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_120-7_0_5_line_60 |  | 52 | 53 | 0.024852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_120-7_0_5_line_61 |  | 53 | 59 | 0.033966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_120-7_0_5_line_62 |  | 54 | 93 | 0.013661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_120-7_0_5_line_63 |  | 55 | 122 | 0.029213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_120-7_0_5_line_64 |  | 56 | 57 | 0.013136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_120-7_0_5_line_65 |  | 56 | 58 | 0.010747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_120-7_0_5_line_66 |  | 59 | 90 | 0.011618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_120-7_0_5_line_67 |  | 60 | 61 | 0.14825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_120-7_0_5_line_68 |  | 61 | 62 | 0.018035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_120-7_0_5_line_69 |  | 62 | 63 | 0.043514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_120-7_0_5_line_70 |  | 63 | 110 | 0.039417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_120-7_0_5_line_71 |  | 64 | 65 | 0.010865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_120-7_0_5_line_72 |  | 66 | 67 | 0.011317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_120-7_0_5_line_73 |  | 66 | 68 | 0.012696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_120-7_0_5_line_74 |  | 67 | 69 | 0.0080793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_120-7_0_5_line_75 |  | 68 | 70 | 0.016641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_120-7_0_5_line_76 |  | 69 | 71 | 0.015227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_120-7_0_5_line_77 |  | 70 | 72 | 0.021624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_120-7_0_5_line_78 |  | 71 | 73 | 0.045041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_120-7_0_5_line_79 |  | 72 | 74 | 0.010769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_120-7_0_5_line_80 |  | 72 | 75 | 0.043457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_120-7_0_5_line_81 |  | 73 | 81 | 0.019129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_120-7_0_5_line_82 |  | 74 | 76 | 0.02918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_120-7_0_5_line_83 |  | 75 | 77 | 0.022567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_120-7_0_5_line_84 |  | 75 | 78 | 0.059948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_120-7_0_5_line_85 |  | 77 | 79 | 0.028026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_120-7_0_5_line_86 |  | 78 | 80 | 0.026469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_120-7_0_5_line_87 |  | 79 | 104 | 0.025852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_120-7_0_5_line_88 |  | 80 | 107 | 0.01284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_120-7_0_5_line_89 |  | 81 | 87 | 0.029422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_120-7_0_5_line_90 |  | 81 | 82 | 0.016568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_120-7_0_5_line_91 |  | 82 | 83 | 0.014193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_120-7_0_5_line_92 |  | 83 | 84 | 0.042937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_120-7_0_5_line_93 |  | 83 | 85 | 0.01798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_120-7_0_5_line_94 |  | 83 | 86 | 0.029157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_120-7_0_5_line_95 |  | 84 | 88 | 0.038901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_120-7_0_5_line_96 |  | 85 | 89 | 0.0044067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_120-7_0_5_line_97 |  | 86 | 90 | 0.0083733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_120-7_0_5_line_98 |  | 87 | 91 | 0.014347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_120-7_0_5_line_99 |  | 88 | 92 | 0.025441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_120-7_0_5_line_100 |  | 89 | 93 | 0.021622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_120-7_0_5_line_101 |  | 91 | 94 | 0.026914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_120-7_0_5_line_102 |  | 92 | 102 | 0.02167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_120-7_0_5_line_103 |  | 94 | 139 | 0.039668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_120-7_0_5_line_104 |  | 95 | 96 | 0.0027703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_120-7_0_5_line_105 |  | 95 | 97 | 0.016229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_120-7_0_5_line_106 |  | 96 | 98 | 0.017127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_120-7_0_5_line_107 |  | 97 | 99 | 0.0052845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_120-7_0_5_line_108 |  | 98 | 100 | 0.01422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_120-7_0_5_line_109 |  | 99 | 101 | 0.0081742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_120-7_0_5_line_110 |  | 100 | 102 | 0.0022563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_120-7_0_5_line_111 |  | 101 | 103 | 0.0025837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_120-7_0_5_line_112 |  | 103 | 133 | 0.0062519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_120-7_0_5_line_113 |  | 105 | 106 | 0.012317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_120-7_0_5_line_114 |  | 107 | 108 | 0.001248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_120-7_0_5_line_115 |  | 108 | 109 | 0.012417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_120-7_0_5_line_116 |  | 109 | 140 | 0.010568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_120-7_0_5_line_117 |  | 111 | 112 | 0.023826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_120-7_0_5_line_118 |  | 112 | 113 | 0.023581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_120-7_0_5_line_119 |  | 113 | 114 | 0.02077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_120-7_0_5_line_120 |  | 114 | 117 | 0.037951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_120-7_0_5_line_121 |  | 114 | 118 | 0.019174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_120-7_0_5_line_122 |  | 115 | 116 | 0.028878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_120-7_0_5_line_123 |  | 116 | 119 | 0.0010499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_120-7_0_5_line_124 |  | 117 | 124 | 0.012055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
125 | LV_120-7_0_5_line_125 |  | 117 | 123 | 0.0017311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_120-7_0_5_line_126 |  | 118 | 125 | 0.019037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_120-7_0_5_line_127 |  | 121 | 137 | 0.017371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_120-7_0_5_line_128 |  | 122 | 123 | 0.0019447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
129 | LV_120-7_0_5_line_129 |  | 124 | 129 | 0.011103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
130 | LV_120-7_0_5_line_130 |  | 125 | 126 | 0.0015781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_120-7_0_5_line_131 |  | 126 | 127 | 0.00069004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_120-7_0_5_line_132 |  | 127 | 128 | 0.023473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_120-7_0_5_line_133 |  | 128 | 138 | 0.0077029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_120-7_0_5_line_134 |  | 130 | 131 | 0.01306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_120-7_0_5_line_135 |  | 130 | 132 | 0.0022692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_120-7_0_5_line_136 |  | 131 | 133 | 0.011811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_120-7_0_5_line_137 |  | 132 | 134 | 0.021227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_120-7_0_5_line_138 |  | 134 | 135 | 0.12095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_120-7_0_5_line_139 |  | 135 | 136 | 0.14827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_120-7_0_5_trafo_202 | 0.63 MVA 20/0.4 kV | 141 | 51 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22
0 | 2710923.1528 | 1237815.5787 | 2710927.4422 | 1237832.1373
1 | 2710808.6718 | 1237970.0361 | 2710927.4422 | 1237832.1373
2 | 2710979.5104 | 1237774.7883 | 2710935.9065 | 1237807.7107 | 2710923.1528 | 1237815.5787
3 | 2710811.5292 | 1237977.0109 | 2710808.6718 | 1237970.0361
4 | 2710979.5104 | 1237774.7883 | 2710965.2321 | 1237757.7526 | 2710940.8314 | 1237738.9598 | 2710899.2839 | 1237714.4757 | 2710894.5157 | 1237707.8453
5 | 2711106.0879 | 1237732.9885 | 2710979.5104 | 1237774.7883
6 | 2710811.5292 | 1237977.0109 | 2710809.4672 | 1238011.6663 | 2710809.4411 | 1238025.3518
7 | 2710823.8727 | 1237991.8973 | 2710811.5292 | 1237977.0109
8 | 2711106.0879 | 1237732.9885 | 2711111.8212 | 1237737.2775
9 | 2710823.8727 | 1237991.8973 | 2711028.404 | 1238011.2548
10 | 2711028.404 | 1238011.2548 | 2711103.1395 | 1237958.9177
11 | 2710823.8727 | 1237991.8973 | 2710821.269 | 1237995.9853 | 2710822.6895 | 1238002.984
12 | 2711118.715 | 1237742.4346 | 2711111.8212 | 1237737.2775
13 | 2711010.5363 | 1237631.1218 | 2711014.4109 | 1237633.9893
14 | 2711035.508 | 1237649.6031 | 2711014.4109 | 1237633.9893
15 | 2711085.8598 | 1237678.9249 | 2711084.3164 | 1237678.0937
16 | 2711068.8943 | 1237669.7885 | 2711084.3164 | 1237678.0937
17 | 2711085.8598 | 1237678.9249 | 2711090.5395 | 1237681.4451
18 | 2711068.1247 | 1237669.374 | 2711068.8943 | 1237669.7885
19 | 2711104.7492 | 1237691.2135 | 2711092.6165 | 1237682.5636 | 2711090.5395 | 1237681.4451
20 | 2711065.6989 | 1237668.0677 | 2711068.1247 | 1237669.374
21 | 2711104.7492 | 1237691.2135 | 2711121.207 | 1237702.947
22 | 2711050.5232 | 1237659.8951 | 2711065.6989 | 1237668.0677
23 | 2711121.207 | 1237702.947 | 2711135.3382 | 1237713.0218
24 | 2711050.5232 | 1237659.8951 | 2711046.4526 | 1237657.703 | 2711045.4086 | 1237656.9303
25 | 2711149.5003 | 1237723.1186 | 2711135.3382 | 1237713.0218
26 | 2711149.5003 | 1237723.1186 | 2711168.5255 | 1237736.6824
27 | 2711381.3626 | 1237504.4977 | 2711372.2509 | 1237496.7326
28 | 2711321.54 | 1237460.6306 | 2711328.2143 | 1237465.0815 | 2711352.2162 | 1237483.7461 | 2711361.483 | 1237487.5561 | 2711372.2509 | 1237496.7326
29 | 2711381.3626 | 1237504.4977 | 2711422.9882 | 1237541.3297 | 2711430.3822 | 1237547.7401 | 2711436.7628 | 1237553.72
30 | 2711399.968 | 1237455.0633 | 2711394.7596 | 1237456.7781 | 2711407.0132 | 1237501.4319 | 2711401.5437 | 1237506.1775 | 2711381.3626 | 1237504.4977
31 | 2711321.54 | 1237460.6306 | 2711317.5548 | 1237469.3517 | 2711316.3997 | 1237472.1164
32 | 2711436.7628 | 1237553.72 | 2711439.0251 | 1237554.1406 | 2711444.0473 | 1237555.08 | 2711451.0223 | 1237551.1634 | 2711453.7219 | 1237542.8074 | 2711453.44 | 1237535.6521 | 2711453.1601 | 1237534.8652
33 | 2711436.7628 | 1237553.72 | 2711484.2584 | 1237642.6035
34 | 2711399.968 | 1237455.0633 | 2711403.5292 | 1237454.4185 | 2711416.4477 | 1237468.0827 | 2711419.6588 | 1237469.9666 | 2711422.5069 | 1237469.8199 | 2711424.3605 | 1237468.2312 | 2711425.8282 | 1237465.8346 | 2711425.4844 | 1237462.381 | 2711422.3948 | 1237454.0276 | 2711419.4904 | 1237446.6896 | 2711419.5321 | 1237444.4664 | 2711420.9732 | 1237443.0812 | 2711423.4054 | 1237443.327 | 2711427.8041 | 1237446.8456 | 2711436.1853 | 1237454.6979 | 2711438.0009 | 1237455.1324 | 2711439.4383 | 1237454.3476 | 2711440.2895 | 1237452.1396 | 2711431.3639 | 1237441.0412 | 2711430.5847 | 1237439.4142 | 2711431.0312 | 1237437.3988 | 2711433.2666 | 1237437.2406 | 2711446.6898 | 1237437.3258
35 | 2711310.5112 | 1237486.2107 | 2711316.3997 | 1237472.1164
36 | 2711450.457 | 1237527.2673 | 2711453.1601 | 1237534.8652
37 | 2711484.2584 | 1237642.6035 | 2711509.7131 | 1237656.7814 | 2711515.0031 | 1237657.1588 | 2711528.2077 | 1237646.2982
38 | 2711446.6898 | 1237437.3258 | 2711463.5687 | 1237451.1737
39 | 2711329.583 | 1237415.5126 | 2711327.4475 | 1237413.571 | 2711326.5476 | 1237408.2944 | 2711327.2501 | 1237399.8899 | 2711325.1443 | 1237395.9584 | 2711317.6668 | 1237392.371 | 2711313.556 | 1237391.2485
40 | 2711329.583 | 1237415.5126 | 2711332.5954 | 1237404.9941 | 2711339.8974 | 1237391.7205 | 2711341.1947 | 1237386.2392
41 | 2711313.556 | 1237391.2485 | 2711301.3137 | 1237387.9055 | 2711301.3137 | 1237387.9055
42 | 2711263.3016 | 1237441.2019 | 2711277.4857 | 1237442.6799 | 2711288.5624 | 1237445.2676
43 | 2711263.3016 | 1237441.2019 | 2711253.8832 | 1237445.4733
44 | 2711263.3016 | 1237441.2019 | 2711266.2477 | 1237431.7942 | 2711275.0005 | 1237429.523 | 2711279.8219 | 1237420.4001
45 | 2711310.5112 | 1237486.2107 | 2711309.2989 | 1237489.1125 | 2711307.8106 | 1237501.8947 | 2711304.6578 | 1237508.6933
46 | 2711310.5112 | 1237486.2107 | 2711293.0374 | 1237480.9903 | 2711285.7487 | 1237477.829 | 2711277.8568 | 1237475.7899
47 | 2711463.5687 | 1237451.1737 | 2711486.6808 | 1237470.1354 | 2711493.2459 | 1237474.3925
48 | 2711294.4304 | 1237393.6887 | 2711294.977 | 1237391.6786 | 2711301.3137 | 1237387.9055
49 | 2711253.8832 | 1237445.4733 | 2711234.1164 | 1237439.0425 | 2711227.336 | 1237437.1879
50 | 2711253.8832 | 1237445.4733 | 2711256.0741 | 1237452.1307 | 2711258.9724 | 1237452.9412 | 2711260.7026 | 1237455.509 | 2711256.7469 | 1237470.3354 | 2711256.7469 | 1237470.3354
51 | 2711294.4304 | 1237393.6887 | 2711291.3032 | 1237405.1871 | 2711285.6552 | 1237409.3623 | 2711279.8219 | 1237420.4001
52 | 2711304.6578 | 1237508.6933 | 2711297.3612 | 1237524.4277 | 2711288.1188 | 1237534.2512 | 2711277.0744 | 1237541.7108
53 | 2711273.5651 | 1237474.681 | 2711277.8568 | 1237475.7899
54 | 2711331.3452 | 1237652.3483 | 2711325.9044 | 1237635.8281 | 2711325.9044 | 1237635.8281
55 | 2711311.8201 | 1237621.3186 | 2711325.9044 | 1237635.8281
56 | 2711296.1409 | 1237605.1663 | 2711311.8201 | 1237621.3186
57 | 2711282.95 | 1237591.5772 | 2711296.1409 | 1237605.1663
58 | 2711282.95 | 1237591.5772 | 2711276.9195 | 1237613.1515
59 | 2711282.95 | 1237591.5772 | 2711278.5823 | 1237585.0257
60 | 2711304.9272 | 1237721.8137 | 2711322.2153 | 1237703.9607
61 | 2711304.9272 | 1237721.8137 | 2711281.3541 | 1237697.3595
62 | 2711272.0791 | 1237625.8566 | 2711274.9602 | 1237620.1611 | 2711276.9195 | 1237613.1515
63 | 2711278.5823 | 1237585.0257 | 2711262.3779 | 1237560.7187
64 | 2711527.3572 | 1237635.5849 | 2711515.2857 | 1237630.4056
65 | 2711528.2077 | 1237646.2982 | 2711527.3572 | 1237635.5849
66 | 2711281.3541 | 1237697.3595 | 2711273.291 | 1237688.995
67 | 2710791.2384 | 1238091.1332 | 2710654.7124 | 1238148.9108
68 | 2710798.3714 | 1238107.468 | 2710795.5822 | 1238104.0689 | 2710791.2384 | 1238091.1332
69 | 2710798.3714 | 1238107.468 | 2710800.1245 | 1238096.2474 | 2710803.3946 | 1238079.562 | 2710805.3455 | 1238064.5334
70 | 2710805.3455 | 1238064.5334 | 2710805.7101 | 1238061.7245 | 2710807.2528 | 1238045.5628 | 2710808.6979 | 1238035.4373 | 2710809.4362 | 1238027.9119 | 2710809.4411 | 1238025.3518
71 | 2711502.7293 | 1237479.653 | 2711497.3122 | 1237477.0293 | 2711493.2459 | 1237474.3925
72 | 2711291.9669 | 1237770.5203 | 2711291.9669 | 1237770.5203 | 2711285.7735 | 1237761.0485
73 | 2711291.9669 | 1237770.5203 | 2711284.449 | 1237780.7517
74 | 2711285.7735 | 1237761.0485 | 2711281.352 | 1237754.2864
75 | 2711274.5953 | 1237794.1619 | 2711284.449 | 1237780.7517
76 | 2711269.3359 | 1237744.933 | 2711281.352 | 1237754.2864 | 2711281.352 | 1237754.2864
77 | 2711261.7913 | 1237811.5873 | 2711274.5953 | 1237794.1619
78 | 2711244.5538 | 1237708.3793 | 2711248.6684 | 1237719.6358 | 2711260.976 | 1237738.4255 | 2711269.3359 | 1237744.933
79 | 2711261.7913 | 1237811.5873 | 2711271.9296 | 1237815.3024
80 | 2711261.7913 | 1237811.5873 | 2711230.7711 | 1237781.06
81 | 2711237.9865 | 1237690.4127 | 2711244.5538 | 1237708.3793
82 | 2711271.9296 | 1237815.3024 | 2711272.0839 | 1237821.1988 | 2711273.9851 | 1237828.3623 | 2711282.5365 | 1237841.7312
83 | 2711230.7711 | 1237781.06 | 2711212.3955 | 1237767.9593
84 | 2711230.7711 | 1237781.06 | 2711198.1225 | 1237783.306 | 2711183.1 | 1237781.7903 | 2711172.4072 | 1237776.0776
85 | 2711212.3955 | 1237767.9593 | 2711189.5757 | 1237751.6901
86 | 2711149.0609 | 1237763.6049 | 2711172.4072 | 1237776.0776
87 | 2711189.5757 | 1237751.6901 | 2711168.5255 | 1237736.6824
88 | 2711149.0609 | 1237763.6049 | 2711141.9009 | 1237759.7796 | 2711138.1196 | 1237756.9509
89 | 2711237.9865 | 1237690.4127 | 2711225.7754 | 1237688.6715 | 2711210.371 | 1237681.2773
90 | 2711237.9865 | 1237690.4127 | 2711239.2636 | 1237679.6059 | 2711240.526 | 1237674.0618
91 | 2711247.2445 | 1237661.9748 | 2711241.7621 | 1237668.6329 | 2711240.526 | 1237674.0618
92 | 2711247.2445 | 1237661.9748 | 2711213.0157 | 1237636.0525
93 | 2711247.2445 | 1237661.9748 | 2711258.2989 | 1237647.7948
94 | 2711247.2445 | 1237661.9748 | 2711267.4798 | 1237682.9666
95 | 2711213.0157 | 1237636.0525 | 2711193.1497 | 1237621.0075 | 2711182.7633 | 1237611.6486
96 | 2711261.0083 | 1237644.3194 | 2711258.2989 | 1237647.7948
97 | 2711267.4798 | 1237682.9666 | 2711273.291 | 1237688.995
98 | 2711199.8961 | 1237671.4728 | 2711210.371 | 1237681.2773
99 | 2711163.0371 | 1237595.8399 | 2711167.8182 | 1237598.182 | 2711182.7633 | 1237611.6486
100 | 2711261.0083 | 1237644.3194 | 2711265.9386 | 1237637.995 | 2711272.0791 | 1237625.8566
101 | 2711199.8961 | 1237671.4728 | 2711180.2465 | 1237653.0808
102 | 2711143.5769 | 1237586.3069 | 2711163.0371 | 1237595.8399
103 | 2711152.2574 | 1237624.9785 | 2711175.1056 | 1237648.2689 | 2711180.2465 | 1237653.0808
104 | 2711117.5366 | 1237566.1393 | 2711115.7178 | 1237564.0496
105 | 2711103.6246 | 1237553.5827 | 2711109.409 | 1237556.801 | 2711115.7178 | 1237564.0496
106 | 2711117.5366 | 1237566.1393 | 2711128.7809 | 1237579.0587 | 2711128.7809 | 1237579.0587
107 | 2711103.6246 | 1237553.5827 | 2711099.0067 | 1237551.0134
108 | 2711128.7809 | 1237579.0587 | 2711141.5507 | 1237585.3142
109 | 2711091.8636 | 1237547.0392 | 2711099.0067 | 1237551.0134
110 | 2711143.5769 | 1237586.3069 | 2711141.5507 | 1237585.3142
111 | 2711089.6059 | 1237545.783 | 2711091.8636 | 1237547.0392
112 | 2711089.6059 | 1237545.783 | 2711084.1426 | 1237542.7434
113 | 2711035.508 | 1237649.6031 | 2711045.4086 | 1237656.9303
114 | 2711137.1203 | 1237756.2033 | 2711138.1196 | 1237756.9509
115 | 2711127.1773 | 1237748.7651 | 2711137.1203 | 1237756.2033
116 | 2711127.1773 | 1237748.7651 | 2711118.715 | 1237742.4346
117 | 2711185.8678 | 1237485.7061 | 2711195.6814 | 1237495.167 | 2711204.5411 | 1237500.2112
118 | 2711204.5411 | 1237500.2112 | 2711225.0334 | 1237511.8784
119 | 2711240.541 | 1237525.453 | 2711230.0342 | 1237514.7256 | 2711225.0334 | 1237511.8784
120 | 2711260.339 | 1237557.6603 | 2711244.7065 | 1237529.7121 | 2711240.541 | 1237525.453
121 | 2711240.541 | 1237525.453 | 2711226.7878 | 1237530.8775 | 2711222.4392 | 1237531.4752
122 | 2711198.051 | 1237433.155 | 2711210.2873 | 1237432.5245 | 2711226.3233 | 1237436.9109
123 | 2711226.3233 | 1237436.9109 | 2711227.336 | 1237437.1879
124 | 2711260.339 | 1237557.6603 | 2711268.8918 | 1237549.1642
125 | 2711260.339 | 1237557.6603 | 2711261.2992 | 1237559.1006
126 | 2711222.4392 | 1237531.4752 | 2711203.5794 | 1237534.0677 | 2711203.5794 | 1237534.0677
127 | 2711273.5651 | 1237474.681 | 2711256.7469 | 1237470.3354
128 | 2711261.2992 | 1237559.1006 | 2711262.3779 | 1237560.7187
129 | 2711268.8918 | 1237549.1642 | 2711274.9513 | 1237543.1448 | 2711277.0744 | 1237541.7108
130 | 2711203.5794 | 1237534.0677 | 2711202.0085 | 1237533.9172
131 | 2711201.3216 | 1237533.8514 | 2711202.0085 | 1237533.9172
132 | 2711178.336 | 1237529.9655 | 2711184.3851 | 1237532.2291 | 2711201.3216 | 1237533.8514
133 | 2711171.1216 | 1237527.2658 | 2711178.336 | 1237529.9655
134 | 2711062.5617 | 1237530.4187 | 2711064.0534 | 1237531.5662 | 2711073.8216 | 1237537.001
135 | 2711062.5617 | 1237530.4187 | 2711060.7632 | 1237529.035
136 | 2711073.8216 | 1237537.001 | 2711084.1426 | 1237542.7434
137 | 2711060.7632 | 1237529.035 | 2711043.9388 | 1237516.0917
138 | 2710992.3735 | 1237413.0889 | 2710992.5615 | 1237426.1026 | 2710994.0356 | 1237430.2334 | 2710999.5237 | 1237436.6187 | 2711007.0659 | 1237449.303 | 2711014.5714 | 1237463.1319 | 2711019.5537 | 1237475.9239 | 2711020.5791 | 1237479.7684 | 2711019.4813 | 1237492.3355 | 2711030.5728 | 1237505.809 | 2711043.9388 | 1237516.0917
139 | 2710992.3735 | 1237413.0889 | 2711030.3828 | 1237419.6933 | 2711037.2781 | 1237419.6221 | 2711041.9244 | 1237418.4192 | 2711047.1959 | 1237415.7489 | 2711062.3941 | 1237404.6911 | 2711077.5704 | 1237393.9998 | 2711090.6943 | 1237383.3925 | 2711105.7816 | 1237365.7386 | 2711118.1524 | 1237357.9195

## bus_geodata
| x | y | coords
0 | 2710927.4422 | 1237832.1373
1 | 2710923.1528 | 1237815.5787
2 | 2710808.6718 | 1237970.0361
3 | 2710979.5104 | 1237774.7883
4 | 2710811.5292 | 1237977.0109
5 | 2710894.5157 | 1237707.8453
6 | 2711106.0879 | 1237732.9885
7 | 2711028.404 | 1238011.2548
8 | 2710823.8727 | 1237991.8973
9 | 2711103.1395 | 1237958.9177
10 | 2710822.6895 | 1238002.984
11 | 2711111.8212 | 1237737.2775
12 | 2711010.5363 | 1237631.1218
13 | 2711014.4109 | 1237633.9893
14 | 2711084.3164 | 1237678.0937
15 | 2711085.8598 | 1237678.9249
16 | 2711068.8943 | 1237669.7885
17 | 2711090.5395 | 1237681.4451
18 | 2711068.1247 | 1237669.374
19 | 2711104.7492 | 1237691.2135
20 | 2711065.6989 | 1237668.0677
21 | 2711121.207 | 1237702.947
22 | 2711050.5232 | 1237659.8951
23 | 2711135.3382 | 1237713.0218
24 | 2711149.5003 | 1237723.1186
25 | 2711372.2509 | 1237496.7326
26 | 2711381.3626 | 1237504.4977
27 | 2711321.54 | 1237460.6306
28 | 2711436.7628 | 1237553.72
29 | 2711399.968 | 1237455.0633
30 | 2711316.3997 | 1237472.1164
31 | 2711453.1601 | 1237534.8652
32 | 2711484.2584 | 1237642.6035
33 | 2711446.6898 | 1237437.3258
34 | 2711329.583 | 1237415.5126
35 | 2711313.556 | 1237391.2485
36 | 2711341.1947 | 1237386.2392
37 | 2711288.5624 | 1237445.2676
38 | 2711263.3016 | 1237441.2019
39 | 2711310.5112 | 1237486.2107
40 | 2711450.457 | 1237527.2673
41 | 2711463.5687 | 1237451.1737
42 | 2711301.3137 | 1237387.9055
43 | 2711253.8832 | 1237445.4733
44 | 2711279.8219 | 1237420.4001
45 | 2711304.6578 | 1237508.6933
46 | 2711277.8568 | 1237475.7899
47 | 2711325.9044 | 1237635.8281
48 | 2711331.3452 | 1237652.3483
49 | 2711311.8201 | 1237621.3186
50 | 2711296.1409 | 1237605.1663
51 | 2711282.95 | 1237591.5772
52 | 2711322.2153 | 1237703.9607
53 | 2711304.9272 | 1237721.8137
54 | 2711276.9195 | 1237613.1515
55 | 2711278.5823 | 1237585.0257
56 | 2711527.3572 | 1237635.5849
57 | 2711515.2857 | 1237630.4056
58 | 2711528.2077 | 1237646.2982
59 | 2711281.3541 | 1237697.3595
60 | 2710654.7124 | 1238148.9108
61 | 2710791.2384 | 1238091.1332
62 | 2710798.3714 | 1238107.468
63 | 2710805.3455 | 1238064.5334
64 | 2711502.7293 | 1237479.653
65 | 2711493.2459 | 1237474.3925
66 | 2711291.9669 | 1237770.5203
67 | 2711285.7735 | 1237761.0485
68 | 2711284.449 | 1237780.7517
69 | 2711281.352 | 1237754.2864
70 | 2711274.5953 | 1237794.1619
71 | 2711269.3359 | 1237744.933
72 | 2711261.7913 | 1237811.5873
73 | 2711244.5538 | 1237708.3793
74 | 2711271.9296 | 1237815.3024
75 | 2711230.7711 | 1237781.06
76 | 2711282.5365 | 1237841.7312
77 | 2711212.3955 | 1237767.9593
78 | 2711172.4072 | 1237776.0776
79 | 2711189.5757 | 1237751.6901
80 | 2711149.0609 | 1237763.6049
81 | 2711237.9865 | 1237690.4127
82 | 2711240.526 | 1237674.0618
83 | 2711247.2445 | 1237661.9748
84 | 2711213.0157 | 1237636.0525
85 | 2711258.2989 | 1237647.7948
86 | 2711267.4798 | 1237682.9666
87 | 2711210.371 | 1237681.2773
88 | 2711182.7633 | 1237611.6486
89 | 2711261.0083 | 1237644.3194
90 | 2711273.291 | 1237688.995
91 | 2711199.8961 | 1237671.4728
92 | 2711163.0371 | 1237595.8399
93 | 2711272.0791 | 1237625.8566
94 | 2711180.2465 | 1237653.0808
95 | 2711115.7178 | 1237564.0496
96 | 2711117.5366 | 1237566.1393
97 | 2711103.6246 | 1237553.5827
98 | 2711128.7809 | 1237579.0587
99 | 2711099.0067 | 1237551.0134
100 | 2711141.5507 | 1237585.3142
101 | 2711091.8636 | 1237547.0392
102 | 2711143.5769 | 1237586.3069
103 | 2711089.6059 | 1237545.783
104 | 2711168.5255 | 1237736.6824
105 | 2711045.4086 | 1237656.9303
106 | 2711035.508 | 1237649.6031
107 | 2711138.1196 | 1237756.9509
108 | 2711137.1203 | 1237756.2033
109 | 2711127.1773 | 1237748.7651
110 | 2710809.4411 | 1238025.3518
111 | 2711185.8678 | 1237485.7061
112 | 2711204.5411 | 1237500.2112
113 | 2711225.0334 | 1237511.8784
114 | 2711240.541 | 1237525.453
115 | 2711198.051 | 1237433.155
116 | 2711226.3233 | 1237436.9109
117 | 2711260.339 | 1237557.6603
118 | 2711222.4392 | 1237531.4752
119 | 2711227.336 | 1237437.1879
120 | 2711294.4304 | 1237393.6887
121 | 2711256.7469 | 1237470.3354
122 | 2711262.3779 | 1237560.7187
123 | 2711261.2992 | 1237559.1006
124 | 2711268.8918 | 1237549.1642
125 | 2711203.5794 | 1237534.0677
126 | 2711202.0085 | 1237533.9172
127 | 2711201.3216 | 1237533.8514
128 | 2711178.336 | 1237529.9655
129 | 2711277.0744 | 1237541.7108
130 | 2711062.5617 | 1237530.4187
131 | 2711073.8216 | 1237537.001
132 | 2711060.7632 | 1237529.035
133 | 2711084.1426 | 1237542.7434
134 | 2711043.9388 | 1237516.0917
135 | 2710992.3735 | 1237413.0889
136 | 2711118.1524 | 1237357.9195
137 | 2711273.5651 | 1237474.681
138 | 2711171.1216 | 1237527.2658
139 | 2711152.2574 | 1237624.9785
140 | 2711118.715 | 1237742.4346
141 | 2711260.339 | 1237557.6603

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97265 | -0.52861 | 0.001881 | 0.00047143
1 | 0.97274 | -0.52676 | 0 | 0
2 | 0.97198 | -0.542 | 0.00049135 | 0.00012314
3 | 0.97312 | -0.51925 | 0 | 0
4 | 0.97195 | -0.54248 | 0 | 0
5 | 0.97293 | -0.52307 | 0.0018946 | 0.00047483
6 | 0.97408 | -0.50019 | 0.0015913 | 0.00039883
7 | 0.97162 | -0.54914 | 0 | 0
8 | 0.97191 | -0.54333 | 0 | 0
9 | 0.97149 | -0.55172 | 0.001527 | 0.00038269
10 | 0.9719 | -0.54352 | 0.00084404 | 0.00021154
11 | 0.97415 | -0.49896 | 0.0013931 | 0.00034913
12 | 0.97216 | -0.53813 | 0.0051838 | 0.0012992
13 | 0.97218 | -0.53767 | 0.00080734 | 0.00020234
14 | 0.97279 | -0.52568 | 0.0010774 | 0.00027002
15 | 0.97281 | -0.5253 | 0.0026965 | 0.0006758
16 | 0.97261 | -0.52909 | 0.00077525 | 0.0001943
17 | 0.97288 | -0.5239 | 0.00087868 | 0.00022022
18 | 0.97261 | -0.52925 | 0.00088619 | 0.0002221
19 | 0.97312 | -0.51906 | 0.00079518 | 0.00019929
20 | 0.97258 | -0.5297 | 0.00064609 | 0.00016193
21 | 0.97342 | -0.51311 | 0.0013661 | 0.00034237
22 | 0.97245 | -0.53232 | 0.00053579 | 0.00013428
23 | 0.9737 | -0.50756 | 0.0020783 | 0.00052087
24 | 0.97402 | -0.50134 | 0.0014623 | 0.0003665
25 | 0.98328 | -0.32048 | 0.076186 | 0.019094
26 | 0.98267 | -0.33246 | 0 | 0
27 | 0.9871 | -0.24648 | 0 | 0
28 | 0.9796 | -0.39216 | 0 | 0
29 | 0.98187 | -0.3481 | 0 | 0
30 | 0.98786 | -0.23167 | 0.0022835 | 0.00057231
31 | 0.9795 | -0.39398 | 0.0016407 | 0.0004112
32 | 0.97571 | -0.4683 | 0.0044101 | 0.0011053
33 | 0.98068 | -0.37139 | 0 | 0
34 | 0.98467 | -0.29406 | 0 | 0
35 | 0.98474 | -0.29259 | 0.0045976 | 0.0011523
36 | 0.9846 | -0.29544 | 0.0024238 | 0.00060745
37 | 0.98581 | -0.27166 | 0.0026675 | 0.00066854
38 | 0.98588 | -0.27043 | 0 | 0
39 | 0.98881 | -0.21341 | 0 | 0
40 | 0.97949 | -0.3942 | 0.0014781 | 0.00037045
41 | 0.98046 | -0.37571 | 0.0025203 | 0.00063164
42 | 0.98482 | -0.29099 | 0.0045429 | 0.0011386
43 | 0.98609 | -0.26637 | 0 | 0
44 | 0.98536 | -0.28053 | 0.0042227 | 0.0010583
45 | 0.99069 | -0.17719 | 0.0018833 | 0.00047201
46 | 0.98757 | -0.23747 | 0.0029623 | 0.00074242
47 | 0.999 | -0.019237 | 0.0093194 | 0.0023357
48 | 0.99895 | -0.020219 | 0.0032348 | 0.0008107
49 | 0.99923 | -0.014804 | 0.002603 | 0.00065237
50 | 0.99954 | -0.008849 | 0.011636 | 0.0029164
51 | 1 | 0 | -0.42497 | -0.10838
52 | 0.99277 | -0.13769 | 0.0022821 | 0.00057195
53 | 0.99282 | -0.13668 | 0 | 0
54 | 0.99807 | -0.036439 | 0.0036349 | 0.00091099
55 | 0.99926 | -0.014033 | 0.0019484 | 0.00048832
56 | 0.97356 | -0.51054 | 0.025037 | 0.006275
57 | 0.97342 | -0.51343 | 0.011983 | 0.0030031
58 | 0.97393 | -0.50322 | 0 | 0
59 | 0.99289 | -0.13531 | 0.003516 | 0.00088119
60 | 0.97184 | -0.54486 | 0.00012424 | 3.1138e-05
61 | 0.97185 | -0.54452 | 0.00029386 | 7.3649e-05
62 | 0.97186 | -0.54437 | 0 | 0
63 | 0.97188 | -0.54403 | 0.00034416 | 8.6256e-05
64 | 0.98009 | -0.3828 | 0.0068048 | 0.0017055
65 | 0.98016 | -0.38146 | 0.0015951 | 0.00039977
66 | 0.98136 | -0.35757 | 0.017387 | 0.0043575
67 | 0.98222 | -0.34083 | 0.0050569 | 0.0012674
68 | 0.9806 | -0.37238 | 0.0029458 | 0.00073828
69 | 0.98287 | -0.32815 | 0.0036762 | 0.00092134
70 | 0.97965 | -0.39095 | 0.0051424 | 0.0012888
71 | 0.98415 | -0.30331 | 0.0037716 | 0.00094526
72 | 0.97851 | -0.4131 | 0 | 0
73 | 0.98809 | -0.22717 | 0.0075738 | 0.0018982
74 | 0.9785 | -0.41343 | 0 | 0
75 | 0.9763 | -0.45641 | 0.0021867 | 0.00054804
76 | 0.97845 | -0.41433 | 0.0017031 | 0.00042683
77 | 0.97564 | -0.46936 | 0.0074227 | 0.0018603
78 | 0.97513 | -0.47955 | 0.004043 | 0.0010133
79 | 0.97502 | -0.48165 | 0.0013373 | 0.00033516
80 | 0.97471 | -0.48783 | 0.0011281 | 0.00028273
81 | 0.9899 | -0.19243 | 0 | 0
82 | 0.99175 | -0.15701 | 0.0018253 | 0.00045746
83 | 0.99336 | -0.12631 | 0 | 0
84 | 0.99191 | -0.15414 | 0.0021118 | 0.00052926
85 | 0.99478 | -0.09915 | 0.0040279 | 0.0010095
86 | 0.99302 | -0.13271 | 0.0028568 | 0.00071597
87 | 0.9894 | -0.20213 | 0.0019951 | 0.00050003
88 | 0.99068 | -0.17797 | 0.0010413 | 0.00026097
89 | 0.99513 | -0.092348 | 0.0039506 | 0.00099011
90 | 0.99295 | -0.13412 | 0.0037532 | 0.00094064
91 | 0.98918 | -0.20636 | 0.0022597 | 0.00056632
92 | 0.9899 | -0.19311 | 0.0013635 | 0.00034173
93 | 0.99692 | -0.058295 | 0.0033754 | 0.00084596
94 | 0.98883 | -0.2132 | 0.0034684 | 0.00086927
95 | 0.98848 | -0.22069 | 0.0016134 | 0.00040436
96 | 0.98853 | -0.21967 | 0.001421 | 0.00035613
97 | 0.98819 | -0.22623 | 0.0012522 | 0.00031382
98 | 0.98888 | -0.2129 | 0.0021835 | 0.00054724
99 | 0.98811 | -0.22792 | 0.00046125 | 0.0001156
100 | 0.9892 | -0.20673 | 0.0062993 | 0.0015788
101 | 0.98798 | -0.23046 | 0.0012913 | 0.00032363
102 | 0.98926 | -0.2055 | 0.001469 | 0.00036816
103 | 0.98794 | -0.23121 | 0.0011929 | 0.00029897
104 | 0.97448 | -0.49236 | 0.0016694 | 0.00041839
105 | 0.97241 | -0.53316 | 0.00066272 | 0.00016609
106 | 0.97233 | -0.53477 | 0.0010662 | 0.00026721
107 | 0.97452 | -0.49158 | 0.0011697 | 0.00029314
108 | 0.9745 | -0.49191 | 0.0014884 | 0.00037302
109 | 0.97435 | -0.49494 | 0.0013071 | 0.0003276
110 | 0.9719 | -0.54347 | 0.00034083 | 8.5421e-05
111 | 0.99515 | -0.092199 | 0.0027066 | 0.00067835
112 | 0.99521 | -0.091064 | 0.0030813 | 0.00077224
113 | 0.99534 | -0.088662 | 0.0028733 | 0.00072011
114 | 0.9955 | -0.085497 | 0.0021994 | 0.00055122
115 | 0.9858 | -0.27187 | 0.0019671 | 0.00049299
116 | 0.98586 | -0.27085 | 0.004048 | 0.0010145
117 | 0.99619 | -0.072256 | 0 | 0
118 | 0.99534 | -0.088528 | 0.0018389 | 0.00046088
119 | 0.98586 | -0.27074 | 0.002734 | 0.00068522
120 | 0.98492 | -0.28902 | 0.0034759 | 0.00087114
121 | 0.98689 | -0.25073 | 0.0027351 | 0.00068548
122 | 0.99653 | -0.065779 | 0.0008965 | 0.00022468
123 | 0.99635 | -0.069218 | 0.0016436 | 0.00041194
124 | 0.99518 | -0.091332 | 0.0016603 | 0.00041612
125 | 0.99522 | -0.090922 | 0.0015789 | 0.00039571
126 | 0.99521 | -0.091077 | 0.0014971 | 0.00037521
127 | 0.99521 | -0.091126 | 0.0014642 | 0.00036696
128 | 0.99515 | -0.092203 | 0.0010831 | 0.00027144
129 | 0.99427 | -0.10877 | 0.0032325 | 0.00081014
130 | 0.98762 | -0.23743 | 0.0015668 | 0.00039267
131 | 0.98773 | -0.23521 | 0.0015212 | 0.00038124
132 | 0.9876 | -0.23775 | 0.001813 | 0.00045438
133 | 0.98785 | -0.23288 | 0.0038915 | 0.0009753
134 | 0.98748 | -0.24008 | 0.0019191 | 0.00048097
135 | 0.98701 | -0.24921 | 0 | 0
136 | 0.98644 | -0.2604 | 0.0042131 | 0.0010559
137 | 0.98742 | -0.24035 | 0.0028751 | 0.00072056
138 | 0.99514 | -0.092409 | 0.0015231 | 0.00038172
139 | 0.98844 | -0.22085 | 0.010804 | 0.0027076
140 | 0.97423 | -0.49725 | 0.0011861 | 0.00029727
141 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0058499 | -0.0014573 | 0.0058504 | 0.0014574 | 5.1338e-07 | 1.1624e-07 | 0.0089463 | 0.0089462 | 0.0089463 | 0.97265 | -0.52861 | 0.97274 | -0.52676 | 2.4578
1 | 0.0039689 | 0.00098591 | -0.0039663 | -0.00098655 | 2.5138e-06 | -6.4845e-07 | 0.0060686 | 0.0060694 | 0.0060694 | 0.97265 | -0.52861 | 0.97198 | -0.542 | 1.6674
2 | -0.0058504 | -0.0014574 | 0.0058525 | 0.0014579 | 2.0857e-06 | 4.718e-07 | 0.0089462 | 0.0089459 | 0.0089462 | 0.97274 | -0.52676 | 0.97312 | -0.51925 | 2.4578
3 | 0.003475 | 0.00086341 | -0.0034749 | -0.00086345 | 7.9914e-08 | -4.2274e-08 | 0.0053172 | 0.0053172 | 0.0053172 | 0.97198 | -0.542 | 0.97195 | -0.54248 | 1.4608
4 | 0.0018949 | 0.00047369 | -0.0018946 | -0.00047483 | 3.4445e-07 | -1.1387e-06 | 0.0028971 | 0.0028976 | 0.0028976 | 0.97312 | -0.51925 | 0.97293 | -0.52307 | 0.79604
5 | -0.0077474 | -0.0019316 | 0.0077544 | 0.0019344 | 7.0108e-06 | 2.8292e-06 | 0.011843 | 0.011842 | 0.011843 | 0.97312 | -0.51925 | 0.97408 | -0.50019 | 3.2536
6 | 0.0011032 | 0.00027283 | -0.0011031 | -0.0002734 | 5.1701e-08 | -5.6677e-07 | 0.0016876 | 0.0016878 | 0.0016878 | 0.97195 | -0.54248 | 0.9719 | -0.54347 | 0.46369
7 | 0.0023717 | 0.00059062 | -0.0023716 | -0.0005908 | 9.543e-08 | -1.7831e-07 | 0.0036296 | 0.0036297 | 0.0036297 | 0.97195 | -0.54248 | 0.97191 | -0.54333 | 0.99717
8 | -0.0093457 | -0.0023333 | 0.0093463 | 0.0023335 | 5.4701e-07 | 2.6095e-07 | 0.014273 | 0.014273 | 0.014273 | 0.97408 | -0.50019 | 0.97415 | -0.49896 | 3.9213
9 | -0.0015272 | -0.00038168 | 0.0015276 | 0.00037941 | 4.2112e-07 | -2.2757e-06 | 0.0023384 | 0.0023375 | 0.0023384 | 0.97162 | -0.54914 | 0.97191 | -0.54333 | 0.64242
10 | 0.0015272 | 0.00038168 | -0.001527 | -0.00038269 | 1.8713e-07 | -1.0101e-06 | 0.0023384 | 0.0023388 | 0.0023388 | 0.97162 | -0.54914 | 0.97149 | -0.55172 | 0.64254
11 | 0.00084405 | 0.00021139 | -0.00084404 | -0.00021154 | 7.5044e-09 | -1.4371e-07 | 0.0012922 | 0.0012923 | 0.0012923 | 0.97191 | -0.54333 | 0.9719 | -0.54352 | 0.35502
12 | -0.010739 | -0.0026827 | 0.01074 | 0.0026831 | 8.6847e-07 | 4.4863e-07 | 0.016401 | 0.016401 | 0.016401 | 0.97415 | -0.49896 | 0.97423 | -0.49725 | 4.5058
13 | -0.0051838 | -0.0012992 | 0.0051839 | 0.0012992 | 1.138e-07 | 1.3063e-08 | 0.0079344 | 0.0079344 | 0.0079344 | 0.97216 | -0.53813 | 0.97218 | -0.53767 | 2.1798
14 | -0.0059912 | -0.0015015 | 0.005992 | 0.0015017 | 8.2765e-07 | 2.0421e-07 | 0.0091701 | 0.00917 | 0.0091701 | 0.97218 | -0.53767 | 0.97233 | -0.53477 | 2.5193
15 | -0.011646 | -0.0029194 | 0.011646 | 0.0029195 | 2.086e-07 | 1.1174e-07 | 0.017814 | 0.017814 | 0.017814 | 0.97279 | -0.52568 | 0.97281 | -0.5253 | 4.8939
16 | 0.010568 | 0.0026494 | -0.010566 | -0.0026485 | 1.7166e-06 | 8.8119e-07 | 0.016166 | 0.016166 | 0.016166 | 0.97279 | -0.52568 | 0.97261 | -0.52909 | 4.4412
17 | -0.014342 | -0.0035953 | 0.014343 | 0.0035959 | 9.593e-07 | 5.4796e-07 | 0.021938 | 0.021938 | 0.021938 | 0.97281 | -0.5253 | 0.97288 | -0.5239 | 6.027
18 | 0.0097912 | 0.0024542 | -0.0097911 | -0.0024542 | 7.3557e-08 | 3.6228e-08 | 0.01498 | 0.01498 | 0.01498 | 0.97261 | -0.52909 | 0.97261 | -0.52925 | 4.1153
19 | -0.015222 | -0.0038161 | 0.015225 | 0.0038181 | 3.5084e-06 | 2.031e-06 | 0.023282 | 0.023282 | 0.023282 | 0.97288 | -0.5239 | 0.97312 | -0.51906 | 6.3962
20 | 0.0089049 | 0.0022321 | -0.0089047 | -0.002232 | 1.9177e-07 | 8.8541e-08 | 0.013624 | 0.013624 | 0.013624 | 0.97261 | -0.52925 | 0.97258 | -0.5297 | 3.7428
21 | -0.016021 | -0.0040174 | 0.016025 | 0.0040201 | 4.5489e-06 | 2.6601e-06 | 0.024498 | 0.024498 | 0.024498 | 0.97312 | -0.51906 | 0.97342 | -0.51311 | 6.7303
22 | 0.0082586 | 0.0020701 | -0.0082576 | -0.0020696 | 1.032e-06 | 4.4658e-07 | 0.012635 | 0.012636 | 0.012636 | 0.97258 | -0.5297 | 0.97245 | -0.53232 | 3.4713
23 | -0.017391 | -0.0043625 | 0.017396 | 0.0043652 | 4.6001e-06 | 2.7283e-06 | 0.026586 | 0.026586 | 0.026586 | 0.97342 | -0.51311 | 0.9737 | -0.50756 | 7.3039
24 | 0.0077218 | 0.0019353 | -0.0077215 | -0.0019352 | 3.1005e-07 | 1.2496e-07 | 0.011816 | 0.011816 | 0.011816 | 0.97245 | -0.53232 | 0.97241 | -0.53316 | 3.2461
25 | -0.019474 | -0.0048861 | 0.01948 | 0.0048895 | 5.7774e-06 | 3.4811e-06 | 0.029762 | 0.029762 | 0.029762 | 0.9737 | -0.50756 | 0.97402 | -0.50134 | 8.1764
26 | -0.020942 | -0.005256 | 0.020951 | 0.0052615 | 8.9701e-06 | 5.4499e-06 | 0.031996 | 0.031996 | 0.031996 | 0.97402 | -0.50134 | 0.97448 | -0.49236 | 8.7902
27 | 0.055883 | 0.01416 | -0.055851 | -0.014139 | 3.2149e-05 | 2.0424e-05 | 0.084624 | 0.084624 | 0.084624 | 0.98328 | -0.32048 | 0.98267 | -0.33246 | 23.2484
28 | -0.13207 | -0.033254 | 0.13254 | 0.033552 | 0.00046907 | 0.00029861 | 0.19992 | 0.19992 | 0.19992 | 0.98328 | -0.32048 | 0.9871 | -0.24648 | 27.4612
29 | 0.044905 | 0.01139 | -0.044777 | -0.011308 | 0.00012848 | 8.1293e-05 | 0.068047 | 0.068048 | 0.068048 | 0.98267 | -0.33246 | 0.9796 | -0.39216 | 18.6944
30 | 0.010946 | 0.0027497 | -0.010937 | -0.0027455 | 8.1603e-06 | 4.2202e-06 | 0.016577 | 0.016577 | 0.016577 | 0.98267 | -0.33246 | 0.98187 | -0.3481 | 4.5541
31 | -0.13254 | -0.033552 | 0.13263 | 0.033612 | 9.4307e-05 | 6.0035e-05 | 0.19992 | 0.19992 | 0.19992 | 0.9871 | -0.24648 | 0.98786 | -0.23167 | 27.4611
32 | 0.0031191 | 0.00078133 | -0.0031188 | -0.00078156 | 2.7095e-07 | -2.3177e-07 | 0.0047378 | 0.004738 | 0.004738 | 0.9796 | -0.39216 | 0.9795 | -0.39398 | 1.3016
33 | 0.041658 | 0.010527 | -0.041506 | -0.010431 | 0.00015148 | 9.568e-05 | 0.06331 | 0.06331 | 0.06331 | 0.9796 | -0.39216 | 0.97571 | -0.4683 | 17.393
34 | 0.010937 | 0.0027455 | -0.010925 | -0.0027392 | 1.2137e-05 | 6.28e-06 | 0.016577 | 0.016578 | 0.016578 | 0.98187 | -0.3481 | 0.98068 | -0.37139 | 4.5543
35 | -0.13492 | -0.034185 | 0.13503 | 0.03426 | 0.00011844 | 7.541e-05 | 0.20336 | 0.20336 | 0.20336 | 0.98786 | -0.23167 | 0.98881 | -0.21341 | 27.9336
36 | 0.0014781 | 0.00037036 | -0.0014781 | -0.00037045 | 1.5249e-08 | -9.1746e-08 | 0.0022455 | 0.0022455 | 0.0022455 | 0.9795 | -0.39398 | 0.97949 | -0.3942 | 0.6169
37 | 0.037096 | 0.009326 | -0.037035 | -0.0092871 | 6.1749e-05 | 3.8878e-05 | 0.056585 | 0.056585 | 0.056585 | 0.97571 | -0.4683 | 0.97393 | -0.50322 | 15.5453
38 | 0.010925 | 0.0027392 | -0.010923 | -0.002738 | 2.25e-06 | 1.1646e-06 | 0.016578 | 0.016578 | 0.016578 | 0.98068 | -0.37139 | 0.98046 | -0.37571 | 4.5543
39 | -0.0024239 | -0.00060715 | 0.0024241 | 0.00060683 | 1.6948e-07 | -3.2007e-07 | 0.0036629 | 0.0036627 | 0.0036629 | 0.98467 | -0.29406 | 0.98474 | -0.29259 | 1.0063
40 | 0.0024239 | 0.00060715 | -0.0024238 | -0.00060745 | 1.5962e-07 | -3.0134e-07 | 0.0036629 | 0.003663 | 0.003663 | 0.98467 | -0.29406 | 0.9846 | -0.29544 | 1.0063
41 | -0.0070217 | -0.0017591 | 0.0070222 | 0.0017593 | 5.3572e-07 | 1.814e-07 | 0.01061 | 0.01061 | 0.01061 | 0.98474 | -0.29259 | 0.98482 | -0.29099 | 2.9148
42 | -0.0026675 | -0.00066854 | 0.0026677 | 0.00066832 | 1.5585e-07 | -2.2713e-07 | 0.0040264 | 0.0040263 | 0.0040264 | 0.98581 | -0.27166 | 0.98588 | -0.27043 | 1.1062
43 | -0.021948 | -0.0055052 | 0.021952 | 0.0055078 | 4.246e-06 | 2.5858e-06 | 0.033128 | 0.033128 | 0.033128 | 0.98588 | -0.27043 | 0.98609 | -0.26637 | 9.1011
44 | 0.01928 | 0.0048369 | -0.019271 | -0.0048313 | 9.28e-06 | 5.5668e-06 | 0.029102 | 0.029102 | 0.029102 | 0.98588 | -0.27043 | 0.98536 | -0.28053 | 7.9951
45 | -0.1744 | -0.044166 | 0.1747 | 0.04436 | 0.00030397 | 0.00019393 | 0.26261 | 0.26261 | 0.26261 | 0.98881 | -0.21341 | 0.99069 | -0.17719 | 36.0727
46 | 0.039365 | 0.0099058 | -0.03932 | -0.0098774 | 4.5203e-05 | 2.849e-05 | 0.059253 | 0.059253 | 0.059253 | 0.98881 | -0.21341 | 0.98757 | -0.23747 | 16.2784
47 | 0.0084027 | 0.0021064 | -0.0084004 | -0.0021054 | 2.3004e-06 | 9.9673e-07 | 0.012753 | 0.012753 | 0.012753 | 0.98046 | -0.37571 | 0.98016 | -0.38146 | 3.5035
48 | -0.011565 | -0.0028978 | 0.011566 | 0.0028984 | 1.083e-06 | 5.7275e-07 | 0.017474 | 0.017474 | 0.017474 | 0.98482 | -0.29099 | 0.98492 | -0.28902 | 4.8006
49 | 0.0087511 | 0.0021932 | -0.0087493 | -0.0021924 | 1.819e-06 | 8.0942e-07 | 0.013205 | 0.013206 | 0.013206 | 0.98609 | -0.26637 | 0.98586 | -0.27074 | 3.6279
50 | -0.030703 | -0.0077011 | 0.030726 | 0.0077154 | 2.2911e-05 | 1.43e-05 | 0.046334 | 0.046333 | 0.046334 | 0.98609 | -0.26637 | 0.98689 | -0.25073 | 12.729
51 | 0.015048 | 0.0037731 | -0.015042 | -0.0037696 | 6.0858e-06 | 3.4948e-06 | 0.022725 | 0.022725 | 0.022725 | 0.98536 | -0.28053 | 0.98492 | -0.28902 | 6.2432
52 | -0.17659 | -0.044832 | 0.17717 | 0.045204 | 0.00058338 | 0.00037222 | 0.26544 | 0.26544 | 0.26544 | 0.99069 | -0.17719 | 0.99427 | -0.10877 | 36.4613
53 | 0.036358 | 0.0091349 | -0.036353 | -0.0091318 | 4.9899e-06 | 3.1368e-06 | 0.05479 | 0.05479 | 0.05479 | 0.98757 | -0.23747 | 0.98742 | -0.24035 | 15.0522
54 | 0.0032349 | 0.00081057 | -0.0032348 | -0.0008107 | 1.5143e-07 | -1.308e-07 | 0.0048183 | 0.0048184 | 0.0048184 | 0.999 | -0.019237 | 0.99895 | -0.020219 | 1.3237
55 | -0.012554 | -0.0031462 | 0.012557 | 0.0031477 | 2.6516e-06 | 1.4322e-06 | 0.0187 | 0.0187 | 0.0187 | 0.999 | -0.019237 | 0.99923 | -0.014804 | 5.1373
56 | -0.01516 | -0.0038 | 0.015164 | 0.0038025 | 4.3023e-06 | 2.4585e-06 | 0.022576 | 0.022576 | 0.022576 | 0.99923 | -0.014804 | 0.99954 | -0.008849 | 6.2021
57 | -0.026801 | -0.0067189 | 0.026812 | 0.0067259 | 1.1306e-05 | 6.9873e-06 | 0.039899 | 0.039899 | 0.039899 | 0.99954 | -0.008849 | 1 | 0 | 10.9612
58 | 0.18906 | 0.048457 | -0.18873 | -0.048244 | 0.00033332 | 0.00021274 | 0.2817 | 0.2817 | 0.2817 | 1 | 0 | 0.99807 | -0.036439 | 38.6955
59 | 0.20745 | 0.053201 | -0.20731 | -0.053111 | 0.00014108 | 9.0082e-05 | 0.30912 | 0.30912 | 0.30912 | 1 | 0 | 0.99926 | -0.014033 | 42.4619
60 | -0.0022821 | -0.00057195 | 0.0022822 | 0.0005717 | 1.0903e-07 | -2.5157e-07 | 0.0034205 | 0.0034204 | 0.0034205 | 0.99277 | -0.13769 | 0.99282 | -0.13668 | 0.93971
61 | -0.0022822 | -0.0005717 | 0.0022824 | 0.00057135 | 1.4901e-07 | -3.439e-07 | 0.0034204 | 0.0034203 | 0.0034204 | 0.99282 | -0.13668 | 0.99289 | -0.13531 | 0.93968
62 | 0.18509 | 0.047333 | -0.18489 | -0.047208 | 0.00019552 | 0.00012478 | 0.27628 | 0.27628 | 0.27628 | 0.99807 | -0.036439 | 0.99692 | -0.058295 | 37.9511
63 | 0.20536 | 0.052622 | -0.20485 | -0.052294 | 0.00051363 | 0.00032796 | 0.30622 | 0.30622 | 0.30622 | 0.99926 | -0.014033 | 0.99653 | -0.065779 | 42.0634
64 | 0.011984 | 0.003004 | -0.011983 | -0.0030031 | 1.6527e-06 | 8.9441e-07 | 0.018317 | 0.018317 | 0.018317 | 0.97356 | -0.51054 | 0.97342 | -0.51343 | 5.0322
65 | -0.037022 | -0.009279 | 0.037035 | 0.0092871 | 1.2904e-05 | 8.1248e-06 | 0.056585 | 0.056585 | 0.056585 | 0.97356 | -0.51054 | 0.97393 | -0.50322 | 15.5453
66 | -0.0057983 | -0.0014525 | 0.0057987 | 0.0014526 | 3.2897e-07 | 6.0272e-08 | 0.0086896 | 0.0086895 | 0.0086896 | 0.99289 | -0.13531 | 0.99295 | -0.13412 | 2.3872
67 | -0.00012424 | -3.1138e-05 | 0.00012424 | 2.9302e-05 | 2.0049e-09 | -1.8357e-06 | 0.00019023 | 0.00018959 | 0.00019023 | 0.97184 | -0.54486 | 0.97185 | -0.54452 | 0.052261
68 | -0.00041811 | -0.00010295 | 0.00041811 | 0.00010273 | 2.7656e-09 | -2.2171e-07 | 0.00063951 | 0.00063943 | 0.00063951 | 0.97185 | -0.54452 | 0.97186 | -0.54437 | 0.17569
69 | -0.00041811 | -0.00010273 | 0.00041812 | 0.00010219 | 6.6699e-09 | -5.3494e-07 | 0.00063943 | 0.00063924 | 0.00063943 | 0.97186 | -0.54437 | 0.97188 | -0.54403 | 0.17567
70 | -0.00076228 | -0.00018845 | 0.0007623 | 0.00018797 | 2.0099e-08 | -4.756e-07 | 0.0011662 | 0.001166 | 0.0011662 | 0.97188 | -0.54403 | 0.9719 | -0.54347 | 0.32038
71 | -0.0068048 | -0.0017055 | 0.0068053 | 0.0017056 | 4.349e-07 | 1.414e-07 | 0.010331 | 0.010331 | 0.010331 | 0.98009 | -0.3828 | 0.98016 | -0.38146 | 2.8383
72 | -0.082164 | -0.020728 | 0.082229 | 0.02077 | 6.592e-05 | 4.2046e-05 | 0.12463 | 0.12463 | 0.12463 | 0.98136 | -0.35757 | 0.98222 | -0.34083 | 34.2396
73 | 0.064777 | 0.016371 | -0.064731 | -0.016342 | 4.5978e-05 | 2.9265e-05 | 0.098269 | 0.098269 | 0.098269 | 0.98136 | -0.35757 | 0.9806 | -0.37238 | 26.997
74 | -0.087286 | -0.022038 | 0.087339 | 0.022072 | 5.3025e-05 | 3.3834e-05 | 0.13229 | 0.13229 | 0.13229 | 0.98222 | -0.34083 | 0.98287 | -0.32815 | 36.3442
75 | 0.061785 | 0.015603 | -0.06173 | -0.015568 | 5.4905e-05 | 3.4929e-05 | 0.093799 | 0.093799 | 0.093799 | 0.9806 | -0.37238 | 0.97965 | -0.39095 | 25.7689
76 | -0.091016 | -0.022993 | 0.091124 | 0.023062 | 0.00010852 | 6.9262e-05 | 0.13786 | 0.13786 | 0.13786 | 0.98287 | -0.32815 | 0.98415 | -0.30331 | 37.8732
77 | 0.056588 | 0.01428 | -0.056528 | -0.014241 | 5.9957e-05 | 3.81e-05 | 0.085988 | 0.085988 | 0.085988 | 0.97965 | -0.39095 | 0.97851 | -0.4131 | 23.6231
78 | -0.094896 | -0.024008 | 0.095244 | 0.02423 | 0.00034811 | 0.00022221 | 0.14356 | 0.14356 | 0.14356 | 0.98415 | -0.30331 | 0.98809 | -0.22717 | 39.4399
79 | 0.0017032 | 0.0004264 | -0.0017032 | -0.00042651 | 2.7087e-08 | -1.1794e-07 | 0.0025899 | 0.0025899 | 0.0025899 | 0.97851 | -0.4131 | 0.9785 | -0.41343 | 0.71151
80 | 0.054825 | 0.013815 | -0.054711 | -0.013743 | 0.00011335 | 7.1997e-05 | 0.083398 | 0.083398 | 0.083398 | 0.97851 | -0.4131 | 0.9763 | -0.45641 | 22.9117
81 | -0.10282 | -0.026128 | 0.10299 | 0.026238 | 0.00017227 | 0.00011001 | 0.15497 | 0.15497 | 0.15497 | 0.98809 | -0.22717 | 0.9899 | -0.19243 | 42.5732
82 | 0.0017032 | 0.00042651 | -0.0017031 | -0.00042683 | 7.3401e-08 | -3.1954e-07 | 0.0025899 | 0.00259 | 0.00259 | 0.9785 | -0.41343 | 0.97845 | -0.41433 | 0.71155
83 | 0.031426 | 0.0079032 | -0.031406 | -0.0078911 | 1.9423e-05 | 1.2148e-05 | 0.047907 | 0.047907 | 0.047907 | 0.9763 | -0.45641 | 0.97564 | -0.46936 | 13.1612
84 | 0.021099 | 0.0052918 | -0.021076 | -0.0052777 | 2.3249e-05 | 1.4131e-05 | 0.032159 | 0.032159 | 0.032159 | 0.9763 | -0.45641 | 0.97513 | -0.47955 | 8.8349
85 | 0.023984 | 0.0060308 | -0.023969 | -0.0060221 | 1.4067e-05 | 8.6534e-06 | 0.036586 | 0.036586 | 0.036586 | 0.97564 | -0.46936 | 0.97502 | -0.48165 | 10.0511
86 | 0.017033 | 0.0042644 | -0.017026 | -0.0042604 | 6.7046e-06 | 3.9609e-06 | 0.02599 | 0.02599 | 0.02599 | 0.97513 | -0.47955 | 0.97471 | -0.48783 | 7.14
87 | 0.022632 | 0.005687 | -0.022621 | -0.0056799 | 1.1569e-05 | 7.0821e-06 | 0.034545 | 0.034545 | 0.034545 | 0.97502 | -0.48165 | 0.97448 | -0.49236 | 9.4905
88 | 0.015898 | 0.0039777 | -0.015895 | -0.003976 | 2.8357e-06 | 1.6548e-06 | 0.024268 | 0.024268 | 0.024268 | 0.97471 | -0.48783 | 0.97452 | -0.49158 | 6.6669
89 | 0.018547 | 0.004655 | -0.018539 | -0.0046498 | 8.5776e-06 | 5.1116e-06 | 0.027883 | 0.027883 | 0.027883 | 0.9899 | -0.19243 | 0.9894 | -0.20213 | 7.6601
90 | -0.12154 | -0.030893 | 0.12174 | 0.031026 | 0.00020772 | 0.00013273 | 0.18285 | 0.18285 | 0.18285 | 0.9899 | -0.19243 | 0.99175 | -0.15701 | 50.2332
91 | -0.12357 | -0.031483 | 0.12375 | 0.0316 | 0.00018331 | 0.00011714 | 0.18559 | 0.18559 | 0.18559 | 0.99175 | -0.15701 | 0.99336 | -0.12631 | 50.9856
92 | 0.036791 | 0.0092788 | -0.036742 | -0.009248 | 4.8942e-05 | 3.0768e-05 | 0.055133 | 0.055133 | 0.055133 | 0.99336 | -0.12631 | 0.99191 | -0.15414 | 15.1464
93 | -0.17296 | -0.043991 | 0.17318 | 0.044135 | 0.00022669 | 0.00014462 | 0.25931 | 0.25931 | 0.25931 | 0.99336 | -0.12631 | 0.99478 | -0.09915 | 35.6201
94 | 0.012413 | 0.0031116 | -0.012409 | -0.0031095 | 3.7805e-06 | 2.0422e-06 | 0.018595 | 0.018595 | 0.018595 | 0.99336 | -0.12631 | 0.99302 | -0.13271 | 5.1084
95 | 0.03463 | 0.0087187 | -0.034591 | -0.008694 | 3.9392e-05 | 2.471e-05 | 0.051965 | 0.051965 | 0.051965 | 0.99191 | -0.15414 | 0.99068 | -0.17797 | 14.2761
96 | -0.17721 | -0.045145 | 0.17727 | 0.045182 | 5.8173e-05 | 3.7116e-05 | 0.26534 | 0.26534 | 0.26534 | 0.99478 | -0.09915 | 0.99513 | -0.092348 | 36.4477
97 | 0.0095525 | 0.0023935 | -0.0095519 | -0.0023932 | 6.4335e-07 | 3.0343e-07 | 0.014314 | 0.014314 | 0.014314 | 0.99302 | -0.13271 | 0.99295 | -0.13412 | 3.9324
98 | 0.016544 | 0.0041498 | -0.01654 | -0.0041479 | 3.3311e-06 | 1.9477e-06 | 0.024882 | 0.024882 | 0.024882 | 0.9894 | -0.20213 | 0.98918 | -0.20636 | 6.8358
99 | 0.03355 | 0.008433 | -0.033526 | -0.0084179 | 2.4235e-05 | 1.5183e-05 | 0.050401 | 0.050401 | 0.050401 | 0.99068 | -0.17797 | 0.9899 | -0.19311 | 13.8465
100 | -0.18122 | -0.046172 | 0.18152 | 0.046362 | 0.00029828 | 0.00019034 | 0.27125 | 0.27125 | 0.27125 | 0.99513 | -0.092348 | 0.99692 | -0.058295 | 37.2591
101 | 0.014281 | 0.0035815 | -0.014276 | -0.0035789 | 4.658e-06 | 2.6358e-06 | 0.021483 | 0.021483 | 0.021483 | 0.98918 | -0.20636 | 0.98883 | -0.2132 | 5.902
102 | 0.032162 | 0.0080761 | -0.032143 | -0.0080643 | 1.8998e-05 | 1.188e-05 | 0.048351 | 0.048352 | 0.048352 | 0.9899 | -0.19311 | 0.98926 | -0.2055 | 13.2834
103 | 0.010807 | 0.0027096 | -0.010804 | -0.0027076 | 3.9347e-06 | 2.0096e-06 | 0.016264 | 0.016264 | 0.016264 | 0.98883 | -0.2132 | 0.98844 | -0.22085 | 4.4681
104 | -0.020753 | -0.0052035 | 0.020754 | 0.0052041 | 1.014e-06 | 6.1344e-07 | 0.031242 | 0.031242 | 0.031242 | 0.98848 | -0.22069 | 0.98853 | -0.21967 | 8.5829
105 | 0.01914 | 0.0047991 | -0.019135 | -0.0047961 | 5.0524e-06 | 3.0256e-06 | 0.028813 | 0.028813 | 0.028813 | 0.98848 | -0.22069 | 0.98819 | -0.22623 | 7.9156
106 | -0.022175 | -0.0055602 | 0.022182 | 0.0055646 | 7.1566e-06 | 4.3606e-06 | 0.033381 | 0.03338 | 0.033381 | 0.98853 | -0.21967 | 0.98888 | -0.2129 | 9.1705
107 | 0.017882 | 0.0044822 | -0.017881 | -0.0044814 | 1.4369e-06 | 8.5192e-07 | 0.026927 | 0.026927 | 0.026927 | 0.98819 | -0.22623 | 0.98811 | -0.22792 | 7.3976
108 | -0.024366 | -0.0061118 | 0.024373 | 0.0061162 | 7.1689e-06 | 4.4056e-06 | 0.036666 | 0.036666 | 0.036666 | 0.98888 | -0.2129 | 0.9892 | -0.20673 | 10.0731
109 | 0.01742 | 0.0043658 | -0.017418 | -0.0043645 | 2.1094e-06 | 1.2453e-06 | 0.026233 | 0.026233 | 0.026233 | 0.98811 | -0.22792 | 0.98798 | -0.23046 | 7.2068
110 | -0.030672 | -0.007695 | 0.030674 | 0.0076961 | 1.8015e-06 | 1.124e-06 | 0.046142 | 0.046142 | 0.046142 | 0.9892 | -0.20673 | 0.98926 | -0.2055 | 12.6764
111 | 0.016126 | 0.0040409 | -0.016126 | -0.0040406 | 5.7155e-07 | 3.3271e-07 | 0.024288 | 0.024288 | 0.024288 | 0.98798 | -0.23046 | 0.98794 | -0.23121 | 6.6725
112 | 0.014933 | 0.0037416 | -0.014932 | -0.0037409 | 1.186e-06 | 6.7898e-07 | 0.022491 | 0.022491 | 0.022491 | 0.98794 | -0.23121 | 0.98785 | -0.23288 | 6.1789
113 | 0.0070588 | 0.0017691 | -0.0070582 | -0.0017689 | 5.3891e-07 | 1.9212e-07 | 0.010802 | 0.010802 | 0.010802 | 0.97241 | -0.53316 | 0.97233 | -0.53477 | 2.9675
114 | 0.014725 | 0.0036829 | -0.014725 | -0.0036828 | 2.3653e-07 | 1.3583e-07 | 0.022482 | 0.022482 | 0.022482 | 0.97452 | -0.49158 | 0.9745 | -0.49191 | 6.1763
115 | 0.013237 | 0.0033097 | -0.013235 | -0.0033087 | 1.9017e-06 | 1.0624e-06 | 0.020209 | 0.020209 | 0.020209 | 0.9745 | -0.49191 | 0.97435 | -0.49494 | 5.5519
116 | 0.011928 | 0.0029811 | -0.011926 | -0.0029804 | 1.3146e-06 | 7.0972e-07 | 0.018213 | 0.018213 | 0.018213 | 0.97435 | -0.49494 | 0.97423 | -0.49725 | 5.0035
117 | -0.0027066 | -0.00067835 | 0.0027068 | 0.00067813 | 1.4634e-07 | -2.1592e-07 | 0.0040471 | 0.004047 | 0.0040471 | 0.99515 | -0.092199 | 0.99521 | -0.091064 | 1.1118
118 | -0.005788 | -0.0014504 | 0.0057887 | 0.0014505 | 6.6225e-07 | 1.1739e-07 | 0.008654 | 0.0086539 | 0.008654 | 0.99521 | -0.091064 | 0.99534 | -0.088662 | 2.3775
119 | -0.008662 | -0.0021706 | 0.0086633 | 0.0021712 | 1.3061e-06 | 5.659e-07 | 0.012949 | 0.012949 | 0.012949 | 0.99534 | -0.088662 | 0.9955 | -0.085497 | 3.5575
120 | -0.01985 | -0.0049748 | 0.019863 | 0.0049824 | 1.2529e-05 | 7.5247e-06 | 0.029671 | 0.029671 | 0.029671 | 0.9955 | -0.085497 | 0.99619 | -0.072256 | 8.1513
121 | 0.0089876 | 0.0022525 | -0.0089863 | -0.0022519 | 1.2977e-06 | 5.8125e-07 | 0.013434 | 0.013434 | 0.013434 | 0.9955 | -0.085497 | 0.99534 | -0.088528 | 3.6907
122 | -0.0019671 | -0.00049299 | 0.0019672 | 0.00049269 | 9.5466e-08 | -3.071e-07 | 0.0029692 | 0.0029691 | 0.0029692 | 0.9858 | -0.27187 | 0.98586 | -0.27085 | 0.81571
123 | -0.0060152 | -0.0015072 | 0.0060152 | 0.0015072 | 3.2452e-08 | 7.3825e-09 | 0.009079 | 0.009079 | 0.009079 | 0.98586 | -0.27085 | 0.98586 | -0.27074 | 2.4942
124 | 0.18238 | 0.046635 | -0.18222 | -0.046527 | 0.00016817 | 0.00010731 | 0.27276 | 0.27276 | 0.27276 | 0.99619 | -0.072256 | 0.99518 | -0.091332 | 37.4667
125 | -0.20225 | -0.051617 | 0.20228 | 0.051636 | 2.9686e-05 | 1.8954e-05 | 0.30243 | 0.30243 | 0.30243 | 0.99619 | -0.072256 | 0.99635 | -0.069218 | 41.5423
126 | 0.0071473 | 0.001791 | -0.0071465 | -0.0017907 | 8.1505e-07 | 2.7423e-07 | 0.010685 | 0.010685 | 0.010685 | 0.99534 | -0.088528 | 0.99522 | -0.090922 | 2.9355
127 | -0.033461 | -0.0084008 | 0.033478 | 0.0084112 | 1.6584e-05 | 1.0392e-05 | 0.050457 | 0.050457 | 0.050457 | 0.98689 | -0.25073 | 0.98742 | -0.24035 | 13.8619
128 | 0.20395 | 0.05207 | -0.20392 | -0.052048 | 3.3893e-05 | 2.1641e-05 | 0.30488 | 0.30488 | 0.30488 | 0.99653 | -0.065779 | 0.99635 | -0.069218 | 41.8795
129 | 0.18056 | 0.046111 | -0.1804 | -0.046014 | 0.00015208 | 9.704e-05 | 0.27028 | 0.27028 | 0.27028 | 0.99518 | -0.091332 | 0.99427 | -0.10877 | 37.1257
130 | 0.0055676 | 0.001395 | -0.0055676 | -0.001395 | 4.1008e-08 | 5.7392e-09 | 0.0083244 | 0.0083244 | 0.0083244 | 0.99522 | -0.090922 | 0.99521 | -0.091077 | 2.2869
131 | 0.0040705 | 0.0010198 | -0.0040705 | -0.0010198 | 9.584e-09 | -2.8325e-09 | 0.0060859 | 0.0060859 | 0.0060859 | 0.99521 | -0.091077 | 0.99521 | -0.091126 | 1.672
132 | 0.0026063 | 0.00065285 | -0.0026061 | -0.00065307 | 1.3366e-07 | -2.1944e-07 | 0.0038967 | 0.0038968 | 0.0038968 | 0.99521 | -0.091126 | 0.99515 | -0.092203 | 1.0706
133 | 0.0015231 | 0.00038162 | -0.0015231 | -0.00038172 | 1.4982e-08 | -9.0491e-08 | 0.0022774 | 0.0022774 | 0.0022774 | 0.99515 | -0.092203 | 0.99514 | -0.092409 | 0.62566
134 | -0.0095168 | -0.0023833 | 0.0095178 | 0.0023838 | 1.0068e-06 | 4.7724e-07 | 0.014338 | 0.014338 | 0.014338 | 0.98762 | -0.23743 | 0.98773 | -0.23521 | 3.939
135 | 0.00795 | 0.0019906 | -0.0079499 | -0.0019906 | 1.2208e-07 | 4.9092e-08 | 0.011977 | 0.011977 | 0.011977 | 0.98762 | -0.23743 | 0.9876 | -0.23775 | 3.2905
136 | -0.011039 | -0.002765 | 0.01104 | 0.0027656 | 1.2248e-06 | 6.327e-07 | 0.01663 | 0.01663 | 0.01663 | 0.98773 | -0.23521 | 0.98785 | -0.23288 | 4.5686
137 | 0.0061369 | 0.0015362 | -0.0061363 | -0.001536 | 6.8049e-07 | 1.6392e-07 | 0.0092458 | 0.0092459 | 0.0092459 | 0.9876 | -0.23775 | 0.98748 | -0.24008 | 2.5401
138 | 0.0042172 | 0.0010551 | -0.0042153 | -0.0010554 | 1.8314e-06 | -3.7448e-07 | 0.0063541 | 0.0063546 | 0.0063546 | 0.98748 | -0.24008 | 0.98701 | -0.24921 | 1.7458
139 | 0.0042153 | 0.0010554 | -0.0042131 | -0.0010559 | 2.2456e-06 | -4.568e-07 | 0.0063546 | 0.0063553 | 0.0063553 | 0.98701 | -0.24921 | 0.98644 | -0.2604 | 1.746

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42497 | 0.10838

## res_load
| p_mw | q_mvar
0 | 0.001881 | 0.00047143
1 | 0.00049135 | 0.00012314
2 | 0.0018946 | 0.00047483
3 | 0.0015913 | 0.00039883
4 | 0.001527 | 0.00038269
5 | 0.00084404 | 0.00021154
6 | 0.0013931 | 0.00034913
7 | 0.0051838 | 0.0012992
8 | 0.00080734 | 0.00020234
9 | 0.0010774 | 0.00027002
10 | 0.0026965 | 0.0006758
11 | 0.00077525 | 0.0001943
12 | 0.00087868 | 0.00022022
13 | 0.00088619 | 0.0002221
14 | 0.00079518 | 0.00019929
15 | 0.00064609 | 0.00016193
16 | 0.0013661 | 0.00034237
17 | 0.00053579 | 0.00013428
18 | 0.0020783 | 0.00052087
19 | 0.0014623 | 0.0003665
20 | 0.076186 | 0.019094
21 | 0.0022835 | 0.00057231
22 | 0.0016407 | 0.0004112
23 | 0.0044101 | 0.0011053
24 | 0.0045976 | 0.0011523
25 | 0.0024238 | 0.00060745
26 | 0.0026675 | 0.00066854
27 | 0.0014781 | 0.00037045
28 | 0.0025203 | 0.00063164
29 | 0.0045429 | 0.0011386
30 | 0.0042227 | 0.0010583
31 | 0.0018833 | 0.00047201
32 | 0.0029623 | 0.00074242
33 | 0.0093194 | 0.0023357
34 | 0.0032348 | 0.0008107
35 | 0.002603 | 0.00065237
36 | 0.011636 | 0.0029164
37 | 0.0022821 | 0.00057195
38 | 0.0036349 | 0.00091099
39 | 0.0019484 | 0.00048832
40 | 0.025037 | 0.006275
41 | 0.011983 | 0.0030031
42 | 0.003516 | 0.00088119
43 | 0.00012424 | 3.1138e-05
44 | 0.00029386 | 7.3649e-05
45 | 0.00034416 | 8.6256e-05
46 | 0.0068048 | 0.0017055
47 | 0.0015951 | 0.00039977
48 | 0.017387 | 0.0043575
49 | 0.0050569 | 0.0012674
50 | 0.0029458 | 0.00073828
51 | 0.0036762 | 0.00092134
52 | 0.0051424 | 0.0012888
53 | 0.0037716 | 0.00094526
54 | 0.0075738 | 0.0018982
55 | 0.0021867 | 0.00054804
56 | 0.0017031 | 0.00042683
57 | 0.0074227 | 0.0018603
58 | 0.004043 | 0.0010133
59 | 0.0013373 | 0.00033516
60 | 0.0011281 | 0.00028273
61 | 0.0018253 | 0.00045746
62 | 0.0021118 | 0.00052926
63 | 0.0040279 | 0.0010095
64 | 0.0028568 | 0.00071597
65 | 0.0019951 | 0.00050003
66 | 0.0010413 | 0.00026097
67 | 0.0039506 | 0.00099011
68 | 0.0037532 | 0.00094064
69 | 0.0022597 | 0.00056632
70 | 0.0013635 | 0.00034173
71 | 0.0033754 | 0.00084596
72 | 0.0034684 | 0.00086927
73 | 0.0016134 | 0.00040436
74 | 0.001421 | 0.00035613
75 | 0.0012522 | 0.00031382
76 | 0.0021835 | 0.00054724
77 | 0.00046125 | 0.0001156
78 | 0.0062993 | 0.0015788
79 | 0.0012913 | 0.00032363
80 | 0.001469 | 0.00036816
81 | 0.0011929 | 0.00029897
82 | 0.0016694 | 0.00041839
83 | 0.00066272 | 0.00016609
84 | 0.0010662 | 0.00026721
85 | 0.0011697 | 0.00029314
86 | 0.0014884 | 0.00037302
87 | 0.0013071 | 0.0003276
88 | 0.00034083 | 8.5421e-05
89 | 0.0027066 | 0.00067835
90 | 0.0030813 | 0.00077224
91 | 0.0028733 | 0.00072011
92 | 0.0021994 | 0.00055122
93 | 0.0019671 | 0.00049299
94 | 0.004048 | 0.0010145
95 | 0.0018389 | 0.00046088
96 | 0.002734 | 0.00068522
97 | 0.0034759 | 0.00087114
98 | 0.0027351 | 0.00068548
99 | 0.0008965 | 0.00022468
100 | 0.0016436 | 0.00041194
101 | 0.0016603 | 0.00041612
102 | 0.0015789 | 0.00039571
103 | 0.0014971 | 0.00037521
104 | 0.0014642 | 0.00036696
105 | 0.0010831 | 0.00027144
106 | 0.0032325 | 0.00081014
107 | 0.0015668 | 0.00039267
108 | 0.0015212 | 0.00038124
109 | 0.001813 | 0.00045438
110 | 0.0038915 | 0.0009753
111 | 0.0019191 | 0.00048097
112 | 0.0042131 | 0.0010559
113 | 0.0028751 | 0.00072056
114 | 0.0015231 | 0.00038172
115 | 0.010804 | 0.0027076
116 | 0.0011861 | 0.00029727

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1