## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_120-8_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_120-8_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_120-8_0_5_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_120-8_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_120-8_0_5_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_120-8_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_120-8_0_5_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_120-8_0_5_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_120-8_0_5_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_120-8_0_5_node_65 | 0.4 | n |  | TRUE
10 | bus_LV_120-8_0_5_node_59 | 0.4 | n |  | TRUE
11 | bus_LV_120-8_0_5_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_120-8_0_5_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_120-8_0_5_node_42 | 0.4 | n |  | TRUE
14 | bus_LV_120-8_0_5_node_39 | 0.4 | n |  | TRUE
15 | bus_LV_120-8_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_120-8_0_5_node_45 | 0.4 | n |  | TRUE
17 | bus_LV_120-8_0_5_node_44 | 0.4 | n |  | TRUE
18 | bus_LV_120-8_0_5_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_120-8_0_5_node_47 | 0.4 | n |  | TRUE
20 | bus_LV_120-8_0_5_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_120-8_0_5_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_120-8_0_5_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_120-8_0_5_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_120-8_0_5_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_120-8_0_5_node_58 | 0.4 | n |  | TRUE
26 | bus_LV_120-8_0_5_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_120-8_0_5_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_120-8_0_5_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_120-8_0_5_node_41 | 0.4 | n |  | TRUE
30 | bus_LV_120-8_0_5_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_120-8_0_5_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_120-8_0_5_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_120-8_0_5_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_120-8_0_5_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_120-8_0_5_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_120-8_0_5_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_120-8_0_5_node_14 | 0.4 | n |  | TRUE
38 | bus_LV_120-8_0_5_node_16 | 0.4 | n |  | TRUE
39 | bus_LV_120-8_0_5_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_120-8_0_5_node_48 | 0.4 | n |  | TRUE
41 | bus_LV_120-8_0_5_node_46 | 0.4 | n |  | TRUE
42 | bus_LV_120-8_0_5_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_120-8_0_5_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_120-8_0_5_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_120-8_0_5_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_120-8_0_5_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_120-8_0_5_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_120-8_0_5_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_120-8_0_5_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_120-8_0_5_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_120-8_0_5_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_120-8_0_5_node_56 | 0.4 | n |  | TRUE
53 | bus_LV_120-8_0_5_node_54 | 0.4 | n |  | TRUE
54 | bus_LV_120-8_0_5_node_57 | 0.4 | n |  | TRUE
55 | bus_LV_120-8_0_5_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_120-8_0_5_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_120-8_0_5_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_120-8_0_5_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_120-8_0_5_node_64 | 0.4 | n |  | TRUE
60 | bus_LV_120-8_0_5_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_120-8_0_5_node_60 | 0.4 | n |  | TRUE
62 | bus_MV_10_0_node_52 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_120-8_0_5_load_0 | 0 | 0.00064067 | 0.00016057 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_120-8_0_5_load_11 | 4 | 0.039278 | 0.009844 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_120-8_0_5_load_24 | 7 | 0.028224 | 0.0070735 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_120-8_0_5_load_65 | 9 | 0.0051057 | 0.0012796 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_120-8_0_5_load_59 | 10 | 0.0090356 | 0.0022645 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_120-8_0_5_load_17 | 11 | 0.046813 | 0.011732 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_120-8_0_5_load_42 | 13 | 0.0091376 | 0.0022901 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_120-8_0_5_load_39 | 14 | 0.025919 | 0.006496 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_120-8_0_5_load_45 | 16 | 0.0021145 | 0.00052995 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_120-8_0_5_load_44 | 17 | 0.046216 | 0.011583 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_120-8_0_5_load_63 | 20 | 0.016798 | 0.0042099 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_120-8_0_5_load_37 | 22 | 0.011065 | 0.0027731 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_120-8_0_5_load_36 | 23 | 0.018882 | 0.0047324 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_120-8_0_5_load_38 | 24 | 0.0016356 | 0.00040991 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_120-8_0_5_load_58 | 25 | 0.0025978 | 0.00065107 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_120-8_0_5_load_25 | 26 | 0.020684 | 0.0051838 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_120-8_0_5_load_19 | 27 | 0.018278 | 0.0045808 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_120-8_0_5_load_41 | 29 | 0.013786 | 0.0034551 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_120-8_0_5_load_40 | 30 | 0.011657 | 0.0029216 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_120-8_0_5_load_15 | 31 | 0.022169 | 0.0055562 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_120-8_0_5_load_43 | 32 | 0.0030059 | 0.00075335 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_120-8_0_5_load_49 | 33 | 0.0012195 | 0.00030564 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_120-8_0_5_load_61 | 34 | 0.0064924 | 0.0016272 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_120-8_0_5_load_35 | 35 | 0.004198 | 0.0010521 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_120-8_0_5_load_14 | 37 | 0.0036702 | 0.00091985 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_120-8_0_5_load_18 | 39 | 0.0007157 | 0.00017937 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_120-8_0_5_load_46 | 41 | 0.0022334 | 0.00055973 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_120-8_0_5_load_22 | 42 | 0.014859 | 0.0037241 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_120-8_0_5_load_26 | 43 | 0.019832 | 0.0049703 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_120-8_0_5_load_34 | 44 | 0.035941 | 0.0090076 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_120-8_0_5_load_31 | 45 | 0.017354 | 0.0043492 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_120-8_0_5_load_28 | 46 | 0.0026444 | 0.00066276 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_120-8_0_5_load_29 | 47 | 0.017029 | 0.0042678 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_120-8_0_5_load_33 | 50 | 0.003382 | 0.0008476 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_120-8_0_5_load_55 | 51 | 0.0056554 | 0.0014174 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_120-8_0_5_load_56 | 52 | 0.0034701 | 0.00086968 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_120-8_0_5_load_54 | 53 | 0.0017966 | 0.00045027 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_120-8_0_5_load_57 | 54 | 0.0018033 | 0.00045196 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_120-8_0_5_load_50 | 55 | 0.0022174 | 0.00055574 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_120-8_0_5_load_51 | 56 | 0.0034952 | 0.00087598 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_120-8_0_5_load_52 | 57 | 0.0015508 | 0.00038867 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_120-8_0_5_load_53 | 58 | 0.0029818 | 0.00074731 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_120-8_0_5_load_64 | 59 | 0.0027009 | 0.0006769 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_120-8_0_5_load_62 | 60 | 0.0049029 | 0.0012288 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_120-8_0_5_load_60 | 61 | 0.0030551 | 0.00076569 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_120-8_0_5_line_0 |  | 0 | 1 | 0.020664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_120-8_0_5_line_1 |  | 1 | 2 | 0.079166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_120-8_0_5_line_2 |  | 2 | 11 | 0.024668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_120-8_0_5_line_3 |  | 2 | 3 | 0.012075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_120-8_0_5_line_4 |  | 3 | 4 | 0.043874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_120-8_0_5_line_5 |  | 5 | 6 | 0.025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_120-8_0_5_line_6 |  | 5 | 7 | 0.010113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_120-8_0_5_line_7 |  | 6 | 10 | 0.034952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_120-8_0_5_line_8 |  | 6 | 24 | 0.016442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_120-8_0_5_line_9 |  | 6 | 25 | 0.015207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_120-8_0_5_line_10 |  | 7 | 26 | 0.00044384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_120-8_0_5_line_11 |  | 8 | 9 | 0.024674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_120-8_0_5_line_12 |  | 8 | 10 | 0.023231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_120-8_0_5_line_13 |  | 9 | 16 | 0.017407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_120-8_0_5_line_14 |  | 11 | 31 | 0.004925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_120-8_0_5_line_15 |  | 12 | 13 | 0.018787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_120-8_0_5_line_16 |  | 12 | 14 | 0.014633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_120-8_0_5_line_17 |  | 13 | 32 | 0.016582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_120-8_0_5_line_18 |  | 14 | 30 | 0.0091627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_120-8_0_5_line_19 |  | 15 | 16 | 0.016566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_120-8_0_5_line_20 |  | 15 | 17 | 0.042915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_120-8_0_5_line_21 |  | 17 | 32 | 6.2912e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_120-8_0_5_line_22 |  | 18 | 19 | 0.004832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_120-8_0_5_line_23 |  | 18 | 20 | 0.032887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_120-8_0_5_line_24 |  | 19 | 33 | 0.0070725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_120-8_0_5_line_25 |  | 20 | 34 | 0.0074885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_120-8_0_5_line_26 |  | 21 | 22 | 0.0090581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_120-8_0_5_line_27 |  | 21 | 23 | 0.019188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_120-8_0_5_line_28 |  | 22 | 35 | 0.0037578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_120-8_0_5_line_29 |  | 23 | 36 | 0.012354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_120-8_0_5_line_30 |  | 24 | 45 | 0.023229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_120-8_0_5_line_31 |  | 26 | 43 | 0.017574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_120-8_0_5_line_32 |  | 27 | 28 | 0.011386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_120-8_0_5_line_33 |  | 28 | 42 | 0.042373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_120-8_0_5_line_34 |  | 28 | 36 | 0.015485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_120-8_0_5_line_35 |  | 29 | 30 | 0.009732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_120-8_0_5_line_36 |  | 31 | 37 | 0.031716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_120-8_0_5_line_37 |  | 33 | 40 | 0.0092654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_120-8_0_5_line_38 |  | 34 | 61 | 0.0086609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_120-8_0_5_line_39 |  | 35 | 44 | 0.027092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_120-8_0_5_line_40 |  | 37 | 38 | 0.020249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_120-8_0_5_line_41 |  | 38 | 39 | 0.017183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_120-8_0_5_line_42 |  | 39 | 40 | 0.0075445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_120-8_0_5_line_43 |  | 40 | 41 | 0.0045355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_120-8_0_5_line_44 |  | 43 | 44 | 0.00033663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_120-8_0_5_line_45 |  | 45 | 47 | 0.0072699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_120-8_0_5_line_46 |  | 46 | 47 | 0.0076759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_120-8_0_5_line_47 |  | 46 | 48 | 0.011326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_120-8_0_5_line_48 |  | 48 | 49 | 0.008267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_120-8_0_5_line_49 |  | 48 | 50 | 0.017547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_120-8_0_5_line_50 |  | 49 | 51 | 0.013146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_120-8_0_5_line_51 |  | 50 | 52 | 0.00035629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_120-8_0_5_line_52 |  | 51 | 53 | 0.0043396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_120-8_0_5_line_53 |  | 52 | 54 | 0.00072331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_120-8_0_5_line_54 |  | 53 | 58 | 0.0044479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_120-8_0_5_line_55 |  | 54 | 59 | 0.014077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_120-8_0_5_line_56 |  | 55 | 56 | 0.005466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_120-8_0_5_line_57 |  | 55 | 57 | 0.007622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_120-8_0_5_line_58 |  | 56 | 58 | 0.021247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_120-8_0_5_line_59 |  | 59 | 60 | 0.0037367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_120-8_0_5_line_60 |  | 60 | 61 | 0.0042587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_120-8_0_5_trafo_55 | 0.63 MVA 20/0.4 kV | 62 | 51 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2711777.8287 | 1237507.2921 | 2711781.9566 | 1237511.5176 | 2711789.4499 | 1237517.4633 | 2711793.833 | 1237520.2455
1 | 2711749.4251 | 1237452.7925 | 2711754.2919 | 1237454.7523 | 2711759.9249 | 1237457.0156 | 2711772.4905 | 1237462.4563 | 2711780.7415 | 1237469.5616 | 2711774.8167 | 1237474.3539 | 2711771.2918 | 1237481.104 | 2711770.1193 | 1237488.3098 | 2711772.3363 | 1237497.9703 | 2711777.8287 | 1237507.2921
2 | 2711749.4251 | 1237452.7925 | 2711730.9524 | 1237444.772 | 2711726.5683 | 1237443.6345
3 | 2711749.4251 | 1237452.7925 | 2711754.2919 | 1237454.7523 | 2711750.7688 | 1237460.6017
4 | 2711750.7688 | 1237460.6017 | 2711722.4049 | 1237448.592 | 2711715.9436 | 1237459.9559
5 | 2711743.5603 | 1237300.0507 | 2711740.9399 | 1237287.2914 | 2711737.5082 | 1237275.8178
6 | 2711737.5082 | 1237275.8178 | 2711727.8287 | 1237278.7472
7 | 2711743.5603 | 1237300.0507 | 2711748.4744 | 1237300.3101 | 2711753.027 | 1237301.6857 | 2711776.7702 | 1237310.3504
8 | 2711743.5603 | 1237300.0507 | 2711735.6449 | 1237301.6364 | 2711728.3932 | 1237305.815
9 | 2711743.5603 | 1237300.0507 | 2711743.2761 | 1237312.3328 | 2711742.5176 | 1237315.1541
10 | 2711727.4039 | 1237278.8758 | 2711727.8287 | 1237278.7472
11 | 2711799.7833 | 1237312.7743 | 2711801.2628 | 1237321.0086 | 2711806.0286 | 1237330.7504 | 2711807.7822 | 1237335.9239
12 | 2711799.7833 | 1237312.7743 | 2711784.6972 | 1237312.1676 | 2711776.7702 | 1237310.3504
13 | 2711807.7822 | 1237335.9239 | 2711809.9358 | 1237342.2775 | 2711811.3268 | 1237349.5872 | 2711811.6126 | 1237352.8324
14 | 2711721.8011 | 1237442.3976 | 2711726.5683 | 1237443.6345
15 | 2711786.6026 | 1237430.7858 | 2711779.5406 | 1237426.0381 | 2711779.396 | 1237421.6652 | 2711780.942 | 1237415.9687
16 | 2711786.6026 | 1237430.7858 | 2711789.0772 | 1237431.5886 | 2711800.8911 | 1237433.8647
17 | 2711780.942 | 1237415.9687 | 2711783.4375 | 1237406.774 | 2711785.7465 | 1237400.1084
18 | 2711800.8911 | 1237433.8647 | 2711806.9248 | 1237435.0272 | 2711809.909 | 1237435.4775
19 | 2711812.8009 | 1237369.3527 | 2711812.4596 | 1237365.3765 | 2711812.1871 | 1237359.3555 | 2711811.6126 | 1237352.8324
20 | 2711812.8009 | 1237369.3527 | 2711805.2315 | 1237371.4564 | 2711798.285 | 1237377.8529 | 2711791.6922 | 1237387.1695 | 2711787.0387 | 1237396.378 | 2711785.7671 | 1237400.049
21 | 2711785.7465 | 1237400.1084 | 2711785.7671 | 1237400.049
22 | 2711651.2991 | 1237394.3567 | 2711653.9703 | 1237398.3879
23 | 2711651.2991 | 1237394.3567 | 2711678.1451 | 1237375.3616
24 | 2711653.9703 | 1237398.3879 | 2711657.0465 | 1237396.1773 | 2711657.905 | 1237397.6057 | 2711657.7307 | 1237399.2141
25 | 2711678.1451 | 1237375.3616 | 2711684.2582 | 1237371.0362
26 | 2711673.8554 | 1237279.0678 | 2711680.6151 | 1237285.0974
27 | 2711673.8554 | 1237279.0678 | 2711677.895 | 1237267.8905 | 2711677.1437 | 1237262.372 | 2711676.9086 | 1237260.6539
28 | 2711683.4194 | 1237287.5987 | 2711683.4194 | 1237287.5987 | 2711680.6151 | 1237285.0974
29 | 2711675.2343 | 1237248.414 | 2711676.9086 | 1237260.6539
30 | 2711711.205 | 1237321.1365 | 2711722.4704 | 1237309.2279 | 2711728.3932 | 1237305.815
31 | 2711727.4039 | 1237278.8758 | 2711710.5831 | 1237283.9663
32 | 2711690.6985 | 1237249.8503 | 2711701.7929 | 1237249.8478 | 2711702.0846 | 1237249.8422
33 | 2711690.6985 | 1237249.8503 | 2711686.9483 | 1237229.9642 | 2711681.2017 | 1237208.5867
34 | 2711690.6985 | 1237249.8503 | 2711675.2343 | 1237248.414
35 | 2711809.909 | 1237435.4775 | 2711814.252 | 1237436.1327 | 2711819.4721 | 1237435.0078
36 | 2711691.5929 | 1237432.7941 | 2711713.3003 | 1237440.1919 | 2711721.8011 | 1237442.3976
37 | 2711655.1286 | 1237408.0172 | 2711657.3648 | 1237402.5883 | 2711657.7307 | 1237399.2141
38 | 2711691.3283 | 1237366.0337 | 2711684.2582 | 1237371.0362
39 | 2711710.2609 | 1237284.0639 | 2711709.0047 | 1237284.444 | 2711683.4194 | 1237287.5987
40 | 2711672.9635 | 1237425.0104 | 2711680.8019 | 1237429.1165 | 2711691.5929 | 1237432.7941
41 | 2711672.9635 | 1237425.0104 | 2711666.5741 | 1237420.3088 | 2711660.27 | 1237413.5387
42 | 2711655.1286 | 1237408.0172 | 2711660.27 | 1237413.5387
43 | 2711655.1286 | 1237408.0172 | 2711651.1199 | 1237405.8958
44 | 2711710.2609 | 1237284.0639 | 2711710.5831 | 1237283.9663
45 | 2711713.0526 | 1237328.1677 | 2711711.205 | 1237321.1365 | 2711711.205 | 1237321.1365
46 | 2711713.0526 | 1237328.1677 | 2711714.1709 | 1237332.4234 | 2711716.5115 | 1237334.7152
47 | 2711724.6037 | 1237342.6388 | 2711716.5115 | 1237334.7152
48 | 2711724.6037 | 1237342.6388 | 2711731.0064 | 1237337.3884
49 | 2711724.6037 | 1237342.6388 | 2711719.9841 | 1237346.4327 | 2711710.3542 | 1237352.8443
50 | 2711731.0064 | 1237337.3884 | 2711741.5266 | 1237345.2722
51 | 2711710.3542 | 1237352.8443 | 2711710.0577 | 1237353.0418
52 | 2711745.444 | 1237346.9441 | 2711742.8939 | 1237346.2968 | 2711741.5266 | 1237345.2722
53 | 2711710.0577 | 1237353.0418 | 2711709.4556 | 1237353.4427
54 | 2711745.444 | 1237346.9441 | 2711749.7553 | 1237348.0384
55 | 2711709.4556 | 1237353.4427 | 2711704.879 | 1237356.4898 | 2711697.857 | 1237361.4181
56 | 2711776.44 | 1237349.2583 | 2711770.9796 | 1237349.0124
57 | 2711776.44 | 1237349.2583 | 2711784.0543 | 1237349.6012
58 | 2711749.7553 | 1237348.0384 | 2711749.7553 | 1237348.0384 | 2711764.764 | 1237348.7324 | 2711770.9796 | 1237349.0124
59 | 2711697.857 | 1237361.4181 | 2711697.1947 | 1237361.8829 | 2711694.8048 | 1237363.5739
60 | 2711691.3283 | 1237366.0337 | 2711694.8048 | 1237363.5739

## bus_geodata
| x | y | coords
0 | 2711793.833 | 1237520.2455
1 | 2711777.8287 | 1237507.2921
2 | 2711749.4251 | 1237452.7925
3 | 2711750.7688 | 1237460.6017
4 | 2711715.9436 | 1237459.9559
5 | 2711737.5082 | 1237275.8178
6 | 2711743.5603 | 1237300.0507
7 | 2711727.8287 | 1237278.7472
8 | 2711799.7833 | 1237312.7743
9 | 2711807.7822 | 1237335.9239
10 | 2711776.7702 | 1237310.3504
11 | 2711726.5683 | 1237443.6345
12 | 2711786.6026 | 1237430.7858
13 | 2711780.942 | 1237415.9687
14 | 2711800.8911 | 1237433.8647
15 | 2711812.8009 | 1237369.3527
16 | 2711811.6126 | 1237352.8324
17 | 2711785.7671 | 1237400.049
18 | 2711651.2991 | 1237394.3567
19 | 2711653.9703 | 1237398.3879
20 | 2711678.1451 | 1237375.3616
21 | 2711673.8554 | 1237279.0678
22 | 2711680.6151 | 1237285.0974
23 | 2711676.9086 | 1237260.6539
24 | 2711728.3932 | 1237305.815
25 | 2711742.5176 | 1237315.1541
26 | 2711727.4039 | 1237278.8758
27 | 2711702.0846 | 1237249.8422
28 | 2711690.6985 | 1237249.8503
29 | 2711819.4721 | 1237435.0078
30 | 2711809.909 | 1237435.4775
31 | 2711721.8011 | 1237442.3976
32 | 2711785.7465 | 1237400.1084
33 | 2711657.7307 | 1237399.2141
34 | 2711684.2582 | 1237371.0362
35 | 2711683.4194 | 1237287.5987
36 | 2711675.2343 | 1237248.414
37 | 2711691.5929 | 1237432.7941
38 | 2711672.9635 | 1237425.0104
39 | 2711660.27 | 1237413.5387
40 | 2711655.1286 | 1237408.0172
41 | 2711651.1199 | 1237405.8958
42 | 2711681.2017 | 1237208.5867
43 | 2711710.5831 | 1237283.9663
44 | 2711710.2609 | 1237284.0639
45 | 2711711.205 | 1237321.1365
46 | 2711716.5115 | 1237334.7152
47 | 2711713.0526 | 1237328.1677
48 | 2711724.6037 | 1237342.6388
49 | 2711731.0064 | 1237337.3884
50 | 2711710.3542 | 1237352.8443
51 | 2711741.5266 | 1237345.2722
52 | 2711710.0577 | 1237353.0418
53 | 2711745.444 | 1237346.9441
54 | 2711709.4556 | 1237353.4427
55 | 2711776.44 | 1237349.2583
56 | 2711770.9796 | 1237349.0124
57 | 2711784.0543 | 1237349.6012
58 | 2711749.7553 | 1237348.0384
59 | 2711697.857 | 1237361.4181
60 | 2711694.8048 | 1237363.5739
61 | 2711691.3283 | 1237366.0337
62 | 2711731.0064 | 1237337.3884

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97952 | -0.39388 | 0.00064067 | 0.00016057
1 | 0.97953 | -0.39364 | 0 | 0
2 | 0.97958 | -0.39272 | 0 | 0
3 | 0.97914 | -0.40134 | 0 | 0
4 | 0.97754 | -0.43272 | 0.039278 | 0.009844
5 | 0.99178 | -0.15679 | 0 | 0
6 | 0.99276 | -0.13776 | 0 | 0
7 | 0.99138 | -0.16449 | 0.028224 | 0.0070735
8 | 0.98613 | -0.26452 | 0 | 0
9 | 0.98345 | -0.31638 | 0.0051057 | 0.0012796
10 | 0.98866 | -0.21595 | 0.0090356 | 0.0022645
11 | 0.98049 | -0.37484 | 0.046813 | 0.011732
12 | 0.97372 | -0.5065 | 0 | 0
13 | 0.97462 | -0.48878 | 0.0091376 | 0.0022901
14 | 0.97302 | -0.52033 | 0.025919 | 0.006496
15 | 0.97994 | -0.38447 | 0 | 0
16 | 0.98163 | -0.35153 | 0.0021145 | 0.00052995
17 | 0.97556 | -0.47032 | 0.046216 | 0.011583
18 | 0.99106 | -0.17018 | 0 | 0
19 | 0.99053 | -0.1802 | 0 | 0
20 | 0.99461 | -0.10229 | 0.016798 | 0.0042099
21 | 0.987 | -0.24929 | 0 | 0
22 | 0.98743 | -0.24086 | 0.011065 | 0.0027731
23 | 0.98608 | -0.26717 | 0.018882 | 0.0047324
24 | 0.9939 | -0.11594 | 0.0016356 | 0.00040991
25 | 0.99272 | -0.13846 | 0.0025978 | 0.00065107
26 | 0.99135 | -0.16506 | 0.020684 | 0.0051838
27 | 0.98504 | -0.28746 | 0.018278 | 0.0045808
28 | 0.98523 | -0.28372 | 0 | 0
29 | 0.97268 | -0.5271 | 0.013786 | 0.0034551
30 | 0.9728 | -0.52462 | 0.011657 | 0.0029216
31 | 0.98089 | -0.3671 | 0.022169 | 0.0055562
32 | 0.97555 | -0.47039 | 0.0030059 | 0.00075335
33 | 0.98977 | -0.19487 | 0.0012195 | 0.00030564
34 | 0.99554 | -0.084685 | 0.0064924 | 0.0016272
35 | 0.98765 | -0.23663 | 0.004198 | 0.0010521
36 | 0.9857 | -0.27451 | 0 | 0
37 | 0.98408 | -0.30473 | 0.0036702 | 0.00091985
38 | 0.98619 | -0.26379 | 0 | 0
39 | 0.98799 | -0.22919 | 0.0007157 | 0.00017937
40 | 0.98878 | -0.21394 | 0 | 0
41 | 0.98877 | -0.21412 | 0.0022334 | 0.00055973
42 | 0.98465 | -0.29503 | 0.014859 | 0.0037241
43 | 0.98936 | -0.20349 | 0.019832 | 0.0049703
44 | 0.98933 | -0.20411 | 0.035941 | 0.0090076
45 | 0.99552 | -0.085023 | 0.017354 | 0.0043492
46 | 0.99665 | -0.063475 | 0.0026444 | 0.00066276
47 | 0.99606 | -0.074815 | 0.017029 | 0.0042678
48 | 0.99754 | -0.046636 | 0 | 0
49 | 0.99849 | -0.028604 | 0 | 0
50 | 0.99689 | -0.058889 | 0.003382 | 0.0008476
51 | 1 | 0 | -0.51945 | -0.13256
52 | 0.99688 | -0.059132 | 0.0034701 | 0.00086968
53 | 0.99995 | -0.00091096 | 0.0017966 | 0.00045027
54 | 0.99686 | -0.059616 | 0.0018033 | 0.00045196
55 | 0.99975 | -0.0047555 | 0.0022174 | 0.00055574
56 | 0.99977 | -0.0043963 | 0.0034952 | 0.00087598
57 | 0.99974 | -0.0049617 | 0.0015508 | 0.00038867
58 | 0.99991 | -0.0017054 | 0.0029818 | 0.00074731
59 | 0.99637 | -0.068923 | 0.0027009 | 0.0006769
60 | 0.99624 | -0.071351 | 0.0049029 | 0.0012288
61 | 0.9961 | -0.074027 | 0.0030551 | 0.00076569
62 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00064067 | -0.00016057 | 0.00064068 | 0.00016031 | 7.3396e-09 | -2.5541e-07 | 0.00097327 | 0.00097317 | 0.00097327 | 0.97952 | -0.39388 | 0.97953 | -0.39364 | 0.26738
1 | -0.00064068 | -0.00016031 | 0.00064071 | 0.00015933 | 2.8105e-08 | -9.7858e-07 | 0.00097317 | 0.00097282 | 0.00097317 | 0.97953 | -0.39364 | 0.97958 | -0.39272 | 0.26736
2 | -0.039994 | -0.010051 | 0.040028 | 0.010072 | 3.4153e-05 | 2.1547e-05 | 0.060762 | 0.060762 | 0.060762 | 0.97958 | -0.39272 | 0.98049 | -0.37484 | 16.6928
3 | 0.039353 | 0.0098913 | -0.039337 | -0.0098811 | 1.6187e-05 | 1.0208e-05 | 0.059789 | 0.059789 | 0.059789 | 0.97958 | -0.39272 | 0.97914 | -0.40134 | 16.4256
4 | 0.039337 | 0.0098811 | -0.039278 | -0.009844 | 5.8815e-05 | 3.709e-05 | 0.059789 | 0.059789 | 0.059789 | 0.97914 | -0.40134 | 0.97754 | -0.43272 | 16.4256
5 | -0.17248 | -0.043427 | 0.17264 | 0.043526 | 0.00015704 | 9.9215e-05 | 0.25885 | 0.25885 | 0.25885 | 0.99178 | -0.15679 | 0.99276 | -0.13776 | 17.7783
6 | 0.17248 | 0.043427 | -0.17242 | -0.043386 | 6.3527e-05 | 4.0136e-05 | 0.25885 | 0.25885 | 0.25885 | 0.99178 | -0.15679 | 0.99138 | -0.16449 | 17.7783
7 | 0.12799 | 0.032857 | -0.12751 | -0.032548 | 0.00048376 | 0.00030916 | 0.19212 | 0.19212 | 0.19212 | 0.99276 | -0.13776 | 0.98866 | -0.21595 | 52.7795
8 | -0.30322 | -0.077034 | 0.30354 | 0.077237 | 0.00031892 | 0.00020326 | 0.45486 | 0.45486 | 0.45486 | 0.99276 | -0.13776 | 0.9939 | -0.11594 | 31.2405
9 | 0.0025979 | 0.00065093 | -0.0025978 | -0.00065107 | 8.6462e-08 | -1.4128e-07 | 0.0038938 | 0.0038939 | 0.0038939 | 0.99276 | -0.13776 | 0.99272 | -0.13846 | 1.0697
10 | 0.14419 | 0.036313 | -0.14419 | -0.03631 | 3.9004e-06 | 2.4848e-06 | 0.21649 | 0.21649 | 0.21649 | 0.99138 | -0.16449 | 0.99135 | -0.16506 | 29.7376
11 | 0.11819 | 0.030106 | -0.1179 | -0.029918 | 0.00029487 | 0.0001884 | 0.17852 | 0.17852 | 0.17852 | 0.98613 | -0.26452 | 0.98345 | -0.31638 | 49.0435
12 | -0.11819 | -0.030106 | 0.11847 | 0.030283 | 0.00027763 | 0.00017739 | 0.17852 | 0.17852 | 0.17852 | 0.98613 | -0.26452 | 0.98866 | -0.21595 | 49.0435
13 | 0.11279 | 0.028638 | -0.1126 | -0.028516 | 0.00019042 | 0.00012165 | 0.17079 | 0.17079 | 0.17079 | 0.98345 | -0.31638 | 0.98163 | -0.35153 | 46.9212
14 | -0.086841 | -0.021805 | 0.086873 | 0.021825 | 3.2086e-05 | 2.0473e-05 | 0.13181 | 0.13181 | 0.13181 | 0.98049 | -0.37484 | 0.98089 | -0.3671 | 36.2106
15 | -0.051403 | -0.012898 | 0.051447 | 0.012926 | 4.348e-05 | 2.7593e-05 | 0.078559 | 0.078559 | 0.078559 | 0.97372 | -0.5065 | 0.97462 | -0.48878 | 21.5821
16 | 0.051403 | 0.012898 | -0.051369 | -0.012877 | 3.3865e-05 | 2.1492e-05 | 0.078559 | 0.078559 | 0.078559 | 0.97372 | -0.5065 | 0.97302 | -0.52033 | 21.5821
17 | -0.060584 | -0.015216 | 0.060638 | 0.01525 | 5.3215e-05 | 3.3851e-05 | 0.09251 | 0.09251 | 0.09251 | 0.97462 | -0.48878 | 0.97555 | -0.47039 | 25.4148
18 | 0.02545 | 0.0063808 | -0.025445 | -0.0063776 | 5.2051e-06 | 3.2175e-06 | 0.038921 | 0.038921 | 0.038921 | 0.97302 | -0.52033 | 0.9728 | -0.52462 | 10.6926
19 | -0.11031 | -0.027875 | 0.11049 | 0.027986 | 0.00017448 | 0.00011146 | 0.16759 | 0.16759 | 0.16759 | 0.97994 | -0.38447 | 0.98163 | -0.35153 | 46.0407
20 | 0.11031 | 0.027875 | -0.10986 | -0.027586 | 0.00045199 | 0.00028873 | 0.16759 | 0.16759 | 0.16759 | 0.97994 | -0.38447 | 0.97556 | -0.47032 | 46.0407
21 | 0.063644 | 0.016003 | -0.063643 | -0.016003 | 2.2241e-07 | 1.4156e-07 | 0.097095 | 0.097095 | 0.097095 | 0.97556 | -0.47032 | 0.97555 | -0.47039 | 26.6744
22 | 0.11795 | 0.030027 | -0.11789 | -0.029991 | 5.6935e-05 | 3.6376e-05 | 0.17726 | 0.17726 | 0.17726 | 0.99106 | -0.17018 | 0.99053 | -0.1802 | 48.6976
23 | -0.11795 | -0.030027 | 0.11834 | 0.030275 | 0.0003875 | 0.00024757 | 0.17726 | 0.17726 | 0.17726 | 0.99106 | -0.17018 | 0.99461 | -0.10229 | 48.6976
24 | 0.11789 | 0.029991 | -0.11781 | -0.029938 | 8.3334e-05 | 5.3243e-05 | 0.17726 | 0.17726 | 0.17726 | 0.99053 | -0.1802 | 0.98977 | -0.19487 | 48.6976
25 | -0.13513 | -0.034485 | 0.13525 | 0.034558 | 0.00011503 | 7.3521e-05 | 0.20239 | 0.20239 | 0.20239 | 0.99461 | -0.10229 | 0.99554 | -0.084685 | 55.6016
26 | -0.052101 | -0.013088 | 0.052122 | 0.013102 | 2.0964e-05 | 1.3301e-05 | 0.07856 | 0.07856 | 0.07856 | 0.987 | -0.24929 | 0.98743 | -0.24086 | 21.5824
27 | 0.052101 | 0.013088 | -0.052057 | -0.01306 | 4.4409e-05 | 2.8177e-05 | 0.07856 | 0.07856 | 0.07856 | 0.987 | -0.24929 | 0.98608 | -0.26717 | 21.5824
28 | -0.063187 | -0.015875 | 0.0632 | 0.015883 | 1.278e-05 | 8.1314e-06 | 0.095234 | 0.095234 | 0.095234 | 0.98743 | -0.24086 | 0.98765 | -0.23663 | 26.1632
29 | 0.033175 | 0.0083279 | -0.033163 | -0.0083206 | 1.1612e-05 | 7.2744e-06 | 0.050066 | 0.050066 | 0.050066 | 0.98608 | -0.26717 | 0.9857 | -0.27451 | 13.7544
30 | -0.30518 | -0.077647 | 0.30563 | 0.077937 | 0.00045542 | 0.00029027 | 0.45731 | 0.45731 | 0.45731 | 0.9939 | -0.11594 | 0.99552 | -0.085023 | 31.4087
31 | 0.12351 | 0.031127 | -0.12328 | -0.030982 | 0.00022664 | 0.00014482 | 0.18544 | 0.18544 | 0.18544 | 0.99135 | -0.16506 | 0.98936 | -0.20349 | 50.9461
32 | -0.018278 | -0.0045808 | 0.018281 | 0.0045828 | 3.2551e-06 | 1.9383e-06 | 0.027611 | 0.027611 | 0.027611 | 0.98504 | -0.28746 | 0.98523 | -0.28372 | 7.5853
33 | 0.014868 | 0.0037287 | -0.014859 | -0.0037241 | 8.0126e-06 | 4.5888e-06 | 0.022456 | 0.022456 | 0.022456 | 0.98523 | -0.28372 | 0.98465 | -0.29503 | 6.1692
34 | -0.033148 | -0.0083115 | 0.033163 | 0.0083206 | 1.4556e-05 | 9.1183e-06 | 0.050066 | 0.050066 | 0.050066 | 0.98523 | -0.28372 | 0.9857 | -0.27451 | 13.7544
35 | -0.013786 | -0.0034551 | 0.013788 | 0.003456 | 1.6232e-06 | 9.1807e-07 | 0.02109 | 0.02109 | 0.02109 | 0.97268 | -0.5271 | 0.9728 | -0.52462 | 5.7939
36 | -0.10904 | -0.027381 | 0.10937 | 0.027589 | 0.00032552 | 0.00020793 | 0.16544 | 0.16544 | 0.16544 | 0.98089 | -0.3671 | 0.98408 | -0.30473 | 45.4499
37 | 0.11659 | 0.029632 | -0.11648 | -0.029564 | 0.00010693 | 6.8314e-05 | 0.17543 | 0.17543 | 0.17543 | 0.98977 | -0.19487 | 0.98878 | -0.21394 | 48.194
38 | -0.14174 | -0.036186 | 0.14181 | 0.036232 | 7.305e-05 | 4.6527e-05 | 0.21209 | 0.21209 | 0.21209 | 0.99554 | -0.084685 | 0.9961 | -0.074027 | 29.1338
39 | -0.067398 | -0.016935 | 0.067503 | 0.017002 | 0.00010479 | 6.6715e-05 | 0.10156 | 0.10156 | 0.10156 | 0.98765 | -0.23663 | 0.98933 | -0.20411 | 27.9008
40 | -0.11304 | -0.028509 | 0.11326 | 0.028651 | 0.00022201 | 0.00014183 | 0.17099 | 0.17099 | 0.17099 | 0.98408 | -0.30473 | 0.98619 | -0.26379 | 46.9745
41 | -0.11326 | -0.028651 | 0.11345 | 0.028771 | 0.0001884 | 0.00012035 | 0.17099 | 0.17099 | 0.17099 | 0.98619 | -0.26379 | 0.98799 | -0.22919 | 46.9745
42 | -0.11416 | -0.028951 | 0.11425 | 0.029004 | 8.3762e-05 | 5.3511e-05 | 0.17207 | 0.17207 | 0.17207 | 0.98799 | -0.22919 | 0.98878 | -0.21394 | 47.2706
43 | 0.0022334 | 0.00055969 | -0.0022334 | -0.00055973 | 1.9213e-08 | -4.5877e-08 | 0.003361 | 0.003361 | 0.003361 | 0.98878 | -0.21394 | 0.98877 | -0.21412 | 0.92336
44 | 0.10345 | 0.026011 | -0.10344 | -0.026009 | 3.0569e-06 | 1.9521e-06 | 0.15562 | 0.15562 | 0.15562 | 0.98936 | -0.20349 | 0.98933 | -0.20411 | 42.7517
45 | -0.32299 | -0.082286 | 0.32315 | 0.082388 | 0.00015916 | 0.00010149 | 0.48325 | 0.48325 | 0.48325 | 0.99552 | -0.085023 | 0.99606 | -0.074815 | 33.1901
46 | 0.34036 | 0.086775 | -0.34018 | -0.086656 | 0.00018621 | 0.00011877 | 0.50869 | 0.50869 | 0.50869 | 0.99665 | -0.063475 | 0.99606 | -0.074815 | 34.9373
47 | -0.34301 | -0.087437 | 0.34329 | 0.087615 | 0.00027903 | 0.00017799 | 0.51264 | 0.51264 | 0.51264 | 0.99665 | -0.063475 | 0.99754 | -0.046636 | 35.2085
48 | -0.50462 | -0.12882 | 0.50506 | 0.1291 | 0.00044011 | 0.00028124 | 0.75357 | 0.75357 | 0.75357 | 0.99754 | -0.046636 | 0.99849 | -0.028604 | 51.7561
49 | 0.16133 | 0.041202 | -0.16124 | -0.041142 | 9.5491e-05 | 6.0199e-05 | 0.24093 | 0.24093 | 0.24093 | 0.99754 | -0.046636 | 0.99689 | -0.058889 | 16.5476
50 | -0.50506 | -0.1291 | 0.50576 | 0.12955 | 0.00069988 | 0.00044724 | 0.75357 | 0.75357 | 0.75357 | 0.99849 | -0.028604 | 1 | 0 | 51.756
51 | 0.15786 | 0.040295 | -0.15785 | -0.040293 | 1.8585e-06 | 1.1709e-06 | 0.23589 | 0.23589 | 0.23589 | 0.99689 | -0.058889 | 0.99688 | -0.059132 | 16.2009
52 | 0.012044 | 0.0030186 | -0.012043 | -0.0030184 | 5.2267e-07 | 2.7758e-07 | 0.017921 | 0.017921 | 0.017921 | 1 | 0 | 0.99995 | -0.00091096 | 4.9235
53 | 0.15438 | 0.039424 | -0.15438 | -0.039421 | 3.6092e-06 | 2.2722e-06 | 0.23071 | 0.23071 | 0.23071 | 0.99688 | -0.059132 | 0.99686 | -0.059616 | 15.8452
54 | 0.010247 | 0.0025681 | -0.010246 | -0.0025679 | 3.878e-07 | 1.8985e-07 | 0.015248 | 0.015248 | 0.015248 | 0.99995 | -0.00091096 | 0.99991 | -0.0017054 | 4.189
55 | 0.15258 | 0.038969 | -0.15251 | -0.038926 | 6.8613e-05 | 4.3179e-05 | 0.22801 | 0.22801 | 0.22801 | 0.99686 | -0.059616 | 0.99637 | -0.068923 | 15.6603
56 | -0.0037683 | -0.00094432 | 0.0037683 | 0.00094429 | 6.4476e-08 | -3.041e-08 | 0.0056086 | 0.0056086 | 0.0056086 | 0.99975 | -0.0047555 | 0.99977 | -0.0043963 | 1.5408
57 | 0.0015508 | 0.00038858 | -0.0015508 | -0.00038867 | 1.5228e-08 | -9.0199e-08 | 0.0023082 | 0.0023082 | 0.0023082 | 0.99975 | -0.0047555 | 0.99974 | -0.0049617 | 0.63412
58 | -0.0072635 | -0.0018203 | 0.0072645 | 0.0018206 | 9.3116e-07 | 3.1729e-07 | 0.010811 | 0.010811 | 0.010811 | 0.99977 | -0.0043963 | 0.99991 | -0.0017054 | 2.97
59 | 0.14981 | 0.038249 | -0.14979 | -0.038238 | 1.7575e-05 | 1.1053e-05 | 0.22398 | 0.22398 | 0.22398 | 0.99637 | -0.068923 | 0.99624 | -0.071351 | 15.3833
60 | 0.14489 | 0.03701 | -0.14487 | -0.036998 | 1.8741e-05 | 1.1773e-05 | 0.21666 | 0.21666 | 0.21666 | 0.99624 | -0.071351 | 0.9961 | -0.074027 | 14.8803

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52511 | 0.13398

## res_load
| p_mw | q_mvar
0 | 0.00064067 | 0.00016057
1 | 0.039278 | 0.009844
2 | 0.028224 | 0.0070735
3 | 0.0051057 | 0.0012796
4 | 0.0090356 | 0.0022645
5 | 0.046813 | 0.011732
6 | 0.0091376 | 0.0022901
7 | 0.025919 | 0.006496
8 | 0.0021145 | 0.00052995
9 | 0.046216 | 0.011583
10 | 0.016798 | 0.0042099
11 | 0.011065 | 0.0027731
12 | 0.018882 | 0.0047324
13 | 0.0016356 | 0.00040991
14 | 0.0025978 | 0.00065107
15 | 0.020684 | 0.0051838
16 | 0.018278 | 0.0045808
17 | 0.013786 | 0.0034551
18 | 0.011657 | 0.0029216
19 | 0.022169 | 0.0055562
20 | 0.0030059 | 0.00075335
21 | 0.0012195 | 0.00030564
22 | 0.0064924 | 0.0016272
23 | 0.004198 | 0.0010521
24 | 0.0036702 | 0.00091985
25 | 0.0007157 | 0.00017937
26 | 0.0022334 | 0.00055973
27 | 0.014859 | 0.0037241
28 | 0.019832 | 0.0049703
29 | 0.035941 | 0.0090076
30 | 0.017354 | 0.0043492
31 | 0.0026444 | 0.00066276
32 | 0.017029 | 0.0042678
33 | 0.003382 | 0.0008476
34 | 0.0056554 | 0.0014174
35 | 0.0034701 | 0.00086968
36 | 0.0017966 | 0.00045027
37 | 0.0018033 | 0.00045196
38 | 0.0022174 | 0.00055574
39 | 0.0034952 | 0.00087598
40 | 0.0015508 | 0.00038867
41 | 0.0029818 | 0.00074731
42 | 0.0027009 | 0.0006769
43 | 0.0049029 | 0.0012288
44 | 0.0030551 | 0.00076569

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1