## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1206-6_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1206-6_0_5_node_9 | 0.4 | n |  | TRUE
2 | bus_LV_1206-6_0_5_node_45 | 0.4 | n |  | TRUE
3 | bus_LV_1206-6_0_5_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_1206-6_0_5_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_1206-6_0_5_node_22 | 0.4 | n |  | TRUE
6 | bus_LV_1206-6_0_5_node_33 | 0.4 | n |  | TRUE
7 | bus_LV_1206-6_0_5_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_1206-6_0_5_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_1206-6_0_5_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1206-6_0_5_node_44 | 0.4 | n |  | TRUE
11 | bus_LV_1206-6_0_5_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_1206-6_0_5_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1206-6_0_5_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1206-6_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1206-6_0_5_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_1206-6_0_5_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_1206-6_0_5_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_1206-6_0_5_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_1206-6_0_5_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1206-6_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1206-6_0_5_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1206-6_0_5_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1206-6_0_5_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_1206-6_0_5_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_1206-6_0_5_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1206-6_0_5_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1206-6_0_5_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1206-6_0_5_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1206-6_0_5_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1206-6_0_5_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1206-6_0_5_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1206-6_0_5_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1206-6_0_5_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_1206-6_0_5_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_1206-6_0_5_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1206-6_0_5_node_43 | 0.4 | n |  | TRUE
37 | bus_LV_1206-6_0_5_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_1206-6_0_5_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_1206-6_0_5_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_1206-6_0_5_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_1206-6_0_5_node_42 | 0.4 | n |  | TRUE
42 | bus_MV_11_0_node_183 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1206-6_0_5_load_0 | 0 | 0.0018465 | 0.00046277 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1206-6_0_5_load_45 | 2 | 0.0071025 | 0.00178 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1206-6_0_5_load_8 | 3 | 0.054776 | 0.013728 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1206-6_0_5_load_33 | 6 | 0.068933 | 0.017276 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1206-6_0_5_load_24 | 7 | 0.045305 | 0.011354 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1206-6_0_5_load_21 | 8 | 0.070965 | 0.017786 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1206-6_0_5_load_12 | 9 | 0.026817 | 0.006721 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1206-6_0_5_load_44 | 10 | 0.048413 | 0.012133 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1206-6_0_5_load_4 | 11 | 0.01931 | 0.0048395 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1206-6_0_5_load_6 | 13 | 0.0063016 | 0.0015793 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1206-6_0_5_load_7 | 14 | 0.0084294 | 0.0021126 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1206-6_0_5_load_25 | 17 | 0.039212 | 0.0098274 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1206-6_0_5_load_11 | 20 | 0.051729 | 0.012964 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1206-6_0_5_load_13 | 21 | 0.0039397 | 0.00098738 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1206-6_0_5_load_14 | 22 | 0.0039288 | 0.00098466 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1206-6_0_5_load_32 | 23 | 0.0028466 | 0.00071344 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1206-6_0_5_load_28 | 24 | 0.010074 | 0.0025248 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1206-6_0_5_load_15 | 25 | 0.0039934 | 0.0010008 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1206-6_0_5_load_16 | 26 | 0.0028728 | 0.00072 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1206-6_0_5_load_18 | 28 | 0.0045626 | 0.0011435 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1206-6_0_5_load_20 | 30 | 0.0048007 | 0.0012032 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1206-6_0_5_load_30 | 31 | 0.0032911 | 0.00082482 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1206-6_0_5_load_26 | 32 | 0.004425 | 0.001109 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1206-6_0_5_load_29 | 35 | 0.0070944 | 0.001778 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1206-6_0_5_load_43 | 36 | 0.0067875 | 0.0017011 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1206-6_0_5_load_41 | 37 | 0.013151 | 0.003296 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1206-6_0_5_load_37 | 38 | 0.0090498 | 0.0022681 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1206-6_0_5_load_39 | 40 | 0.0017688 | 0.00044329 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1206-6_0_5_load_42 | 41 | 0.0019759 | 0.00049521 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1206-6_0_5_line_0 |  | 0 | 1 | 0.041105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1206-6_0_5_line_1 |  | 0 | 2 | 0.08994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1206-6_0_5_line_2 |  | 1 | 3 | 0.014935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1206-6_0_5_line_3 |  | 3 | 19 | 0.013792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1206-6_0_5_line_4 |  | 4 | 5 | 0.021393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1206-6_0_5_line_5 |  | 4 | 6 | 0.004015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1206-6_0_5_line_6 |  | 5 | 7 | 0.0085613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1206-6_0_5_line_7 |  | 5 | 8 | 0.022935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1206-6_0_5_line_8 |  | 6 | 9 | 0.0033477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1206-6_0_5_line_9 |  | 7 | 10 | 0.017157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1206-6_0_5_line_10 |  | 8 | 15 | 0.010502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1206-6_0_5_line_11 |  | 9 | 19 | 0.013418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1206-6_0_5_line_12 |  | 11 | 12 | 0.02614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1206-6_0_5_line_13 |  | 12 | 13 | 0.022686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1206-6_0_5_line_14 |  | 12 | 14 | 0.020889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1206-6_0_5_line_15 |  | 13 | 15 | 0.0097497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1206-6_0_5_line_16 |  | 14 | 16 | 0.030483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1206-6_0_5_line_17 |  | 15 | 17 | 0.013187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1206-6_0_5_line_18 |  | 16 | 18 | 0.004113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1206-6_0_5_line_19 |  | 17 | 36 | 0.00048443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1206-6_0_5_line_20 |  | 18 | 38 | 0.017687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1206-6_0_5_line_21 |  | 19 | 20 | 0.044323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1206-6_0_5_line_22 |  | 20 | 21 | 0.030754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1206-6_0_5_line_23 |  | 21 | 22 | 0.010777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1206-6_0_5_line_24 |  | 22 | 23 | 0.038067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1206-6_0_5_line_25 |  | 23 | 24 | 0.029433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1206-6_0_5_line_26 |  | 24 | 34 | 0.025948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1206-6_0_5_line_27 |  | 25 | 26 | 0.01363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1206-6_0_5_line_28 |  | 25 | 27 | 0.046383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1206-6_0_5_line_29 |  | 26 | 28 | 0.0050536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1206-6_0_5_line_30 |  | 27 | 29 | 0.006821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1206-6_0_5_line_31 |  | 27 | 30 | 0.040343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1206-6_0_5_line_32 |  | 29 | 31 | 0.019483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1206-6_0_5_line_33 |  | 29 | 32 | 0.015377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1206-6_0_5_line_34 |  | 30 | 33 | 0.03661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1206-6_0_5_line_35 |  | 32 | 34 | 0.047711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1206-6_0_5_line_36 |  | 33 | 35 | 0.050153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1206-6_0_5_line_37 |  | 36 | 37 | 0.019542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1206-6_0_5_line_38 |  | 37 | 41 | 0.00026037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1206-6_0_5_line_39 |  | 38 | 39 | 0.023617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1206-6_0_5_line_40 |  | 39 | 40 | 0.004601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1206-6_0_5_trafo_22 | 0.63 MVA 20/0.4 kV | 42 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2692382.6178 | 1186172.9705 | 2692412.1191 | 1186144.3475
1 | 2692412.1191 | 1186144.3475 | 2692499.8117 | 1186164.3289
2 | 2692382.6178 | 1186172.9705 | 2692373.1983 | 1186161.3802
3 | 2692364.4998 | 1186150.677 | 2692373.1983 | 1186161.3802
4 | 2692328.8095 | 1186130.0693 | 2692349.255 | 1186136.5552
5 | 2692349.255 | 1186136.5552 | 2692352.2005 | 1186139.2837
6 | 2692328.8095 | 1186130.0693 | 2692333.4414 | 1186122.8693
7 | 2692328.8095 | 1186130.0693 | 2692306.7024 | 1186123.9632
8 | 2692352.2005 | 1186139.2837 | 2692354.6564 | 1186141.5587
9 | 2692342.7241 | 1186108.4401 | 2692333.4414 | 1186122.8693
10 | 2692296.579 | 1186121.167 | 2692306.7024 | 1186123.9632
11 | 2692364.4998 | 1186150.677 | 2692354.6564 | 1186141.5587
12 | 2692265.0049 | 1186113.7427 | 2692258.7768 | 1186139.1297
13 | 2692265.0049 | 1186113.7427 | 2692287.0882 | 1186118.9354
14 | 2692265.0049 | 1186113.7427 | 2692244.7624 | 1186108.5874
15 | 2692296.579 | 1186121.167 | 2692287.0882 | 1186118.9354
16 | 2692214.6823 | 1186104.0951 | 2692235.6372 | 1186106.2635 | 2692244.7624 | 1186108.5874
17 | 2692296.579 | 1186121.167 | 2692300.5604 | 1186108.5955
18 | 2692214.6823 | 1186104.0951 | 2692215.3401 | 1186100.036
19 | 2692300.7067 | 1186108.1337 | 2692300.5604 | 1186108.5955
20 | 2692215.3401 | 1186100.036 | 2692218.8622 | 1186082.703
21 | 2692364.4998 | 1186150.677 | 2692354.7204 | 1186171.1392 | 2692354.9039 | 1186188.9311 | 2692353.3033 | 1186192.4334
22 | 2692336.9491 | 1186216.952 | 2692343.6168 | 1186213.6283 | 2692353.3033 | 1186192.4334
23 | 2692327.3039 | 1186221.7599 | 2692336.9491 | 1186216.952
24 | 2692327.3039 | 1186221.7599 | 2692310.7286 | 1186235.5354 | 2692300.0234 | 1186248.1099
25 | 2692300.0234 | 1186248.1099 | 2692299.4892 | 1186248.7373 | 2692281.8281 | 1186246.8084 | 2692271.6908 | 1186242.9605
26 | 2692251.1743 | 1186242.1111 | 2692253.4961 | 1186236.0541 | 2692271.6908 | 1186242.9605
27 | 2692180.1936 | 1186160.1863 | 2692179.9145 | 1186165.2878 | 2692180.6864 | 1186173.7734
28 | 2692184.8883 | 1186219.9656 | 2692180.6864 | 1186173.7734
29 | 2692180.1936 | 1186160.1863 | 2692180.4696 | 1186155.1402
30 | 2692184.8883 | 1186219.9656 | 2692191.5664 | 1186221.4471
31 | 2692184.8883 | 1186219.9656 | 2692176.9494 | 1186259.5193
32 | 2692196.93 | 1186202.7178 | 2692191.5664 | 1186221.4471
33 | 2692191.5664 | 1186221.4471 | 2692206.0955 | 1186226.4839
34 | 2692169.745 | 1186295.4138 | 2692176.9494 | 1186259.5193
35 | 2692251.1743 | 1186242.1111 | 2692206.0955 | 1186226.4839
36 | 2692169.745 | 1186295.4138 | 2692193.576 | 1186292.6565 | 2692205.9402 | 1186284.6973 | 2692216.9918 | 1186281.6718
37 | 2692306.6068 | 1186089.5036 | 2692300.7067 | 1186108.1337
38 | 2692306.6855 | 1186089.2554 | 2692306.6068 | 1186089.5036
39 | 2692223.5652 | 1186059.5591 | 2692218.8622 | 1186082.703
40 | 2692223.5652 | 1186059.5591 | 2692224.8183 | 1186055.1321

## bus_geodata
| x | y | coords
0 | 2692412.1191 | 1186144.3475
1 | 2692382.6178 | 1186172.9705
2 | 2692499.8117 | 1186164.3289
3 | 2692373.1983 | 1186161.3802
4 | 2692349.255 | 1186136.5552
5 | 2692328.8095 | 1186130.0693
6 | 2692352.2005 | 1186139.2837
7 | 2692333.4414 | 1186122.8693
8 | 2692306.7024 | 1186123.9632
9 | 2692354.6564 | 1186141.5587
10 | 2692342.7241 | 1186108.4401
11 | 2692258.7768 | 1186139.1297
12 | 2692265.0049 | 1186113.7427
13 | 2692287.0882 | 1186118.9354
14 | 2692244.7624 | 1186108.5874
15 | 2692296.579 | 1186121.167
16 | 2692214.6823 | 1186104.0951
17 | 2692300.5604 | 1186108.5955
18 | 2692215.3401 | 1186100.036
19 | 2692364.4998 | 1186150.677
20 | 2692353.3033 | 1186192.4334
21 | 2692336.9491 | 1186216.952
22 | 2692327.3039 | 1186221.7599
23 | 2692300.0234 | 1186248.1099
24 | 2692271.6908 | 1186242.9605
25 | 2692180.6864 | 1186173.7734
26 | 2692180.1936 | 1186160.1863
27 | 2692184.8883 | 1186219.9656
28 | 2692180.4696 | 1186155.1402
29 | 2692191.5664 | 1186221.4471
30 | 2692176.9494 | 1186259.5193
31 | 2692196.93 | 1186202.7178
32 | 2692206.0955 | 1186226.4839
33 | 2692169.745 | 1186295.4138
34 | 2692251.1743 | 1186242.1111
35 | 2692216.9918 | 1186281.6718
36 | 2692300.7067 | 1186108.1337
37 | 2692306.6068 | 1186089.5036
38 | 2692218.8622 | 1186082.703
39 | 2692223.5652 | 1186059.5591
40 | 2692224.8183 | 1186055.1321
41 | 2692306.6855 | 1186089.2554
42 | 2692349.255 | 1186136.5552

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99436 | -0.10815 | 0.0018465 | 0.00046277
1 | 0.9947 | -0.10166 | 0 | 0
2 | 0.99378 | -0.11942 | 0.0071025 | 0.00178
3 | 0.99482 | -0.099307 | 0.054776 | 0.013728
4 | 0.99743 | -0.049169 | 0 | 0
5 | 1 | 0 | -0.53765 | -0.13522
6 | 0.99695 | -0.058425 | 0.068933 | 0.017276
7 | 0.99927 | -0.013995 | 0.045305 | 0.011354
8 | 0.99815 | -0.035434 | 0.070965 | 0.017786
9 | 0.99665 | -0.064125 | 0.026817 | 0.006721
10 | 0.99852 | -0.028504 | 0.048413 | 0.012133
11 | 0.99549 | -0.086832 | 0.01931 | 0.0048395
12 | 0.99595 | -0.077958 | 0 | 0
13 | 0.99674 | -0.062599 | 0.0063016 | 0.0015793
14 | 0.99558 | -0.085027 | 0.0084294 | 0.0021126
15 | 0.99714 | -0.054928 | 0 | 0
16 | 0.99528 | -0.090829 | 0 | 0
17 | 0.99641 | -0.069068 | 0.039212 | 0.0098274
18 | 0.99524 | -0.091612 | 0 | 0
19 | 0.99562 | -0.08384 | 0 | 0
20 | 0.99141 | -0.1649 | 0.051729 | 0.012964
21 | 0.98994 | -0.19321 | 0.0039397 | 0.00098738
22 | 0.98947 | -0.2024 | 0.0039288 | 0.00098466
23 | 0.98793 | -0.23224 | 0.0028466 | 0.00071344
24 | 0.98681 | -0.25388 | 0.010074 | 0.0025248
25 | 0.98369 | -0.31468 | 0.0039934 | 0.0010008
26 | 0.9836 | -0.3165 | 0.0028728 | 0.00072
27 | 0.98418 | -0.30513 | 0 | 0
28 | 0.98358 | -0.31692 | 0.0045626 | 0.0011435
29 | 0.98433 | -0.30227 | 0 | 0
30 | 0.98374 | -0.31377 | 0.0048007 | 0.0012032
31 | 0.98427 | -0.30342 | 0.0032911 | 0.00082482
32 | 0.98471 | -0.29491 | 0.004425 | 0.001109
33 | 0.9835 | -0.31845 | 0 | 0
34 | 0.98607 | -0.26832 | 0 | 0
35 | 0.98317 | -0.32487 | 0.0070944 | 0.001778
36 | 0.9964 | -0.069255 | 0.0067875 | 0.0017011
37 | 0.99613 | -0.074446 | 0.013151 | 0.003296
38 | 0.99506 | -0.09498 | 0.0090498 | 0.0022681
39 | 0.99503 | -0.095715 | 0 | 0
40 | 0.99502 | -0.095859 | 0.0017688 | 0.00044329
41 | 0.99613 | -0.074455 | 0.0019759 | 0.00049521
42 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0089528 | -0.0022441 | 0.0089555 | 0.0022453 | 2.7667e-06 | 1.2373e-06 | 0.013397 | 0.013397 | 0.013397 | 0.99436 | -0.10815 | 0.9947 | -0.10166 | 3.6806
1 | 0.0071063 | 0.0017813 | -0.0071025 | -0.00178 | 3.8143e-06 | 1.2752e-06 | 0.010634 | 0.010635 | 0.010635 | 0.99436 | -0.10815 | 0.99378 | -0.11942 | 2.9216
2 | -0.0089555 | -0.0022453 | 0.0089565 | 0.0022458 | 1.0053e-06 | 4.4947e-07 | 0.013397 | 0.013397 | 0.013397 | 0.9947 | -0.10166 | 0.99482 | -0.099307 | 3.6806
3 | -0.063733 | -0.015974 | 0.06378 | 0.016004 | 4.7002e-05 | 2.9902e-05 | 0.09533 | 0.095329 | 0.09533 | 0.99482 | -0.099307 | 0.99562 | -0.08384 | 26.1894
4 | -0.26411 | -0.066601 | 0.26473 | 0.066999 | 0.00062316 | 0.00039826 | 0.39415 | 0.39415 | 0.39415 | 0.99743 | -0.049169 | 1 | 0 | 54.1417
5 | 0.26411 | 0.066601 | -0.26399 | -0.066526 | 0.00011695 | 7.4746e-05 | 0.39415 | 0.39415 | 0.39415 | 0.99743 | -0.049169 | 0.99695 | -0.058425 | 54.1417
6 | 0.093813 | 0.023549 | -0.093751 | -0.023509 | 6.2574e-05 | 3.9935e-05 | 0.13961 | 0.13961 | 0.13961 | 1 | 0 | 0.99927 | -0.013995 | 38.3541
7 | 0.17746 | 0.04467 | -0.17716 | -0.044479 | 0.00030001 | 0.00019141 | 0.26413 | 0.26413 | 0.26413 | 1 | 0 | 0.99815 | -0.035434 | 36.2818
8 | 0.19506 | 0.04925 | -0.195 | -0.049216 | 5.3251e-05 | 3.3993e-05 | 0.29126 | 0.29126 | 0.29126 | 0.99695 | -0.058425 | 0.99665 | -0.064125 | 40.0089
9 | 0.048446 | 0.012155 | -0.048413 | -0.012133 | 3.3489e-05 | 2.1208e-05 | 0.072146 | 0.072146 | 0.072146 | 0.99927 | -0.013995 | 0.99852 | -0.028504 | 19.8203
10 | 0.10619 | 0.026693 | -0.1061 | -0.02663 | 9.874e-05 | 6.3057e-05 | 0.15834 | 0.15834 | 0.15834 | 0.99815 | -0.035434 | 0.99714 | -0.054928 | 43.4996
11 | 0.16819 | 0.042495 | -0.16803 | -0.042393 | 0.00015878 | 0.00010127 | 0.25123 | 0.25123 | 0.25123 | 0.99665 | -0.064125 | 0.99562 | -0.08384 | 34.5091
12 | -0.01931 | -0.0048395 | 0.019318 | 0.0048443 | 8.1663e-06 | 4.8864e-06 | 0.028863 | 0.028863 | 0.028863 | 0.99549 | -0.086832 | 0.99595 | -0.077958 | 7.9295
13 | -0.038577 | -0.0096745 | 0.038606 | 0.0096923 | 2.8263e-05 | 1.7793e-05 | 0.05764 | 0.05764 | 0.05764 | 0.99595 | -0.077958 | 0.99674 | -0.062599 | 15.8351
14 | 0.01926 | 0.0048302 | -0.019253 | -0.0048263 | 6.4866e-06 | 3.8797e-06 | 0.028776 | 0.028777 | 0.028777 | 0.99595 | -0.077958 | 0.99558 | -0.085027 | 7.9056
15 | -0.044907 | -0.011272 | 0.044924 | 0.011282 | 1.6435e-05 | 1.0392e-05 | 0.067047 | 0.067047 | 0.067047 | 0.99674 | -0.062599 | 0.99714 | -0.054928 | 18.4195
16 | 0.010824 | 0.0027137 | -0.010821 | -0.0027122 | 2.9918e-06 | 1.5185e-06 | 0.016178 | 0.016178 | 0.016178 | 0.99558 | -0.085027 | 0.99528 | -0.090829 | 4.4445
17 | 0.061172 | 0.015348 | -0.06113 | -0.015322 | 4.1213e-05 | 2.6204e-05 | 0.091291 | 0.091291 | 0.091291 | 0.99714 | -0.054928 | 0.99641 | -0.069068 | 25.08
18 | 0.010821 | 0.0027122 | -0.01082 | -0.0027119 | 4.0368e-07 | 2.0491e-07 | 0.016178 | 0.016178 | 0.016178 | 0.99528 | -0.090829 | 0.99524 | -0.091612 | 4.4445
19 | 0.021919 | 0.0054946 | -0.021918 | -0.0054944 | 1.9464e-07 | 1.1826e-07 | 0.032733 | 0.032733 | 0.032733 | 0.99641 | -0.069068 | 0.9964 | -0.069255 | 8.9926
20 | 0.01082 | 0.0027119 | -0.010819 | -0.0027111 | 1.736e-06 | 8.8121e-07 | 0.016178 | 0.016178 | 0.016178 | 0.99524 | -0.091612 | 0.99506 | -0.09498 | 4.4445
21 | 0.10425 | 0.026389 | -0.10384 | -0.026132 | 0.00040395 | 0.00025796 | 0.1559 | 0.1559 | 0.1559 | 0.99562 | -0.08384 | 0.99141 | -0.1649 | 42.8289
22 | 0.052115 | 0.013167 | -0.052044 | -0.013122 | 7.0628e-05 | 4.4806e-05 | 0.078257 | 0.078257 | 0.078257 | 0.99141 | -0.1649 | 0.98994 | -0.19321 | 21.4992
23 | 0.048104 | 0.012135 | -0.048083 | -0.012121 | 2.1146e-05 | 1.3395e-05 | 0.072335 | 0.072335 | 0.072335 | 0.98994 | -0.19321 | 0.98947 | -0.2024 | 19.8723
24 | 0.044154 | 0.011137 | -0.044091 | -0.011097 | 6.2989e-05 | 3.9825e-05 | 0.066427 | 0.066427 | 0.066427 | 0.98947 | -0.2024 | 0.98793 | -0.23224 | 18.2492
25 | 0.041245 | 0.010384 | -0.041202 | -0.010357 | 4.2619e-05 | 2.69e-05 | 0.062139 | 0.06214 | 0.06214 | 0.98793 | -0.23224 | 0.98681 | -0.25388 | 17.0713
26 | 0.031128 | 0.0078319 | -0.031107 | -0.0078185 | 2.1448e-05 | 1.3396e-05 | 0.046949 | 0.046949 | 0.046949 | 0.98681 | -0.25388 | 0.98607 | -0.26832 | 12.8981
27 | 0.0074361 | 0.0018637 | -0.0074355 | -0.0018635 | 6.4671e-07 | 2.4088e-07 | 0.011248 | 0.011249 | 0.011249 | 0.98369 | -0.31468 | 0.9836 | -0.3165 | 3.0903
28 | -0.01143 | -0.0028646 | 0.011435 | 0.0028673 | 5.1992e-06 | 2.7384e-06 | 0.017289 | 0.017289 | 0.017289 | 0.98369 | -0.31468 | 0.98418 | -0.30513 | 4.7498
29 | 0.0045626 | 0.0011435 | -0.0045626 | -0.0011435 | 9.0292e-08 | -6.3553e-09 | 0.0069025 | 0.0069025 | 0.0069025 | 0.9836 | -0.3165 | 0.98358 | -0.31692 | 1.8963
30 | -0.023338 | -0.0058524 | 0.023342 | 0.0058544 | 3.1851e-06 | 1.9517e-06 | 0.035287 | 0.035287 | 0.035287 | 0.98418 | -0.30513 | 0.98433 | -0.30227 | 9.6943
31 | 0.011904 | 0.0029851 | -0.011899 | -0.0029825 | 4.9007e-06 | 2.624e-06 | 0.017998 | 0.017998 | 0.017998 | 0.98418 | -0.30513 | 0.98374 | -0.31377 | 4.9446
32 | 0.0032913 | 0.00082469 | -0.0032911 | -0.00082482 | 1.8086e-07 | -1.3189e-07 | 0.0049754 | 0.0049755 | 0.0049755 | 0.98433 | -0.30227 | 0.98427 | -0.30342 | 1.3669
33 | -0.026633 | -0.0066791 | 0.026642 | 0.0066848 | 9.348e-06 | 5.7872e-06 | 0.040263 | 0.040263 | 0.040263 | 0.98433 | -0.30227 | 0.98471 | -0.29491 | 11.0612
34 | 0.0070982 | 0.0017793 | -0.0070966 | -0.0017788 | 1.5827e-06 | 5.4823e-07 | 0.010737 | 0.010737 | 0.010737 | 0.98374 | -0.31377 | 0.9835 | -0.31845 | 2.9497
35 | -0.031067 | -0.0077938 | 0.031107 | 0.0078185 | 3.9437e-05 | 2.4632e-05 | 0.046949 | 0.046949 | 0.046949 | 0.98471 | -0.29491 | 0.98607 | -0.26832 | 12.8982
36 | 0.0070966 | 0.0017788 | -0.0070944 | -0.001778 | 2.1682e-06 | 7.5145e-07 | 0.010737 | 0.010737 | 0.010737 | 0.9835 | -0.31845 | 0.98317 | -0.32487 | 2.9498
37 | 0.015131 | 0.0037933 | -0.015127 | -0.0037912 | 3.7419e-06 | 2.1404e-06 | 0.022597 | 0.022597 | 0.022597 | 0.9964 | -0.069255 | 0.99613 | -0.074446 | 6.2079
38 | 0.0019759 | 0.00049521 | -0.0019759 | -0.00049521 | 8.5076e-10 | -2.8448e-09 | 0.0029516 | 0.0029516 | 0.0029516 | 0.99613 | -0.074446 | 0.99613 | -0.074455 | 0.81089
39 | 0.0017688 | 0.00044297 | -0.0017688 | -0.00044324 | 6.1961e-08 | -2.6712e-07 | 0.002645 | 0.0026451 | 0.0026451 | 0.99506 | -0.09498 | 0.99503 | -0.095715 | 0.72667
40 | 0.0017688 | 0.00044324 | -0.0017688 | -0.00044329 | 1.2072e-08 | -5.2036e-08 | 0.0026451 | 0.0026451 | 0.0026451 | 0.99503 | -0.095715 | 0.99502 | -0.095859 | 0.72668

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53765 | 0.13522

## res_load
| p_mw | q_mvar
0 | 0.0018465 | 0.00046277
1 | 0.0071025 | 0.00178
2 | 0.054776 | 0.013728
3 | 0.068933 | 0.017276
4 | 0.045305 | 0.011354
5 | 0.070965 | 0.017786
6 | 0.026817 | 0.006721
7 | 0.048413 | 0.012133
8 | 0.01931 | 0.0048395
9 | 0.0063016 | 0.0015793
10 | 0.0084294 | 0.0021126
11 | 0.039212 | 0.0098274
12 | 0.051729 | 0.012964
13 | 0.0039397 | 0.00098738
14 | 0.0039288 | 0.00098466
15 | 0.0028466 | 0.00071344
16 | 0.010074 | 0.0025248
17 | 0.0039934 | 0.0010008
18 | 0.0028728 | 0.00072
19 | 0.0045626 | 0.0011435
20 | 0.0048007 | 0.0012032
21 | 0.0032911 | 0.00082482
22 | 0.004425 | 0.001109
23 | 0.0070944 | 0.001778
24 | 0.0067875 | 0.0017011
25 | 0.013151 | 0.003296
26 | 0.0090498 | 0.0022681
27 | 0.0017688 | 0.00044329
28 | 0.0019759 | 0.00049521

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1