## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1214-1_1_10_node_141 | 0.4 | n |  | TRUE
1 | bus_LV_1214-1_1_10_node_40 | 0.4 | n |  | TRUE
2 | bus_LV_1214-1_1_10_node_26 | 0.4 | n |  | TRUE
3 | bus_LV_1214-1_1_10_node_27 | 0.4 | n |  | TRUE
4 | bus_LV_1214-1_1_10_node_30 | 0.4 | n |  | TRUE
5 | bus_LV_1214-1_1_10_node_28 | 0.4 | n |  | TRUE
6 | bus_LV_1214-1_1_10_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_1214-1_1_10_node_119 | 0.4 | n |  | TRUE
8 | bus_LV_1214-1_1_10_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_1214-1_1_10_node_118 | 0.4 | n |  | TRUE
10 | bus_LV_1214-1_1_10_node_115 | 0.4 | n |  | TRUE
11 | bus_LV_1214-1_1_10_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_1214-1_1_10_node_79 | 0.4 | n |  | TRUE
13 | bus_LV_1214-1_1_10_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_1214-1_1_10_node_33 | 0.4 | n |  | TRUE
15 | bus_LV_1214-1_1_10_node_59 | 0.4 | n |  | TRUE
16 | bus_LV_1214-1_1_10_node_70 | 0.4 | n |  | TRUE
17 | bus_LV_1214-1_1_10_node_85 | 0.4 | n |  | TRUE
18 | bus_LV_1214-1_1_10_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_1214-1_1_10_node_39 | 0.4 | n |  | TRUE
20 | bus_LV_1214-1_1_10_node_73 | 0.4 | n |  | TRUE
21 | bus_LV_1214-1_1_10_node_56 | 0.4 | n |  | TRUE
22 | bus_LV_1214-1_1_10_node_60 | 0.4 | n |  | TRUE
23 | bus_LV_1214-1_1_10_node_58 | 0.4 | n |  | TRUE
24 | bus_LV_1214-1_1_10_node_71 | 0.4 | n |  | TRUE
25 | bus_LV_1214-1_1_10_node_72 | 0.4 | n |  | TRUE
26 | bus_LV_1214-1_1_10_node_74 | 0.4 | n |  | TRUE
27 | bus_LV_1214-1_1_10_node_75 | 0.4 | n |  | TRUE
28 | bus_LV_1214-1_1_10_node_76 | 0.4 | n |  | TRUE
29 | bus_LV_1214-1_1_10_node_77 | 0.4 | n |  | TRUE
30 | bus_LV_1214-1_1_10_node_112 | 0.4 | n |  | TRUE
31 | bus_LV_1214-1_1_10_node_78 | 0.4 | n |  | TRUE
32 | bus_LV_1214-1_1_10_node_80 | 0.4 | n |  | TRUE
33 | bus_LV_1214-1_1_10_node_81 | 0.4 | n |  | TRUE
34 | bus_LV_1214-1_1_10_node_82 | 0.4 | n |  | TRUE
35 | bus_LV_1214-1_1_10_node_87 | 0.4 | n |  | TRUE
36 | bus_LV_1214-1_1_10_node_83 | 0.4 | n |  | TRUE
37 | bus_LV_1214-1_1_10_node_84 | 0.4 | n |  | TRUE
38 | bus_LV_1214-1_1_10_node_86 | 0.4 | n |  | TRUE
39 | bus_LV_1214-1_1_10_node_88 | 0.4 | n |  | TRUE
40 | bus_LV_1214-1_1_10_node_89 | 0.4 | n |  | TRUE
41 | bus_LV_1214-1_1_10_node_90 | 0.4 | n |  | TRUE
42 | bus_LV_1214-1_1_10_node_91 | 0.4 | n |  | TRUE
43 | bus_LV_1214-1_1_10_node_92 | 0.4 | n |  | TRUE
44 | bus_LV_1214-1_1_10_node_93 | 0.4 | n |  | TRUE
45 | bus_LV_1214-1_1_10_node_94 | 0.4 | n |  | TRUE
46 | bus_LV_1214-1_1_10_node_95 | 0.4 | n |  | TRUE
47 | bus_LV_1214-1_1_10_node_99 | 0.4 | n |  | TRUE
48 | bus_LV_1214-1_1_10_node_108 | 0.4 | n |  | TRUE
49 | bus_LV_1214-1_1_10_node_96 | 0.4 | n |  | TRUE
50 | bus_LV_1214-1_1_10_node_97 | 0.4 | n |  | TRUE
51 | bus_LV_1214-1_1_10_node_98 | 0.4 | n |  | TRUE
52 | bus_LV_1214-1_1_10_node_100 | 0.4 | n |  | TRUE
53 | bus_LV_1214-1_1_10_node_111 | 0.4 | n |  | TRUE
54 | bus_LV_1214-1_1_10_node_101 | 0.4 | n |  | TRUE
55 | bus_LV_1214-1_1_10_node_102 | 0.4 | n |  | TRUE
56 | bus_LV_1214-1_1_10_node_103 | 0.4 | n |  | TRUE
57 | bus_LV_1214-1_1_10_node_104 | 0.4 | n |  | TRUE
58 | bus_LV_1214-1_1_10_node_105 | 0.4 | n |  | TRUE
59 | bus_LV_1214-1_1_10_node_106 | 0.4 | n |  | TRUE
60 | bus_LV_1214-1_1_10_node_107 | 0.4 | n |  | TRUE
61 | bus_LV_1214-1_1_10_node_121 | 0.4 | n |  | TRUE
62 | bus_LV_1214-1_1_10_node_113 | 0.4 | n |  | TRUE
63 | bus_LV_1214-1_1_10_node_109 | 0.4 | n |  | TRUE
64 | bus_LV_1214-1_1_10_node_110 | 0.4 | n |  | TRUE
65 | bus_LV_1214-1_1_10_node_114 | 0.4 | n |  | TRUE
66 | bus_LV_1214-1_1_10_node_122 | 0.4 | n |  | TRUE
67 | bus_LV_1214-1_1_10_node_116 | 0.4 | n |  | TRUE
68 | bus_LV_1214-1_1_10_node_117 | 0.4 | n |  | TRUE
69 | bus_LV_1214-1_1_10_node_120 | 0.4 | n |  | TRUE
70 | bus_MV_12_0_node_6 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1214-1_1_10_load_141 | 0 | 0.0012857 | 0.00032222 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1214-1_1_10_load_40 | 1 | 0.0016198 | 0.00040595 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1214-1_1_10_load_26 | 2 | 0.044908 | 0.011255 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1214-1_1_10_load_119 | 7 | 0.00082103 | 0.00020577 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1214-1_1_10_load_118 | 9 | 0.0011236 | 0.00028159 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1214-1_1_10_load_115 | 10 | 0.0018783 | 0.00047075 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1214-1_1_10_load_79 | 12 | 0.021658 | 0.005428 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1214-1_1_10_load_59 | 15 | 0.00018617 | 4.6659e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1214-1_1_10_load_70 | 16 | 0.01994 | 0.0049976 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1214-1_1_10_load_85 | 17 | 0.023222 | 0.00582 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1214-1_1_10_load_60 | 22 | 0.00013419 | 3.3632e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1214-1_1_10_load_58 | 23 | 0.000265 | 6.6416e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1214-1_1_10_load_71 | 24 | 0.0012789 | 0.00032052 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1214-1_1_10_load_74 | 26 | 0.0010049 | 0.00025184 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1214-1_1_10_load_75 | 27 | 0.0039072 | 0.00097925 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1214-1_1_10_load_77 | 29 | 0.0026352 | 0.00066044 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1214-1_1_10_load_112 | 30 | 0.0013106 | 0.00032848 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1214-1_1_10_load_78 | 31 | 0.030958 | 0.0077587 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1214-1_1_10_load_80 | 32 | 0.0043742 | 0.0010963 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1214-1_1_10_load_81 | 33 | 0.0088339 | 0.002214 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1214-1_1_10_load_82 | 34 | 0.054498 | 0.013658 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1214-1_1_10_load_87 | 35 | 0.013299 | 0.0033332 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1214-1_1_10_load_83 | 36 | 0.029974 | 0.0075123 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1214-1_1_10_load_84 | 37 | 0.027783 | 0.0069632 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1214-1_1_10_load_86 | 38 | 0.0069397 | 0.0017393 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1214-1_1_10_load_88 | 39 | 0.0031742 | 0.00079552 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1214-1_1_10_load_90 | 41 | 0.0020137 | 0.00050467 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1214-1_1_10_load_92 | 43 | 0.0022137 | 0.00055481 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1214-1_1_10_load_93 | 44 | 0.0021398 | 0.0005363 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1214-1_1_10_load_94 | 45 | 0.003228 | 0.00080902 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1214-1_1_10_load_95 | 46 | 0.0055801 | 0.0013985 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1214-1_1_10_load_108 | 48 | 0.0018142 | 0.00045467 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1214-1_1_10_load_96 | 49 | 0.0013089 | 0.00032804 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1214-1_1_10_load_97 | 50 | 0.00095819 | 0.00024014 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1214-1_1_10_load_98 | 51 | 0.0045384 | 0.0011374 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1214-1_1_10_load_100 | 52 | 0.0025095 | 0.00062895 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1214-1_1_10_load_111 | 53 | 0.0034224 | 0.00085774 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1214-1_1_10_load_101 | 54 | 0.0014464 | 0.0003625 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1214-1_1_10_load_102 | 55 | 0.00089378 | 0.000224 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1214-1_1_10_load_103 | 56 | 0.0005774 | 0.00014471 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1214-1_1_10_load_104 | 57 | 0.00056464 | 0.00014151 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1214-1_1_10_load_105 | 58 | 0.0019762 | 0.00049529 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1214-1_1_10_load_106 | 59 | 0.0009619 | 0.00024108 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1214-1_1_10_load_107 | 60 | 0.00064802 | 0.00016241 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1214-1_1_10_load_109 | 63 | 0.00077084 | 0.00019319 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1214-1_1_10_load_122 | 66 | 0.0014411 | 0.00036117 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1214-1_1_10_load_116 | 67 | 0.0010341 | 0.00025916 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1214-1_1_10_load_117 | 68 | 0.0005587 | 0.00014002 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1214-1_1_10_load_120 | 69 | 0.0016987 | 0.00042573 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1214-1_1_10_line_0 |  | 0 | 1 | 0.027474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1214-1_1_10_line_1 |  | 1 | 19 | 0.12312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1214-1_1_10_line_2 |  | 2 | 3 | 0.14581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1214-1_1_10_line_3 |  | 3 | 4 | 0.19233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1214-1_1_10_line_4 |  | 4 | 11 | 0.37793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_1214-1_1_10_line_5 |  | 4 | 12 | 0.080867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1214-1_1_10_line_6 |  | 4 | 5 | 0.23197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_1214-1_1_10_line_7 |  | 5 | 6 | 0.10578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1214-1_1_10_line_8 |  | 5 | 7 | 0.11218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_1214-1_1_10_line_9 |  | 6 | 16 | 0.0078855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1214-1_1_10_line_10 |  | 7 | 68 | 0.058754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_1214-1_1_10_line_11 |  | 8 | 9 | 0.018156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_1214-1_1_10_line_12 |  | 8 | 10 | 0.022564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_1214-1_1_10_line_13 |  | 9 | 69 | 0.0024132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_1214-1_1_10_line_14 |  | 10 | 67 | 0.019873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_1214-1_1_10_line_15 |  | 11 | 17 | 0.054669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_1214-1_1_10_line_16 |  | 12 | 31 | 0.00042367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1214-1_1_10_line_17 |  | 13 | 14 | 0.036903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1214-1_1_10_line_18 |  | 13 | 15 | 0.71267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1214-1_1_10_line_19 |  | 14 | 16 | 0.016173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1214-1_1_10_line_20 |  | 15 | 23 | 0.069207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1214-1_1_10_line_21 |  | 17 | 36 | 0.053979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1214-1_1_10_line_22 |  | 18 | 19 | 0.063774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1214-1_1_10_line_23 |  | 18 | 20 | 0.29641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1214-1_1_10_line_24 |  | 20 | 24 | 0.036167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1214-1_1_10_line_25 |  | 21 | 22 | 0.012572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1214-1_1_10_line_26 |  | 21 | 23 | 0.15994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1214-1_1_10_line_27 |  | 24 | 25 | 0.027844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1214-1_1_10_line_28 |  | 25 | 26 | 0.12215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1214-1_1_10_line_29 |  | 25 | 27 | 0.079182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1214-1_1_10_line_30 |  | 26 | 28 | 0.022692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1214-1_1_10_line_31 |  | 27 | 29 | 0.013104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1214-1_1_10_line_32 |  | 28 | 30 | 0.023157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1214-1_1_10_line_33 |  | 30 | 53 | 0.015776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1214-1_1_10_line_34 |  | 31 | 32 | 0.026194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1214-1_1_10_line_35 |  | 32 | 33 | 0.0074808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1214-1_1_10_line_36 |  | 33 | 34 | 0.01615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1214-1_1_10_line_37 |  | 34 | 35 | 7.6743e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1214-1_1_10_line_38 |  | 36 | 37 | 0.1209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1214-1_1_10_line_39 |  | 37 | 38 | 0.020901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1214-1_1_10_line_40 |  | 39 | 40 | 0.042629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1214-1_1_10_line_41 |  | 39 | 41 | 0.0010419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1214-1_1_10_line_42 |  | 40 | 42 | 0.007413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1214-1_1_10_line_43 |  | 40 | 43 | 0.028471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1214-1_1_10_line_44 |  | 42 | 44 | 0.019211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1214-1_1_10_line_45 |  | 42 | 45 | 0.073732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1214-1_1_10_line_46 |  | 43 | 46 | 0.014077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1214-1_1_10_line_47 |  | 44 | 47 | 0.043517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1214-1_1_10_line_48 |  | 45 | 48 | 0.020515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1214-1_1_10_line_49 |  | 47 | 52 | 0.030425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1214-1_1_10_line_50 |  | 47 | 50 | 0.068039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1214-1_1_10_line_51 |  | 48 | 63 | 0.04555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1214-1_1_10_line_52 |  | 49 | 50 | 0.010289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1214-1_1_10_line_53 |  | 49 | 51 | 0.016798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1214-1_1_10_line_54 |  | 52 | 53 | 0.022766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1214-1_1_10_line_55 |  | 54 | 55 | 0.014037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_1214-1_1_10_line_56 |  | 54 | 56 | 0.011867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_1214-1_1_10_line_57 |  | 55 | 57 | 0.047357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_1214-1_1_10_line_58 |  | 56 | 58 | 0.017615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_1214-1_1_10_line_59 |  | 57 | 59 | 0.0014155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_1214-1_1_10_line_60 |  | 58 | 60 | 0.010844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_1214-1_1_10_line_61 |  | 59 | 61 | 0.21625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_1214-1_1_10_line_62 |  | 60 | 62 | 0.016023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_1214-1_1_10_line_63 |  | 61 | 64 | 0.27321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_1214-1_1_10_line_64 |  | 62 | 65 | 0.15873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_1214-1_1_10_line_65 |  | 63 | 64 | 0.071218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1214-1_1_10_line_66 |  | 65 | 66 | 0.044661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_1214-1_1_10_line_67 |  | 66 | 69 | 0.029411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_1214-1_1_10_line_68 |  | 67 | 68 | 0.019563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1214-1_1_10_trafo_119 | 0.63 MVA 20/0.4 kV | 70 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50
0 | 2687755.53 | 1195438.9853 | 2687731.5793 | 1195425.5241
1 | 2687823.9094 | 1195336.7229 | 2687822.7829 | 1195338.7076 | 2687807.2948 | 1195363.8741 | 2687785.025 | 1195398.3803 | 2687762.3358 | 1195430.8458 | 2687755.53 | 1195438.9853
2 | 2688836.1204 | 1193640.1545 | 2688810.9514 | 1193633.9881 | 2688775.9865 | 1193628.9216 | 2688775.0662 | 1193628.7856 | 2688748.8958 | 1193625.8845 | 2688721.962 | 1193624.6065 | 2688691.652 | 1193625.9274
3 | 2688771.6438 | 1193537.8993 | 2688760.2596 | 1193551.5057 | 2688759.0175 | 1193558.1582 | 2688760.7811 | 1193564.644 | 2688769.7018 | 1193574.238 | 2688737.8537 | 1193600.0154 | 2688747.0569 | 1193604.955 | 2688760.0732 | 1193608.7394 | 2688787.739 | 1193615.6542 | 2688814.8689 | 1193626.3192 | 2688836.1204 | 1193640.1545
4 | 2688735.2006 | 1193359.6344 | 2688805.0867 | 1193389.8681 | 2688851.7906 | 1193409.9074 | 2688870.5632 | 1193420.8154 | 2688873.6241 | 1193422.5842 | 2688877.1884 | 1193424.8497 | 2688913.2845 | 1193447.7338 | 2688890.8157 | 1193471.6485 | 2688869.8347 | 1193491.3828 | 2688808.6642 | 1193542.1513 | 2688797.6984 | 1193538.8643 | 2688787.592 | 1193537.2577 | 2688771.6438 | 1193537.8993
5 | 2688771.6438 | 1193537.8993 | 2688744.23 | 1193541.1948 | 2688725.071 | 1193546.5807 | 2688706.4663 | 1193552.6199 | 2688692.673 | 1193552.5026
6 | 2688657.8384 | 1193682.4484 | 2688648.5479 | 1193680.8319 | 2688646.4972 | 1193669.5388 | 2688642.9996 | 1193654.0438 | 2688667.3854 | 1193645.1772 | 2688669.6426 | 1193644.0878 | 2688693.8172 | 1193631.4825 | 2688713.484 | 1193618.5658 | 2688737.8537 | 1193600.0154 | 2688769.7018 | 1193574.238 | 2688760.7811 | 1193564.644 | 2688759.0175 | 1193558.1582 | 2688760.2596 | 1193551.5057 | 2688771.6438 | 1193537.8993
7 | 2688657.8384 | 1193682.4484 | 2688659.5034 | 1193682.7399 | 2688666.1103 | 1193683.8829 | 2688716.7281 | 1193691.2157 | 2688722.3402 | 1193693.6449 | 2688732.0791 | 1193694.323 | 2688744.2965 | 1193694.9157 | 2688762.4211 | 1193694.9957
8 | 2688657.8384 | 1193682.4484 | 2688654.1711 | 1193697.4258 | 2688639.2376 | 1193722.7206 | 2688614.8629 | 1193748.3425 | 2688605.4808 | 1193752.9176 | 2688590.5351 | 1193753.3299 | 2688583.9243 | 1193753.881
9 | 2688762.4211 | 1193694.9957 | 2688762.5142 | 1193693.863 | 2688762.4735 | 1193687.1141
10 | 2688525.5557 | 1193760.1724 | 2688540.9293 | 1193757.465 | 2688583.9243 | 1193753.881
11 | 2688467.988 | 1193748.9918 | 2688455.2202 | 1193761.9001
12 | 2688467.988 | 1193748.9918 | 2688487.5869 | 1193760.174
13 | 2688455.2202 | 1193761.9001 | 2688453.5232 | 1193763.6158
14 | 2688487.5869 | 1193760.174 | 2688494.8355 | 1193764.3097 | 2688501.5035 | 1193764.4083 | 2688506.2889 | 1193763.5656
15 | 2688735.2006 | 1193359.6344 | 2688720.6316 | 1193353.6034 | 2688710.3997 | 1193354.2632 | 2688705.4584 | 1193356.4358 | 2688702.0862 | 1193363.3124 | 2688697.8765 | 1193378.3244
16 | 2688692.673 | 1193552.5026 | 2688692.2494 | 1193552.499
17 | 2688762.1989 | 1193670.9438 | 2688786.0906 | 1193671.2317 | 2688799.065 | 1193672.1804
18 | 2688799.065 | 1193672.1804 | 2688810.9462 | 1193672.835 | 2688821.7928 | 1193675.909 | 2688829.8942 | 1193680.6101 | 2688837.3098 | 1193686.8241 | 2688851.5454 | 1193702.4121 | 2688864.5352 | 1193720.2719 | 2688875.3314 | 1193734.9415 | 2688884.9303 | 1193745.5464 | 2688896.5379 | 1193754.3356 | 2688917.3264 | 1193773.6345 | 2688924.3533 | 1193780.8658 | 2688935.9532 | 1193792.7235 | 2688943.9734 | 1193801.8374 | 2688949.8771 | 1193811.2979 | 2688954.2045 | 1193822.1913 | 2688957.2169 | 1193834.3772 | 2688960.0471 | 1193847.0273 | 2688963.2671 | 1193856.5257 | 2688968.3452 | 1193865.6292 | 2688973.7261 | 1193873.8478 | 2688979.0822 | 1193879.6311 | 2688989.7427 | 1193888.0172 | 2689003.0956 | 1193898.8339 | 2689011.5619 | 1193903.5628 | 2689022.2136 | 1193906.9012 | 2689030.659 | 1193909.9621 | 2689038.784 | 1193915.0863 | 2689045.8987 | 1193923.0528 | 2689049.4033 | 1193932.3664 | 2689051.8014 | 1193943.8205 | 2689053.9278 | 1193976.5842 | 2689057.1792 | 1193999.3137 | 2689058.5938 | 1194019.4809 | 2689060.0041 | 1194029.1859 | 2689061.2156 | 1194034.3294 | 2689063.0228 | 1194039.9043 | 2689068.2349 | 1194052.2676 | 2689073.2416 | 1194061.0255 | 2689079.5624 | 1194070.5923 | 2689087.2469 | 1194079.1789 | 2689096.8485 | 1194090.5624 | 2689101.2011 | 1194098.1988 | 2689104.5223 | 1194105.4862 | 2689105.9201 | 1194110.3991 | 2689110.9141 | 1194123.0704 | 2689119.2362 | 1194135.4022 | 2689147.0199 | 1194175.6306 | 2689158.7504 | 1194195.0067 | 2689179.5359 | 1194226.6144 | 2689182.6105 | 1194231.5372
19 | 2688762.1989 | 1193670.9438 | 2688762.4526 | 1193683.6334 | 2688762.4735 | 1193687.1141
20 | 2689182.6105 | 1194231.5372 | 2689186.7473 | 1194300.6206
21 | 2688683.3014 | 1193430.2988 | 2688697.8765 | 1193378.3244
22 | 2687823.9094 | 1195336.7229 | 2687830.2848 | 1195325.4983 | 2687837.6448 | 1195311.0527 | 2687846.7839 | 1195292.7308 | 2687852.6284 | 1195279.7862
23 | 2687952.5433 | 1195000.7213 | 2687852.6284 | 1195279.7862
24 | 2687952.5433 | 1195000.7213 | 2687950.1226 | 1194975.1583 | 2687949.1336 | 1194964.715
25 | 2689073.6487 | 1194382.114 | 2689082.8216 | 1194374.668 | 2689083.4159 | 1194374.1654
26 | 2689073.6487 | 1194382.114 | 2689068.9133 | 1194373.5825 | 2689066.9457 | 1194364.4585 | 2689068.0964 | 1194356.7929 | 2689072.7897 | 1194351.2704 | 2689082.7849 | 1194346.4384 | 2689106.0574 | 1194341.5596 | 2689124.2698 | 1194336.1385 | 2689149.7272 | 1194323.7654 | 2689186.7473 | 1194300.6206
27 | 2687949.3673 | 1194936.8784 | 2687949.0145 | 1194963.4568 | 2687949.1336 | 1194964.715
28 | 2687949.3673 | 1194936.8784 | 2687951.7035 | 1194921.5697 | 2687956.0659 | 1194905.8016 | 2687966.5605 | 1194871.5564 | 2687975.0279 | 1194859.0841 | 2687982.2552 | 1194849.5732 | 2687993.3678 | 1194840.1529 | 2688003.8802 | 1194832.6773
29 | 2687949.3673 | 1194936.8784 | 2687960.5381 | 1194935.4084 | 2687963.3746 | 1194934.2605 | 2687964.8677 | 1194932.7482 | 2687965.9498 | 1194930.6739 | 2687966.4378 | 1194928.0683 | 2687967.7217 | 1194915.9128 | 2687968.5678 | 1194912.2673 | 2687969.6823 | 1194909.0372 | 2687971.3978 | 1194905.8715 | 2687974.8971 | 1194900.5974 | 2687976.1402 | 1194899.5039 | 2687977.9812 | 1194898.686 | 2687988.052 | 1194896.3548 | 2687990.0694 | 1194895.4617 | 2687991.9814 | 1194893.9667 | 2687997.0244 | 1194885.5802
30 | 2688016.3258 | 1194814.5076 | 2688013.4603 | 1194823.3155 | 2688005.8364 | 1194831.2862 | 2688003.8802 | 1194832.6773
31 | 2688003.7775 | 1194874.3499 | 2687997.0244 | 1194885.5802
32 | 2688016.3258 | 1194814.5076 | 2688019.8009 | 1194808.2992 | 2688022.4592 | 1194801.6675 | 2688023.6922 | 1194797.116 | 2688024.5678 | 1194793.0263 | 2688024.5678 | 1194793.0263
33 | 2688024.5678 | 1194793.0263 | 2688025.1607 | 1194787.954 | 2688025.3577 | 1194783.8877 | 2688025.1829 | 1194777.6478 | 2688025.1589 | 1194777.2932
34 | 2688692.2494 | 1193552.499 | 2688680.1263 | 1193552.396 | 2688666.9353 | 1193547.5005
35 | 2688666.9353 | 1193547.5005 | 2688659.9219 | 1193544.8976
36 | 2688644.7808 | 1193539.2784 | 2688659.9219 | 1193544.8976
37 | 2688644.7808 | 1193539.2784 | 2688644.7088 | 1193539.2517
38 | 2688683.3014 | 1193430.2988 | 2688683.3014 | 1193430.2988 | 2688677.2237 | 1193430.4644 | 2688674.0874 | 1193424.5252 | 2688675.1948 | 1193420.7837 | 2688681.6578 | 1193415.1981 | 2688681.4881 | 1193410.1925 | 2688678.8429 | 1193407.118 | 2688671.7384 | 1193406.1009 | 2688642.9919 | 1193415.9591 | 2688639.2188 | 1193419.0385 | 2688622.8897 | 1193447.9372 | 2688616.0392 | 1193456.5022
39 | 2688602.9841 | 1193472.8249 | 2688616.0392 | 1193456.5022
40 | 2687985.0259 | 1194669.5773 | 2687981.8132 | 1194661.5805 | 2687980.487 | 1194656.9247 | 2687979.2445 | 1194652.2813 | 2687978.8321 | 1194648.7174 | 2687978.7369 | 1194644.3132 | 2687979.1072 | 1194640.3828 | 2687979.9593 | 1194635.3032 | 2687982.161 | 1194628.3727
41 | 2687982.4765 | 1194627.3797 | 2687982.161 | 1194628.3727
42 | 2687978.3551 | 1194672.848 | 2687985.0259 | 1194669.5773
43 | 2687985.0259 | 1194669.5773 | 2687989.2477 | 1194672.1855 | 2688009.7172 | 1194683.7453
44 | 2687978.3551 | 1194672.848 | 2687980.2639 | 1194676.2337 | 2687985.2689 | 1194684.6571 | 2687988.3218 | 1194689.2633
45 | 2687978.3551 | 1194672.848 | 2687974.7476 | 1194664.7453 | 2687972.8003 | 1194659.8358 | 2687971.3146 | 1194654.1103 | 2687970.2815 | 1194648.7028 | 2687969.7033 | 1194643.969 | 2687969.6067 | 1194639.1423 | 2687969.8104 | 1194634.6202 | 2687970.2682 | 1194629.924 | 2687971.4351 | 1194624.6823 | 2687973.9885 | 1194614.3021 | 2687977.8927 | 1194601.6308
46 | 2688021.9747 | 1194690.6675 | 2688009.7172 | 1194683.7453
47 | 2688011.0697 | 1194726.3409 | 2688004.6615 | 1194714.8838 | 2687993.3059 | 1194696.783 | 2687988.3218 | 1194689.2633
48 | 2687977.8927 | 1194601.6308 | 2687983.9336 | 1194582.0249
49 | 2688011.0697 | 1194726.3409 | 2688014.9207 | 1194734.9808 | 2688018.1721 | 1194743.9677 | 2688020.6248 | 1194751.2973 | 2688021.5462 | 1194754.8597
50 | 2688011.0697 | 1194726.3409 | 2688017.1705 | 1194725.5524 | 2688022.903 | 1194725.4478 | 2688025.8652 | 1194726.1251 | 2688028.5818 | 1194727.4437 | 2688031.109 | 1194729.1931 | 2688033.3874 | 1194731.2835 | 2688042.3096 | 1194741.7659 | 2688046.036 | 1194744.8894 | 2688049.954 | 1194746.9039 | 2688056.8254 | 1194748.6395 | 2688061.6907 | 1194748.4221 | 2688065.9757 | 1194747.2511 | 2688069.335 | 1194745.2881 | 2688069.7937 | 1194744.8915
51 | 2687983.9336 | 1194582.0249 | 2687984.833 | 1194579.1059 | 2687998.8636 | 1194538.9936
52 | 2688076.6844 | 1194737.3357 | 2688073.4185 | 1194741.7571 | 2688069.7937 | 1194744.8915
53 | 2688081.3336 | 1194721.2717 | 2688078.8435 | 1194732.52 | 2688076.6844 | 1194737.3357
54 | 2688021.5462 | 1194754.8597 | 2688022.2761 | 1194757.6812 | 2688023.8459 | 1194765.4537 | 2688024.7762 | 1194771.6269 | 2688025.1589 | 1194777.2932
55 | 2688296.155 | 1194004.5098 | 2688290.6897 | 1194017.4393
56 | 2688296.155 | 1194004.5098 | 2688300.7753 | 1193993.579
57 | 2688272.0846 | 1194060.9886 | 2688282.4259 | 1194036.9896 | 2688290.6897 | 1194017.4393
58 | 2688307.6336 | 1193977.3538 | 2688300.7753 | 1193993.579
59 | 2688272.0846 | 1194060.9886 | 2688271.5245 | 1194062.2885
60 | 2688307.6336 | 1193977.3538 | 2688311.8557 | 1193967.3653
61 | 2688156.3334 | 1194237.3355 | 2688162.0067 | 1194220.5973 | 2688171.1806 | 1194188.2119 | 2688177.734 | 1194167.6177 | 2688180.8539 | 1194160.7259 | 2688184.7907 | 1194154.2465 | 2688190.4366 | 1194146.1023 | 2688197.8139 | 1194137.8725 | 2688204.9781 | 1194131.6853 | 2688243.3464 | 1194102.7327 | 2688251.7841 | 1194093.9293 | 2688254.448 | 1194090.5664 | 2688260.0155 | 1194083.6108 | 2688261.6432 | 1194081.2556 | 2688263.9166 | 1194077.4978 | 2688265.9094 | 1194073.647 | 2688270.5244 | 1194064.6093 | 2688271.5245 | 1194062.2885
62 | 2688318.9102 | 1193952.9858 | 2688313.1247 | 1193964.3632 | 2688311.8557 | 1193967.3653
63 | 2688156.3334 | 1194237.3355 | 2688153.4842 | 1194246.0324 | 2688149.7881 | 1194256.8626 | 2688144.9221 | 1194267.442 | 2688139.8547 | 1194277.7184 | 2688130.3683 | 1194292.0322 | 2688118.0255 | 1194308.3051 | 2688108.346 | 1194319.6921 | 2688090.7922 | 1194341.5252 | 2688081.377 | 1194352.5714 | 2688070.8199 | 1194368.704 | 2688049.5676 | 1194403.6356 | 2688034.0031 | 1194430.1457 | 2688022.214 | 1194453.3647 | 2688016.2003 | 1194469.9646
64 | 2688318.9102 | 1193952.9858 | 2688323.5084 | 1193944.5816 | 2688335.7827 | 1193925.8065 | 2688359.9768 | 1193889.0626 | 2688370.8849 | 1193872.4909 | 2688374.9021 | 1193866.2796 | 2688385.0502 | 1193850.5974 | 2688405.9181 | 1193820.2753
65 | 2688016.2003 | 1194469.9646 | 2688007.2892 | 1194506.3344 | 2688003.5195 | 1194523.7455 | 2688001.6439 | 1194531.0448 | 2687998.8636 | 1194538.9936
66 | 2688405.9181 | 1193820.2753 | 2688411.5044 | 1193812.5974 | 2688426.0689 | 1193794.1342 | 2688433.6483 | 1193785.2874
67 | 2688433.6483 | 1193785.2874 | 2688438.3158 | 1193779.8394 | 2688452.543 | 1193764.6067 | 2688453.5232 | 1193763.6158
68 | 2688506.2889 | 1193763.5656 | 2688525.5557 | 1193760.1724

## bus_geodata
| x | y | coords
0 | 2687731.5793 | 1195425.5241
1 | 2687755.53 | 1195438.9853
2 | 2688691.652 | 1193625.9274
3 | 2688836.1204 | 1193640.1545
4 | 2688771.6438 | 1193537.8993
5 | 2688657.8384 | 1193682.4484
6 | 2688762.4211 | 1193694.9957
7 | 2688583.9243 | 1193753.881
8 | 2688467.988 | 1193748.9918
9 | 2688455.2202 | 1193761.9001
10 | 2688487.5869 | 1193760.174
11 | 2688735.2006 | 1193359.6344
12 | 2688692.673 | 1193552.5026
13 | 2688799.065 | 1193672.1804
14 | 2688762.1989 | 1193670.9438
15 | 2689182.6105 | 1194231.5372
16 | 2688762.4735 | 1193687.1141
17 | 2688697.8765 | 1193378.3244
18 | 2687852.6284 | 1195279.7862
19 | 2687823.9094 | 1195336.7229
20 | 2687952.5433 | 1195000.7213
21 | 2689073.6487 | 1194382.114
22 | 2689083.4159 | 1194374.1654
23 | 2689186.7473 | 1194300.6206
24 | 2687949.1336 | 1194964.715
25 | 2687949.3674 | 1194936.8784
26 | 2688003.8802 | 1194832.6773
27 | 2687997.0244 | 1194885.5802
28 | 2688016.3258 | 1194814.5076
29 | 2688003.7775 | 1194874.3499
30 | 2688024.5678 | 1194793.0263
31 | 2688692.2494 | 1193552.499
32 | 2688666.9353 | 1193547.5005
33 | 2688659.9219 | 1193544.8976
34 | 2688644.7808 | 1193539.2784
35 | 2688644.7088 | 1193539.2517
36 | 2688683.3014 | 1193430.2988
37 | 2688616.0392 | 1193456.5022
38 | 2688602.9841 | 1193472.8249
39 | 2687982.161 | 1194628.3727
40 | 2687985.0259 | 1194669.5773
41 | 2687982.4765 | 1194627.3797
42 | 2687978.3551 | 1194672.848
43 | 2688009.7172 | 1194683.7453
44 | 2687988.3218 | 1194689.2633
45 | 2687977.8927 | 1194601.6308
46 | 2688021.9747 | 1194690.6675
47 | 2688011.0697 | 1194726.3409
48 | 2687983.9336 | 1194582.0249
49 | 2688076.6844 | 1194737.3357
50 | 2688069.7937 | 1194744.8915
51 | 2688081.3336 | 1194721.2717
52 | 2688021.5462 | 1194754.8597
53 | 2688025.1589 | 1194777.2932
54 | 2688296.155 | 1194004.5098
55 | 2688290.6897 | 1194017.4393
56 | 2688300.7753 | 1193993.579
57 | 2688272.0846 | 1194060.9886
58 | 2688307.6336 | 1193977.3538
59 | 2688271.5245 | 1194062.2885
60 | 2688311.8557 | 1193967.3653
61 | 2688156.3334 | 1194237.3355
62 | 2688318.9102 | 1193952.9858
63 | 2687998.8636 | 1194538.9936
64 | 2688016.2003 | 1194469.9646
65 | 2688405.9181 | 1193820.2753
66 | 2688433.6483 | 1193785.2874
67 | 2688506.2889 | 1193763.5656
68 | 2688525.5557 | 1193760.1724
69 | 2688453.5232 | 1193763.6158
70 | 2688657.8384 | 1193682.4484

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97262 | -0.52904 | 0.0012857 | 0.00032222
1 | 0.97265 | -0.52839 | 0.0016198 | 0.00040595
2 | 0.97234 | -0.53198 | 0.044908 | 0.011255
3 | 0.97845 | -0.41201 | 0 | 0
4 | 0.98248 | -0.3337 | 0 | 0
5 | 0.994 | -0.11297 | 0 | 0
6 | 0.99202 | -0.15142 | 0 | 0
7 | 1 | 0 | -0.35782 | -0.09211
8 | 0.99865 | -0.02558 | 0 | 0
9 | 0.99845 | -0.029274 | 0.0011236 | 0.00028159
10 | 0.99889 | -0.02099 | 0.0018783 | 0.00047075
11 | 0.97628 | -0.45452 | 0 | 0
12 | 0.97746 | -0.43175 | 0.021658 | 0.005428
13 | 0.99184 | -0.15487 | 0 | 0
14 | 0.99186 | -0.15446 | 0 | 0
15 | 0.99146 | -0.16251 | 0.00018617 | 4.6659e-05
16 | 0.99187 | -0.15429 | 0.01994 | 0.0049976
17 | 0.97539 | -0.47212 | 0.023222 | 0.00582
18 | 0.97316 | -0.51838 | 0 | 0
19 | 0.97299 | -0.52179 | 0 | 0
20 | 0.97396 | -0.50248 | 0 | 0
21 | 0.99142 | -0.1634 | 0 | 0
22 | 0.99142 | -0.16343 | 0.00013419 | 3.3632e-05
23 | 0.99144 | -0.16301 | 0.000265 | 6.6416e-05
24 | 0.97406 | -0.50053 | 0.0012789 | 0.00032052
25 | 0.97417 | -0.49838 | 0 | 0
26 | 0.97539 | -0.4743 | 0.0010049 | 0.00025184
27 | 0.97368 | -0.50791 | 0.0039072 | 0.00097925
28 | 0.97563 | -0.46941 | 0 | 0
29 | 0.97365 | -0.50854 | 0.0026352 | 0.00066044
30 | 0.97589 | -0.46443 | 0.0013106 | 0.00032848
31 | 0.97741 | -0.43262 | 0.030958 | 0.0077587
32 | 0.97544 | -0.47141 | 0.0043742 | 0.0010963
33 | 0.9749 | -0.48192 | 0.0088339 | 0.002214
34 | 0.97388 | -0.50202 | 0.054498 | 0.013658
35 | 0.97388 | -0.50204 | 0.013299 | 0.0033332
36 | 0.9743 | -0.49347 | 0.029974 | 0.0075123
37 | 0.97038 | -0.57087 | 0.027783 | 0.0069632
38 | 0.97024 | -0.57355 | 0.0069397 | 0.0017393
39 | 0.97821 | -0.41873 | 0.0031742 | 0.00079552
40 | 0.97842 | -0.41471 | 0 | 0
41 | 0.97821 | -0.41877 | 0.0020137 | 0.00050467
42 | 0.97851 | -0.41295 | 0 | 0
43 | 0.97821 | -0.41875 | 0.0022137 | 0.00055481
44 | 0.97801 | -0.42273 | 0.0021398 | 0.0005363
45 | 0.98131 | -0.35816 | 0.003228 | 0.00080902
46 | 0.97814 | -0.42018 | 0.0055801 | 0.0013985
47 | 0.97696 | -0.44322 | 0 | 0
48 | 0.98215 | -0.34178 | 0.0018142 | 0.00045467
49 | 0.97648 | -0.45279 | 0.0013089 | 0.00032804
50 | 0.97653 | -0.45169 | 0.00095819 | 0.00024014
51 | 0.97641 | -0.45418 | 0.0045384 | 0.0011374
52 | 0.97643 | -0.45379 | 0.0025095 | 0.00062895
53 | 0.97608 | -0.46065 | 0.0034224 | 0.00085774
54 | 0.99555 | -0.084257 | 0.0014464 | 0.0003625
55 | 0.99542 | -0.086688 | 0.00089378 | 0.000224
56 | 0.99566 | -0.082141 | 0.0005774 | 0.00014471
57 | 0.995 | -0.094746 | 0.00056464 | 0.00014151
58 | 0.99583 | -0.078966 | 0.0019762 | 0.00049529
59 | 0.99499 | -0.094984 | 0.0009619 | 0.00024108
60 | 0.99594 | -0.076937 | 0.00064802 | 0.00016241
61 | 0.99311 | -0.13068 | 0 | 0
62 | 0.9961 | -0.073902 | 0 | 0
63 | 0.98409 | -0.304 | 0.00077084 | 0.00019319
64 | 0.98718 | -0.24426 | 0 | 0
65 | 0.99768 | -0.043884 | 0 | 0
66 | 0.99813 | -0.035453 | 0.0014411 | 0.00036117
67 | 0.99911 | -0.016819 | 0.0010341 | 0.00025916
68 | 0.99933 | -0.012644 | 0.0005587 | 0.00014002
69 | 0.99843 | -0.029756 | 0.0016987 | 0.00042573
70 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0012857 | -0.00032222 | 0.0012857 | 0.0003219 | 3.9858e-08 | -3.1548e-07 | 0.001967 | 0.0019668 | 0.001967 | 0.97262 | -0.52904 | 0.97265 | -0.52839 | 0.54037
1 | -0.0029055 | -0.00072786 | 0.0029064 | 0.00072691 | 9.1205e-07 | -9.4491e-07 | 0.0044449 | 0.0044443 | 0.0044449 | 0.97265 | -0.52839 | 0.97299 | -0.52179 | 1.2211
2 | -0.044908 | -0.011255 | 0.045167 | 0.011419 | 0.00025825 | 0.00016346 | 0.068725 | 0.068725 | 0.068725 | 0.97234 | -0.53198 | 0.97845 | -0.41201 | 18.8805
3 | -0.045167 | -0.011419 | 0.045337 | 0.011523 | 0.00017032 | 0.00010415 | 0.068725 | 0.068723 | 0.068725 | 0.97845 | -0.41201 | 0.98248 | -0.3337 | 9.4402
4 | 0.088702 | 0.022504 | -0.088189 | -0.0222 | 0.00051235 | 0.00030413 | 0.13444 | 0.13445 | 0.13445 | 0.98248 | -0.3337 | 0.97628 | -0.45452 | 7.3874
5 | 0.13451 | 0.034055 | -0.13388 | -0.033653 | 0.00063005 | 0.00040119 | 0.20384 | 0.20385 | 0.20385 | 0.98248 | -0.3337 | 0.97746 | -0.43175 | 28.0007
6 | -0.26855 | -0.068082 | 0.27143 | 0.069911 | 0.002882 | 0.0018296 | 0.40701 | 0.407 | 0.40701 | 0.98248 | -0.3337 | 0.994 | -0.11297 | 22.3631
7 | 0.020566 | 0.0051558 | -0.020529 | -0.0051331 | 3.7601e-05 | 2.2696e-05 | 0.030788 | 0.030789 | 0.030789 | 0.994 | -0.11297 | 0.99202 | -0.15142 | 8.4585
8 | -0.292 | -0.075067 | 0.29361 | 0.076092 | 0.0016126 | 0.0010247 | 0.43779 | 0.43779 | 0.43779 | 0.994 | -0.11297 | 1 | 0 | 24.0545
9 | 0.020529 | 0.0051331 | -0.020526 | -0.0051314 | 2.8032e-06 | 1.6922e-06 | 0.030789 | 0.030789 | 0.030789 | 0.99202 | -0.15142 | 0.99187 | -0.15429 | 8.4585
10 | 0.062565 | 0.016018 | -0.062527 | -0.015998 | 3.8292e-05 | 2.0655e-05 | 0.093218 | 0.093219 | 0.093219 | 1 | 0 | 0.99933 | -0.012644 | 5.1219
11 | 0.059018 | 0.015107 | -0.059007 | -0.015102 | 1.0557e-05 | 5.5691e-06 | 0.088051 | 0.088051 | 0.088051 | 0.99865 | -0.02558 | 0.99845 | -0.029274 | 4.838
12 | -0.059018 | -0.015107 | 0.059031 | 0.015114 | 1.3121e-05 | 6.9206e-06 | 0.088051 | 0.08805 | 0.088051 | 0.99865 | -0.02558 | 0.99889 | -0.02099 | 4.838
13 | 0.057884 | 0.01482 | -0.057883 | -0.01482 | 1.3504e-06 | 7.0642e-07 | 0.086377 | 0.086377 | 0.086377 | 0.99845 | -0.029274 | 0.99843 | -0.029756 | 4.746
14 | -0.060909 | -0.015585 | 0.060922 | 0.015592 | 1.2302e-05 | 6.572e-06 | 0.090848 | 0.090848 | 0.090848 | 0.99889 | -0.02099 | 0.99911 | -0.016819 | 4.9917
15 | 0.088189 | 0.0222 | -0.088115 | -0.022156 | 7.4119e-05 | 4.4021e-05 | 0.13445 | 0.13445 | 0.13445 | 0.97628 | -0.45452 | 0.97539 | -0.47212 | 7.3874
16 | 0.11222 | 0.028225 | -0.11222 | -0.028222 | 4.6389e-06 | 2.9636e-06 | 0.17087 | 0.17087 | 0.17087 | 0.97746 | -0.43175 | 0.97741 | -0.43262 | 46.9436
17 | -0.00058558 | -0.00013453 | 0.00058559 | 0.00013406 | 1.0578e-08 | -4.6951e-07 | 0.00087437 | 0.00087421 | 0.00087437 | 0.99184 | -0.15487 | 0.99186 | -0.15446 | 0.24021
18 | 0.00058558 | 0.00013453 | -0.00058538 | -0.0001436 | 2.0503e-07 | -9.0631e-06 | 0.00087437 | 0.00087746 | 0.00087746 | 0.99184 | -0.15487 | 0.99146 | -0.16251 | 0.24106
19 | -0.00058559 | -0.00013406 | 0.0005856 | 0.00013386 | 4.6347e-09 | -2.0577e-07 | 0.00087421 | 0.00087414 | 0.00087421 | 0.99186 | -0.15446 | 0.99187 | -0.15429 | 0.24017
20 | 0.00039921 | 9.6938e-05 | -0.0003992 | -9.7824e-05 | 9.2872e-09 | -8.8655e-07 | 0.00059805 | 0.00059836 | 0.00059836 | 0.99146 | -0.16251 | 0.99144 | -0.16301 | 0.16439
21 | 0.064893 | 0.016336 | -0.064827 | -0.016296 | 6.6165e-05 | 4.0326e-05 | 0.099024 | 0.099025 | 0.099025 | 0.97539 | -0.47212 | 0.9743 | -0.49347 | 9.0682
22 | 0.0029069 | 0.00072642 | -0.0029064 | -0.00072691 | 4.7234e-07 | -4.8992e-07 | 0.004444 | 0.0044443 | 0.0044443 | 0.97316 | -0.51838 | 0.97299 | -0.52179 | 1.221
23 | -0.0029069 | -0.00072642 | 0.0029091 | 0.00072414 | 2.1946e-06 | -2.2813e-06 | 0.004444 | 0.0044427 | 0.004444 | 0.97316 | -0.51838 | 0.97396 | -0.50248 | 1.2209
24 | -0.0029091 | -0.00072414 | 0.0029093 | 0.00072386 | 2.6769e-07 | -2.7883e-07 | 0.0044427 | 0.0044425 | 0.0044427 | 0.97396 | -0.50248 | 0.97406 | -0.50053 | 1.2205
25 | 0.00013419 | 3.347e-05 | -0.00013419 | -3.3632e-05 | 1.912e-10 | -1.6199e-07 | 0.00020135 | 0.00020141 | 0.00020141 | 0.99142 | -0.1634 | 0.99142 | -0.16343 | 0.055332
26 | -0.00013419 | -3.347e-05 | 0.0001342 | 3.1409e-05 | 2.423e-09 | -2.0609e-06 | 0.00020135 | 0.00020065 | 0.00020135 | 0.99142 | -0.1634 | 0.99144 | -0.16301 | 0.055317
27 | -0.0041882 | -0.0010444 | 0.0041887 | 0.0010443 | 4.2718e-07 | -7.3236e-08 | 0.0063962 | 0.0063961 | 0.0063962 | 0.97406 | -0.50053 | 0.97417 | -0.49838 | 1.7572
28 | -0.010734 | -0.0026848 | 0.010746 | 0.0026912 | 1.2311e-05 | 6.3564e-06 | 0.016394 | 0.016394 | 0.016394 | 0.97417 | -0.49838 | 0.97539 | -0.4743 | 4.5039
29 | 0.0065455 | 0.0016405 | -0.0065425 | -0.0016396 | 2.9683e-06 | 9.1436e-07 | 0.0099981 | 0.0099984 | 0.0099984 | 0.97417 | -0.49838 | 0.97368 | -0.50791 | 2.7468
30 | -0.011751 | -0.002943 | 0.011754 | 0.0029445 | 2.7347e-06 | 1.4669e-06 | 0.017927 | 0.017927 | 0.017927 | 0.97539 | -0.4743 | 0.97563 | -0.46941 | 4.9249
31 | 0.0026353 | 0.00066033 | -0.0026352 | -0.00066044 | 7.9703e-08 | -1.1197e-07 | 0.0040273 | 0.0040273 | 0.0040273 | 0.97368 | -0.50791 | 0.97365 | -0.50854 | 1.1064
32 | -0.011754 | -0.0029445 | 0.011757 | 0.002946 | 2.7907e-06 | 1.4968e-06 | 0.017927 | 0.017926 | 0.017927 | 0.97563 | -0.46941 | 0.97589 | -0.46443 | 4.9249
33 | -0.013067 | -0.0032744 | 0.01307 | 0.0032757 | 2.3486e-06 | 1.306e-06 | 0.019925 | 0.019925 | 0.019925 | 0.97589 | -0.46443 | 0.97608 | -0.46065 | 5.4739
34 | 0.081259 | 0.020464 | -0.081109 | -0.020368 | 0.00015041 | 9.5936e-05 | 0.12374 | 0.12374 | 0.12374 | 0.97741 | -0.43262 | 0.97544 | -0.47141 | 33.9958
35 | 0.076735 | 0.019271 | -0.076696 | -0.019247 | 3.8449e-05 | 2.4514e-05 | 0.11707 | 0.11707 | 0.11707 | 0.97544 | -0.47141 | 0.9749 | -0.48192 | 32.1626
36 | 0.067862 | 0.017033 | -0.067797 | -0.016992 | 6.4988e-05 | 4.1391e-05 | 0.10359 | 0.10359 | 0.10359 | 0.9749 | -0.48192 | 0.97388 | -0.50202 | 28.4584
37 | 0.013299 | 0.0033332 | -0.013299 | -0.0033332 | 1.1884e-08 | 6.6496e-09 | 0.020321 | 0.020321 | 0.020321 | 0.97388 | -0.50202 | 0.97388 | -0.50204 | 5.5826
38 | 0.034853 | 0.0087835 | -0.034724 | -0.0087027 | 0.00012854 | 8.0769e-05 | 0.053247 | 0.053247 | 0.053247 | 0.9743 | -0.49347 | 0.97038 | -0.57087 | 14.6283
39 | 0.0069406 | 0.0017396 | -0.0069397 | -0.0017393 | 8.8785e-07 | 3.1005e-07 | 0.010643 | 0.010643 | 0.010643 | 0.97038 | -0.57087 | 0.97024 | -0.57355 | 2.9239
40 | -0.0051878 | -0.0013002 | 0.0051888 | 0.0013003 | 9.9551e-07 | 1.0186e-07 | 0.0078915 | 0.0078913 | 0.0078915 | 0.97821 | -0.41873 | 0.97842 | -0.41471 | 2.168
41 | 0.0020137 | 0.00050466 | -0.0020137 | -0.00050467 | 3.666e-09 | -1.0734e-08 | 0.0030631 | 0.0030631 | 0.0030631 | 0.97821 | -0.41873 | 0.97821 | -0.41877 | 0.84152
42 | -0.012985 | -0.0032543 | 0.012986 | 0.0032549 | 1.084e-06 | 6.0067e-07 | 0.019747 | 0.019747 | 0.019747 | 0.97842 | -0.41471 | 0.97851 | -0.41295 | 5.4251
43 | 0.0077957 | 0.001954 | -0.0077942 | -0.0019534 | 1.5008e-06 | 6.03e-07 | 0.011856 | 0.011856 | 0.011856 | 0.97842 | -0.41471 | 0.97821 | -0.41875 | 3.2572
44 | 0.028004 | 0.007038 | -0.027991 | -0.0070298 | 1.3069e-05 | 8.1231e-06 | 0.042592 | 0.042593 | 0.042593 | 0.97851 | -0.41295 | 0.97801 | -0.42273 | 11.7012
45 | -0.040989 | -0.010293 | 0.041097 | 0.010361 | 0.00010745 | 6.7841e-05 | 0.06234 | 0.062339 | 0.06234 | 0.97851 | -0.41295 | 0.98131 | -0.35816 | 17.1263
46 | 0.0055805 | 0.0013986 | -0.0055801 | -0.0013985 | 3.804e-07 | 6.6746e-08 | 0.0084888 | 0.0084888 | 0.0084888 | 0.97821 | -0.41875 | 0.97814 | -0.42018 | 2.3321
47 | 0.025851 | 0.0064935 | -0.025826 | -0.0064779 | 2.5252e-05 | 1.5616e-05 | 0.039337 | 0.039337 | 0.039337 | 0.97801 | -0.42273 | 0.97696 | -0.44322 | 10.8069
48 | -0.044325 | -0.01117 | 0.04436 | 0.011192 | 3.4777e-05 | 2.1998e-05 | 0.067234 | 0.067234 | 0.067234 | 0.98131 | -0.35816 | 0.98215 | -0.34178 | 18.471
49 | 0.019017 | 0.0047714 | -0.019007 | -0.0047656 | 9.5731e-06 | 5.746e-06 | 0.028966 | 0.028967 | 0.028967 | 0.97696 | -0.44322 | 0.97643 | -0.45379 | 7.9578
50 | 0.0068088 | 0.0017066 | -0.0068061 | -0.0017057 | 2.7442e-06 | 9.0467e-07 | 0.010371 | 0.010371 | 0.010371 | 0.97696 | -0.44322 | 0.97653 | -0.45169 | 2.8492
51 | -0.046174 | -0.011646 | 0.046257 | 0.011699 | 8.3656e-05 | 5.2962e-05 | 0.069983 | 0.069983 | 0.069983 | 0.98215 | -0.34178 | 0.98409 | -0.304 | 19.226
52 | -0.0058476 | -0.0014655 | 0.0058479 | 0.0014655 | 3.0637e-07 | 6.7359e-08 | 0.0089109 | 0.0089109 | 0.0089109 | 0.97648 | -0.45279 | 0.97653 | -0.45169 | 2.448
53 | 0.0045387 | 0.0011374 | -0.0045384 | -0.0011374 | 3.0133e-07 | -1.7266e-08 | 0.0069163 | 0.0069164 | 0.0069164 | 0.97648 | -0.45279 | 0.97641 | -0.45418 | 1.9001
54 | 0.016498 | 0.0041367 | -0.016492 | -0.0041335 | 5.3966e-06 | 3.1692e-06 | 0.025142 | 0.025142 | 0.025142 | 0.97643 | -0.45379 | 0.97608 | -0.46065 | 6.9072
55 | 0.049951 | 0.012794 | -0.049945 | -0.012792 | 5.8837e-06 | 2.8531e-06 | 0.074758 | 0.074758 | 0.074758 | 0.99555 | -0.084257 | 0.99542 | -0.086688 | 4.1076
56 | -0.051397 | -0.013157 | 0.051402 | 0.01316 | 5.266e-06 | 2.5986e-06 | 0.07692 | 0.076919 | 0.07692 | 0.99555 | -0.084257 | 0.99566 | -0.082141 | 4.2264
57 | 0.049051 | 0.012568 | -0.049032 | -0.012558 | 1.9147e-05 | 9.1775e-06 | 0.073422 | 0.073423 | 0.073423 | 0.99542 | -0.086688 | 0.995 | -0.094746 | 4.0342
58 | -0.05198 | -0.013304 | 0.051988 | 0.013308 | 7.9929e-06 | 3.9698e-06 | 0.077782 | 0.077782 | 0.077782 | 0.99566 | -0.082141 | 0.99583 | -0.078966 | 4.2737
59 | 0.048467 | 0.012417 | -0.048467 | -0.012417 | 5.5921e-07 | 2.6597e-07 | 0.072579 | 0.072579 | 0.072579 | 0.995 | -0.094746 | 0.99499 | -0.094984 | 3.9878
60 | -0.053964 | -0.013804 | 0.053969 | 0.013806 | 5.3013e-06 | 2.6873e-06 | 0.080735 | 0.080735 | 0.080735 | 0.99583 | -0.078966 | 0.99594 | -0.076937 | 4.436
61 | 0.047505 | 0.012176 | -0.047423 | -0.012137 | 8.2086e-05 | 3.8519e-05 | 0.07114 | 0.071145 | 0.071145 | 0.99499 | -0.094984 | 0.99311 | -0.13068 | 3.9091
62 | -0.054617 | -0.013969 | 0.054625 | 0.013973 | 8.022e-06 | 4.0913e-06 | 0.081703 | 0.081702 | 0.081703 | 0.99594 | -0.076937 | 0.9961 | -0.073902 | 4.4892
63 | 0.047423 | 0.012137 | -0.047163 | -0.011978 | 0.00025931 | 0.00015893 | 0.071145 | 0.071148 | 0.071148 | 0.99311 | -0.13068 | 0.98718 | -0.24426 | 9.7731
64 | -0.054625 | -0.013973 | 0.054705 | 0.014013 | 7.9464e-05 | 4.0509e-05 | 0.081702 | 0.081699 | 0.081702 | 0.9961 | -0.073902 | 0.99768 | -0.043884 | 4.4891
65 | -0.047028 | -0.011893 | 0.047163 | 0.011978 | 0.00013519 | 8.5614e-05 | 0.071148 | 0.071148 | 0.071148 | 0.98409 | -0.304 | 0.98718 | -0.24426 | 19.5462
66 | -0.054705 | -0.014013 | 0.054727 | 0.014025 | 2.2357e-05 | 1.1391e-05 | 0.081699 | 0.081698 | 0.081699 | 0.99768 | -0.043884 | 0.99813 | -0.035453 | 4.4889
67 | -0.056168 | -0.014386 | 0.056184 | 0.014394 | 1.5507e-05 | 8.002e-06 | 0.083846 | 0.083845 | 0.083846 | 0.99813 | -0.035453 | 0.99843 | -0.029756 | 4.6069
68 | -0.061956 | -0.015851 | 0.061968 | 0.015858 | 1.2524e-05 | 6.7339e-06 | 0.092388 | 0.092387 | 0.092388 | 0.99911 | -0.016819 | 0.99933 | -0.012644 | 5.0763

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35865 | 0.092316

## res_load
| p_mw | q_mvar
0 | 0.0012857 | 0.00032222
1 | 0.0016198 | 0.00040595
2 | 0.044908 | 0.011255
3 | 0.00082103 | 0.00020577
4 | 0.0011236 | 0.00028159
5 | 0.0018783 | 0.00047075
6 | 0.021658 | 0.005428
7 | 0.00018617 | 4.6659e-05
8 | 0.01994 | 0.0049976
9 | 0.023222 | 0.00582
10 | 0.00013419 | 3.3632e-05
11 | 0.000265 | 6.6416e-05
12 | 0.0012789 | 0.00032052
13 | 0.0010049 | 0.00025184
14 | 0.0039072 | 0.00097925
15 | 0.0026352 | 0.00066044
16 | 0.0013106 | 0.00032848
17 | 0.030958 | 0.0077587
18 | 0.0043742 | 0.0010963
19 | 0.0088339 | 0.002214
20 | 0.054498 | 0.013658
21 | 0.013299 | 0.0033332
22 | 0.029974 | 0.0075123
23 | 0.027783 | 0.0069632
24 | 0.0069397 | 0.0017393
25 | 0.0031742 | 0.00079552
26 | 0.0020137 | 0.00050467
27 | 0.0022137 | 0.00055481
28 | 0.0021398 | 0.0005363
29 | 0.003228 | 0.00080902
30 | 0.0055801 | 0.0013985
31 | 0.0018142 | 0.00045467
32 | 0.0013089 | 0.00032804
33 | 0.00095819 | 0.00024014
34 | 0.0045384 | 0.0011374
35 | 0.0025095 | 0.00062895
36 | 0.0034224 | 0.00085774
37 | 0.0014464 | 0.0003625
38 | 0.00089378 | 0.000224
39 | 0.0005774 | 0.00014471
40 | 0.00056464 | 0.00014151
41 | 0.0019762 | 0.00049529
42 | 0.0009619 | 0.00024108
43 | 0.00064802 | 0.00016241
44 | 0.00077084 | 0.00019319
45 | 0.0014411 | 0.00036117
46 | 0.0010341 | 0.00025916
47 | 0.0005587 | 0.00014002
48 | 0.0016987 | 0.00042573

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1