## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1216-1_1_3_node_7 | 0.4 | n |  | TRUE
1 | bus_LV_1216-1_1_3_node_8 | 0.4 | n |  | TRUE
2 | bus_LV_1216-1_1_3_node_9 | 0.4 | n |  | TRUE
3 | bus_LV_1216-1_1_3_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_1216-1_1_3_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_1216-1_1_3_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_1216-1_1_3_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_1216-1_1_3_node_77 | 0.4 | n |  | TRUE
8 | bus_LV_1216-1_1_3_node_55 | 0.4 | n |  | TRUE
9 | bus_LV_1216-1_1_3_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_1216-1_1_3_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_1216-1_1_3_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1216-1_1_3_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1216-1_1_3_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_1216-1_1_3_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_1216-1_1_3_node_41 | 0.4 | n |  | TRUE
16 | bus_LV_1216-1_1_3_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_1216-1_1_3_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_1216-1_1_3_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_1216-1_1_3_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_1216-1_1_3_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_1216-1_1_3_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_1216-1_1_3_node_45 | 0.4 | n |  | TRUE
23 | bus_LV_1216-1_1_3_node_101 | 0.4 | n |  | TRUE
24 | bus_LV_1216-1_1_3_node_99 | 0.4 | n |  | TRUE
25 | bus_LV_1216-1_1_3_node_44 | 0.4 | n |  | TRUE
26 | bus_LV_1216-1_1_3_node_74 | 0.4 | n |  | TRUE
27 | bus_LV_1216-1_1_3_node_93 | 0.4 | n |  | TRUE
28 | bus_LV_1216-1_1_3_node_94 | 0.4 | n |  | TRUE
29 | bus_LV_1216-1_1_3_node_53 | 0.4 | n |  | TRUE
30 | bus_LV_1216-1_1_3_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_1216-1_1_3_node_62 | 0.4 | n |  | TRUE
32 | bus_LV_1216-1_1_3_node_57 | 0.4 | n |  | TRUE
33 | bus_LV_1216-1_1_3_node_58 | 0.4 | n |  | TRUE
34 | bus_LV_1216-1_1_3_node_59 | 0.4 | n |  | TRUE
35 | bus_LV_1216-1_1_3_node_154 | 0.4 | n |  | TRUE
36 | bus_LV_1216-1_1_3_node_151 | 0.4 | n |  | TRUE
37 | bus_LV_1216-1_1_3_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_1216-1_1_3_node_64 | 0.4 | n |  | TRUE
39 | bus_LV_1216-1_1_3_node_65 | 0.4 | n |  | TRUE
40 | bus_LV_1216-1_1_3_node_71 | 0.4 | n |  | TRUE
41 | bus_LV_1216-1_1_3_node_66 | 0.4 | n |  | TRUE
42 | bus_LV_1216-1_1_3_node_95 | 0.4 | n |  | TRUE
43 | bus_LV_1216-1_1_3_node_67 | 0.4 | n |  | TRUE
44 | bus_LV_1216-1_1_3_node_68 | 0.4 | n |  | TRUE
45 | bus_LV_1216-1_1_3_node_69 | 0.4 | n |  | TRUE
46 | bus_LV_1216-1_1_3_node_70 | 0.4 | n |  | TRUE
47 | bus_LV_1216-1_1_3_node_72 | 0.4 | n |  | TRUE
48 | bus_LV_1216-1_1_3_node_73 | 0.4 | n |  | TRUE
49 | bus_LV_1216-1_1_3_node_325 | 0.4 | n |  | TRUE
50 | bus_LV_1216-1_1_3_node_313 | 0.4 | n |  | TRUE
51 | bus_LV_1216-1_1_3_node_88 | 0.4 | n |  | TRUE
52 | bus_LV_1216-1_1_3_node_89 | 0.4 | n |  | TRUE
53 | bus_LV_1216-1_1_3_node_90 | 0.4 | n |  | TRUE
54 | bus_LV_1216-1_1_3_node_91 | 0.4 | n |  | TRUE
55 | bus_LV_1216-1_1_3_node_92 | 0.4 | n |  | TRUE
56 | bus_LV_1216-1_1_3_node_324 | 0.4 | n |  | TRUE
57 | bus_LV_1216-1_1_3_node_323 | 0.4 | n |  | TRUE
58 | bus_LV_1216-1_1_3_node_96 | 0.4 | n |  | TRUE
59 | bus_LV_1216-1_1_3_node_97 | 0.4 | n |  | TRUE
60 | bus_LV_1216-1_1_3_node_98 | 0.4 | n |  | TRUE
61 | bus_LV_1216-1_1_3_node_107 | 0.4 | n |  | TRUE
62 | bus_LV_1216-1_1_3_node_100 | 0.4 | n |  | TRUE
63 | bus_LV_1216-1_1_3_node_102 | 0.4 | n |  | TRUE
64 | bus_LV_1216-1_1_3_node_134 | 0.4 | n |  | TRUE
65 | bus_LV_1216-1_1_3_node_119 | 0.4 | n |  | TRUE
66 | bus_LV_1216-1_1_3_node_120 | 0.4 | n |  | TRUE
67 | bus_LV_1216-1_1_3_node_121 | 0.4 | n |  | TRUE
68 | bus_LV_1216-1_1_3_node_122 | 0.4 | n |  | TRUE
69 | bus_LV_1216-1_1_3_node_123 | 0.4 | n |  | TRUE
70 | bus_LV_1216-1_1_3_node_124 | 0.4 | n |  | TRUE
71 | bus_LV_1216-1_1_3_node_125 | 0.4 | n |  | TRUE
72 | bus_LV_1216-1_1_3_node_135 | 0.4 | n |  | TRUE
73 | bus_LV_1216-1_1_3_node_155 | 0.4 | n |  | TRUE
74 | bus_LV_1216-1_1_3_node_136 | 0.4 | n |  | TRUE
75 | bus_LV_1216-1_1_3_node_311 | 0.4 | n |  | TRUE
76 | bus_LV_1216-1_1_3_node_147 | 0.4 | n |  | TRUE
77 | bus_LV_1216-1_1_3_node_148 | 0.4 | n |  | TRUE
78 | bus_LV_1216-1_1_3_node_262 | 0.4 | n |  | TRUE
79 | bus_LV_1216-1_1_3_node_152 | 0.4 | n |  | TRUE
80 | bus_LV_1216-1_1_3_node_153 | 0.4 | n |  | TRUE
81 | bus_LV_1216-1_1_3_node_284 | 0.4 | n |  | TRUE
82 | bus_LV_1216-1_1_3_node_316 | 0.4 | n |  | TRUE
83 | bus_LV_1216-1_1_3_node_156 | 0.4 | n |  | TRUE
84 | bus_LV_1216-1_1_3_node_322 | 0.4 | n |  | TRUE
85 | bus_LV_1216-1_1_3_node_245 | 0.4 | n |  | TRUE
86 | bus_LV_1216-1_1_3_node_246 | 0.4 | n |  | TRUE
87 | bus_LV_1216-1_1_3_node_247 | 0.4 | n |  | TRUE
88 | bus_LV_1216-1_1_3_node_248 | 0.4 | n |  | TRUE
89 | bus_LV_1216-1_1_3_node_249 | 0.4 | n |  | TRUE
90 | bus_LV_1216-1_1_3_node_250 | 0.4 | n |  | TRUE
91 | bus_LV_1216-1_1_3_node_251 | 0.4 | n |  | TRUE
92 | bus_LV_1216-1_1_3_node_252 | 0.4 | n |  | TRUE
93 | bus_LV_1216-1_1_3_node_264 | 0.4 | n |  | TRUE
94 | bus_LV_1216-1_1_3_node_304 | 0.4 | n |  | TRUE
95 | bus_LV_1216-1_1_3_node_265 | 0.4 | n |  | TRUE
96 | bus_LV_1216-1_1_3_node_266 | 0.4 | n |  | TRUE
97 | bus_LV_1216-1_1_3_node_269 | 0.4 | n |  | TRUE
98 | bus_LV_1216-1_1_3_node_270 | 0.4 | n |  | TRUE
99 | bus_LV_1216-1_1_3_node_271 | 0.4 | n |  | TRUE
100 | bus_LV_1216-1_1_3_node_272 | 0.4 | n |  | TRUE
101 | bus_LV_1216-1_1_3_node_273 | 0.4 | n |  | TRUE
102 | bus_LV_1216-1_1_3_node_274 | 0.4 | n |  | TRUE
103 | bus_LV_1216-1_1_3_node_301 | 0.4 | n |  | TRUE
104 | bus_LV_1216-1_1_3_node_300 | 0.4 | n |  | TRUE
105 | bus_LV_1216-1_1_3_node_275 | 0.4 | n |  | TRUE
106 | bus_LV_1216-1_1_3_node_276 | 0.4 | n |  | TRUE
107 | bus_LV_1216-1_1_3_node_285 | 0.4 | n |  | TRUE
108 | bus_LV_1216-1_1_3_node_286 | 0.4 | n |  | TRUE
109 | bus_LV_1216-1_1_3_node_287 | 0.4 | n |  | TRUE
110 | bus_LV_1216-1_1_3_node_288 | 0.4 | n |  | TRUE
111 | bus_LV_1216-1_1_3_node_289 | 0.4 | n |  | TRUE
112 | bus_LV_1216-1_1_3_node_302 | 0.4 | n |  | TRUE
113 | bus_LV_1216-1_1_3_node_303 | 0.4 | n |  | TRUE
114 | bus_LV_1216-1_1_3_node_305 | 0.4 | n |  | TRUE
115 | bus_LV_1216-1_1_3_node_310 | 0.4 | n |  | TRUE
116 | bus_LV_1216-1_1_3_node_312 | 0.4 | n |  | TRUE
117 | bus_LV_1216-1_1_3_node_317 | 0.4 | n |  | TRUE
118 | bus_LV_1216-1_1_3_node_318 | 0.4 | n |  | TRUE
119 | bus_LV_1216-1_1_3_node_319 | 0.4 | n |  | TRUE
120 | bus_LV_1216-1_1_3_node_320 | 0.4 | n |  | TRUE
121 | bus_LV_1216-1_1_3_node_321 | 0.4 | n |  | TRUE
122 | bus_MV_11_0_node_34 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1216-1_1_3_load_7 | 0 | 0.0003082 | 7.7241e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1216-1_1_3_load_8 | 1 | 0.00051838 | 0.00012992 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1216-1_1_3_load_10 | 3 | 0.00026493 | 6.6398e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1216-1_1_3_load_11 | 4 | 0.00014782 | 3.7047e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1216-1_1_3_load_12 | 5 | 0.00031364 | 7.8606e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1216-1_1_3_load_13 | 6 | 0.00016807 | 4.2122e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1216-1_1_3_load_77 | 7 | 0.00020613 | 5.1661e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1216-1_1_3_load_55 | 8 | 0.00014709 | 3.6864e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1216-1_1_3_load_14 | 9 | 0.00022398 | 5.6134e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1216-1_1_3_load_15 | 10 | 0.00019863 | 4.978e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1216-1_1_3_load_16 | 11 | 0.00017009 | 4.263e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1216-1_1_3_load_18 | 13 | 0.00016983 | 4.2563e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1216-1_1_3_load_19 | 14 | 0.00016018 | 4.0145e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1216-1_1_3_load_27 | 16 | 0.00031322 | 7.8501e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1216-1_1_3_load_28 | 17 | 0.00021948 | 5.5008e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1216-1_1_3_load_30 | 18 | 0.00032848 | 8.2324e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1216-1_1_3_load_31 | 19 | 0.00018231 | 4.5691e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1216-1_1_3_load_42 | 20 | 0.0025993 | 0.00065143 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1216-1_1_3_load_99 | 24 | 0.00041201 | 0.00010326 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1216-1_1_3_load_74 | 26 | 0.0016479 | 0.00041299 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1216-1_1_3_load_93 | 27 | 0.00026387 | 6.6131e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1216-1_1_3_load_94 | 28 | 0.0019554 | 0.00049006 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1216-1_1_3_load_53 | 29 | 0.00012509 | 3.1351e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1216-1_1_3_load_54 | 30 | 0.00015126 | 3.791e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1216-1_1_3_load_62 | 31 | 0.00013269 | 3.3256e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1216-1_1_3_load_59 | 34 | 0.0027214 | 0.00068206 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1216-1_1_3_load_154 | 35 | 0.0040221 | 0.001008 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1216-1_1_3_load_151 | 36 | 0.0013578 | 0.0003403 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1216-1_1_3_load_63 | 37 | 0.00020677 | 5.1822e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1216-1_1_3_load_65 | 39 | 0.00012828 | 3.2151e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1216-1_1_3_load_71 | 40 | 0.0049509 | 0.0012408 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1216-1_1_3_load_66 | 41 | 0.00012817 | 3.2121e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1216-1_1_3_load_95 | 42 | 0.00028794 | 7.2164e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1216-1_1_3_load_67 | 43 | 0.0037698 | 0.0009448 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1216-1_1_3_load_68 | 44 | 0.0038033 | 0.0009532 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1216-1_1_3_load_70 | 46 | 0.0019041 | 0.00047721 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1216-1_1_3_load_72 | 47 | 0.0012625 | 0.00031641 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1216-1_1_3_load_325 | 49 | 0.0057569 | 0.0014428 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1216-1_1_3_load_88 | 51 | 0.0024008 | 0.0006017 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1216-1_1_3_load_89 | 52 | 0.001441 | 0.00036116 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1216-1_1_3_load_92 | 55 | 0.001828 | 0.00045815 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1216-1_1_3_load_324 | 56 | 0.0041086 | 0.0010297 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1216-1_1_3_load_323 | 57 | 0.0027146 | 0.00068035 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1216-1_1_3_load_96 | 58 | 0.00030641 | 7.6793e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1216-1_1_3_load_97 | 59 | 0.0003615 | 9.0601e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1216-1_1_3_load_98 | 60 | 0.0002618 | 6.5613e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1216-1_1_3_load_107 | 61 | 0.0005935 | 0.00014874 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1216-1_1_3_load_100 | 62 | 0.0002899 | 7.2656e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1216-1_1_3_load_102 | 63 | 0.0028945 | 0.00072543 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1216-1_1_3_load_134 | 64 | 0.0058754 | 0.0014725 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1216-1_1_3_load_119 | 65 | 0.0045666 | 0.0011445 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1216-1_1_3_load_120 | 66 | 0.0029266 | 0.00073346 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1216-1_1_3_load_121 | 67 | 0.0026655 | 0.00066803 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1216-1_1_3_load_122 | 68 | 0.0044219 | 0.0011082 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1216-1_1_3_load_123 | 69 | 0.020525 | 0.0051441 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1216-1_1_3_load_124 | 70 | 0.0029663 | 0.00074344 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1216-1_1_3_load_125 | 71 | 0.0028643 | 0.00071786 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1216-1_1_3_load_135 | 72 | 0.0028182 | 0.00070631 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1216-1_1_3_load_155 | 73 | 0.0060366 | 0.0015129 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1216-1_1_3_load_136 | 74 | 0.0034425 | 0.00086277 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1216-1_1_3_load_311 | 75 | 0.0017708 | 0.00044381 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1216-1_1_3_load_147 | 76 | 0.00094011 | 0.00023561 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1216-1_1_3_load_148 | 77 | 0.00078899 | 0.00019774 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1216-1_1_3_load_262 | 78 | 0.0017874 | 0.00044796 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1216-1_1_3_load_152 | 79 | 0.0016281 | 0.00040805 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1216-1_1_3_load_153 | 80 | 0.00078596 | 0.00019698 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1216-1_1_3_load_284 | 81 | 0.0012094 | 0.00030311 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1216-1_1_3_load_316 | 82 | 0.0051577 | 0.0012926 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1216-1_1_3_load_156 | 83 | 0.0028463 | 0.00071335 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1216-1_1_3_load_322 | 84 | 0.016501 | 0.0041357 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1216-1_1_3_load_245 | 85 | 0.0015154 | 0.0003798 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1216-1_1_3_load_246 | 86 | 0.0026911 | 0.00067445 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1216-1_1_3_load_247 | 87 | 0.001283 | 0.00032156 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1216-1_1_3_load_248 | 88 | 0.0037859 | 0.00094884 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1216-1_1_3_load_249 | 89 | 0.0015201 | 0.00038096 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1216-1_1_3_load_250 | 90 | 0.0026164 | 0.00065572 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1216-1_1_3_load_251 | 91 | 0.0012453 | 0.00031211 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1216-1_1_3_load_252 | 92 | 0.0016712 | 0.00041885 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1216-1_1_3_load_264 | 93 | 0.0026881 | 0.0006737 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1216-1_1_3_load_304 | 94 | 0.0014269 | 0.00035761 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1216-1_1_3_load_265 | 95 | 0.0024839 | 0.00062253 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1216-1_1_3_load_266 | 96 | 0.0012728 | 0.00031899 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1216-1_1_3_load_271 | 99 | 0.0035041 | 0.0008782 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1216-1_1_3_load_272 | 100 | 0.00092319 | 0.00023137 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1216-1_1_3_load_273 | 101 | 0.0011352 | 0.00028452 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1216-1_1_3_load_274 | 102 | 0.0016082 | 0.00040306 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1216-1_1_3_load_301 | 103 | 0.001031 | 0.00025839 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1216-1_1_3_load_300 | 104 | 0.00093539 | 0.00023443 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1216-1_1_3_load_276 | 106 | 0.0024055 | 0.00060289 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1216-1_1_3_load_285 | 107 | 0.00092708 | 0.00023235 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1216-1_1_3_load_286 | 108 | 0.00078624 | 0.00019705 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1216-1_1_3_load_287 | 109 | 0.0014658 | 0.00036736 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1216-1_1_3_load_288 | 110 | 0.0010617 | 0.00026608 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1216-1_1_3_load_289 | 111 | 0.0010284 | 0.00025774 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1216-1_1_3_load_305 | 114 | 0.0017543 | 0.00043967 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1216-1_1_3_load_310 | 115 | 0.0040441 | 0.0010135 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1216-1_1_3_load_312 | 116 | 0.0027899 | 0.00069921 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1216-1_1_3_load_317 | 117 | 0.0043884 | 0.0010998 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1216-1_1_3_load_318 | 118 | 0.0040576 | 0.0010169 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1216-1_1_3_load_319 | 119 | 0.0031583 | 0.00079155 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1216-1_1_3_load_320 | 120 | 0.0086682 | 0.0021725 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1216-1_1_3_load_321 | 121 | 0.0065002 | 0.0016291 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1216-1_1_3_line_0 |  | 0 | 1 | 7.759e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1216-1_1_3_line_1 |  | 0 | 2 | 0.023835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1216-1_1_3_line_2 |  | 2 | 3 | 0.0054403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1216-1_1_3_line_3 |  | 2 | 4 | 0.11595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1216-1_1_3_line_4 |  | 3 | 5 | 0.076444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1216-1_1_3_line_5 |  | 4 | 6 | 0.031226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1216-1_1_3_line_6 |  | 5 | 7 | 0.04814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1216-1_1_3_line_7 |  | 6 | 8 | 0.03057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1216-1_1_3_line_8 |  | 7 | 19 | 0.03431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1216-1_1_3_line_9 |  | 8 | 30 | 0.039381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1216-1_1_3_line_10 |  | 9 | 10 | 0.008984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1216-1_1_3_line_11 |  | 9 | 11 | 0.012232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1216-1_1_3_line_12 |  | 10 | 12 | 0.043592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1216-1_1_3_line_13 |  | 11 | 13 | 0.03098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1216-1_1_3_line_14 |  | 12 | 14 | 0.19026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1216-1_1_3_line_15 |  | 14 | 15 | 0.044423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1216-1_1_3_line_16 |  | 15 | 20 | 0.021389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1216-1_1_3_line_17 |  | 15 | 21 | 0.01191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1216-1_1_3_line_18 |  | 16 | 17 | 0.04935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1216-1_1_3_line_19 |  | 17 | 18 | 0.044475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1216-1_1_3_line_20 |  | 18 | 19 | 0.063556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1216-1_1_3_line_21 |  | 20 | 22 | 0.029531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1216-1_1_3_line_22 |  | 21 | 23 | 0.19779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1216-1_1_3_line_23 |  | 21 | 24 | 0.025205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1216-1_1_3_line_24 |  | 22 | 27 | 0.021781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1216-1_1_3_line_25 |  | 22 | 28 | 0.0059086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1216-1_1_3_line_26 |  | 23 | 63 | 0.03861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1216-1_1_3_line_27 |  | 23 | 25 | 0.004629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1216-1_1_3_line_28 |  | 24 | 62 | 0.011228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1216-1_1_3_line_29 |  | 25 | 26 | 0.034661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1216-1_1_3_line_30 |  | 26 | 47 | 0.03768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1216-1_1_3_line_31 |  | 28 | 51 | 0.20266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1216-1_1_3_line_32 |  | 29 | 30 | 0.013506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1216-1_1_3_line_33 |  | 29 | 31 | 0.50992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1216-1_1_3_line_34 |  | 31 | 37 | 0.06627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1216-1_1_3_line_35 |  | 31 | 38 | 0.13931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1216-1_1_3_line_36 |  | 32 | 33 | 0.052061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1216-1_1_3_line_37 |  | 32 | 34 | 0.0089432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1216-1_1_3_line_38 |  | 33 | 35 | 0.07742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1216-1_1_3_line_39 |  | 34 | 36 | 0.18183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1216-1_1_3_line_40 |  | 35 | 82 | 0.004128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_1216-1_1_3_line_41 |  | 36 | 79 | 0.007101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1216-1_1_3_line_42 |  | 37 | 39 | 0.099222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1216-1_1_3_line_43 |  | 38 | 40 | 0.17436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1216-1_1_3_line_44 |  | 39 | 41 | 0.004919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1216-1_1_3_line_45 |  | 40 | 45 | 0.096208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1216-1_1_3_line_46 |  | 41 | 42 | 0.025911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1216-1_1_3_line_47 |  | 42 | 58 | 0.0035099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1216-1_1_3_line_48 |  | 43 | 44 | 0.024349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1216-1_1_3_line_49 |  | 43 | 45 | 0.010006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1216-1_1_3_line_50 |  | 44 | 46 | 0.011407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1216-1_1_3_line_51 |  | 45 | 47 | 0.0037813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1216-1_1_3_line_52 |  | 46 | 48 | 0.0096573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1216-1_1_3_line_53 |  | 48 | 49 | 0.038109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1216-1_1_3_line_54 |  | 48 | 50 | 0.007543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1216-1_1_3_line_55 |  | 50 | 55 | 0.010017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1216-1_1_3_line_56 |  | 50 | 116 | 0.014938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1216-1_1_3_line_57 |  | 52 | 53 | 0.09794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1216-1_1_3_line_58 |  | 53 | 54 | 0.06109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1216-1_1_3_line_59 |  | 53 | 55 | 0.0093832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1216-1_1_3_line_60 |  | 54 | 56 | 0.072974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1216-1_1_3_line_61 |  | 54 | 57 | 0.034877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1216-1_1_3_line_62 |  | 58 | 59 | 0.03693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1216-1_1_3_line_63 |  | 59 | 60 | 0.015521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1216-1_1_3_line_64 |  | 60 | 61 | 0.05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1216-1_1_3_line_65 |  | 63 | 64 | 0.018468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1216-1_1_3_line_66 |  | 65 | 66 | 0.011621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1216-1_1_3_line_67 |  | 65 | 67 | 0.0045761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1216-1_1_3_line_68 |  | 66 | 68 | 0.0078023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1216-1_1_3_line_69 |  | 67 | 69 | 0.011662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1216-1_1_3_line_70 |  | 68 | 70 | 5.0137e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1216-1_1_3_line_71 |  | 69 | 71 | 0.00409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1216-1_1_3_line_72 |  | 70 | 72 | 0.018038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1216-1_1_3_line_73 |  | 71 | 73 | 0.0081289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1216-1_1_3_line_74 |  | 72 | 74 | 0.0089388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1216-1_1_3_line_75 |  | 73 | 83 | 0.02241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1216-1_1_3_line_76 |  | 74 | 75 | 0.0085592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1216-1_1_3_line_77 |  | 75 | 115 | 0.017439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1216-1_1_3_line_78 |  | 76 | 77 | 0.075916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1216-1_1_3_line_79 |  | 76 | 78 | 0.70322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1216-1_1_3_line_80 |  | 78 | 94 | 0.056405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1216-1_1_3_line_81 |  | 79 | 80 | 0.015356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1216-1_1_3_line_82 |  | 80 | 81 | 0.020514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1216-1_1_3_line_83 |  | 81 | 107 | 0.0068452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1216-1_1_3_line_84 |  | 82 | 117 | 0.0038692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_1216-1_1_3_line_85 |  | 83 | 84 | 0.020466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1216-1_1_3_line_86 |  | 84 | 121 | 0.0098476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1216-1_1_3_line_87 |  | 85 | 86 | 0.026581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1216-1_1_3_line_88 |  | 86 | 87 | 0.0024221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1216-1_1_3_line_89 |  | 87 | 88 | 0.035977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1216-1_1_3_line_90 |  | 88 | 89 | 0.01997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1216-1_1_3_line_91 |  | 89 | 90 | 0.018661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1216-1_1_3_line_92 |  | 90 | 91 | 0.0098004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1216-1_1_3_line_93 |  | 91 | 92 | 0.029946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1216-1_1_3_line_94 |  | 92 | 93 | 0.032615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1216-1_1_3_line_95 |  | 93 | 95 | 0.028786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1216-1_1_3_line_96 |  | 94 | 113 | 0.04533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1216-1_1_3_line_97 |  | 95 | 96 | 0.021776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1216-1_1_3_line_98 |  | 96 | 97 | 0.01276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1216-1_1_3_line_99 |  | 97 | 98 | 0.033631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1216-1_1_3_line_100 |  | 97 | 99 | 0.021179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1216-1_1_3_line_101 |  | 98 | 100 | 0.010619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1216-1_1_3_line_102 |  | 98 | 101 | 0.010197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1216-1_1_3_line_103 |  | 99 | 102 | 0.0050744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1216-1_1_3_line_104 |  | 100 | 103 | 0.16322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1216-1_1_3_line_105 |  | 101 | 104 | 0.024429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1216-1_1_3_line_106 |  | 102 | 105 | 0.039958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1216-1_1_3_line_107 |  | 103 | 112 | 0.024502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1216-1_1_3_line_108 |  | 104 | 111 | 0.027449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1216-1_1_3_line_109 |  | 105 | 106 | 0.052136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1216-1_1_3_line_110 |  | 107 | 108 | 0.018199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1216-1_1_3_line_111 |  | 108 | 109 | 0.0018465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1216-1_1_3_line_112 |  | 109 | 110 | 0.015807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1216-1_1_3_line_113 |  | 110 | 111 | 0.016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1216-1_1_3_line_114 |  | 112 | 113 | 0.052755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1216-1_1_3_line_115 |  | 113 | 114 | 0.0049787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1216-1_1_3_line_116 |  | 115 | 116 | 0.0045752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1216-1_1_3_line_117 |  | 117 | 118 | 0.0035566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
118 | LV_1216-1_1_3_line_118 |  | 118 | 119 | 0.0091037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
119 | LV_1216-1_1_3_line_119 |  | 119 | 120 | 0.0053351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
120 | LV_1216-1_1_3_line_120 |  | 120 | 121 | 0.012961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1216-1_1_3_trafo_154 | 0.63 MVA 20/0.4 kV | 122 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2695461.0572 | 1181389.772 | 2695461.1313 | 1181389.7949
1 | 2695482.6883 | 1181399.8673 | 2695464.66 | 1181390.8856 | 2695461.1313 | 1181389.7949
2 | 2695482.6883 | 1181399.8673 | 2695484.5714 | 1181404.9713
3 | 2695482.6883 | 1181399.8673 | 2695519.0939 | 1181343.2222 | 2695561.9645 | 1181327.1507 | 2695563.1882 | 1181324.6027
4 | 2695536.9155 | 1181418.518 | 2695536.9984 | 1181417.944 | 2695535.5454 | 1181413.7404 | 2695530.8168 | 1181409.9404 | 2695522.5602 | 1181406.0841 | 2695513.9312 | 1181405.9466 | 2695505.847 | 1181411.3991 | 2695499.0235 | 1181418.2725 | 2695491.3045 | 1181420.9402 | 2695484.6516 | 1181417.1095 | 2695485.4487 | 1181407.3494 | 2695484.5714 | 1181404.9713
5 | 2695563.1882 | 1181324.6027 | 2695573.8394 | 1181302.4242 | 2695579.6144 | 1181299.1831
6 | 2695536.9155 | 1181418.518 | 2695535.9251 | 1181425.376 | 2695534.0943 | 1181429.5384 | 2695533.8561 | 1181434.8936 | 2695534.6884 | 1181442.5784 | 2695532.3693 | 1181447.6669 | 2695528.1818 | 1181449.6904 | 2695526.3328 | 1181455.4757 | 2695530.23 | 1181461.5973 | 2695530.23 | 1181461.5973
7 | 2695606.2734 | 1181284.2214 | 2695579.6144 | 1181299.1831
8 | 2695512.6871 | 1181488.7795 | 2695512.6871 | 1181488.7795 | 2695515.0211 | 1181482.7573 | 2695526.3677 | 1181472.9318 | 2695530.1114 | 1181469.0335 | 2695530.23 | 1181461.5973
9 | 2695606.2734 | 1181284.2214 | 2695640.6159 | 1181264.9476
10 | 2695044.5967 | 1180533.4098 | 2695038.035 | 1180527.2734
11 | 2695044.5967 | 1180533.4098 | 2695053.5307 | 1180541.7649
12 | 2695008.0345 | 1180497.3427 | 2695009.3543 | 1180501.3105 | 2695016.8695 | 1180505.2877 | 2695024.4527 | 1180510.2777 | 2695028.5117 | 1180514.4558 | 2695036.5805 | 1180525.9132 | 2695038.035 | 1180527.2734
13 | 2695075.7327 | 1180562.9573 | 2695072.9392 | 1180558.4657 | 2695067.1439 | 1180552.5034 | 2695058.3129 | 1180546.2372 | 2695053.5307 | 1180541.7649
14 | 2695008.0345 | 1180497.3427 | 2695056.5026 | 1180489.8727 | 2695068.813 | 1180488.7005 | 2695076.2946 | 1180489.0193 | 2695084.4513 | 1180491.0833 | 2695096.8553 | 1180497.0059 | 2695141.3867 | 1180527.7207 | 2695151.2618 | 1180532.6917 | 2695161.9276 | 1180535.0179 | 2695184.9739 | 1180537.0737
15 | 2695229.2183 | 1180541.0567 | 2695215.457 | 1180539.7929 | 2695184.9739 | 1180537.0737
16 | 2695229.2183 | 1180541.0567 | 2695229.2176 | 1180536.7762 | 2695225.4173 | 1180532.1907 | 2695218.9749 | 1180523.0862
17 | 2695229.2183 | 1180541.0567 | 2695236.6405 | 1180541.2636 | 2695237.1579 | 1180545.7191
18 | 2695531.0426 | 1181591.2373 | 2695531.0426 | 1181591.2373 | 2695533.839 | 1181586.3899 | 2695537.1496 | 1181578.9934 | 2695538.8383 | 1181573.2056 | 2695537.5065 | 1181566.6691 | 2695537.5882 | 1181561.5449 | 2695541.9434 | 1181559.0571 | 2695546.03 | 1181553.7744 | 2695550.5716 | 1181549.6553
19 | 2695544.7587 | 1181512.7947 | 2695541.0153 | 1181517.149 | 2695539.6358 | 1181523.1864 | 2695541.7993 | 1181528.3353 | 2695545.7374 | 1181531.8892 | 2695547.4045 | 1181537.5082 | 2695545.246 | 1181542.5882 | 2695549.3814 | 1181543.8215 | 2695550.5716 | 1181549.6553 | 2695550.5716 | 1181549.6553
20 | 2695544.7587 | 1181512.7947 | 2695544.7587 | 1181512.7947 | 2695541.5891 | 1181511.3433 | 2695537.256 | 1181512.4416 | 2695532.8969 | 1181514.6958 | 2695528.7168 | 1181516.2635 | 2695526.8448 | 1181513.4319 | 2695528.8579 | 1181507.4157 | 2695531.0572 | 1181499.7792 | 2695531.0081 | 1181492.7962 | 2695526.8987 | 1181489.9289 | 2695521.4839 | 1181488.4528 | 2695517.4752 | 1181489.3228 | 2695514.25 | 1181491.3616 | 2695512.6871 | 1181488.7795
21 | 2695200.751 | 1180499.9008 | 2695210.1005 | 1180510.5449 | 2695218.9749 | 1180523.0862
22 | 2695237.1579 | 1180545.7191 | 2695249.4426 | 1180546.1589 | 2695302.3757 | 1180542.3086 | 2695309.9014 | 1180540.327 | 2695317.2138 | 1180535.9071 | 2695332.0012 | 1180527.4145 | 2695349.093 | 1180516.6906 | 2695366.4537 | 1180510.6739 | 2695389.671 | 1180506.7629 | 2695427.0851 | 1180504.5902
23 | 2695237.1579 | 1180545.7191 | 2695236.8458 | 1180549.4943 | 2695231.7029 | 1180560.6531 | 2695231.8056 | 1180564.7684 | 2695233.3665 | 1180569.533
24 | 2695200.751 | 1180499.9008 | 2695180.7686 | 1180491.1002
25 | 2695200.751 | 1180499.9008 | 2695198.0649 | 1180494.6379
26 | 2695427.0851 | 1180504.5902 | 2695425.162 | 1180509.2625 | 2695425.6193 | 1180512.205 | 2695427.1835 | 1180514.2423 | 2695433.4889 | 1180515.0209 | 2695440.4826 | 1180514.7877 | 2695445.4349 | 1180515.6226 | 2695450.2844 | 1180517.6344 | 2695452.6803 | 1180520.6967 | 2695452.9958 | 1180521.0844
27 | 2695428.0814 | 1180500.0698 | 2695427.0851 | 1180504.5902
28 | 2695236.862 | 1180580.203 | 2695233.3665 | 1180569.533
29 | 2695428.0814 | 1180500.0698 | 2695439.2725 | 1180500.5927 | 2695447.2836 | 1180499.7975 | 2695462.3891 | 1180496.7612
30 | 2695462.3891 | 1180496.7612 | 2695476.1384 | 1180493.9976 | 2695487.2374 | 1180494.0633 | 2695499.2196 | 1180497.8174
31 | 2695198.0649 | 1180494.6379 | 2695262.43 | 1180302.466
32 | 2695640.6159 | 1181264.9476 | 2695652.3936 | 1181258.3377 | 2695652.3936 | 1181258.3377
33 | 2695450.3875 | 1180790.133 | 2695652.3936 | 1181258.3377
34 | 2695450.3875 | 1180790.133 | 2695449.8017 | 1180790.1444 | 2695437.5395 | 1180788.804 | 2695430.0501 | 1180788.5179 | 2695421.8046 | 1180788.709 | 2695409.1444 | 1180792.2098 | 2695386.026 | 1180800.2323
35 | 2695572.5487 | 1180730.0836 | 2695570.6717 | 1180728.9863 | 2695568.0199 | 1180730.0114 | 2695563.5151 | 1180733.2194 | 2695533.1479 | 1180756.8061 | 2695521.883 | 1180765.7434 | 2695514.3126 | 1180770.0589 | 2695490.0041 | 1180778.7551 | 2695462.7679 | 1180788.0495 | 2695454.5011 | 1180790.0525 | 2695450.3875 | 1180790.133
36 | 2695848.1009 | 1180545.631 | 2695856.3658 | 1180544.7292 | 2695881.6973 | 1180538.5636 | 2695899.3662 | 1180536.2336
37 | 2695899.3662 | 1180536.2336 | 2695908.2227 | 1180534.9907
38 | 2695848.1009 | 1180545.631 | 2695837.5286 | 1180545.5954 | 2695784.8378 | 1180542.8628 | 2695770.7611 | 1180542.3447
39 | 2696069.9496 | 1180470.0122 | 2696067.29 | 1180471.7359 | 2696038.3431 | 1180492.2965 | 2696024.4246 | 1180500.8457 | 2696016.5819 | 1180503.0437 | 2696006.5048 | 1180503.5605 | 2695986.9434 | 1180501.9352 | 2695976.7965 | 1180503.4737 | 2695967.2531 | 1180508.3574 | 2695953.6124 | 1180519.6019 | 2695946.927 | 1180527.7668 | 2695942.2795 | 1180530.3274 | 2695934.6788 | 1180532.207 | 2695914.6564 | 1180534.0879 | 2695908.2227 | 1180534.9907
40 | 2695770.7611 | 1180542.3447 | 2695766.6359 | 1180542.1928
41 | 2696069.9496 | 1180470.0122 | 2696075.9085 | 1180466.1501
42 | 2695291.3342 | 1180828.5891 | 2695296.0757 | 1180828.9351 | 2695305.8355 | 1180826.7111 | 2695319.9228 | 1180821.843 | 2695360.252 | 1180809.1762 | 2695386.026 | 1180800.2323
43 | 2695529.8366 | 1180561.0399 | 2695572.5487 | 1180730.0836
44 | 2695291.3342 | 1180828.5891 | 2695290.2311 | 1180828.5087 | 2695286.5562 | 1180827.4917
45 | 2695502.828 | 1180498.948 | 2695501.7294 | 1180502.6884 | 2695500.6652 | 1180504.2725 | 2695493.1918 | 1180505.8433 | 2695489.7603 | 1180508.3236 | 2695487.3405 | 1180512.043 | 2695484.4175 | 1180523.8484 | 2695485.0689 | 1180530.4296 | 2695486.5121 | 1180534.3106 | 2695488.8495 | 1180535.7599 | 2695497.476 | 1180538.5324 | 2695503.2724 | 1180542.0047 | 2695517.0445 | 1180553.1311 | 2695529.8366 | 1180561.0399
46 | 2695261.4255 | 1180821.2352 | 2695261.4255 | 1180821.2352 | 2695271.6888 | 1180823.3774 | 2695286.5562 | 1180827.4917
47 | 2695261.4255 | 1180821.2352 | 2695257.9226 | 1180821.0143
48 | 2695512.2348 | 1180502.3591 | 2695513.5073 | 1180502.8205 | 2695529.4088 | 1180508.3218 | 2695535.3649 | 1180509.9288
49 | 2695502.828 | 1180498.948 | 2695512.2348 | 1180502.3591
50 | 2695535.3649 | 1180509.9288 | 2695535.3649 | 1180509.9288 | 2695538.6374 | 1180510.2256 | 2695546.7212 | 1180509.4505
51 | 2695502.828 | 1180498.948 | 2695499.2196 | 1180497.8174
52 | 2695556.3344 | 1180508.5287 | 2695546.7212 | 1180509.4505
53 | 2695556.3344 | 1180508.5287 | 2695558.2492 | 1180526.9042 | 2695560.0809 | 1180533.2374 | 2695567.318 | 1180544.093
54 | 2695556.3344 | 1180508.5287 | 2695563.8699 | 1180507.8595
55 | 2695563.8699 | 1180507.8595 | 2695565.6876 | 1180498.0086
56 | 2695563.8699 | 1180507.8595 | 2695576.6629 | 1180507.0851 | 2695578.7845 | 1180507.0708
57 | 2695567.3903 | 1180488.7812 | 2695558.839 | 1180484.1642 | 2695551.6463 | 1180480.1026 | 2695537.8072 | 1180479.8819 | 2695521.8606 | 1180468.5763 | 2695501.3171 | 1180459.0541 | 2695494.1812 | 1180444.231 | 2695491.7232 | 1180437.1675
58 | 2695567.3903 | 1180488.7812 | 2695561.8673 | 1180483.0117 | 2695576.1594 | 1180477.347 | 2695590.7986 | 1180474.8232 | 2695601.2531 | 1180470.2759 | 2695602.4912 | 1180458.7549
59 | 2695567.3903 | 1180488.7812 | 2695565.6876 | 1180498.0086
60 | 2695602.4912 | 1180458.7549 | 2695614.2901 | 1180452.7837 | 2695627.0183 | 1180454.1653 | 2695644.7135 | 1180457.861 | 2695669.0518 | 1180473.7149
61 | 2695602.4912 | 1180458.7549 | 2695593.9049 | 1180452.9811 | 2695581.8676 | 1180448.9866 | 2695570.0354 | 1180448.3851
62 | 2695224.5744 | 1180832.4319 | 2695229.0082 | 1180828.7695 | 2695237.0077 | 1180822.904 | 2695244.5451 | 1180820.6445 | 2695251.0545 | 1180820.5812 | 2695257.9226 | 1180821.0143
63 | 2695224.5744 | 1180832.4319 | 2695212.6077 | 1180842.3169
64 | 2695168.3071 | 1180857.2572 | 2695190.7842 | 1180858.9707 | 2695207.7603 | 1180846.321 | 2695212.6077 | 1180842.3169
65 | 2695464.6536 | 1180535.4077 | 2695452.9958 | 1180521.0844
66 | 2695640.9598 | 1180525.4891 | 2695641.6213 | 1180525.7215 | 2695652.3696 | 1180527.6498
67 | 2695656.9371 | 1180527.93 | 2695652.3696 | 1180527.6498 | 2695652.3696 | 1180527.6498
68 | 2695640.9598 | 1180525.4891 | 2695633.5989 | 1180522.9018
69 | 2695656.9371 | 1180527.93 | 2695658.002 | 1180527.9954 | 2695663.3036 | 1180528.0022 | 2695668.5746 | 1180527.5167
70 | 2695633.5516 | 1180522.8852 | 2695633.5989 | 1180522.9018
71 | 2695672.6473 | 1180527.1415 | 2695668.5746 | 1180527.5167
72 | 2695633.5516 | 1180522.8852 | 2695625.782 | 1180520.1543 | 2695616.6062 | 1180516.706
73 | 2695672.6473 | 1180527.1415 | 2695679.6606 | 1180526.4955 | 2695680.7441 | 1180526.5672
74 | 2695608.2562 | 1180513.5172 | 2695609.5919 | 1180514.07 | 2695616.6062 | 1180516.706
75 | 2695703.0362 | 1180528.7399 | 2695702.1948 | 1180528.5342 | 2695688.078 | 1180527.0524 | 2695680.7441 | 1180526.5672
76 | 2695608.2562 | 1180513.5172 | 2695600.3474 | 1180510.2443
77 | 2695583.3596 | 1180507.0399 | 2695585.4798 | 1180507.0256 | 2695591.4313 | 1180507.4763 | 2695597.9955 | 1180509.271 | 2695600.3474 | 1180510.2443
78 | 2696490.2905 | 1181192.0721 | 2696463.7833 | 1181196.0638 | 2696414.8976 | 1181200.7472
79 | 2696455.5289 | 1180489.7131 | 2696490.2905 | 1181192.0721
80 | 2696427.5391 | 1180440.7428 | 2696455.5289 | 1180489.7131
81 | 2696075.9085 | 1180466.1501 | 2696083.8796 | 1180460.9837 | 2696089.0312 | 1180458.1972
82 | 2696107.6025 | 1180449.5741 | 2696098.1132 | 1180453.2847 | 2696089.0312 | 1180458.1972
83 | 2696107.6025 | 1180449.5741 | 2696113.9776 | 1180447.0813
84 | 2695762.7693 | 1180542.0505 | 2695766.6359 | 1180542.1928
85 | 2695722.9167 | 1180533.5997 | 2695703.0362 | 1180528.7399
86 | 2695732.4826 | 1180535.9381 | 2695722.9167 | 1180533.5997
87 | 2696447.2474 | 1180322.256 | 2696429.648 | 1180331.9961 | 2696423.7416 | 1180334.6289
88 | 2696421.5294 | 1180335.615 | 2696423.7416 | 1180334.6289
89 | 2696421.5294 | 1180335.615 | 2696391.8279 | 1180348.8544 | 2696388.6725 | 1180350.2698
90 | 2696371.7355 | 1180360.5973 | 2696372.4663 | 1180359.9503 | 2696380.4622 | 1180353.9528 | 2696388.6725 | 1180350.2698
91 | 2696371.7355 | 1180360.5973 | 2696357.7629 | 1180372.9666
92 | 2696357.7629 | 1180372.9666 | 2696350.4247 | 1180379.4627
93 | 2696325.9889 | 1180396.7395 | 2696348.1781 | 1180381.4515 | 2696350.4247 | 1180379.4627
94 | 2696325.9889 | 1180396.7395 | 2696317.6175 | 1180402.5073 | 2696303.8678 | 1180410.9697 | 2696297.5801 | 1180411.4184
95 | 2696297.5801 | 1180411.4184 | 2696283.7756 | 1180412.4035 | 2696269.1677 | 1180409.2416
96 | 2696463.7016 | 1180415.7751 | 2696458.9082 | 1180416.9321 | 2696454.0009 | 1180419.477 | 2696448.8305 | 1180423.174 | 2696441.0809 | 1180433.8117 | 2696438.0712 | 1180436.6428 | 2696427.5391 | 1180440.7428
97 | 2696249.1346 | 1180400.8546 | 2696266.2427 | 1180408.6085 | 2696269.1677 | 1180409.2416
98 | 2696236.8352 | 1180398.3188 | 2696244.5742 | 1180398.7877 | 2696249.1346 | 1180400.8546
99 | 2696236.8352 | 1180398.3188 | 2696233.2299 | 1180403.5198 | 2696226.566 | 1180424.1149 | 2696224.8977 | 1180429.5249
100 | 2696236.8352 | 1180398.3188 | 2696227.3765 | 1180391.7183 | 2696224.0124 | 1180382.6788
101 | 2696224.8977 | 1180429.5249 | 2696235.1867 | 1180432.1508
102 | 2696224.8977 | 1180429.5249 | 2696214.7404 | 1180428.6231
103 | 2696224.0124 | 1180382.6788 | 2696222.2426 | 1180377.9231
104 | 2696235.1867 | 1180432.1508 | 2696244.7023 | 1180434.5793 | 2696266.6315 | 1180442.9033 | 2696286.3873 | 1180447.1787 | 2696302.0551 | 1180449.6097 | 2696314.3338 | 1180450.4296 | 2696328.296 | 1180448.7083 | 2696342.5866 | 1180444.135 | 2696360.2058 | 1180436.3798 | 2696390.4066 | 1180422.4831
105 | 2696190.3523 | 1180427.3948 | 2696206.0931 | 1180427.8554 | 2696214.7404 | 1180428.6231
106 | 2696208.9126 | 1180340.267 | 2696212.3997 | 1180351.4746 | 2696222.2426 | 1180377.9231
107 | 2696412.6651 | 1180412.241 | 2696390.4066 | 1180422.4831
108 | 2696190.3523 | 1180427.3948 | 2696188.4236 | 1180427.3383 | 2696175.4041 | 1180428.3968 | 2696163.2497 | 1180431.1266
109 | 2696208.9126 | 1180340.267 | 2696205.4189 | 1180321.8548 | 2696216.1944 | 1180307.8299 | 2696230.5701 | 1180301.4962
110 | 2696130.9709 | 1180440.5799 | 2696129.1408 | 1180441.1521 | 2696113.9776 | 1180447.0813
111 | 2696130.9709 | 1180440.5799 | 2696132.7333 | 1180440.0289
112 | 2696132.7333 | 1180440.0289 | 2696147.8205 | 1180435.3119
113 | 2696147.8205 | 1180435.3119 | 2696155.9985 | 1180432.7551 | 2696163.2497 | 1180431.1266
114 | 2696412.6651 | 1180412.241 | 2696414.3631 | 1180414.4919 | 2696419.5318 | 1180415.6424 | 2696446.1177 | 1180412.7792 | 2696452.366 | 1180413.7804 | 2696461.0051 | 1180414.3308 | 2696463.7016 | 1180415.7751
115 | 2696463.7016 | 1180415.7751 | 2696468.6126 | 1180414.9571
116 | 2695583.3596 | 1180507.0399 | 2695578.7845 | 1180507.0708
117 | 2695762.7693 | 1180542.0505 | 2695759.2151 | 1180541.9197
118 | 2695759.2151 | 1180541.9197 | 2695759.2151 | 1180541.9197 | 2695750.2894 | 1180540.1284
119 | 2695750.2894 | 1180540.1284 | 2695746.5743 | 1180539.3829 | 2695745.0726 | 1180539.0158
120 | 2695732.4826 | 1180535.9381 | 2695745.0726 | 1180539.0158

## bus_geodata
| x | y | coords
0 | 2695461.1313 | 1181389.7949
1 | 2695461.0572 | 1181389.772
2 | 2695482.6883 | 1181399.8673
3 | 2695484.5714 | 1181404.9713
4 | 2695563.1882 | 1181324.6027
5 | 2695536.9155 | 1181418.518
6 | 2695579.6144 | 1181299.1831
7 | 2695530.23 | 1181461.5973
8 | 2695606.2734 | 1181284.2214
9 | 2695044.5967 | 1180533.4098
10 | 2695038.035 | 1180527.2734
11 | 2695053.5307 | 1180541.7649
12 | 2695008.0345 | 1180497.3427
13 | 2695075.7327 | 1180562.9573
14 | 2695184.9739 | 1180537.0737
15 | 2695229.2183 | 1180541.0567
16 | 2695531.0426 | 1181591.2373
17 | 2695550.5716 | 1181549.6553
18 | 2695544.7587 | 1181512.7947
19 | 2695512.6871 | 1181488.7795
20 | 2695218.9749 | 1180523.0862
21 | 2695237.1579 | 1180545.7191
22 | 2695200.751 | 1180499.9008
23 | 2695427.0851 | 1180504.5902
24 | 2695233.3665 | 1180569.533
25 | 2695428.0814 | 1180500.0698
26 | 2695462.3891 | 1180496.7612
27 | 2695180.7686 | 1180491.1002
28 | 2695198.0649 | 1180494.6379
29 | 2695652.3936 | 1181258.3377
30 | 2695640.6159 | 1181264.9476
31 | 2695450.3875 | 1180790.133
32 | 2695899.3662 | 1180536.2336
33 | 2695848.1009 | 1180545.631
34 | 2695908.2227 | 1180534.9907
35 | 2695770.7611 | 1180542.3447
36 | 2696069.9496 | 1180470.0122
37 | 2695386.026 | 1180800.2323
38 | 2695572.5487 | 1180730.0836
39 | 2695291.3342 | 1180828.5891
40 | 2695529.8366 | 1180561.0399
41 | 2695286.5562 | 1180827.4917
42 | 2695261.4255 | 1180821.2352
43 | 2695512.2348 | 1180502.3591
44 | 2695535.3649 | 1180509.9288
45 | 2695502.828 | 1180498.948
46 | 2695546.7212 | 1180509.4505
47 | 2695499.2196 | 1180497.8174
48 | 2695556.3344 | 1180508.5287
49 | 2695567.318 | 1180544.093
50 | 2695563.8699 | 1180507.8595
51 | 2695262.43 | 1180302.466
52 | 2695491.7232 | 1180437.1675
53 | 2695567.3903 | 1180488.7812
54 | 2695602.4912 | 1180458.7549
55 | 2695565.6876 | 1180498.0086
56 | 2695669.0518 | 1180473.7149
57 | 2695570.0354 | 1180448.3851
58 | 2695257.9226 | 1180821.0143
59 | 2695224.5744 | 1180832.4319
60 | 2695212.6077 | 1180842.3169
61 | 2695168.3071 | 1180857.2572
62 | 2695236.862 | 1180580.203
63 | 2695452.9958 | 1180521.0844
64 | 2695464.6536 | 1180535.4077
65 | 2695652.3696 | 1180527.6498
66 | 2695640.9598 | 1180525.4891
67 | 2695656.9371 | 1180527.93
68 | 2695633.5989 | 1180522.9018
69 | 2695668.5746 | 1180527.5167
70 | 2695633.5516 | 1180522.8852
71 | 2695672.6473 | 1180527.1415
72 | 2695616.6062 | 1180516.706
73 | 2695680.7441 | 1180526.5672
74 | 2695608.2562 | 1180513.5172
75 | 2695600.3474 | 1180510.2443
76 | 2696490.2905 | 1181192.0721
77 | 2696414.8976 | 1181200.7472
78 | 2696455.5289 | 1180489.7131
79 | 2696075.9085 | 1180466.1501
80 | 2696089.0312 | 1180458.1972
81 | 2696107.6025 | 1180449.5741
82 | 2695766.6359 | 1180542.1928
83 | 2695703.0362 | 1180528.7399
84 | 2695722.9167 | 1180533.5997
85 | 2696447.2474 | 1180322.256
86 | 2696423.7416 | 1180334.6289
87 | 2696421.5294 | 1180335.615
88 | 2696388.6725 | 1180350.2698
89 | 2696371.7355 | 1180360.5973
90 | 2696357.7629 | 1180372.9666
91 | 2696350.4247 | 1180379.4627
92 | 2696325.9889 | 1180396.7395
93 | 2696297.5801 | 1180411.4184
94 | 2696427.5391 | 1180440.7428
95 | 2696269.1677 | 1180409.2416
96 | 2696249.1346 | 1180400.8546
97 | 2696236.8352 | 1180398.3188
98 | 2696224.8977 | 1180429.5249
99 | 2696224.0124 | 1180382.6788
100 | 2696235.1867 | 1180432.1508
101 | 2696214.7404 | 1180428.6231
102 | 2696222.2426 | 1180377.9231
103 | 2696390.4066 | 1180422.4831
104 | 2696190.3523 | 1180427.3948
105 | 2696208.9126 | 1180340.267
106 | 2696230.5701 | 1180301.4962
107 | 2696113.9776 | 1180447.0813
108 | 2696130.9709 | 1180440.5799
109 | 2696132.7333 | 1180440.0289
110 | 2696147.8205 | 1180435.3119
111 | 2696163.2497 | 1180431.1266
112 | 2696412.6651 | 1180412.241
113 | 2696463.7016 | 1180415.7751
114 | 2696468.6126 | 1180414.9571
115 | 2695583.3596 | 1180507.0399
116 | 2695578.7845 | 1180507.0708
117 | 2695762.7693 | 1180542.0505
118 | 2695759.2151 | 1180541.9197
119 | 2695750.2894 | 1180540.1284
120 | 2695745.0726 | 1180539.0158
121 | 2695732.4826 | 1180535.9381
122 | 2695848.1009 | 1180545.631

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97584 | -0.4684 | 0.0003082 | 7.7241e-05
1 | 0.97584 | -0.4684 | 0.00051838 | 0.00012992
2 | 0.97586 | -0.46804 | 0 | 0
3 | 0.97585 | -0.46822 | 0.00026493 | 6.6398e-05
4 | 0.97614 | -0.46238 | 0.00014782 | 3.7047e-05
5 | 0.97574 | -0.47042 | 0.00031364 | 7.8606e-05
6 | 0.97622 | -0.46077 | 0.00016807 | 4.2122e-05
7 | 0.97568 | -0.47153 | 0.00020613 | 5.1661e-05
8 | 0.97631 | -0.4591 | 0.00014709 | 3.6864e-05
9 | 0.97741 | -0.43696 | 0.00022398 | 5.6134e-05
10 | 0.97741 | -0.43687 | 0.00019863 | 4.978e-05
11 | 0.9774 | -0.43704 | 0.00017009 | 4.263e-05
12 | 0.97744 | -0.43626 | 0 | 0
13 | 0.9774 | -0.43714 | 0.00016983 | 4.2563e-05
14 | 0.97758 | -0.4336 | 0.00016018 | 4.0145e-05
15 | 0.97761 | -0.43284 | 0 | 0
16 | 0.97556 | -0.47391 | 0.00031322 | 7.8501e-05
17 | 0.97557 | -0.47363 | 0.00021948 | 5.5008e-05
18 | 0.9756 | -0.47319 | 0.00032848 | 8.2324e-05
19 | 0.97565 | -0.47219 | 0.00018231 | 4.5691e-05
20 | 0.97747 | -0.43566 | 0.0025993 | 0.00065143
21 | 0.9777 | -0.43107 | 0 | 0
22 | 0.97734 | -0.43815 | 0 | 0
23 | 0.97933 | -0.39914 | 0 | 0
24 | 0.97769 | -0.43139 | 0.00041201 | 0.00010326
25 | 0.9794 | -0.39765 | 0 | 0
26 | 0.97997 | -0.38655 | 0.0016479 | 0.00041299
27 | 0.97734 | -0.43826 | 0.00026387 | 6.6131e-05
28 | 0.97732 | -0.43862 | 0.0019554 | 0.00049006
29 | 0.97646 | -0.45603 | 0.00012509 | 3.1351e-05
30 | 0.97642 | -0.45684 | 0.00015126 | 3.791e-05
31 | 0.97807 | -0.4242 | 0.00013269 | 3.3256e-05
32 | 0.99351 | -0.12277 | 0 | 0
33 | 0.99612 | -0.073218 | 0 | 0
34 | 0.99306 | -0.13131 | 0.0027214 | 0.00068206
35 | 1 | 0 | -0.22833 | -0.057902
36 | 0.9844 | -0.29769 | 0.0013578 | 0.0003403
37 | 0.97793 | -0.42695 | 0.00020677 | 5.1822e-05
38 | 0.97882 | -0.40936 | 0 | 0
39 | 0.97774 | -0.4307 | 0.00012828 | 3.2151e-05
40 | 0.97975 | -0.39082 | 0.0049509 | 0.0012408
41 | 0.97773 | -0.43088 | 0.00012817 | 3.2121e-05
42 | 0.97768 | -0.43174 | 0.00028794 | 7.2164e-05
43 | 0.981 | -0.36627 | 0.0037698 | 0.0009448
44 | 0.98179 | -0.35079 | 0.0038033 | 0.0009532
45 | 0.98071 | -0.37195 | 0 | 0
46 | 0.9822 | -0.34276 | 0.0019041 | 0.00047721
47 | 0.98064 | -0.37336 | 0.0012625 | 0.00031641
48 | 0.98257 | -0.33563 | 0 | 0
49 | 0.98236 | -0.3396 | 0.0057569 | 0.0014428
50 | 0.98289 | -0.32929 | 0 | 0
51 | 0.97687 | -0.44752 | 0.0024008 | 0.0006017
52 | 0.9826 | -0.33507 | 0.001441 | 0.00036116
53 | 0.98273 | -0.33252 | 0 | 0
54 | 0.98234 | -0.34005 | 0 | 0
55 | 0.9828 | -0.33112 | 0.001828 | 0.00045815
56 | 0.98206 | -0.34546 | 0.0041086 | 0.0010297
57 | 0.98225 | -0.34176 | 0.0027146 | 0.00068035
58 | 0.97768 | -0.43183 | 0.00030641 | 7.6793e-05
59 | 0.97764 | -0.43265 | 0.0003615 | 9.0601e-05
60 | 0.97763 | -0.4329 | 0.0002618 | 6.5613e-05
61 | 0.9776 | -0.43344 | 0.0005935 | 0.00014874
62 | 0.97768 | -0.43145 | 0.0002899 | 7.2656e-05
63 | 0.97901 | -0.40529 | 0.0028945 | 0.00072543
64 | 0.97891 | -0.40727 | 0.0058754 | 0.0014725
65 | 0.98867 | -0.21695 | 0.0045666 | 0.0011445
66 | 0.98779 | -0.23393 | 0.0029266 | 0.00073346
67 | 0.98904 | -0.2099 | 0.0026655 | 0.00066803
68 | 0.98723 | -0.24494 | 0.0044219 | 0.0011082
69 | 0.99 | -0.1914 | 0.020525 | 0.0051441
70 | 0.98722 | -0.24501 | 0.0029663 | 0.00074344
71 | 0.99041 | -0.18342 | 0.0028643 | 0.00071786
72 | 0.98603 | -0.26813 | 0.0028182 | 0.00070631
73 | 0.99125 | -0.16719 | 0.0060366 | 0.0015129
74 | 0.98546 | -0.27915 | 0.0034425 | 0.00086277
75 | 0.98495 | -0.28919 | 0.0017708 | 0.00044381
76 | 0.97449 | -0.4919 | 0.00094011 | 0.00023561
77 | 0.97444 | -0.493 | 0.00078899 | 0.00019774
78 | 0.97562 | -0.46943 | 0.0017874 | 0.00044796
79 | 0.98407 | -0.30407 | 0.0016281 | 0.00040805
80 | 0.98338 | -0.31744 | 0.00078596 | 0.00019698
81 | 0.98248 | -0.33504 | 0.0012094 | 0.00030311
82 | 0.99968 | -0.0061115 | 0.0051577 | 0.0012926
83 | 0.9937 | -0.12018 | 0.0028463 | 0.00071335
84 | 0.99599 | -0.076425 | 0.016501 | 0.0041357
85 | 0.97397 | -0.50171 | 0.0015154 | 0.0003798
86 | 0.97401 | -0.50097 | 0.0026911 | 0.00067445
87 | 0.97402 | -0.50078 | 0.001283 | 0.00032156
88 | 0.9742 | -0.49715 | 0.0037859 | 0.00094884
89 | 0.97438 | -0.49375 | 0.0015201 | 0.00038096
90 | 0.97456 | -0.49005 | 0.0026164 | 0.00065572
91 | 0.97469 | -0.48764 | 0.0012453 | 0.00031211
92 | 0.9751 | -0.47959 | 0.0016712 | 0.00041885
93 | 0.97559 | -0.46983 | 0.0026881 | 0.0006737
94 | 0.97581 | -0.46577 | 0.0014269 | 0.00035761
95 | 0.9761 | -0.4598 | 0.0024839 | 0.00062253
96 | 0.97654 | -0.45124 | 0.0012728 | 0.00031899
97 | 0.97681 | -0.44593 | 0 | 0
98 | 0.97775 | -0.42733 | 0 | 0
99 | 0.97666 | -0.44884 | 0.0035041 | 0.0008782
100 | 0.97767 | -0.42901 | 0.00092319 | 0.00023137
101 | 0.97812 | -0.42008 | 0.0011352 | 0.00028452
102 | 0.97664 | -0.44921 | 0.0016082 | 0.00040306
103 | 0.9765 | -0.45214 | 0.001031 | 0.00025839
104 | 0.97903 | -0.40224 | 0.00093539 | 0.00023443
105 | 0.97655 | -0.45097 | 0 | 0
106 | 0.97643 | -0.45326 | 0.0024055 | 0.00060289
107 | 0.98218 | -0.34077 | 0.00092708 | 0.00023235
108 | 0.98141 | -0.35571 | 0.00078624 | 0.00019705
109 | 0.98134 | -0.3572 | 0.0014658 | 0.00036736
110 | 0.9807 | -0.36955 | 0.0010617 | 0.00026608
111 | 0.98008 | -0.38177 | 0.0010284 | 0.00025774
112 | 0.97634 | -0.45516 | 0 | 0
113 | 0.97602 | -0.46165 | 0 | 0
114 | 0.97601 | -0.46181 | 0.0017543 | 0.00043967
115 | 0.98392 | -0.30912 | 0.0040441 | 0.0010135
116 | 0.98367 | -0.31402 | 0.0027899 | 0.00069921
117 | 0.99939 | -0.011669 | 0.0043884 | 0.0010998
118 | 0.99912 | -0.016645 | 0.0040576 | 0.0010169
119 | 0.99847 | -0.029069 | 0.0031583 | 0.00079155
120 | 0.9981 | -0.03621 | 0.0086682 | 0.0021725
121 | 0.99724 | -0.052596 | 0.0065002 | 0.0016291
122 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00051838 | 0.00012992 | -0.00051838 | -0.00012992 | 1.735e-11 | -9.5845e-10 | 0.00079046 | 0.00079046 | 0.00079046 | 0.97584 | -0.4684 | 0.97584 | -0.4684 | 0.21716
1 | -0.00082658 | -0.00020716 | 0.00082659 | 0.00020687 | 1.4198e-08 | -2.8869e-07 | 0.0012604 | 0.0012603 | 0.0012604 | 0.97584 | -0.4684 | 0.97586 | -0.46804 | 0.34627
2 | 0.0018285 | 0.00045438 | -0.0018285 | -0.00045444 | 1.5844e-08 | -5.7827e-08 | 0.0027868 | 0.0027868 | 0.0027868 | 0.97586 | -0.46804 | 0.97585 | -0.46822 | 0.76561
3 | -0.0026551 | -0.00066125 | 0.0026558 | 0.00066026 | 7.1207e-07 | -9.9326e-07 | 0.0040471 | 0.0040466 | 0.0040471 | 0.97586 | -0.46804 | 0.97614 | -0.46238 | 1.1118
4 | 0.0015636 | 0.00038804 | -0.0015634 | -0.00038889 | 1.6279e-07 | -8.5074e-07 | 0.0023828 | 0.0023832 | 0.0023832 | 0.97585 | -0.46822 | 0.97574 | -0.47042 | 0.65472
5 | -0.0028036 | -0.00069731 | 0.0028039 | 0.00069705 | 2.1369e-07 | -2.5362e-07 | 0.0042719 | 0.0042718 | 0.0042719 | 0.97614 | -0.46238 | 0.97622 | -0.46077 | 1.1736
6 | 0.0012498 | 0.00031029 | -0.0012497 | -0.00031085 | 6.5512e-08 | -5.5932e-07 | 0.0019049 | 0.0019051 | 0.0019051 | 0.97574 | -0.47042 | 0.97568 | -0.47153 | 0.52338
7 | -0.0029719 | -0.00073918 | 0.0029722 | 0.00073894 | 2.3503e-07 | -2.3183e-07 | 0.004528 | 0.0045278 | 0.004528 | 0.97622 | -0.46077 | 0.97631 | -0.4591 | 1.2439
8 | 0.0010436 | 0.00025919 | -0.0010435 | -0.00025959 | 3.256e-08 | -4.0764e-07 | 0.0015907 | 0.0015909 | 0.0015909 | 0.97568 | -0.47153 | 0.97565 | -0.47219 | 0.43705
9 | -0.0031193 | -0.00077581 | 0.0031196 | 0.00077553 | 3.3347e-07 | -2.791e-07 | 0.004752 | 0.0047518 | 0.004752 | 0.97631 | -0.4591 | 0.97642 | -0.45684 | 1.3055
10 | -0.0005639 | -0.00014079 | 0.0005639 | 0.00014067 | 2.4817e-09 | -1.1101e-07 | 0.0008583 | 0.00085825 | 0.0008583 | 0.97741 | -0.43696 | 0.97741 | -0.43687 | 0.2358
11 | 0.00033992 | 8.4652e-05 | -0.00033992 | -8.4805e-05 | 1.2277e-09 | -1.5252e-07 | 0.00051731 | 0.00051737 | 0.00051737 | 0.97741 | -0.43696 | 0.9774 | -0.43704 | 0.14213
12 | -0.00076253 | -0.00019046 | 0.00076255 | 0.00018992 | 2.2017e-08 | -5.3228e-07 | 0.0011606 | 0.0011604 | 0.0011606 | 0.97741 | -0.43687 | 0.97744 | -0.43626 | 0.31886
13 | 0.00016983 | 4.2175e-05 | -0.00016983 | -4.2563e-05 | 7.7618e-10 | -3.8777e-07 | 0.00025841 | 0.00025855 | 0.00025855 | 0.9774 | -0.43704 | 0.9774 | -0.43714 | 0.07103
14 | -0.00076255 | -0.00018992 | 0.00076265 | 0.0001876 | 9.601e-08 | -2.3236e-06 | 0.0011604 | 0.0011596 | 0.0011604 | 0.97744 | -0.43626 | 0.97758 | -0.4336 | 0.3188
15 | -0.00092283 | -0.00022774 | 0.00092286 | 0.00022721 | 3.2806e-08 | -5.3598e-07 | 0.0014034 | 0.0014032 | 0.0014034 | 0.97758 | -0.4336 | 0.97761 | -0.43284 | 0.38556
16 | 0.007222 | 0.0018075 | -0.007221 | -0.0018071 | 9.6906e-07 | 3.5205e-07 | 0.010992 | 0.010992 | 0.010992 | 0.97761 | -0.43284 | 0.97747 | -0.43566 | 3.0197
17 | -0.0081448 | -0.0020347 | 0.0081455 | 0.002035 | 6.8618e-07 | 2.898e-07 | 0.012395 | 0.012395 | 0.012395 | 0.97761 | -0.43284 | 0.9777 | -0.43107 | 3.4052
18 | -0.00031322 | -7.8501e-05 | 0.00031322 | 7.7887e-05 | 4.2221e-09 | -6.1349e-07 | 0.00047775 | 0.00047753 | 0.00047775 | 0.97556 | -0.47391 | 0.97557 | -0.47363 | 0.13125
19 | -0.00053271 | -0.0001329 | 0.00053272 | 0.00013235 | 1.1002e-08 | -5.4829e-07 | 0.00081231 | 0.00081211 | 0.00081231 | 0.97557 | -0.47363 | 0.9756 | -0.47319 | 0.22316
20 | -0.0008612 | -0.00021467 | 0.00086124 | 0.0002139 | 4.1086e-08 | -7.6735e-07 | 0.0013131 | 0.0013128 | 0.0013131 | 0.9756 | -0.47319 | 0.97565 | -0.47219 | 0.36075
21 | 0.0046217 | 0.0011557 | -0.0046212 | -0.0011557 | 5.4805e-07 | -1.9367e-08 | 0.0070348 | 0.0070349 | 0.0070349 | 0.97747 | -0.43566 | 0.97734 | -0.43815 | 1.9327
22 | -0.0088474 | -0.0022105 | 0.0088609 | 0.0022166 | 1.3443e-05 | 6.1188e-06 | 0.013463 | 0.013462 | 0.013463 | 0.9777 | -0.43107 | 0.97933 | -0.39914 | 3.6986
23 | 0.00070193 | 0.00017547 | -0.00070192 | -0.00017578 | 1.0785e-08 | -3.0919e-07 | 0.0010681 | 0.0010682 | 0.0010682 | 0.9777 | -0.43107 | 0.97769 | -0.43139 | 0.29348
24 | 0.00026387 | 6.5859e-05 | -0.00026387 | -6.6131e-05 | 1.318e-09 | -2.7211e-07 | 0.00040165 | 0.00040174 | 0.00040174 | 0.97734 | -0.43815 | 0.97734 | -0.43826 | 0.11037
25 | 0.0043573 | 0.0010899 | -0.0043572 | -0.0010899 | 9.7494e-08 | -1.1647e-08 | 0.0066333 | 0.0066333 | 0.0066333 | 0.97734 | -0.43815 | 0.97732 | -0.43862 | 1.8223
26 | 0.0087731 | 0.0021992 | -0.0087705 | -0.0021981 | 2.5729e-06 | 1.161e-06 | 0.01333 | 0.01333 | 0.01333 | 0.97933 | -0.39914 | 0.97901 | -0.40529 | 3.6622
27 | -0.017634 | -0.0044158 | 0.017635 | 0.0044166 | 1.246e-06 | 7.3922e-07 | 0.026792 | 0.026792 | 0.026792 | 0.97933 | -0.39914 | 0.9794 | -0.39765 | 7.3605
28 | 0.0002899 | 7.2516e-05 | -0.0002899 | -7.2656e-05 | 8.196e-10 | -1.4028e-07 | 0.00044117 | 0.00044122 | 0.00044122 | 0.97769 | -0.43139 | 0.97768 | -0.43145 | 0.12122
29 | -0.017635 | -0.0044166 | 0.017645 | 0.0044221 | 9.3302e-06 | 5.5349e-06 | 0.026792 | 0.026792 | 0.026792 | 0.9794 | -0.39765 | 0.97997 | -0.38655 | 7.3605
30 | -0.019292 | -0.0048351 | 0.019304 | 0.0048424 | 1.2126e-05 | 7.2853e-06 | 0.029294 | 0.029294 | 0.029294 | 0.97997 | -0.38655 | 0.98064 | -0.37336 | 8.0479
31 | 0.0024018 | 0.00059982 | -0.0024008 | -0.0006017 | 1.0162e-06 | -1.8881e-06 | 0.0036561 | 0.0036571 | 0.0036571 | 0.97732 | -0.43862 | 0.97687 | -0.44752 | 1.0047
32 | 0.003271 | 0.00081335 | -0.0032708 | -0.00081344 | 1.2572e-07 | -8.8473e-08 | 0.0049823 | 0.0049823 | 0.0049823 | 0.97646 | -0.45603 | 0.97642 | -0.45684 | 1.3688
33 | -0.0033961 | -0.0008447 | 0.0034012 | 0.00084158 | 5.1147e-06 | -3.1157e-06 | 0.0051729 | 0.0051706 | 0.0051729 | 0.97646 | -0.45603 | 0.97807 | -0.4242 | 1.4211
34 | 0.0022752 | 0.00056675 | -0.0022749 | -0.00056739 | 2.9757e-07 | -6.4113e-07 | 0.0034602 | 0.0034605 | 0.0034605 | 0.97807 | -0.4242 | 0.97793 | -0.42695 | 0.95069
35 | -0.0058091 | -0.0014416 | 0.0058131 | 0.0014425 | 4.0754e-06 | 8.5856e-07 | 0.0088327 | 0.0088321 | 0.0088327 | 0.97807 | -0.4242 | 0.97882 | -0.40936 | 2.4266
36 | -0.054785 | -0.014018 | 0.054916 | 0.014102 | 0.00013177 | 8.3657e-05 | 0.082156 | 0.082156 | 0.082156 | 0.99351 | -0.12277 | 0.99612 | -0.073218 | 22.5703
37 | 0.054785 | 0.014018 | -0.054762 | -0.014004 | 2.2636e-05 | 1.4371e-05 | 0.082156 | 0.082156 | 0.082156 | 0.99351 | -0.12277 | 0.99306 | -0.13131 | 22.5703
38 | -0.054916 | -0.014102 | 0.055112 | 0.014226 | 0.00019596 | 0.0001244 | 0.082156 | 0.082155 | 0.082156 | 0.99612 | -0.073218 | 1 | 0 | 22.5702
39 | 0.052041 | 0.013321 | -0.051625 | -0.013058 | 0.00041568 | 0.0002637 | 0.078078 | 0.078079 | 0.078079 | 0.99306 | -0.13131 | 0.9844 | -0.29769 | 21.4503
40 | 0.17157 | 0.043676 | -0.17152 | -0.043644 | 5.0541e-05 | 3.2238e-05 | 0.25554 | 0.25554 | 0.25554 | 1 | 0 | 0.99968 | -0.0061115 | 35.1012
41 | 0.050267 | 0.012717 | -0.050252 | -0.012708 | 1.5392e-05 | 9.7603e-06 | 0.076026 | 0.076026 | 0.076026 | 0.9844 | -0.29769 | 0.98407 | -0.30407 | 20.8864
42 | 0.0020681 | 0.00051557 | -0.0020678 | -0.00051658 | 3.6829e-07 | -1.0089e-06 | 0.0031459 | 0.0031463 | 0.0031463 | 0.97793 | -0.42695 | 0.97774 | -0.4307 | 0.86438
43 | -0.0058131 | -0.0014425 | 0.0058182 | 0.0014435 | 5.0999e-06 | 1.0703e-06 | 0.0088321 | 0.0088313 | 0.0088321 | 0.97882 | -0.40936 | 0.97975 | -0.39082 | 2.4264
44 | 0.0019395 | 0.00048443 | -0.0019395 | -0.00048448 | 1.6065e-08 | -5.141e-08 | 0.0029511 | 0.0029511 | 0.0029511 | 0.97774 | -0.4307 | 0.97773 | -0.43088 | 0.81075
45 | -0.010769 | -0.0026843 | 0.010779 | 0.0026893 | 9.6448e-06 | 4.9599e-06 | 0.016351 | 0.01635 | 0.016351 | 0.97975 | -0.39082 | 0.98071 | -0.37195 | 4.4919
46 | 0.0018113 | 0.00045236 | -0.0018112 | -0.00045264 | 7.3808e-08 | -2.777e-07 | 0.0027561 | 0.0027562 | 0.0027562 | 0.97773 | -0.43088 | 0.97768 | -0.43174 | 0.75719
47 | 0.0015233 | 0.00038047 | -0.0015233 | -0.00038051 | 7.0719e-09 | -3.9489e-08 | 0.0023179 | 0.002318 | 0.002318 | 0.97768 | -0.43174 | 0.97768 | -0.43183 | 0.6368
48 | -0.035125 | -0.008799 | 0.035151 | 0.0088153 | 2.5918e-05 | 1.628e-05 | 0.053278 | 0.053278 | 0.053278 | 0.981 | -0.36627 | 0.98179 | -0.35079 | 14.6368
49 | 0.031356 | 0.0078542 | -0.031347 | -0.0078489 | 8.4875e-06 | 5.3057e-06 | 0.04756 | 0.04756 | 0.04756 | 0.981 | -0.36627 | 0.98071 | -0.37195 | 13.0659
50 | -0.038955 | -0.0097685 | 0.03897 | 0.0097779 | 1.4911e-05 | 9.399e-06 | 0.059042 | 0.059042 | 0.059042 | 0.98179 | -0.35079 | 0.9822 | -0.34276 | 16.2204
51 | 0.020568 | 0.0051596 | -0.020567 | -0.0051588 | 1.3812e-06 | 8.3626e-07 | 0.03121 | 0.03121 | 0.03121 | 0.98071 | -0.37195 | 0.98064 | -0.37336 | 8.5741
52 | -0.040874 | -0.010255 | 0.040888 | 0.010264 | 1.3888e-05 | 8.7661e-06 | 0.061927 | 0.061927 | 0.061927 | 0.9822 | -0.34276 | 0.98257 | -0.33563 | 17.0128
53 | 0.005758 | 0.001443 | -0.0057569 | -0.0014428 | 1.0867e-06 | 2.1288e-07 | 0.0087199 | 0.0087201 | 0.0087201 | 0.98257 | -0.33563 | 0.98236 | -0.3396 | 2.3956
54 | -0.046645 | -0.011707 | 0.04666 | 0.011716 | 1.4118e-05 | 8.9396e-06 | 0.070647 | 0.070647 | 0.070647 | 0.98257 | -0.33563 | 0.98289 | -0.32929 | 19.4084
55 | 0.010098 | 0.0025292 | -0.010097 | -0.0025287 | 8.7779e-07 | 4.3484e-07 | 0.015286 | 0.015286 | 0.015286 | 0.98289 | -0.32929 | 0.9828 | -0.33112 | 4.1996
56 | -0.056757 | -0.014245 | 0.056799 | 0.014271 | 4.1366e-05 | 2.6285e-05 | 0.085933 | 0.085933 | 0.085933 | 0.98289 | -0.32929 | 0.98367 | -0.31402 | 23.608
57 | -0.001441 | -0.00036116 | 0.0014412 | 0.00036003 | 1.7487e-07 | -1.1288e-06 | 0.0021823 | 0.0021818 | 0.0021823 | 0.9826 | -0.33507 | 0.98273 | -0.33252 | 0.59953
58 | 0.0068269 | 0.0017103 | -0.0068245 | -0.0017095 | 2.4479e-06 | 7.9296e-07 | 0.010337 | 0.010337 | 0.010337 | 0.98273 | -0.33252 | 0.98234 | -0.34005 | 2.8399
59 | -0.0082682 | -0.0020703 | 0.0082687 | 0.0020706 | 5.5145e-07 | 2.3403e-07 | 0.012519 | 0.012519 | 0.012519 | 0.98273 | -0.33252 | 0.9828 | -0.33112 | 3.4392
60 | 0.0041096 | 0.0010295 | -0.0041086 | -0.0010297 | 1.0605e-06 | -2.449e-07 | 0.006225 | 0.0062253 | 0.0062253 | 0.98234 | -0.34005 | 0.98206 | -0.34546 | 1.7102
61 | 0.0027149 | 0.00068005 | -0.0027146 | -0.00068035 | 2.2118e-07 | -2.9995e-07 | 0.0041122 | 0.0041124 | 0.0041124 | 0.98234 | -0.34005 | 0.98225 | -0.34176 | 1.1298
62 | 0.0012169 | 0.00030372 | -0.0012168 | -0.00030415 | 4.7485e-08 | -4.327e-07 | 0.0018516 | 0.0018518 | 0.0018518 | 0.97768 | -0.43183 | 0.97764 | -0.43265 | 0.50873
63 | 0.00085532 | 0.00021355 | -0.00085531 | -0.00021374 | 9.8608e-09 | -1.8831e-07 | 0.0013016 | 0.0013016 | 0.0013016 | 0.97764 | -0.43265 | 0.97763 | -0.4329 | 0.35759
64 | 0.00059351 | 0.00014813 | -0.0005935 | -0.00014874 | 1.5298e-08 | -6.1714e-07 | 0.00090314 | 0.00090337 | 0.00090337 | 0.97763 | -0.4329 | 0.9776 | -0.43344 | 0.24818
65 | 0.005876 | 0.0014726 | -0.0058754 | -0.0014725 | 5.524e-07 | 1.2134e-07 | 0.008931 | 0.0089311 | 0.0089311 | 0.97901 | -0.40529 | 0.97891 | -0.40727 | 2.4536
66 | 0.08231 | 0.020793 | -0.082243 | -0.02075 | 6.6942e-05 | 4.2694e-05 | 0.12394 | 0.12394 | 0.12394 | 0.98867 | -0.21695 | 0.98779 | -0.23393 | 34.0494
67 | -0.086876 | -0.021937 | 0.086906 | 0.021956 | 2.9365e-05 | 1.8735e-05 | 0.13081 | 0.13081 | 0.13081 | 0.98867 | -0.21695 | 0.98904 | -0.2099 | 35.9376
68 | 0.079316 | 0.020017 | -0.079274 | -0.01999 | 4.1804e-05 | 2.6655e-05 | 0.11953 | 0.11953 | 0.11953 | 0.98779 | -0.23393 | 0.98723 | -0.24494 | 32.8383
69 | -0.089571 | -0.022624 | 0.089651 | 0.022675 | 7.9492e-05 | 5.0725e-05 | 0.13482 | 0.13482 | 0.13482 | 0.98904 | -0.2099 | 0.99 | -0.1914 | 37.0393
70 | 0.074852 | 0.018882 | -0.074852 | -0.018882 | 2.3951e-07 | 1.5264e-07 | 0.11287 | 0.11287 | 0.11287 | 0.98723 | -0.24494 | 0.98722 | -0.24501 | 31.0072
71 | -0.11018 | -0.027819 | 0.11022 | 0.027846 | 4.2098e-05 | 2.689e-05 | 0.16567 | 0.16567 | 0.16567 | 0.99 | -0.1914 | 0.99041 | -0.18342 | 45.5146
72 | 0.071886 | 0.018138 | -0.071806 | -0.018087 | 7.9477e-05 | 5.0635e-05 | 0.1084 | 0.1084 | 0.1084 | 0.98722 | -0.24501 | 0.98603 | -0.26813 | 29.7789
73 | -0.11308 | -0.028564 | 0.11317 | 0.02862 | 8.8073e-05 | 5.6262e-05 | 0.16998 | 0.16998 | 0.16998 | 0.99041 | -0.18342 | 0.99125 | -0.16719 | 46.6969
74 | 0.068988 | 0.017381 | -0.068952 | -0.017358 | 3.6355e-05 | 2.3153e-05 | 0.10414 | 0.10414 | 0.10414 | 0.98603 | -0.26813 | 0.98546 | -0.27915 | 28.6105
75 | -0.11921 | -0.030133 | 0.11948 | 0.030305 | 0.00026939 | 0.00017212 | 0.17904 | 0.17904 | 0.17904 | 0.99125 | -0.16719 | 0.9937 | -0.12018 | 49.1864
76 | 0.065509 | 0.016495 | -0.065478 | -0.016475 | 3.1423e-05 | 2.0002e-05 | 0.098944 | 0.098944 | 0.098944 | 0.98546 | -0.27915 | 0.98495 | -0.28919 | 27.1825
77 | 0.063707 | 0.016031 | -0.063646 | -0.015993 | 6.0609e-05 | 3.8568e-05 | 0.096269 | 0.096269 | 0.096269 | 0.98495 | -0.28919 | 0.98392 | -0.30912 | 26.4476
78 | 0.00078903 | 0.00019682 | -0.00078899 | -0.00019774 | 4.1313e-08 | -9.1931e-07 | 0.0012045 | 0.0012048 | 0.0012048 | 0.97449 | -0.4919 | 0.97444 | -0.493 | 0.331
79 | -0.0017291 | -0.00043243 | 0.001731 | 0.00042484 | 1.8357e-06 | -7.5964e-06 | 0.00264 | 0.0026369 | 0.00264 | 0.97449 | -0.4919 | 0.97562 | -0.46943 | 0.72527
80 | -0.0035184 | -0.0008728 | 0.003519 | 0.00087249 | 6.0833e-07 | -3.1516e-07 | 0.005363 | 0.0053627 | 0.005363 | 0.97562 | -0.46943 | 0.97581 | -0.46577 | 1.4733
81 | 0.048624 | 0.0123 | -0.048592 | -0.01228 | 3.1163e-05 | 1.975e-05 | 0.073565 | 0.073565 | 0.073565 | 0.98407 | -0.30407 | 0.98338 | -0.31744 | 20.2101
82 | 0.047806 | 0.012083 | -0.047766 | -0.012057 | 4.0297e-05 | 2.553e-05 | 0.072375 | 0.072375 | 0.072375 | 0.98338 | -0.31744 | 0.98248 | -0.33504 | 19.8834
83 | 0.046557 | 0.011754 | -0.046544 | -0.011746 | 1.2774e-05 | 8.0888e-06 | 0.070544 | 0.070544 | 0.070544 | 0.98248 | -0.33504 | 0.98218 | -0.34077 | 19.3802
84 | 0.16636 | 0.042351 | -0.16632 | -0.042323 | 4.4569e-05 | 2.8423e-05 | 0.24786 | 0.24786 | 0.24786 | 0.99968 | -0.0061115 | 0.99939 | -0.011669 | 34.0466
85 | -0.12232 | -0.031018 | 0.12258 | 0.031183 | 0.00025786 | 0.00016477 | 0.1833 | 0.1833 | 0.1833 | 0.9937 | -0.12018 | 0.99599 | -0.076425 | 50.3573
86 | -0.13908 | -0.035319 | 0.13924 | 0.035421 | 0.0001597 | 0.00010208 | 0.20795 | 0.20795 | 0.20795 | 0.99599 | -0.076425 | 0.99724 | -0.052596 | 57.1302
87 | -0.0015154 | -0.0003798 | 0.0015155 | 0.00037951 | 5.3429e-08 | -2.9663e-07 | 0.0023152 | 0.0023151 | 0.0023152 | 0.97397 | -0.50171 | 0.97401 | -0.50097 | 0.63606
88 | -0.0042066 | -0.001054 | 0.0042066 | 0.001054 | 3.751e-08 | -6.1395e-09 | 0.0064264 | 0.0064264 | 0.0064264 | 0.97401 | -0.50097 | 0.97402 | -0.50078 | 1.7655
89 | -0.0054897 | -0.0013755 | 0.0054906 | 0.0013757 | 9.4886e-07 | 1.594e-07 | 0.0083865 | 0.0083863 | 0.0083865 | 0.97402 | -0.50078 | 0.9742 | -0.49715 | 2.304
90 | -0.0092765 | -0.0023245 | 0.009278 | 0.0023252 | 1.5034e-06 | 7.1349e-07 | 0.014169 | 0.014169 | 0.014169 | 0.9742 | -0.49715 | 0.97438 | -0.49375 | 3.8926
91 | -0.010798 | -0.0027062 | 0.0108 | 0.0027072 | 1.9029e-06 | 9.8538e-07 | 0.01649 | 0.01649 | 0.01649 | 0.97438 | -0.49375 | 0.97456 | -0.49005 | 4.5303
92 | -0.013416 | -0.0033629 | 0.013418 | 0.0033638 | 1.5422e-06 | 8.6488e-07 | 0.020485 | 0.020485 | 0.020485 | 0.97456 | -0.49005 | 0.97469 | -0.48764 | 5.6277
93 | -0.014663 | -0.0036759 | 0.014669 | 0.0036791 | 5.6277e-06 | 3.2283e-06 | 0.022386 | 0.022386 | 0.022386 | 0.97469 | -0.48764 | 0.9751 | -0.47959 | 6.15
94 | -0.01634 | -0.0040979 | 0.016348 | 0.0041024 | 7.6052e-06 | 4.4603e-06 | 0.024936 | 0.024936 | 0.024936 | 0.9751 | -0.47959 | 0.97559 | -0.46983 | 6.8506
95 | -0.019036 | -0.0047761 | 0.019045 | 0.0047816 | 9.1009e-06 | 5.4649e-06 | 0.029036 | 0.029036 | 0.029036 | 0.97559 | -0.46983 | 0.9761 | -0.4598 | 7.9769
96 | -0.0049459 | -0.0012301 | 0.0049468 | 0.0012301 | 9.6602e-07 | 5.1859e-08 | 0.0075386 | 0.0075384 | 0.0075386 | 0.97581 | -0.46577 | 0.97602 | -0.46165 | 2.071
97 | -0.021529 | -0.0054041 | 0.021538 | 0.0054095 | 8.7974e-06 | 5.358e-06 | 0.032823 | 0.032823 | 0.032823 | 0.9761 | -0.4598 | 0.97654 | -0.45124 | 9.0172
98 | -0.02281 | -0.0057284 | 0.022816 | 0.005732 | 5.7822e-06 | 3.5409e-06 | 0.034762 | 0.034762 | 0.034762 | 0.97654 | -0.45124 | 0.97681 | -0.44593 | 9.55
99 | -0.030336 | -0.0076157 | 0.030363 | 0.0076325 | 2.6938e-05 | 1.6819e-05 | 0.046216 | 0.046216 | 0.046216 | 0.97681 | -0.44593 | 0.97775 | -0.42733 | 12.6968
100 | 0.0075194 | 0.0018837 | -0.0075184 | -0.0018833 | 1.0421e-06 | 4.0184e-07 | 0.011454 | 0.011454 | 0.011454 | 0.97681 | -0.44593 | 0.97666 | -0.44884 | 3.1468
101 | 0.0086676 | 0.0021642 | -0.0086669 | -0.0021639 | 6.9257e-07 | 3.1008e-07 | 0.013188 | 0.013188 | 0.013188 | 0.97775 | -0.42733 | 0.97767 | -0.42901 | 3.6231
102 | -0.03903 | -0.0097967 | 0.039044 | 0.0098052 | 1.3494e-05 | 8.5084e-06 | 0.059404 | 0.059404 | 0.059404 | 0.97775 | -0.42733 | 0.97812 | -0.42008 | 16.3198
103 | 0.0040143 | 0.0010051 | -0.0040142 | -0.0010051 | 7.1173e-08 | -1.7949e-08 | 0.0061158 | 0.0061158 | 0.0061158 | 0.97666 | -0.44884 | 0.97664 | -0.44921 | 1.6802
104 | 0.0077437 | 0.0019325 | -0.0077352 | -0.0019291 | 8.4984e-06 | 3.3947e-06 | 0.011783 | 0.011784 | 0.011784 | 0.97767 | -0.42901 | 0.9765 | -0.45214 | 3.2373
105 | -0.040179 | -0.01009 | 0.040213 | 0.010111 | 3.4234e-05 | 2.1603e-05 | 0.061131 | 0.061131 | 0.061131 | 0.97812 | -0.42008 | 0.97903 | -0.40224 | 16.7943
106 | 0.002406 | 0.00060203 | -0.0024058 | -0.0006024 | 2.0133e-07 | -3.7112e-07 | 0.0036655 | 0.0036657 | 0.0036657 | 0.97664 | -0.44921 | 0.97655 | -0.45097 | 1.007
107 | 0.0067042 | 0.0016707 | -0.0067032 | -0.0016704 | 9.5832e-07 | 3.0686e-07 | 0.010213 | 0.010213 | 0.010213 | 0.9765 | -0.45214 | 0.97634 | -0.45516 | 2.8057
108 | -0.041148 | -0.010346 | 0.041189 | 0.010371 | 4.0277e-05 | 2.5431e-05 | 0.062553 | 0.062553 | 0.062553 | 0.97903 | -0.40224 | 0.98008 | -0.38177 | 17.1848
109 | 0.0024058 | 0.0006024 | -0.0024055 | -0.00060289 | 2.6273e-07 | -4.8407e-07 | 0.0036657 | 0.0036659 | 0.0036659 | 0.97655 | -0.45097 | 0.97643 | -0.45326 | 1.0071
110 | 0.045617 | 0.011514 | -0.045584 | -0.011493 | 3.2623e-05 | 2.0648e-05 | 0.069139 | 0.069139 | 0.069139 | 0.98218 | -0.34077 | 0.98141 | -0.35571 | 18.9943
111 | 0.044798 | 0.011296 | -0.044795 | -0.011294 | 3.1969e-06 | 2.0227e-06 | 0.067947 | 0.067947 | 0.067947 | 0.98141 | -0.35571 | 0.98134 | -0.3572 | 18.6668
112 | 0.043329 | 0.010927 | -0.043303 | -0.010911 | 2.5606e-05 | 1.6189e-05 | 0.065725 | 0.065725 | 0.065725 | 0.98134 | -0.3572 | 0.9807 | -0.36955 | 18.0562
113 | 0.042242 | 0.010644 | -0.042217 | -0.010629 | 2.4664e-05 | 1.5583e-05 | 0.064114 | 0.064114 | 0.064114 | 0.9807 | -0.36955 | 0.98008 | -0.38177 | 17.6137
114 | 0.0067032 | 0.0016704 | -0.0067012 | -0.0016698 | 2.0634e-06 | 6.6107e-07 | 0.010213 | 0.010213 | 0.010213 | 0.97634 | -0.45516 | 0.97602 | -0.46165 | 2.8058
115 | 0.0017543 | 0.00043962 | -0.0017543 | -0.00043967 | 1.3356e-08 | -5.3673e-08 | 0.0026746 | 0.0026746 | 0.0026746 | 0.97602 | -0.46165 | 0.97601 | -0.46181 | 0.73479
116 | 0.059602 | 0.014979 | -0.059588 | -0.01497 | 1.3944e-05 | 8.8664e-06 | 0.090153 | 0.090153 | 0.090153 | 0.98392 | -0.30912 | 0.98367 | -0.31402 | 24.7674
117 | 0.16193 | 0.041223 | -0.16189 | -0.041198 | 3.8836e-05 | 2.4762e-05 | 0.24133 | 0.24133 | 0.24133 | 0.99939 | -0.011669 | 0.99912 | -0.016645 | 33.1491
118 | 0.15783 | 0.040181 | -0.15774 | -0.040121 | 9.4493e-05 | 6.0237e-05 | 0.23528 | 0.23528 | 0.23528 | 0.99912 | -0.016645 | 0.99847 | -0.029069 | 32.319
119 | 0.15458 | 0.03933 | -0.15453 | -0.039296 | 5.3183e-05 | 3.3898e-05 | 0.23058 | 0.23058 | 0.23058 | 0.99847 | -0.029069 | 0.9981 | -0.03621 | 31.6725
120 | 0.14586 | 0.037123 | -0.14574 | -0.03705 | 0.00011512 | 7.3339e-05 | 0.21765 | 0.21765 | 0.21765 | 0.9981 | -0.03621 | 0.99724 | -0.052596 | 29.8974

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.23235 | 0.05891

## res_load
| p_mw | q_mvar
0 | 0.0003082 | 7.7241e-05
1 | 0.00051838 | 0.00012992
2 | 0.00026493 | 6.6398e-05
3 | 0.00014782 | 3.7047e-05
4 | 0.00031364 | 7.8606e-05
5 | 0.00016807 | 4.2122e-05
6 | 0.00020613 | 5.1661e-05
7 | 0.00014709 | 3.6864e-05
8 | 0.00022398 | 5.6134e-05
9 | 0.00019863 | 4.978e-05
10 | 0.00017009 | 4.263e-05
11 | 0.00016983 | 4.2563e-05
12 | 0.00016018 | 4.0145e-05
13 | 0.00031322 | 7.8501e-05
14 | 0.00021948 | 5.5008e-05
15 | 0.00032848 | 8.2324e-05
16 | 0.00018231 | 4.5691e-05
17 | 0.0025993 | 0.00065143
18 | 0.00041201 | 0.00010326
19 | 0.0016479 | 0.00041299
20 | 0.00026387 | 6.6131e-05
21 | 0.0019554 | 0.00049006
22 | 0.00012509 | 3.1351e-05
23 | 0.00015126 | 3.791e-05
24 | 0.00013269 | 3.3256e-05
25 | 0.0027214 | 0.00068206
26 | 0.0040221 | 0.001008
27 | 0.0013578 | 0.0003403
28 | 0.00020677 | 5.1822e-05
29 | 0.00012828 | 3.2151e-05
30 | 0.0049509 | 0.0012408
31 | 0.00012817 | 3.2121e-05
32 | 0.00028794 | 7.2164e-05
33 | 0.0037698 | 0.0009448
34 | 0.0038033 | 0.0009532
35 | 0.0019041 | 0.00047721
36 | 0.0012625 | 0.00031641
37 | 0.0057569 | 0.0014428
38 | 0.0024008 | 0.0006017
39 | 0.001441 | 0.00036116
40 | 0.001828 | 0.00045815
41 | 0.0041086 | 0.0010297
42 | 0.0027146 | 0.00068035
43 | 0.00030641 | 7.6793e-05
44 | 0.0003615 | 9.0601e-05
45 | 0.0002618 | 6.5613e-05
46 | 0.0005935 | 0.00014874
47 | 0.0002899 | 7.2656e-05
48 | 0.0028945 | 0.00072543
49 | 0.0058754 | 0.0014725
50 | 0.0045666 | 0.0011445
51 | 0.0029266 | 0.00073346
52 | 0.0026655 | 0.00066803
53 | 0.0044219 | 0.0011082
54 | 0.020525 | 0.0051441
55 | 0.0029663 | 0.00074344
56 | 0.0028643 | 0.00071786
57 | 0.0028182 | 0.00070631
58 | 0.0060366 | 0.0015129
59 | 0.0034425 | 0.00086277
60 | 0.0017708 | 0.00044381
61 | 0.00094011 | 0.00023561
62 | 0.00078899 | 0.00019774
63 | 0.0017874 | 0.00044796
64 | 0.0016281 | 0.00040805
65 | 0.00078596 | 0.00019698
66 | 0.0012094 | 0.00030311
67 | 0.0051577 | 0.0012926
68 | 0.0028463 | 0.00071335
69 | 0.016501 | 0.0041357
70 | 0.0015154 | 0.0003798
71 | 0.0026911 | 0.00067445
72 | 0.001283 | 0.00032156
73 | 0.0037859 | 0.00094884
74 | 0.0015201 | 0.00038096
75 | 0.0026164 | 0.00065572
76 | 0.0012453 | 0.00031211
77 | 0.0016712 | 0.00041885
78 | 0.0026881 | 0.0006737
79 | 0.0014269 | 0.00035761
80 | 0.0024839 | 0.00062253
81 | 0.0012728 | 0.00031899
82 | 0.0035041 | 0.0008782
83 | 0.00092319 | 0.00023137
84 | 0.0011352 | 0.00028452
85 | 0.0016082 | 0.00040306
86 | 0.001031 | 0.00025839
87 | 0.00093539 | 0.00023443
88 | 0.0024055 | 0.00060289
89 | 0.00092708 | 0.00023235
90 | 0.00078624 | 0.00019705
91 | 0.0014658 | 0.00036736
92 | 0.0010617 | 0.00026608
93 | 0.0010284 | 0.00025774
94 | 0.0017543 | 0.00043967
95 | 0.0040441 | 0.0010135
96 | 0.0027899 | 0.00069921
97 | 0.0043884 | 0.0010998
98 | 0.0040576 | 0.0010169
99 | 0.0031583 | 0.00079155
100 | 0.0086682 | 0.0021725
101 | 0.0065002 | 0.0016291

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1