## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1216-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1216-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1216-4_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1216-4_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1216-4_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1216-4_0_3_node_103 | 0.4 | n |  | TRUE
6 | bus_LV_1216-4_0_3_node_97 | 0.4 | n |  | TRUE
7 | bus_LV_1216-4_0_3_node_92 | 0.4 | n |  | TRUE
8 | bus_LV_1216-4_0_3_node_101 | 0.4 | n |  | TRUE
9 | bus_LV_1216-4_0_3_node_104 | 0.4 | n |  | TRUE
10 | bus_LV_1216-4_0_3_node_100 | 0.4 | n |  | TRUE
11 | bus_LV_1216-4_0_3_node_96 | 0.4 | n |  | TRUE
12 | bus_LV_1216-4_0_3_node_93 | 0.4 | n |  | TRUE
13 | bus_LV_1216-4_0_3_node_90 | 0.4 | n |  | TRUE
14 | bus_LV_1216-4_0_3_node_102 | 0.4 | n |  | TRUE
15 | bus_LV_1216-4_0_3_node_5 | 0.4 | n |  | TRUE
16 | bus_LV_1216-4_0_3_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_1216-4_0_3_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_1216-4_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1216-4_0_3_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_1216-4_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1216-4_0_3_node_116 | 0.4 | n |  | TRUE
22 | bus_LV_1216-4_0_3_node_115 | 0.4 | n |  | TRUE
23 | bus_LV_1216-4_0_3_node_113 | 0.4 | n |  | TRUE
24 | bus_LV_1216-4_0_3_node_9 | 0.4 | n |  | TRUE
25 | bus_LV_1216-4_0_3_node_126 | 0.4 | n |  | TRUE
26 | bus_LV_1216-4_0_3_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_1216-4_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1216-4_0_3_node_112 | 0.4 | n |  | TRUE
29 | bus_LV_1216-4_0_3_node_12 | 0.4 | n |  | TRUE
30 | bus_LV_1216-4_0_3_node_111 | 0.4 | n |  | TRUE
31 | bus_LV_1216-4_0_3_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_1216-4_0_3_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_1216-4_0_3_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_1216-4_0_3_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_1216-4_0_3_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_1216-4_0_3_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_1216-4_0_3_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_1216-4_0_3_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_1216-4_0_3_node_61 | 0.4 | n |  | TRUE
40 | bus_LV_1216-4_0_3_node_58 | 0.4 | n |  | TRUE
41 | bus_LV_1216-4_0_3_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_1216-4_0_3_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_1216-4_0_3_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_1216-4_0_3_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_1216-4_0_3_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_1216-4_0_3_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_1216-4_0_3_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_1216-4_0_3_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_1216-4_0_3_node_59 | 0.4 | n |  | TRUE
50 | bus_LV_1216-4_0_3_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_1216-4_0_3_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_1216-4_0_3_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_1216-4_0_3_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_1216-4_0_3_node_33 | 0.4 | n |  | TRUE
55 | bus_LV_1216-4_0_3_node_34 | 0.4 | n |  | TRUE
56 | bus_LV_1216-4_0_3_node_65 | 0.4 | n |  | TRUE
57 | bus_LV_1216-4_0_3_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_1216-4_0_3_node_63 | 0.4 | n |  | TRUE
59 | bus_LV_1216-4_0_3_node_36 | 0.4 | n |  | TRUE
60 | bus_LV_1216-4_0_3_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_1216-4_0_3_node_76 | 0.4 | n |  | TRUE
62 | bus_LV_1216-4_0_3_node_77 | 0.4 | n |  | TRUE
63 | bus_LV_1216-4_0_3_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_1216-4_0_3_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_1216-4_0_3_node_39 | 0.4 | n |  | TRUE
66 | bus_LV_1216-4_0_3_node_40 | 0.4 | n |  | TRUE
67 | bus_LV_1216-4_0_3_node_41 | 0.4 | n |  | TRUE
68 | bus_LV_1216-4_0_3_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_1216-4_0_3_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_1216-4_0_3_node_81 | 0.4 | n |  | TRUE
71 | bus_LV_1216-4_0_3_node_75 | 0.4 | n |  | TRUE
72 | bus_LV_1216-4_0_3_node_117 | 0.4 | n |  | TRUE
73 | bus_LV_1216-4_0_3_node_119 | 0.4 | n |  | TRUE
74 | bus_LV_1216-4_0_3_node_73 | 0.4 | n |  | TRUE
75 | bus_LV_1216-4_0_3_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_1216-4_0_3_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_1216-4_0_3_node_48 | 0.4 | n |  | TRUE
78 | bus_LV_1216-4_0_3_node_49 | 0.4 | n |  | TRUE
79 | bus_LV_1216-4_0_3_node_50 | 0.4 | n |  | TRUE
80 | bus_LV_1216-4_0_3_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_1216-4_0_3_node_118 | 0.4 | n |  | TRUE
82 | bus_LV_1216-4_0_3_node_54 | 0.4 | n |  | TRUE
83 | bus_LV_1216-4_0_3_node_55 | 0.4 | n |  | TRUE
84 | bus_LV_1216-4_0_3_node_56 | 0.4 | n |  | TRUE
85 | bus_LV_1216-4_0_3_node_57 | 0.4 | n |  | TRUE
86 | bus_LV_1216-4_0_3_node_86 | 0.4 | n |  | TRUE
87 | bus_LV_1216-4_0_3_node_87 | 0.4 | n |  | TRUE
88 | bus_LV_1216-4_0_3_node_105 | 0.4 | n |  | TRUE
89 | bus_LV_1216-4_0_3_node_88 | 0.4 | n |  | TRUE
90 | bus_LV_1216-4_0_3_node_108 | 0.4 | n |  | TRUE
91 | bus_LV_1216-4_0_3_node_114 | 0.4 | n |  | TRUE
92 | bus_LV_1216-4_0_3_node_60 | 0.4 | n |  | TRUE
93 | bus_LV_1216-4_0_3_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_1216-4_0_3_node_62 | 0.4 | n |  | TRUE
95 | bus_LV_1216-4_0_3_node_64 | 0.4 | n |  | TRUE
96 | bus_LV_1216-4_0_3_node_66 | 0.4 | n |  | TRUE
97 | bus_LV_1216-4_0_3_node_70 | 0.4 | n |  | TRUE
98 | bus_LV_1216-4_0_3_node_67 | 0.4 | n |  | TRUE
99 | bus_LV_1216-4_0_3_node_68 | 0.4 | n |  | TRUE
100 | bus_LV_1216-4_0_3_node_69 | 0.4 | n |  | TRUE
101 | bus_LV_1216-4_0_3_node_71 | 0.4 | n |  | TRUE
102 | bus_LV_1216-4_0_3_node_72 | 0.4 | n |  | TRUE
103 | bus_LV_1216-4_0_3_node_74 | 0.4 | n |  | TRUE
104 | bus_LV_1216-4_0_3_node_107 | 0.4 | n |  | TRUE
105 | bus_LV_1216-4_0_3_node_120 | 0.4 | n |  | TRUE
106 | bus_LV_1216-4_0_3_node_78 | 0.4 | n |  | TRUE
107 | bus_LV_1216-4_0_3_node_79 | 0.4 | n |  | TRUE
108 | bus_LV_1216-4_0_3_node_80 | 0.4 | n |  | TRUE
109 | bus_LV_1216-4_0_3_node_84 | 0.4 | n |  | TRUE
110 | bus_LV_1216-4_0_3_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_1216-4_0_3_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_1216-4_0_3_node_83 | 0.4 | n |  | TRUE
113 | bus_LV_1216-4_0_3_node_85 | 0.4 | n |  | TRUE
114 | bus_LV_1216-4_0_3_node_106 | 0.4 | n |  | TRUE
115 | bus_LV_1216-4_0_3_node_91 | 0.4 | n |  | TRUE
116 | bus_LV_1216-4_0_3_node_98 | 0.4 | n |  | TRUE
117 | bus_LV_1216-4_0_3_node_99 | 0.4 | n |  | TRUE
118 | bus_LV_1216-4_0_3_node_94 | 0.4 | n |  | TRUE
119 | bus_LV_1216-4_0_3_node_128 | 0.4 | n |  | TRUE
120 | bus_LV_1216-4_0_3_node_127 | 0.4 | n |  | TRUE
121 | bus_LV_1216-4_0_3_node_123 | 0.4 | n |  | TRUE
122 | bus_LV_1216-4_0_3_node_121 | 0.4 | n |  | TRUE
123 | bus_LV_1216-4_0_3_node_109 | 0.4 | n |  | TRUE
124 | bus_LV_1216-4_0_3_node_110 | 0.4 | n |  | TRUE
125 | bus_LV_1216-4_0_3_node_124 | 0.4 | n |  | TRUE
126 | bus_LV_1216-4_0_3_node_125 | 0.4 | n |  | TRUE
127 | bus_MV_11_0_node_184 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1216-4_0_3_load_0 | 0 | 0.0033026 | 0.0008277 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1216-4_0_3_load_1 | 1 | 0.0011571 | 0.00028999 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1216-4_0_3_load_103 | 5 | 0.0011742 | 0.00029429 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1216-4_0_3_load_101 | 8 | 0.002938 | 0.00073634 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1216-4_0_3_load_104 | 9 | 0.0011899 | 0.00029822 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1216-4_0_3_load_96 | 11 | 0.001467 | 0.00036767 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1216-4_0_3_load_93 | 12 | 0.0011195 | 0.00028058 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1216-4_0_3_load_102 | 14 | 0.0022406 | 0.00056155 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1216-4_0_3_load_5 | 15 | 0.00090255 | 0.0002262 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1216-4_0_3_load_7 | 17 | 0.00067869 | 0.0001701 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1216-4_0_3_load_8 | 19 | 0.00056203 | 0.00014086 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1216-4_0_3_load_13 | 20 | 0.00048229 | 0.00012087 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1216-4_0_3_load_115 | 22 | 0.00029919 | 7.4983e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1216-4_0_3_load_113 | 23 | 0.0003001 | 7.5212e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1216-4_0_3_load_126 | 25 | 0.00030065 | 7.535e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1216-4_0_3_load_11 | 26 | 0.00039662 | 9.9402e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1216-4_0_3_load_12 | 29 | 0.00081613 | 0.00020454 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1216-4_0_3_load_111 | 30 | 0.0019617 | 0.00049165 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1216-4_0_3_load_14 | 31 | 0.00044458 | 0.00011142 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1216-4_0_3_load_16 | 32 | 0.017514 | 0.0043895 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1216-4_0_3_load_19 | 33 | 0.0015924 | 0.0003991 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1216-4_0_3_load_20 | 34 | 0.0014385 | 0.00036052 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1216-4_0_3_load_21 | 35 | 0.0038169 | 0.00095659 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1216-4_0_3_load_18 | 36 | 0.0021053 | 0.00052765 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1216-4_0_3_load_22 | 37 | 0.0012608 | 0.00031599 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1216-4_0_3_load_61 | 39 | 0.0010378 | 0.0002601 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1216-4_0_3_load_58 | 40 | 0.00075955 | 0.00019036 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1216-4_0_3_load_23 | 41 | 0.0011965 | 0.00029987 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1216-4_0_3_load_24 | 42 | 0.0015537 | 0.0003894 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1216-4_0_3_load_25 | 43 | 0.004749 | 0.0011902 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1216-4_0_3_load_26 | 44 | 0.0016689 | 0.00041827 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1216-4_0_3_load_27 | 45 | 0.0047839 | 0.001199 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1216-4_0_3_load_43 | 46 | 0.0011029 | 0.00027642 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1216-4_0_3_load_51 | 48 | 0.0010624 | 0.00026627 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1216-4_0_3_load_59 | 49 | 0.0021979 | 0.00055084 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1216-4_0_3_load_29 | 50 | 0.0012278 | 0.00030771 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1216-4_0_3_load_30 | 51 | 0.00094888 | 0.00023781 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1216-4_0_3_load_32 | 53 | 0.00065277 | 0.0001636 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1216-4_0_3_load_33 | 54 | 0.0012394 | 0.00031062 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1216-4_0_3_load_34 | 55 | 0.001072 | 0.00026868 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1216-4_0_3_load_65 | 56 | 0.0014259 | 0.00035736 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1216-4_0_3_load_35 | 57 | 0.0016206 | 0.00040617 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1216-4_0_3_load_63 | 58 | 0.0021407 | 0.00053652 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1216-4_0_3_load_36 | 59 | 0.0015916 | 0.00039888 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1216-4_0_3_load_45 | 60 | 0.026416 | 0.0066204 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1216-4_0_3_load_76 | 61 | 0.0012137 | 0.00030418 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1216-4_0_3_load_77 | 62 | 0.0025252 | 0.00063287 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1216-4_0_3_load_37 | 63 | 0.0027466 | 0.00068836 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1216-4_0_3_load_38 | 64 | 0.002403 | 0.00060224 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1216-4_0_3_load_41 | 67 | 0.0045311 | 0.0011356 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1216-4_0_3_load_42 | 68 | 0.002403 | 0.00060224 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1216-4_0_3_load_53 | 69 | 0.0025097 | 0.00062898 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1216-4_0_3_load_81 | 70 | 0.0032055 | 0.00080338 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1216-4_0_3_load_117 | 72 | 0.0013161 | 0.00032984 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1216-4_0_3_load_119 | 73 | 0.00058535 | 0.0001467 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1216-4_0_3_load_73 | 74 | 0.0025097 | 0.00062898 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1216-4_0_3_load_46 | 75 | 0.0015224 | 0.00038155 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1216-4_0_3_load_47 | 76 | 0.0010077 | 0.00025255 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1216-4_0_3_load_48 | 77 | 0.0018388 | 0.00046085 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1216-4_0_3_load_50 | 79 | 0.0016775 | 0.00042042 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1216-4_0_3_load_52 | 80 | 0.0024198 | 0.00060647 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1216-4_0_3_load_118 | 81 | 0.0014826 | 0.00037157 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1216-4_0_3_load_54 | 82 | 0.00066305 | 0.00016618 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1216-4_0_3_load_55 | 83 | 0.0011253 | 0.00028204 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1216-4_0_3_load_56 | 84 | 0.0026313 | 0.00065946 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1216-4_0_3_load_87 | 87 | 0.00065816 | 0.00016495 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1216-4_0_3_load_105 | 88 | 0.0012028 | 0.00030145 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1216-4_0_3_load_88 | 89 | 0.00084843 | 0.00021264 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1216-4_0_3_load_108 | 90 | 0.0014255 | 0.00035727 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1216-4_0_3_load_60 | 92 | 0.0011125 | 0.00027882 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1216-4_0_3_load_95 | 93 | 0.0014087 | 0.00035306 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1216-4_0_3_load_62 | 94 | 0.0021882 | 0.00054841 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1216-4_0_3_load_64 | 95 | 0.0031694 | 0.00079432 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1216-4_0_3_load_70 | 97 | 0.0028703 | 0.00071937 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1216-4_0_3_load_67 | 98 | 0.0025105 | 0.00062919 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1216-4_0_3_load_68 | 99 | 0.0026779 | 0.00067115 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1216-4_0_3_load_69 | 100 | 0.001358 | 0.00034035 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1216-4_0_3_load_71 | 101 | 0.00064363 | 0.00016131 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1216-4_0_3_load_72 | 102 | 0.00041952 | 0.00010514 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1216-4_0_3_load_74 | 103 | 0.0010088 | 0.00025284 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1216-4_0_3_load_107 | 104 | 0.00041959 | 0.00010516 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1216-4_0_3_load_120 | 105 | 0.0015789 | 0.0003957 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1216-4_0_3_load_78 | 106 | 0.0010357 | 0.00025956 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1216-4_0_3_load_84 | 109 | 0.0020161 | 0.00050527 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1216-4_0_3_load_89 | 110 | 0.0047108 | 0.0011806 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1216-4_0_3_load_82 | 111 | 0.00087101 | 0.0002183 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1216-4_0_3_load_83 | 112 | 0.0017655 | 0.00044248 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1216-4_0_3_load_106 | 114 | 0.0016421 | 0.00041154 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1216-4_0_3_load_91 | 115 | 0.0010203 | 0.00025571 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1216-4_0_3_load_99 | 117 | 0.00063348 | 0.00015876 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1216-4_0_3_load_94 | 118 | 0.0034983 | 0.00087675 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1216-4_0_3_load_128 | 119 | 0.003619 | 0.00090699 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1216-4_0_3_load_127 | 120 | 0.0011282 | 0.00028275 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1216-4_0_3_load_121 | 122 | 0.0007982 | 0.00020005 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1216-4_0_3_load_109 | 123 | 0.00066283 | 0.00016612 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1216-4_0_3_load_110 | 124 | 0.0016985 | 0.00042569 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1216-4_0_3_load_124 | 125 | 0.0016235 | 0.00040689 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1216-4_0_3_load_125 | 126 | 0.0013427 | 0.00033651 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 100 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1216-4_0_3_line_0 |  | 0 | 1 | 0.12608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1216-4_0_3_line_1 |  | 0 | 2 | 0.019533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1216-4_0_3_line_2 |  | 1 | 3 | 0.037423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1216-4_0_3_line_3 |  | 2 | 4 | 0.20035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1216-4_0_3_line_4 |  | 3 | 5 | 0.0076789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1216-4_0_3_line_5 |  | 3 | 6 | 0.064224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1216-4_0_3_line_6 |  | 4 | 7 | 0.20536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1216-4_0_3_line_7 |  | 4 | 8 | 0.21652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1216-4_0_3_line_8 |  | 5 | 9 | 0.022632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1216-4_0_3_line_9 |  | 6 | 10 | 0.016888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1216-4_0_3_line_10 |  | 6 | 11 | 0.015291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1216-4_0_3_line_11 |  | 7 | 12 | 0.084276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1216-4_0_3_line_12 |  | 7 | 13 | 0.064862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1216-4_0_3_line_13 |  | 8 | 14 | 0.0052987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1216-4_0_3_line_14 |  | 10 | 119 | 0.061215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1216-4_0_3_line_15 |  | 10 | 120 | 0.008088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1216-4_0_3_line_16 |  | 11 | 93 | 0.030576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1216-4_0_3_line_17 |  | 12 | 118 | 0.048476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1216-4_0_3_line_18 |  | 13 | 115 | 0.040615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1216-4_0_3_line_19 |  | 15 | 16 | 0.021379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1216-4_0_3_line_20 |  | 15 | 17 | 0.23941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1216-4_0_3_line_21 |  | 16 | 18 | 0.043928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1216-4_0_3_line_22 |  | 17 | 19 | 0.02159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1216-4_0_3_line_23 |  | 17 | 20 | 0.13886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1216-4_0_3_line_24 |  | 18 | 26 | 0.017999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1216-4_0_3_line_25 |  | 18 | 27 | 0.12842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1216-4_0_3_line_26 |  | 18 | 24 | 0.04892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1216-4_0_3_line_27 |  | 19 | 28 | 0.16455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1216-4_0_3_line_28 |  | 20 | 29 | 0.0071906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1216-4_0_3_line_29 |  | 21 | 22 | 0.0085703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1216-4_0_3_line_30 |  | 21 | 23 | 0.33604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1216-4_0_3_line_31 |  | 22 | 91 | 0.125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1216-4_0_3_line_32 |  | 23 | 28 | 0.1841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1216-4_0_3_line_33 |  | 24 | 25 | 0.00327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1216-4_0_3_line_34 |  | 27 | 31 | 0.0099996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1216-4_0_3_line_35 |  | 28 | 30 | 0.32762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1216-4_0_3_line_36 |  | 30 | 124 | 0.0019588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1216-4_0_3_line_37 |  | 32 | 33 | 0.1178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1216-4_0_3_line_38 |  | 33 | 34 | 0.15284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1216-4_0_3_line_39 |  | 33 | 35 | 0.11194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1216-4_0_3_line_40 |  | 33 | 36 | 0.10601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1216-4_0_3_line_41 |  | 34 | 37 | 0.0096734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1216-4_0_3_line_42 |  | 37 | 38 | 0.016488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1216-4_0_3_line_43 |  | 38 | 39 | 0.017155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_1216-4_0_3_line_44 |  | 38 | 40 | 0.049623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_1216-4_0_3_line_45 |  | 39 | 48 | 0.049915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_1216-4_0_3_line_46 |  | 40 | 49 | 0.042731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_1216-4_0_3_line_47 |  | 41 | 42 | 0.018593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1216-4_0_3_line_48 |  | 41 | 43 | 0.023904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1216-4_0_3_line_49 |  | 42 | 44 | 0.017969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1216-4_0_3_line_50 |  | 43 | 45 | 0.076837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1216-4_0_3_line_51 |  | 44 | 46 | 0.012756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1216-4_0_3_line_52 |  | 46 | 47 | 0.012302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1216-4_0_3_line_53 |  | 47 | 60 | 0.032427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_1216-4_0_3_line_54 |  | 47 | 55 | 0.0039202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_1216-4_0_3_line_55 |  | 48 | 78 | 0.019851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_1216-4_0_3_line_56 |  | 49 | 92 | 0.037385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1216-4_0_3_line_57 |  | 50 | 51 | 0.0063942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_1216-4_0_3_line_58 |  | 50 | 52 | 0.019048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_1216-4_0_3_line_59 |  | 51 | 53 | 0.014105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_1216-4_0_3_line_60 |  | 52 | 54 | 0.014297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_1216-4_0_3_line_61 |  | 52 | 55 | 0.011683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_1216-4_0_3_line_62 |  | 53 | 56 | 0.0052949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_1216-4_0_3_line_63 |  | 54 | 57 | 0.028583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_1216-4_0_3_line_64 |  | 56 | 58 | 0.0026893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_1216-4_0_3_line_65 |  | 57 | 59 | 0.039573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_1216-4_0_3_line_66 |  | 58 | 94 | 0.019237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_1216-4_0_3_line_67 |  | 59 | 61 | 0.019741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_1216-4_0_3_line_68 |  | 60 | 66 | 0.026714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_1216-4_0_3_line_69 |  | 61 | 62 | 0.060509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_1216-4_0_3_line_70 |  | 62 | 79 | 0.02487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_1216-4_0_3_line_71 |  | 63 | 64 | 0.0067992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_1216-4_0_3_line_72 |  | 63 | 65 | 0.0057712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_1216-4_0_3_line_73 |  | 64 | 66 | 0.022574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_1216-4_0_3_line_74 |  | 65 | 67 | 0.0066944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1216-4_0_3_line_75 |  | 65 | 68 | 0.015771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_1216-4_0_3_line_76 |  | 66 | 69 | 0.042216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1216-4_0_3_line_77 |  | 67 | 70 | 0.0045954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1216-4_0_3_line_78 |  | 68 | 71 | 0.020131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_1216-4_0_3_line_79 |  | 69 | 72 | 0.03226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1216-4_0_3_line_80 |  | 71 | 73 | 0.034551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1216-4_0_3_line_81 |  | 71 | 74 | 0.010068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_1216-4_0_3_line_82 |  | 72 | 81 | 0.017361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1216-4_0_3_line_83 |  | 73 | 105 | 0.017379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1216-4_0_3_line_84 |  | 74 | 101 | 0.0054309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_1216-4_0_3_line_85 |  | 75 | 76 | 0.032818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_1216-4_0_3_line_86 |  | 75 | 77 | 0.033519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_1216-4_0_3_line_87 |  | 76 | 78 | 0.06558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_1216-4_0_3_line_88 |  | 77 | 79 | 0.071413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_1216-4_0_3_line_89 |  | 78 | 80 | 0.087654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1216-4_0_3_line_90 |  | 81 | 125 | 0.0032976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1216-4_0_3_line_91 |  | 82 | 83 | 0.073461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1216-4_0_3_line_92 |  | 82 | 84 | 0.0054239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1216-4_0_3_line_93 |  | 83 | 85 | 0.062414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1216-4_0_3_line_94 |  | 85 | 86 | 0.14388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1216-4_0_3_line_95 |  | 85 | 87 | 0.093271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1216-4_0_3_line_96 |  | 86 | 88 | 0.02282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1216-4_0_3_line_97 |  | 86 | 89 | 0.011914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1216-4_0_3_line_98 |  | 87 | 90 | 0.050117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1216-4_0_3_line_99 |  | 88 | 114 | 0.026321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1216-4_0_3_line_100 |  | 89 | 113 | 0.0093798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1216-4_0_3_line_101 |  | 90 | 104 | 0.051369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1216-4_0_3_line_102 |  | 91 | 114 | 0.29577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1216-4_0_3_line_103 |  | 92 | 93 | 0.014794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1216-4_0_3_line_104 |  | 94 | 95 | 0.0055656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_1216-4_0_3_line_105 |  | 95 | 96 | 0.012474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_1216-4_0_3_line_106 |  | 96 | 97 | 0.0097764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1216-4_0_3_line_107 |  | 96 | 98 | 0.021137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_1216-4_0_3_line_108 |  | 98 | 99 | 0.010681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_1216-4_0_3_line_109 |  | 99 | 100 | 0.011855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_1216-4_0_3_line_110 |  | 101 | 102 | 0.02059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1216-4_0_3_line_111 |  | 102 | 103 | 0.0029927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1216-4_0_3_line_112 |  | 103 | 104 | 0.0043155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1216-4_0_3_line_113 |  | 106 | 107 | 0.14061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1216-4_0_3_line_114 |  | 107 | 108 | 0.022232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1216-4_0_3_line_115 |  | 108 | 109 | 0.035725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1216-4_0_3_line_116 |  | 108 | 110 | 0.040892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1216-4_0_3_line_117 |  | 109 | 111 | 0.001218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1216-4_0_3_line_118 |  | 111 | 112 | 0.0089936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1216-4_0_3_line_119 |  | 112 | 113 | 0.10811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1216-4_0_3_line_120 |  | 115 | 116 | 0.23832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1216-4_0_3_line_121 |  | 116 | 117 | 0.023953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1216-4_0_3_line_122 |  | 117 | 121 | 0.084413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1216-4_0_3_line_123 |  | 121 | 122 | 0.03859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1216-4_0_3_line_124 |  | 123 | 124 | 0.0017195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1216-4_0_3_line_125 |  | 125 | 126 | 0.015662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1216-4_0_3_trafo_69 | 0.63 MVA 20/0.4 kV | 127 | 100 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21
0 | 2694029.0518 | 1182098.1884 | 2694020.7903 | 1182159.3011 | 2694018.0955 | 1182178.2041 | 2694013.1291 | 1182223.2479
1 | 2694031.6685 | 1182078.8318 | 2694029.0518 | 1182098.1884
2 | 2694009.4192 | 1182260.4869 | 2694013.0378 | 1182224.0761 | 2694013.1291 | 1182223.2479
3 | 2694031.6685 | 1182078.8318 | 2694079.1357 | 1182087.5153 | 2694093.6139 | 1182090.5667 | 2694099.6466 | 1182089.1605 | 2694103.4198 | 1182084.2722 | 2694138.5405 | 1182018.3818 | 2694153.2406 | 1181990.8063 | 2694171.5508 | 1181995.9416
4 | 2694009.4192 | 1182260.4869 | 2694006.2804 | 1182259.0256 | 2694004.0705 | 1182257.2565 | 2694003.2147 | 1182256.1666
5 | 2694009.4192 | 1182260.4869 | 2694004.863 | 1182324.5338
6 | 2694171.5508 | 1181995.9416 | 2694201.6787 | 1182005.2875 | 2694215.652 | 1182011.322 | 2694226.9627 | 1182015.2245 | 2694238.11 | 1182014.9551 | 2694248.5742 | 1182015.8646 | 2694260.058 | 1182017.9909 | 2694269.6942 | 1182023.9573 | 2694286.6881 | 1182037.4998 | 2694298.1041 | 1182053.6341 | 2694329.1168 | 1182077.0924 | 2694343.7057 | 1182092.9988
7 | 2694171.5508 | 1181995.9416 | 2694171.6851 | 1182018.9805 | 2694168.1938 | 1182027.3087 | 2694165.1549 | 1182034.5433 | 2694150.4672 | 1182064.7429 | 2694129.9225 | 1182108.5036 | 2694125.7313 | 1182117.6325 | 2694123.753 | 1182121.5372 | 2694121.3655 | 1182125.2354 | 2694119.1149 | 1182128.4911 | 2694110.0698 | 1182140.3232 | 2694105.2519 | 1182147.0519 | 2694101.4586 | 1182155.1641 | 2694099.7704 | 1182160.0518 | 2694098.5857 | 1182166.9154 | 2694097.8076 | 1182174.1522 | 2694097.895 | 1182176.8553 | 2694098.3837 | 1182179.7759 | 2694100.721 | 1182187.0506 | 2694101.6626 | 1182190.801 | 2694101.9148 | 1182193.2177 | 2694101.885 | 1182193.9677
8 | 2693994.4624 | 1182235.392 | 2694001.8167 | 1182254.386 | 2694003.2147 | 1182256.1666
9 | 2693990.242 | 1182316.0103 | 2694004.863 | 1182324.5338
10 | 2694004.863 | 1182324.5338 | 2694004.1017 | 1182339.8059
11 | 2694343.7057 | 1182092.9988 | 2694332.8158 | 1182099.2425 | 2694329.1366 | 1182104.4545 | 2694328.8951 | 1182113.0006 | 2694327.126 | 1182124.4689 | 2694320.9861 | 1182138.5035 | 2694314.1426 | 1182146.3008 | 2694305.3626 | 1182152.9113 | 2694302.9335 | 1182161.0636
12 | 2694343.7057 | 1182092.9988 | 2694348.7283 | 1182105.2967 | 2694354.0856 | 1182108.95 | 2694353.5137 | 1182113.7441 | 2694355.9157 | 1182123.6771 | 2694369.3541 | 1182150.5501
13 | 2694101.6748 | 1182199.2622 | 2694101.885 | 1182193.9677
14 | 2693990.242 | 1182316.0103 | 2693959.9804 | 1182313.3231 | 2693950.3349 | 1182315.7512 | 2693945.7546 | 1182324.8852 | 2693947.0683 | 1182335.5904
15 | 2693984.7915 | 1182310.021 | 2693990.242 | 1182316.0103
16 | 2694002.6649 | 1182370.3476 | 2694002.7565 | 1182366.7943 | 2694004.1017 | 1182339.8059
17 | 2694269.2822 | 1182159.8371 | 2694270.5619 | 1182165.8722 | 2694281.0805 | 1182169.6177 | 2694290.1998 | 1182174.9312 | 2694296.6782 | 1182173.3432 | 2694301.4519 | 1182166.0359 | 2694302.9335 | 1182161.0636
18 | 2694369.3541 | 1182150.5501 | 2694391.7383 | 1182184.4403
19 | 2695143.8372 | 1183272.129 | 2695164.8128 | 1183267.997
20 | 2695180.1603 | 1183029.0804 | 2695164.8128 | 1183267.997
21 | 2695143.8372 | 1183272.129 | 2695160.5024 | 1183294.9637 | 2695174.1006 | 1183302.7291
22 | 2695180.1603 | 1183029.0804 | 2695172.3877 | 1183008.938
23 | 2695180.1603 | 1183029.0804 | 2695315.9921 | 1183057.9393
24 | 2695174.1006 | 1183302.7291 | 2695167.9656 | 1183293.8148 | 2695173.5602 | 1183289.3177
25 | 2695174.1006 | 1183302.7291 | 2695286.1824 | 1183365.4054
26 | 2695127.6323 | 1183290.0166 | 2695151.2919 | 1183294.1059 | 2695160.5024 | 1183294.9637 | 2695174.1006 | 1183302.7291
27 | 2695115.9209 | 1182863.3363 | 2695157.0609 | 1182904.0152 | 2695164.7206 | 1182989.0688 | 2695172.3877 | 1183008.938
28 | 2695315.9921 | 1183057.9393 | 2695315.0818 | 1183065.072
29 | 2694706.1327 | 1182782.5297 | 2694708.6475 | 1182774.3367
30 | 2694706.1327 | 1182782.5297 | 2695019.8932 | 1182902.8496
31 | 2694704.532 | 1182659.6484 | 2694714.5424 | 1182680.9757 | 2694724.2677 | 1182704.8779 | 2694719.876 | 1182713.6141 | 2694724.1637 | 1182738.4977 | 2694719.8425 | 1182742.7766 | 2694719.5697 | 1182753.2678 | 2694711.7363 | 1182764.2733 | 2694708.6475 | 1182774.3367
32 | 2695115.9209 | 1182863.3363 | 2695099.2849 | 1182872.7228 | 2695088.2608 | 1182872.5478 | 2695080.7476 | 1182849.3916 | 2695072.1054 | 1182831.4542 | 2695051.5723 | 1182834.2637 | 2695042.3236 | 1182854.5411 | 2695033.5272 | 1182879.5286 | 2695030.4582 | 1182907.8758 | 2695019.8932 | 1182902.8496
33 | 2695127.6323 | 1183290.0166 | 2695125.4178 | 1183292.4274
34 | 2695286.1824 | 1183365.4054 | 2695294.0847 | 1183359.278
35 | 2695115.9209 | 1182863.3363 | 2695063.7041 | 1182539.9018
36 | 2695062.7082 | 1182538.2151 | 2695063.7041 | 1182539.9018
37 | 2694035.9758 | 1182690.0741 | 2693923.1288 | 1182723.8898
38 | 2694035.9758 | 1182690.0741 | 2694037.6665 | 1182626.9847 | 2694037.9338 | 1182612.3907 | 2694037.5773 | 1182597.6424 | 2694037.1209 | 1182585.3608 | 2694035.9812 | 1182573.8022 | 2694034.1582 | 1182561.9884 | 2694032.3976 | 1182550.5757 | 2694029.8684 | 1182538.9954 | 2694029.5962 | 1182537.9083
39 | 2694032.977 | 1182801.9759 | 2694035.9758 | 1182690.0741
40 | 2694035.9758 | 1182690.0741 | 2693941.1296 | 1182642.7143
41 | 2694027.2469 | 1182528.5245 | 2694029.5962 | 1182537.9083
42 | 2694023.2426 | 1182512.5302 | 2694027.2469 | 1182528.5245
43 | 2694023.2426 | 1182512.5302 | 2694033.2819 | 1182508.3517 | 2694037.5318 | 1182503.7266
44 | 2694023.2426 | 1182512.5302 | 2694011.6103 | 1182470.2877 | 2694010.3864 | 1182464.6102
45 | 2694037.5318 | 1182503.7266 | 2694037.2757 | 1182497.1739 | 2694029.5306 | 1182481.209 | 2694029.2017 | 1182473.9437 | 2694032.6791 | 1182467.4496 | 2694042.441 | 1182462.4359
46 | 2694010.3864 | 1182464.6102 | 2694006.8123 | 1182448.0316 | 2694004.0045 | 1182428.8866 | 2694003.4379 | 1182422.4902
47 | 2694181.9315 | 1182795.0402 | 2694174.7347 | 1182793.7201 | 2694163.5396 | 1182792.3732
48 | 2694139.641 | 1182792.2751 | 2694139.7901 | 1182792.2814 | 2694162.8291 | 1182792.2878 | 2694163.5396 | 1182792.3732
49 | 2694199.6059 | 1182798.282 | 2694181.9315 | 1182795.0402
50 | 2694063.0182 | 1182786.6282 | 2694090.6203 | 1182788.8072 | 2694116.5198 | 1182790.9596 | 2694129.8617 | 1182791.8586 | 2694139.641 | 1182792.2751
51 | 2694199.6059 | 1182798.282 | 2694207.553 | 1182799.7397 | 2694211.9295 | 1182801.3868
52 | 2694222.0033 | 1182808.3389 | 2694216.2577 | 1182803.679 | 2694212.6089 | 1182801.6425 | 2694211.9295 | 1182801.3868
53 | 2694222.0033 | 1182808.3389 | 2694232.0666 | 1182839.1646
54 | 2694222.0033 | 1182808.3389 | 2694222.6072 | 1182804.4655
55 | 2694061.5268 | 1182457.0178 | 2694056.9799 | 1182458.1805 | 2694042.8878 | 1182462.2065 | 2694042.441 | 1182462.4359
56 | 2694002.2836 | 1182385.1369 | 2694002.2296 | 1182387.2323 | 2694002.5653 | 1182407.2058 | 2694003.0508 | 1182418.1203 | 2694003.4379 | 1182422.4902
57 | 2694249.0149 | 1182787.3281 | 2694243.1136 | 1182789.7898
58 | 2694224.4069 | 1182792.9224 | 2694240.6676 | 1182790.8101 | 2694243.1136 | 1182789.7898
59 | 2694258.911 | 1182777.9224 | 2694253.3048 | 1182785.5387 | 2694249.0149 | 1182787.3281
60 | 2694224.4069 | 1182792.9224 | 2694222.6343 | 1182788.6141 | 2694220.5389 | 1182784.9232 | 2694217.8963 | 1182782.0354 | 2694216.7098 | 1182781.151
61 | 2694224.4069 | 1182792.9224 | 2694222.6072 | 1182804.4655
62 | 2694258.911 | 1182777.9224 | 2694262.0499 | 1182773.6582
63 | 2694216.7098 | 1182781.151 | 2694213.0203 | 1182778.4009 | 2694207.6213 | 1182775.0028 | 2694203.8586 | 1182771.4747 | 2694196.6834 | 1182761.3073
64 | 2694262.0499 | 1182773.6582 | 2694263.6441 | 1182771.4924
65 | 2694196.6834 | 1182761.3073 | 2694179.7229 | 1182737.2738 | 2694174.5542 | 1182728.5301
66 | 2694265.1601 | 1182752.3152 | 2694265.1601 | 1182752.3152 | 2694263.6441 | 1182771.4924
67 | 2694174.5542 | 1182728.5301 | 2694166.6605 | 1182715.1767 | 2694163.874 | 1182711.9953
68 | 2694242.3063 | 1182863.8155 | 2694239.7158 | 1182858.1045 | 2694233.7327 | 1182844.2683 | 2694232.0666 | 1182839.1646
69 | 2694122.4989 | 1182675.4279 | 2694125.66 | 1182687.96 | 2694127.5857 | 1182692.7377 | 2694130.0902 | 1182696.157 | 2694133.5295 | 1182698.8905 | 2694137.6047 | 1182701.0114 | 2694144.0705 | 1182702.6139 | 2694154.1682 | 1182704.9073 | 2694158.1786 | 1182706.7715 | 2694161.4767 | 1182709.2582 | 2694163.874 | 1182711.9953
70 | 2694122.4989 | 1182675.4279 | 2694116.4161 | 1182651.3133
71 | 2694251.9861 | 1182884.2017 | 2694255.0978 | 1182890.247
72 | 2694257.7391 | 1182895.3783 | 2694255.0978 | 1182890.247
73 | 2694242.3063 | 1182863.8155 | 2694248.2768 | 1182876.9956 | 2694251.9861 | 1182884.2017
74 | 2694257.7391 | 1182895.3783 | 2694254.7734 | 1182901.3799 | 2694254.7734 | 1182901.3799
75 | 2694257.7391 | 1182895.3783 | 2694273.2788 | 1182892.6867
76 | 2694242.3063 | 1182863.8155 | 2694283.6532 | 1182855.2933
77 | 2694250.9595 | 1182903.9434 | 2694254.7734 | 1182901.3799
78 | 2694293.2439 | 1182892.7239 | 2694280.3354 | 1182891.4645 | 2694273.2788 | 1182892.6867
79 | 2694283.6532 | 1182855.2933 | 2694300.9911 | 1182851.7197 | 2694305.2795 | 1182847.0731 | 2694307.0936 | 1182839.041 | 2694307.0936 | 1182839.041
80 | 2694293.2439 | 1182892.7239 | 2694301.5525 | 1182904.8289 | 2694308.6373 | 1182915.1247 | 2694311.4163 | 1182921.9516
81 | 2694293.2439 | 1182892.7239 | 2694302.4755 | 1182888.7058
82 | 2694303.7335 | 1182822.0086 | 2694307.0936 | 1182839.041
83 | 2694312.6687 | 1182938.9255 | 2694313.3793 | 1182926.7734 | 2694311.4163 | 1182921.9516
84 | 2694302.4755 | 1182888.7058 | 2694307.4552 | 1182886.5384
85 | 2694090.4735 | 1182549.6498 | 2694080.0386 | 1182518.5354
86 | 2694090.4735 | 1182549.6498 | 2694091.6779 | 1182553.241 | 2694098.9497 | 1182582.0693
87 | 2694061.5268 | 1182457.0178 | 2694066.967 | 1182465.1083 | 2694067.1427 | 1182485.0459 | 2694078.4008 | 1182513.6519 | 2694080.0386 | 1182518.5354
88 | 2694098.9497 | 1182582.0693 | 2694116.4161 | 1182651.3133
89 | 2694090.6598 | 1182398.7714 | 2694075.7396 | 1182397.1584 | 2694065.9243 | 1182398.2495 | 2694058.2606 | 1182406.768 | 2694055.8126 | 1182417.2474 | 2694055.7909 | 1182429.8217 | 2694057.2477 | 1182438.6946 | 2694061.337 | 1182449.6546 | 2694061.5268 | 1182457.0178
90 | 2694303.7335 | 1182822.0086 | 2694303.0953 | 1182818.7733
91 | 2694295.0194 | 1182607.5575 | 2694321.4577 | 1182620.2946 | 2694342.9486 | 1182640.0899 | 2694350.9463 | 1182652.657
92 | 2694290.133 | 1182605.2034 | 2694295.0194 | 1182607.5575
93 | 2694395.9632 | 1182690.4231 | 2694383.1825 | 1182688.2983 | 2694369.8792 | 1182681.5401 | 2694356.9215 | 1182662.046 | 2694350.9463 | 1182652.657
94 | 2694398.8689 | 1182556.4282 | 2694401.6963 | 1182588.7821 | 2694411.0908 | 1182600.3263 | 2694410.0142 | 1182610.0044 | 2694401.3257 | 1182615.6934 | 2694396.068 | 1182624.1604 | 2694395.224 | 1182652.0426 | 2694397.3105 | 1182680.5269 | 2694395.9632 | 1182690.4231
95 | 2694395.9632 | 1182690.4231 | 2694390.5312 | 1182715.7759 | 2694379.8874 | 1182733.1305 | 2694363.8526 | 1182777.2938
96 | 2694398.8689 | 1182556.4282 | 2694417.6956 | 1182557.2585 | 2694421.592 | 1182556.4698
97 | 2694398.8689 | 1182556.4282 | 2694399.3128 | 1182544.5227
98 | 2694363.8526 | 1182777.2938 | 2694362.7243 | 1182780.4014 | 2694353.0326 | 1182811.0128 | 2694346.605 | 1182824.2352
99 | 2694435.6494 | 1182536.4392 | 2694432.6818 | 1182544.9645 | 2694426.7664 | 1182555.4225 | 2694421.592 | 1182556.4698
100 | 2694399.6624 | 1182535.1493 | 2694399.3128 | 1182544.5227
101 | 2694346.605 | 1182824.2352 | 2694342.8202 | 1182832.0209 | 2694338.5603 | 1182855.2242 | 2694335.4664 | 1182867.9058 | 2694330.8063 | 1182871.7909
102 | 2694435.6494 | 1182536.4392 | 2694704.532 | 1182659.6484
103 | 2694002.6649 | 1182370.3476 | 2694002.2836 | 1182385.1369
104 | 2694265.1601 | 1182752.3152 | 2694264.427 | 1182746.7981
105 | 2694262.7839 | 1182734.4331 | 2694264.427 | 1182746.7981
106 | 2694262.7839 | 1182734.4331 | 2694261.4994 | 1182724.7415
107 | 2694262.7839 | 1182734.4331 | 2694249.1407 | 1182730.3493 | 2694242.2458 | 1182730.4328
108 | 2694242.2458 | 1182730.4328 | 2694231.5657 | 1182730.562
109 | 2694227.8405 | 1182719.3074 | 2694231.5657 | 1182730.562
110 | 2694307.4552 | 1182886.5384 | 2694319.3019 | 1182881.3822 | 2694325.1931 | 1182876.4707
111 | 2694327.4917 | 1182874.5543 | 2694325.1931 | 1182876.4707
112 | 2694327.4917 | 1182874.5543 | 2694330.8063 | 1182871.7909
113 | 2694341.8377 | 1182379.9071 | 2694340.2128 | 1182400.6502 | 2694336.1991 | 1182407.7138 | 2694319.5851 | 1182408.4306 | 2694301.2199 | 1182417.5475 | 2694277.5966 | 1182429.8281 | 2694252.0954 | 1182437.2096 | 2694230.7775 | 1182435.6995
114 | 2694341.8377 | 1182379.9071 | 2694351.0791 | 1182387.6241 | 2694360.1536 | 1182392.3588
115 | 2694360.1536 | 1182392.3588 | 2694367.0369 | 1182406.2649 | 2694369.5136 | 1182426.3216
116 | 2694360.1536 | 1182392.3588 | 2694354.6111 | 1182378.1737 | 2694350.6819 | 1182358.5327 | 2694349.9112 | 1182352.9538
117 | 2694369.6629 | 1182427.5304 | 2694369.5136 | 1182426.3216
118 | 2694369.6629 | 1182427.5304 | 2694370.1389 | 1182431.3852 | 2694370.4449 | 1182436.4855
119 | 2694399.6624 | 1182535.1493 | 2694400.1454 | 1182520.9702 | 2694391.0548 | 1182506.1287 | 2694377.1271 | 1182493.8905 | 2694374.8876 | 1182486.7396 | 2694372.2923 | 1182467.2753 | 2694370.4449 | 1182436.4855
120 | 2694532.134 | 1182230.4544 | 2694497.2508 | 1182246.7036 | 2694507.8063 | 1182201.1299 | 2694479.7211 | 1182215.3852 | 2694456.4627 | 1182235.4425 | 2694433.4879 | 1182237.5263 | 2694410.9247 | 1182213.489 | 2694391.7383 | 1182184.4403
121 | 2694532.134 | 1182230.4544 | 2694544.5662 | 1182224.7134 | 2694554.6799 | 1182226.4345
122 | 2694631.1383 | 1182213.7724 | 2694624.5878 | 1182224.2757 | 2694596.7787 | 1182233.5983 | 2694554.6799 | 1182226.4345
123 | 2694631.1383 | 1182213.7724 | 2694612.8118 | 1182188.456 | 2694608.9622 | 1182182.2104
124 | 2695061.8339 | 1182536.7345 | 2695062.7082 | 1182538.2151
125 | 2694300.064 | 1182803.4077 | 2694303.0953 | 1182818.7733

## bus_geodata
| x | y | coords
0 | 2694029.0518 | 1182098.1884
1 | 2694013.1291 | 1182223.2479
2 | 2694031.6685 | 1182078.8318
3 | 2694009.4192 | 1182260.4869
4 | 2694171.5508 | 1181995.9416
5 | 2694003.2147 | 1182256.1666
6 | 2694004.863 | 1182324.5338
7 | 2694343.7057 | 1182092.9987
8 | 2694101.885 | 1182193.9677
9 | 2693994.4624 | 1182235.392
10 | 2693990.242 | 1182316.0103
11 | 2694004.1017 | 1182339.8059
12 | 2694302.9335 | 1182161.0636
13 | 2694369.3541 | 1182150.5501
14 | 2694101.6748 | 1182199.2622
15 | 2695164.8128 | 1183267.997
16 | 2695143.8372 | 1183272.129
17 | 2695180.1603 | 1183029.0804
18 | 2695174.1006 | 1183302.7291
19 | 2695172.3877 | 1183008.938
20 | 2695315.9921 | 1183057.9393
21 | 2694706.1327 | 1182782.5297
22 | 2694708.6475 | 1182774.3367
23 | 2695019.8932 | 1182902.8496
24 | 2695127.6323 | 1183290.0166
25 | 2695125.4178 | 1183292.4274
26 | 2695173.5602 | 1183289.3178
27 | 2695286.1824 | 1183365.4054
28 | 2695115.9209 | 1182863.3363
29 | 2695315.0818 | 1183065.072
30 | 2695063.7041 | 1182539.9018
31 | 2695294.0847 | 1183359.278
32 | 2693923.1288 | 1182723.8898
33 | 2694035.9758 | 1182690.0741
34 | 2694029.5962 | 1182537.9083
35 | 2694032.977 | 1182801.9759
36 | 2693941.1296 | 1182642.7143
37 | 2694027.2469 | 1182528.5245
38 | 2694023.2426 | 1182512.5302
39 | 2694037.5318 | 1182503.7266
40 | 2694010.3864 | 1182464.6102
41 | 2694163.5396 | 1182792.3732
42 | 2694181.9315 | 1182795.0402
43 | 2694139.641 | 1182792.2751
44 | 2694199.6059 | 1182798.282
45 | 2694063.0182 | 1182786.6282
46 | 2694211.9295 | 1182801.3868
47 | 2694222.0033 | 1182808.3389
48 | 2694042.441 | 1182462.4359
49 | 2694003.4379 | 1182422.4902
50 | 2694243.1136 | 1182789.7898
51 | 2694249.0149 | 1182787.3281
52 | 2694224.4069 | 1182792.9224
53 | 2694258.911 | 1182777.9224
54 | 2694216.7098 | 1182781.151
55 | 2694222.6072 | 1182804.4655
56 | 2694262.0499 | 1182773.6582
57 | 2694196.6834 | 1182761.3073
58 | 2694263.6441 | 1182771.4924
59 | 2694174.5542 | 1182728.5301
60 | 2694232.0666 | 1182839.1646
61 | 2694163.874 | 1182711.9953
62 | 2694122.4989 | 1182675.4279
63 | 2694255.0978 | 1182890.247
64 | 2694251.9861 | 1182884.2017
65 | 2694257.7391 | 1182895.3783
66 | 2694242.3063 | 1182863.8155
67 | 2694254.7734 | 1182901.3799
68 | 2694273.2788 | 1182892.6867
69 | 2694283.6532 | 1182855.2933
70 | 2694250.9595 | 1182903.9434
71 | 2694293.2439 | 1182892.7239
72 | 2694307.0936 | 1182839.041
73 | 2694311.4163 | 1182921.9516
74 | 2694302.4755 | 1182888.7058
75 | 2694090.4735 | 1182549.6498
76 | 2694080.0386 | 1182518.5354
77 | 2694098.9497 | 1182582.0693
78 | 2694061.5268 | 1182457.0178
79 | 2694116.4161 | 1182651.3133
80 | 2694090.6598 | 1182398.7714
81 | 2694303.7335 | 1182822.0086
82 | 2694295.0194 | 1182607.5575
83 | 2694350.9463 | 1182652.657
84 | 2694290.133 | 1182605.2034
85 | 2694395.9632 | 1182690.4231
86 | 2694398.8689 | 1182556.4282
87 | 2694363.8526 | 1182777.2938
88 | 2694421.592 | 1182556.4698
89 | 2694399.3128 | 1182544.5227
90 | 2694346.605 | 1182824.2352
91 | 2694704.532 | 1182659.6484
92 | 2694002.2836 | 1182385.1369
93 | 2694002.6649 | 1182370.3476
94 | 2694265.1601 | 1182752.3152
95 | 2694264.427 | 1182746.7981
96 | 2694262.7839 | 1182734.4331
97 | 2694261.4994 | 1182724.7415
98 | 2694242.2458 | 1182730.4328
99 | 2694231.5657 | 1182730.562
100 | 2694227.8405 | 1182719.3074
101 | 2694307.4552 | 1182886.5384
102 | 2694325.1931 | 1182876.4707
103 | 2694327.4917 | 1182874.5543
104 | 2694330.8063 | 1182871.7909
105 | 2694312.6687 | 1182938.9255
106 | 2694230.7775 | 1182435.6995
107 | 2694341.8377 | 1182379.9071
108 | 2694360.1536 | 1182392.3588
109 | 2694369.5136 | 1182426.3216
110 | 2694349.9111 | 1182352.9538
111 | 2694369.6629 | 1182427.5304
112 | 2694370.4449 | 1182436.4855
113 | 2694399.6624 | 1182535.1493
114 | 2694435.6494 | 1182536.4392
115 | 2694391.7383 | 1182184.4403
116 | 2694532.134 | 1182230.4544
117 | 2694554.6799 | 1182226.4345
118 | 2694269.2822 | 1182159.8371
119 | 2693947.0683 | 1182335.5904
120 | 2693984.7915 | 1182310.021
121 | 2694631.1383 | 1182213.7724
122 | 2694608.9622 | 1182182.2104
123 | 2695061.8339 | 1182536.7345
124 | 2695062.7082 | 1182538.2151
125 | 2694303.0953 | 1182818.7733
126 | 2694300.064 | 1182803.4077
127 | 2694262.7839 | 1182734.4331

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97558 | -0.4715 | 0.0033026 | 0.0008277
1 | 0.97741 | -0.43556 | 0.0011571 | 0.00028999
2 | 0.97535 | -0.4759 | 0 | 0
3 | 0.97799 | -0.42413 | 0 | 0
4 | 0.97307 | -0.5211 | 0 | 0
5 | 0.97797 | -0.42446 | 0.0011742 | 0.00029429
6 | 0.97913 | -0.40178 | 0 | 0
7 | 0.97171 | -0.54795 | 0 | 0
8 | 0.97202 | -0.54177 | 0.002938 | 0.00073634
9 | 0.97795 | -0.42495 | 0.0011899 | 0.00029822
10 | 0.97905 | -0.40324 | 0 | 0
11 | 0.97947 | -0.39515 | 0.001467 | 0.00036767
12 | 0.97135 | -0.55514 | 0.0011195 | 0.00028058
13 | 0.97156 | -0.5509 | 0 | 0
14 | 0.97201 | -0.54199 | 0.0022406 | 0.00056155
15 | 0.97032 | -0.5765 | 0.00090255 | 0.0002262
16 | 0.9703 | -0.57695 | 0 | 0
17 | 0.97078 | -0.56738 | 0.00067869 | 0.0001701
18 | 0.97025 | -0.57789 | 0 | 0
19 | 0.97086 | -0.56577 | 0.00056203 | 0.00014086
20 | 0.97061 | -0.57073 | 0.00048229 | 0.00012087
21 | 0.97598 | -0.46432 | 0 | 0
22 | 0.97606 | -0.46287 | 0.00029919 | 7.4983e-05
23 | 0.9731 | -0.5214 | 0.0003001 | 7.5212e-05
24 | 0.97024 | -0.57816 | 0 | 0
25 | 0.97024 | -0.57818 | 0.00030065 | 7.535e-05
26 | 0.97025 | -0.57802 | 0.00039662 | 9.9402e-05
27 | 0.9702 | -0.57895 | 0 | 0
28 | 0.97156 | -0.55176 | 0 | 0
29 | 0.97061 | -0.57083 | 0.00081613 | 0.00020454
30 | 0.97024 | -0.57798 | 0.0019617 | 0.00049165
31 | 0.9702 | -0.57903 | 0.00044458 | 0.00011142
32 | 0.97646 | -0.4542 | 0.017514 | 0.0043895
33 | 0.97838 | -0.41655 | 0.0015924 | 0.0003991
34 | 0.98193 | -0.34711 | 0.0014385 | 0.00036052
35 | 0.97798 | -0.42434 | 0.0038169 | 0.00095659
36 | 0.97817 | -0.42062 | 0.0021053 | 0.00052765
37 | 0.98216 | -0.34248 | 0.0012608 | 0.00031599
38 | 0.98259 | -0.33422 | 0 | 0
39 | 0.9829 | -0.32817 | 0.0010378 | 0.0002601
40 | 0.98212 | -0.34343 | 0.00075955 | 0.00019036
41 | 0.99132 | -0.16592 | 0.0011965 | 0.00029987
42 | 0.9915 | -0.16238 | 0.0015537 | 0.0003894
43 | 0.99111 | -0.16997 | 0.004749 | 0.0011902
44 | 0.9917 | -0.15847 | 0.0016689 | 0.00041827
45 | 0.99077 | -0.17649 | 0.0047839 | 0.001199
46 | 0.99186 | -0.15532 | 0.0011029 | 0.00027642
47 | 0.99203 | -0.15203 | 0 | 0
48 | 0.98382 | -0.3103 | 0.0010624 | 0.00026627
49 | 0.98152 | -0.35504 | 0.0021979 | 0.00055084
50 | 0.99358 | -0.12223 | 0.0012278 | 0.00030771
51 | 0.99394 | -0.11538 | 0.00094888 | 0.00023781
52 | 0.99253 | -0.14253 | 0 | 0
53 | 0.99473 | -0.10021 | 0.00065277 | 0.0001636
54 | 0.99218 | -0.14906 | 0.0012394 | 0.00031062
55 | 0.99216 | -0.14966 | 0.001072 | 0.00026868
56 | 0.99503 | -0.0945 | 0.0014259 | 0.00035736
57 | 0.99151 | -0.16191 | 0.0016206 | 0.00040617
58 | 0.99519 | -0.091579 | 0.0021407 | 0.00053652
59 | 0.9906 | -0.17935 | 0.0015916 | 0.00039888
60 | 0.99117 | -0.16877 | 0.026416 | 0.0066204
61 | 0.99016 | -0.18788 | 0.0012137 | 0.00030418
62 | 0.98882 | -0.21362 | 0.0025252 | 0.00063287
63 | 0.9902 | -0.18747 | 0.0027466 | 0.00068836
64 | 0.9903 | -0.18545 | 0.002403 | 0.00060224
65 | 0.99011 | -0.1891 | 0 | 0
66 | 0.99067 | -0.17841 | 0 | 0
67 | 0.99006 | -0.19002 | 0.0045311 | 0.0011356
68 | 0.98992 | -0.19281 | 0.002403 | 0.00060224
69 | 0.99035 | -0.18461 | 0.0025097 | 0.00062898
70 | 0.99005 | -0.19028 | 0.0032055 | 0.00080338
71 | 0.98969 | -0.19728 | 0 | 0
72 | 0.99018 | -0.18792 | 0.0013161 | 0.00032984
73 | 0.98962 | -0.19861 | 0.00058535 | 0.0001467
74 | 0.98958 | -0.19938 | 0.0025097 | 0.00062898
75 | 0.98612 | -0.2657 | 0.0015224 | 0.00038155
76 | 0.98547 | -0.27828 | 0.0010077 | 0.00025255
77 | 0.9868 | -0.25256 | 0.0018388 | 0.00046085
78 | 0.98419 | -0.30307 | 0 | 0
79 | 0.98829 | -0.22385 | 0.0016775 | 0.00042042
80 | 0.984 | -0.30689 | 0.0024198 | 0.00060647
81 | 0.99011 | -0.18929 | 0.0014826 | 0.00037157
82 | 0.983 | -0.32675 | 0.00066305 | 0.00016618
83 | 0.98323 | -0.32238 | 0.0011253 | 0.00028204
84 | 0.98299 | -0.327 | 0.0026313 | 0.00065946
85 | 0.98348 | -0.3174 | 0 | 0
86 | 0.98033 | -0.379 | 0 | 0
87 | 0.98591 | -0.27027 | 0.00065816 | 0.00016495
88 | 0.98006 | -0.38414 | 0.0012028 | 0.00030145
89 | 0.9802 | -0.38143 | 0.00084843 | 0.00021264
90 | 0.98724 | -0.24445 | 0.0014255 | 0.00035727
91 | 0.97717 | -0.44102 | 0 | 0
92 | 0.98055 | -0.3739 | 0.0011125 | 0.00027882
93 | 0.98019 | -0.38108 | 0.0014087 | 0.00035306
94 | 0.99629 | -0.070469 | 0.0021882 | 0.00054841
95 | 0.99661 | -0.064299 | 0.0031694 | 0.00079432
96 | 0.99735 | -0.050253 | 0 | 0
97 | 0.99733 | -0.050745 | 0.0028703 | 0.00071937
98 | 0.99862 | -0.026148 | 0.0025105 | 0.00062919
99 | 0.99927 | -0.013834 | 0.0026779 | 0.00067115
100 | 1 | 0 | -0.20491 | -0.051936
101 | 0.9895 | -0.20096 | 0.00064363 | 0.00016131
102 | 0.98889 | -0.21271 | 0.00041952 | 0.00010514
103 | 0.9888 | -0.2144 | 0.0010088 | 0.00025284
104 | 0.98868 | -0.21675 | 0.00041959 | 0.00010516
105 | 0.98959 | -0.19909 | 0.0015789 | 0.0003957
106 | 0.97864 | -0.41204 | 0.0010357 | 0.00025956
107 | 0.97878 | -0.40939 | 0 | 0
108 | 0.9788 | -0.40897 | 0 | 0
109 | 0.97899 | -0.40523 | 0.0020161 | 0.00050527
110 | 0.97862 | -0.41247 | 0.0047108 | 0.0011806
111 | 0.979 | -0.40506 | 0.00087101 | 0.0002183
112 | 0.97907 | -0.40364 | 0.0017655 | 0.00044248
113 | 0.98011 | -0.38321 | 0 | 0
114 | 0.97979 | -0.3895 | 0.0016421 | 0.00041154
115 | 0.97147 | -0.55275 | 0.0010203 | 0.00025571
116 | 0.97115 | -0.55909 | 0 | 0
117 | 0.97112 | -0.55973 | 0.00063348 | 0.00015876
118 | 0.97119 | -0.55827 | 0.0034983 | 0.00087675
119 | 0.97885 | -0.40727 | 0.003619 | 0.00090699
120 | 0.97905 | -0.4034 | 0.0011282 | 0.00028275
121 | 0.97106 | -0.56097 | 0 | 0
122 | 0.97103 | -0.56154 | 0.0007982 | 0.00020005
123 | 0.97024 | -0.57809 | 0.00066283 | 0.00016612
124 | 0.97024 | -0.57807 | 0.0016985 | 0.00042569
125 | 0.9901 | -0.18947 | 0.0016235 | 0.00040689
126 | 0.99008 | -0.18984 | 0.0013427 | 0.00033651
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.015597 | -0.0039114 | 0.015624 | 0.0039269 | 2.676e-05 | 1.5549e-05 | 0.023791 | 0.02379 | 0.023791 | 0.97558 | -0.4715 | 0.97741 | -0.43556 | 6.536
1 | 0.012295 | 0.0030837 | -0.012292 | -0.0030823 | 2.5761e-06 | 1.4049e-06 | 0.018754 | 0.018754 | 0.018754 | 0.97558 | -0.4715 | 0.97535 | -0.4759 | 5.1521
2 | -0.016781 | -0.0042169 | 0.01679 | 0.0042223 | 9.1626e-06 | 5.3947e-06 | 0.025552 | 0.025552 | 0.025552 | 0.97741 | -0.43556 | 0.97799 | -0.42413 | 7.0198
3 | 0.012292 | 0.0030823 | -0.012266 | -0.0030678 | 2.6426e-05 | 1.4418e-05 | 0.018754 | 0.018755 | 0.018755 | 0.97535 | -0.4759 | 0.97307 | -0.5211 | 5.1524
4 | 0.0023642 | 0.00059217 | -0.0023642 | -0.00059224 | 3.7258e-08 | -7.2508e-08 | 0.003597 | 0.0035971 | 0.0035971 | 0.97799 | -0.42413 | 0.97797 | -0.42446 | 0.9882
5 | -0.019155 | -0.0048145 | 0.019175 | 0.0048268 | 2.0463e-05 | 1.2289e-05 | 0.029149 | 0.029148 | 0.029149 | 0.97799 | -0.42413 | 0.97913 | -0.40178 | 8.0079
6 | 0.007082 | 0.0017694 | -0.007073 | -0.0017662 | 9.0297e-06 | 3.2315e-06 | 0.010828 | 0.010829 | 0.010829 | 0.97307 | -0.5211 | 0.97171 | -0.54795 | 2.9749
7 | 0.0051838 | 0.0012984 | -0.0051787 | -0.0012978 | 5.1024e-06 | 5.7882e-07 | 0.0079268 | 0.0079278 | 0.0079278 | 0.97307 | -0.5211 | 0.97202 | -0.54177 | 2.178
8 | 0.0011899 | 0.00029795 | -0.0011899 | -0.00029822 | 2.7819e-08 | -2.6617e-07 | 0.0018104 | 0.0018105 | 0.0018105 | 0.97797 | -0.42446 | 0.97795 | -0.42495 | 0.4974
9 | 0.0047482 | 0.0011893 | -0.0047479 | -0.0011893 | 3.2974e-07 | -1.3553e-09 | 0.0072157 | 0.0072158 | 0.0072158 | 0.97913 | -0.40178 | 0.97905 | -0.40324 | 1.9824
10 | -0.023923 | -0.0060161 | 0.023931 | 0.0060207 | 7.5826e-06 | 4.6605e-06 | 0.036364 | 0.036364 | 0.036364 | 0.97913 | -0.40178 | 0.97947 | -0.39515 | 9.9902
11 | 0.0046199 | 0.001157 | -0.0046183 | -0.0011571 | 1.5817e-06 | -3.1281e-08 | 0.0070743 | 0.0070747 | 0.0070747 | 0.97171 | -0.54795 | 0.97135 | -0.55514 | 1.9436
12 | 0.0024531 | 0.00060916 | -0.0024527 | -0.00060974 | 3.4289e-07 | -5.8391e-07 | 0.0037545 | 0.0037548 | 0.0037548 | 0.97171 | -0.54795 | 0.97156 | -0.5509 | 1.0315
13 | 0.0022406 | 0.0005615 | -0.0022406 | -0.00056155 | 2.3378e-08 | -5.0716e-08 | 0.0034301 | 0.0034301 | 0.0034301 | 0.97202 | -0.54177 | 0.97201 | -0.54199 | 0.94233
14 | 0.0036196 | 0.00090667 | -0.003619 | -0.00090699 | 6.9473e-07 | -3.2502e-07 | 0.0055011 | 0.0055014 | 0.0055014 | 0.97905 | -0.40324 | 0.97885 | -0.40727 | 1.5114
15 | 0.0011282 | 0.00028266 | -0.0011282 | -0.00028275 | 8.9175e-09 | -9.6002e-08 | 0.0017147 | 0.0017147 | 0.0017147 | 0.97905 | -0.40324 | 0.97905 | -0.4034 | 0.47107
16 | -0.025398 | -0.0063884 | 0.025415 | 0.006399 | 1.7078e-05 | 1.0545e-05 | 0.038593 | 0.038593 | 0.038593 | 0.97947 | -0.39515 | 0.98019 | -0.38108 | 10.6024
17 | 0.0034988 | 0.00087649 | -0.0034983 | -0.00087675 | 5.2223e-07 | -2.6573e-07 | 0.0053597 | 0.0053599 | 0.0053599 | 0.97135 | -0.55514 | 0.97119 | -0.55827 | 1.4725
18 | 0.0024527 | 0.00060974 | -0.0024525 | -0.0006101 | 2.1474e-07 | -3.6549e-07 | 0.0037548 | 0.0037549 | 0.0037549 | 0.97156 | -0.5509 | 0.97147 | -0.55275 | 1.0316
19 | 0.001142 | 0.00028286 | -0.0011419 | -0.00028311 | 2.4554e-08 | -2.4835e-07 | 0.00175 | 0.0017501 | 0.0017501 | 0.97032 | -0.5765 | 0.9703 | -0.57695 | 0.4808
20 | -0.0020445 | -0.00050906 | 0.0020454 | 0.00050667 | 8.8156e-07 | -2.3944e-06 | 0.0031341 | 0.003133 | 0.0031341 | 0.97032 | -0.5765 | 0.97078 | -0.56738 | 0.86102
21 | 0.0011419 | 0.00028311 | -0.0011419 | -0.00028362 | 5.0462e-08 | -5.1027e-07 | 0.0017501 | 0.0017503 | 0.0017503 | 0.9703 | -0.57695 | 0.97025 | -0.57789 | 0.48085
22 | -0.0040227 | -0.0010005 | 0.004023 | 0.0010004 | 3.0754e-07 | -7.0133e-08 | 0.0061633 | 0.0061632 | 0.0061633 | 0.97078 | -0.56738 | 0.97086 | -0.56577 | 1.6932
23 | 0.0012986 | 0.00032374 | -0.0012984 | -0.00032533 | 2.0626e-07 | -1.5846e-06 | 0.0019899 | 0.0019905 | 0.0019905 | 0.97078 | -0.56738 | 0.97061 | -0.57073 | 0.54685
24 | 0.00039662 | 9.9182e-05 | -0.00039662 | -9.9402e-05 | 2.4971e-09 | -2.207e-07 | 0.00060819 | 0.00060828 | 0.00060828 | 0.97025 | -0.57789 | 0.97025 | -0.57802 | 0.16711
25 | 0.00044461 | 0.00010973 | -0.00044458 | -0.0001113 | 2.2368e-08 | -1.5716e-06 | 0.00068125 | 0.00068182 | 0.00068182 | 0.97025 | -0.57789 | 0.9702 | -0.57895 | 0.18731
26 | 0.00030066 | 7.4708e-05 | -0.00030065 | -7.531e-05 | 3.8982e-09 | -6.0168e-07 | 0.00046086 | 0.00046108 | 0.00046108 | 0.97025 | -0.57789 | 0.97024 | -0.57816 | 0.12667
27 | -0.004585 | -0.0011413 | 0.0045881 | 0.0011412 | 3.0446e-06 | -8.7767e-08 | 0.0070246 | 0.0070238 | 0.0070246 | 0.97086 | -0.56577 | 0.97156 | -0.55176 | 1.9298
28 | 0.00081613 | 0.00020445 | -0.00081613 | -0.00020454 | 4.2211e-09 | -8.617e-08 | 0.0012512 | 0.0012512 | 0.0012512 | 0.97061 | -0.57073 | 0.97061 | -0.57083 | 0.34373
29 | -0.0092546 | -0.0023171 | 0.0092553 | 0.0023174 | 6.3976e-07 | 3.0234e-07 | 0.014109 | 0.014109 | 0.014109 | 0.97598 | -0.46432 | 0.97606 | -0.46287 | 3.8761
30 | 0.0092546 | 0.0023171 | -0.0092295 | -0.0023052 | 2.5088e-05 | 1.1869e-05 | 0.014109 | 0.014111 | 0.014111 | 0.97598 | -0.46432 | 0.9731 | -0.5214 | 3.8765
31 | -0.0095544 | -0.0023924 | 0.0095644 | 0.0023972 | 9.9441e-06 | 4.8001e-06 | 0.014565 | 0.014565 | 0.014565 | 0.97606 | -0.46287 | 0.97717 | -0.44102 | 4.0014
32 | 0.0089294 | 0.00223 | -0.0089166 | -0.002224 | 1.2867e-05 | 5.9514e-06 | 0.013652 | 0.013652 | 0.013652 | 0.9731 | -0.5214 | 0.97156 | -0.55176 | 3.7507
33 | 0.00030065 | 7.531e-05 | -0.00030065 | -7.535e-05 | 2.6071e-10 | -4.0218e-08 | 0.00046108 | 0.0004611 | 0.0004611 | 0.97024 | -0.57816 | 0.97024 | -0.57818 | 0.12667
34 | 0.00044458 | 0.0001113 | -0.00044458 | -0.00011142 | 1.7434e-09 | -1.2237e-07 | 0.00068182 | 0.00068187 | 0.00068187 | 0.9702 | -0.57895 | 0.9702 | -0.57903 | 0.18733
35 | 0.0043285 | 0.0010828 | -0.0043231 | -0.0010834 | 5.3994e-06 | -5.9605e-07 | 0.0066286 | 0.0066301 | 0.0066301 | 0.97156 | -0.55176 | 0.97024 | -0.57798 | 1.8215
36 | 0.0023614 | 0.00059177 | -0.0023614 | -0.00059179 | 9.6339e-09 | -1.8025e-08 | 0.0036215 | 0.0036215 | 0.0036215 | 0.97024 | -0.57798 | 0.97024 | -0.57807 | 0.99492
37 | -0.017514 | -0.0043895 | 0.017546 | 0.0044082 | 3.1469e-05 | 1.8663e-05 | 0.02669 | 0.026689 | 0.02669 | 0.97646 | -0.4542 | 0.97838 | -0.41655 | 7.3324
38 | -0.025062 | -0.0062899 | 0.025146 | 0.0063413 | 8.3287e-05 | 5.1377e-05 | 0.03812 | 0.03812 | 0.03812 | 0.97838 | -0.41655 | 0.98193 | -0.34711 | 10.4726
39 | 0.0038183 | 0.00095609 | -0.0038169 | -0.00095659 | 1.4156e-06 | -4.992e-07 | 0.0058069 | 0.0058074 | 0.0058074 | 0.97838 | -0.41655 | 0.97798 | -0.42434 | 1.5954
40 | 0.0021057 | 0.00052658 | -0.0021053 | -0.00052765 | 4.0771e-07 | -1.0701e-06 | 0.0032022 | 0.0032027 | 0.0032027 | 0.97838 | -0.41655 | 0.97817 | -0.42062 | 0.87986
41 | -0.026584 | -0.0067018 | 0.02659 | 0.0067055 | 5.8913e-06 | 3.648e-06 | 0.0403 | 0.0403 | 0.0403 | 0.98193 | -0.34711 | 0.98216 | -0.34248 | 11.0713
42 | -0.027851 | -0.0070215 | 0.027862 | 0.0070283 | 1.1016e-05 | 6.8415e-06 | 0.04221 | 0.04221 | 0.04221 | 0.98216 | -0.34248 | 0.98259 | -0.33422 | 11.5961
43 | -0.05882 | -0.014838 | 0.058837 | 0.014848 | 1.7028e-05 | 1.0246e-05 | 0.089111 | 0.089111 | 0.089111 | 0.98259 | -0.33422 | 0.9829 | -0.32817 | 8.1603
44 | 0.030958 | 0.0078099 | -0.030945 | -0.0078031 | 1.3645e-05 | 6.8479e-06 | 0.046901 | 0.046902 | 0.046902 | 0.98259 | -0.33422 | 0.98212 | -0.34343 | 4.295
45 | -0.059875 | -0.015109 | 0.059926 | 0.01514 | 5.1308e-05 | 3.0937e-05 | 0.090682 | 0.090681 | 0.090682 | 0.9829 | -0.32817 | 0.98382 | -0.3103 | 8.3042
46 | 0.030185 | 0.0076127 | -0.030168 | -0.0076031 | 1.6771e-05 | 9.6524e-06 | 0.045751 | 0.045751 | 0.045751 | 0.98212 | -0.34343 | 0.98152 | -0.35504 | 6.2845
47 | -0.010733 | -0.0026899 | 0.010735 | 0.0026908 | 1.8096e-06 | 9.1839e-07 | 0.01611 | 0.01611 | 0.01611 | 0.99132 | -0.16592 | 0.9915 | -0.16238 | 4.4259
48 | 0.0095362 | 0.00239 | -0.0095344 | -0.0023891 | 1.8367e-06 | 8.674e-07 | 0.014314 | 0.014314 | 0.014314 | 0.99132 | -0.16592 | 0.99111 | -0.16997 | 3.9325
49 | -0.012288 | -0.0030802 | 0.012291 | 0.0030814 | 2.2918e-06 | 1.2349e-06 | 0.018442 | 0.018442 | 0.018442 | 0.9915 | -0.16238 | 0.9917 | -0.15847 | 5.0665
50 | 0.0047854 | 0.0011989 | -0.0047839 | -0.001199 | 1.4874e-06 | -3.7945e-08 | 0.0071845 | 0.0071849 | 0.0071849 | 0.99111 | -0.16997 | 0.99077 | -0.17649 | 1.9739
51 | -0.013959 | -0.0034997 | 0.013962 | 0.0035009 | 2.0987e-06 | 1.1786e-06 | 0.020946 | 0.020946 | 0.020946 | 0.9917 | -0.15847 | 0.99186 | -0.15532 | 5.7544
52 | -0.015064 | -0.0037773 | 0.015067 | 0.0037786 | 2.3565e-06 | 1.3493e-06 | 0.022601 | 0.022601 | 0.022601 | 0.99186 | -0.15532 | 0.99203 | -0.15203 | 6.209
53 | 0.087736 | 0.022133 | -0.087665 | -0.022089 | 7.0253e-05 | 4.3707e-05 | 0.13165 | 0.13165 | 0.13165 | 0.99203 | -0.15203 | 0.99117 | -0.16877 | 12.0561
54 | -0.1028 | -0.025912 | 0.10281 | 0.025919 | 1.1659e-05 | 7.3102e-06 | 0.15425 | 0.15425 | 0.15425 | 0.99203 | -0.15203 | 0.99216 | -0.14966 | 14.1257
55 | -0.060989 | -0.015406 | 0.06101 | 0.015419 | 2.1134e-05 | 1.277e-05 | 0.092288 | 0.092288 | 0.092288 | 0.98382 | -0.3103 | 0.98419 | -0.30307 | 8.4513
56 | 0.027971 | 0.0070522 | -0.027945 | -0.0070365 | 2.5226e-05 | 1.5673e-05 | 0.042419 | 0.042419 | 0.042419 | 0.98152 | -0.35504 | 0.98055 | -0.3739 | 11.6537
57 | -0.18353 | -0.046553 | 0.18359 | 0.046592 | 6.0472e-05 | 3.8454e-05 | 0.27506 | 0.27506 | 0.27506 | 0.99358 | -0.12223 | 0.99394 | -0.11538 | 25.1888
58 | 0.18231 | 0.046246 | -0.18213 | -0.046133 | 0.00017774 | 0.00011301 | 0.27322 | 0.27322 | 0.27322 | 0.99358 | -0.12223 | 0.99253 | -0.14253 | 25.0205
59 | -0.18454 | -0.04683 | 0.18468 | 0.046915 | 0.00013478 | 8.5711e-05 | 0.27648 | 0.27648 | 0.27648 | 0.99394 | -0.11538 | 0.99473 | -0.10021 | 25.3189
60 | 0.078207 | 0.019923 | -0.078182 | -0.019907 | 2.4617e-05 | 1.5201e-05 | 0.11736 | 0.11736 | 0.11736 | 0.99253 | -0.14253 | 0.99218 | -0.14906 | 10.7476
61 | 0.10392 | 0.02621 | -0.10389 | -0.026188 | 3.5475e-05 | 2.2251e-05 | 0.15586 | 0.15586 | 0.15586 | 0.99253 | -0.14253 | 0.99216 | -0.14966 | 14.2729
62 | -0.18533 | -0.047079 | 0.18538 | 0.047111 | 5.0953e-05 | 3.2403e-05 | 0.27746 | 0.27746 | 0.27746 | 0.99473 | -0.10021 | 0.99503 | -0.0945 | 25.4083
63 | 0.076943 | 0.019597 | -0.076895 | -0.019567 | 4.7668e-05 | 2.9401e-05 | 0.11551 | 0.11551 | 0.11551 | 0.99218 | -0.14906 | 0.99151 | -0.16191 | 10.5775
64 | -0.18681 | -0.047469 | 0.18683 | 0.047485 | 2.6278e-05 | 1.6713e-05 | 0.27959 | 0.27959 | 0.27959 | 0.99503 | -0.0945 | 0.99519 | -0.091579 | 25.6036
65 | 0.075274 | 0.019161 | -0.075211 | -0.019122 | 6.3245e-05 | 3.8947e-05 | 0.11307 | 0.11307 | 0.11307 | 0.99151 | -0.16191 | 0.9906 | -0.17935 | 10.3548
66 | -0.18897 | -0.048022 | 0.18917 | 0.048144 | 0.0001923 | 0.00012232 | 0.28279 | 0.28279 | 0.28279 | 0.99519 | -0.091579 | 0.99629 | -0.070469 | 25.8967
67 | 0.07362 | 0.018723 | -0.073589 | -0.018705 | 3.0231e-05 | 1.8586e-05 | 0.11068 | 0.11068 | 0.11068 | 0.9906 | -0.17935 | 0.99016 | -0.18788 | 10.1359
68 | 0.06125 | 0.015469 | -0.061221 | -0.015452 | 2.8261e-05 | 1.7054e-05 | 0.091995 | 0.091995 | 0.091995 | 0.99117 | -0.16877 | 0.99067 | -0.17841 | 8.4245
69 | 0.072376 | 0.018401 | -0.072286 | -0.018346 | 8.9634e-05 | 5.5034e-05 | 0.10886 | 0.10886 | 0.10886 | 0.99016 | -0.18788 | 0.98882 | -0.21362 | 9.9689
70 | 0.069761 | 0.017713 | -0.069727 | -0.017692 | 3.4314e-05 | 2.1004e-05 | 0.10506 | 0.10506 | 0.10506 | 0.98882 | -0.21362 | 0.98829 | -0.22385 | 9.621
71 | -0.050517 | -0.012762 | 0.050522 | 0.012764 | 4.9026e-06 | 2.8753e-06 | 0.075951 | 0.075951 | 0.075951 | 0.9902 | -0.18747 | 0.9903 | -0.18545 | 6.9552
72 | 0.047771 | 0.012073 | -0.047767 | -0.012071 | 3.7214e-06 | 2.159e-06 | 0.071823 | 0.071824 | 0.071824 | 0.9902 | -0.18747 | 0.99011 | -0.1891 | 6.5772
73 | -0.052925 | -0.013367 | 0.052943 | 0.013377 | 1.7862e-05 | 1.056e-05 | 0.079561 | 0.079561 | 0.079561 | 0.9903 | -0.18545 | 0.99067 | -0.17841 | 7.2858
74 | 0.007737 | 0.0019391 | -0.0077367 | -0.001939 | 3.3942e-07 | 1.3114e-07 | 0.011628 | 0.011628 | 0.011628 | 0.99011 | -0.1891 | 0.99006 | -0.19002 | 3.1945
75 | 0.04003 | 0.010132 | -0.040023 | -0.010128 | 7.1434e-06 | 3.9634e-06 | 0.060196 | 0.060196 | 0.060196 | 0.99011 | -0.1891 | 0.98992 | -0.19281 | 5.5125
76 | 0.0082782 | 0.0020747 | -0.0082757 | -0.0020737 | 2.4476e-06 | 1.0231e-06 | 0.012434 | 0.012434 | 0.012434 | 0.99067 | -0.17841 | 0.99035 | -0.18461 | 3.416
77 | 0.0032056 | 0.00080335 | -0.0032055 | -0.00080338 | 3.9999e-08 | -3.3496e-08 | 0.0048178 | 0.0048178 | 0.0048178 | 0.99006 | -0.19002 | 0.99005 | -0.19028 | 1.3236
78 | 0.03762 | 0.0095257 | -0.037612 | -0.0095213 | 8.057e-06 | 4.3802e-06 | 0.056584 | 0.056584 | 0.056584 | 0.98992 | -0.19281 | 0.98969 | -0.19728 | 5.1817
79 | 0.0057661 | 0.0014447 | -0.0057652 | -0.0014446 | 9.0801e-07 | 1.661e-07 | 0.0086635 | 0.0086637 | 0.0086637 | 0.99035 | -0.18461 | 0.99018 | -0.18792 | 2.3801
80 | 0.0021644 | 0.00054185 | -0.0021643 | -0.0005422 | 1.372e-07 | -3.5615e-07 | 0.003254 | 0.0032542 | 0.0032542 | 0.98969 | -0.19728 | 0.98962 | -0.19861 | 0.894
81 | 0.035448 | 0.0089795 | -0.035444 | -0.0089776 | 3.5794e-06 | 1.9027e-06 | 0.05333 | 0.05333 | 0.05333 | 0.98969 | -0.19728 | 0.98958 | -0.19938 | 4.8837
82 | 0.0044491 | 0.0011147 | -0.0044488 | -0.0011148 | 2.9102e-07 | -3.7038e-08 | 0.0066859 | 0.006686 | 0.006686 | 0.99018 | -0.18792 | 0.99011 | -0.18929 | 1.8368
83 | 0.0015789 | 0.0003955 | -0.0015789 | -0.0003957 | 3.6731e-08 | -1.9978e-07 | 0.002374 | 0.0023741 | 0.0023741 | 0.98962 | -0.19861 | 0.98959 | -0.19909 | 0.65222
84 | 0.032934 | 0.0083486 | -0.032932 | -0.0083471 | 2.5008e-06 | 1.461e-06 | 0.049557 | 0.049557 | 0.049557 | 0.98958 | -0.19938 | 0.9895 | -0.20096 | 6.8072
85 | 0.064552 | 0.016346 | -0.064513 | -0.016323 | 3.897e-05 | 2.3686e-05 | 0.097467 | 0.097467 | 0.097467 | 0.98612 | -0.2657 | 0.98547 | -0.27828 | 8.9256
86 | -0.066075 | -0.016728 | 0.066116 | 0.016753 | 4.1701e-05 | 2.5405e-05 | 0.099764 | 0.099764 | 0.099764 | 0.98612 | -0.2657 | 0.9868 | -0.25256 | 9.1359
87 | 0.063506 | 0.01607 | -0.06343 | -0.016024 | 7.5464e-05 | 4.5793e-05 | 0.095946 | 0.095947 | 0.095947 | 0.98547 | -0.27828 | 0.98419 | -0.30307 | 8.7863
88 | -0.067955 | -0.017214 | 0.068049 | 0.017271 | 9.3851e-05 | 5.7323e-05 | 0.10254 | 0.10254 | 0.10254 | 0.9868 | -0.25256 | 0.98829 | -0.22385 | 9.3898
89 | 0.0024203 | 0.00060564 | -0.0024198 | -0.00060647 | 4.401e-07 | -8.32e-07 | 0.0036589 | 0.0036593 | 0.0036593 | 0.98419 | -0.30307 | 0.984 | -0.30689 | 1.0053
90 | 0.0029662 | 0.00074319 | -0.0029662 | -0.00074321 | 2.4575e-08 | -2.6683e-08 | 0.0044579 | 0.0044579 | 0.0044579 | 0.99011 | -0.18929 | 0.9901 | -0.18947 | 1.2247
91 | -0.0032944 | -0.00082559 | 0.003295 | 0.00082509 | 6.8502e-07 | -4.9308e-07 | 0.0049868 | 0.0049865 | 0.0049868 | 0.983 | -0.32675 | 0.98323 | -0.32238 | 1.37
92 | 0.0026313 | 0.00065941 | -0.0026313 | -0.00065946 | 3.2269e-08 | -4.8107e-08 | 0.0039831 | 0.0039831 | 0.0039831 | 0.983 | -0.32675 | 0.98299 | -0.327 | 1.0943
93 | -0.0044204 | -0.0011071 | 0.0044214 | 0.001107 | 1.0473e-06 | -1.215e-07 | 0.0066895 | 0.0066893 | 0.0066895 | 0.98323 | -0.32238 | 0.98348 | -0.3174 | 1.8378
94 | 0.023771 | 0.0059912 | -0.023701 | -0.0059483 | 6.9838e-05 | 4.2877e-05 | 0.035978 | 0.035978 | 0.035978 | 0.98348 | -0.3174 | 0.98033 | -0.379 | 9.8841
95 | -0.028192 | -0.0070982 | 0.028256 | 0.0071378 | 6.3673e-05 | 3.9564e-05 | 0.042667 | 0.042666 | 0.042667 | 0.98348 | -0.3174 | 0.98591 | -0.27027 | 11.7217
96 | 0.012439 | 0.0031247 | -0.012436 | -0.003123 | 3.0514e-06 | 1.6653e-06 | 0.018883 | 0.018883 | 0.018883 | 0.98033 | -0.379 | 0.98006 | -0.38414 | 5.1877
97 | 0.011262 | 0.0028237 | -0.011261 | -0.002823 | 1.3057e-06 | 6.8544e-07 | 0.017095 | 0.017095 | 0.017095 | 0.98033 | -0.379 | 0.9802 | -0.38143 | 4.6965
98 | -0.028914 | -0.0073027 | 0.02895 | 0.007325 | 3.5824e-05 | 2.2288e-05 | 0.04366 | 0.04366 | 0.04366 | 0.98591 | -0.27027 | 0.98724 | -0.24445 | 11.9945
99 | 0.011233 | 0.0028215 | -0.01123 | -0.00282 | 2.8717e-06 | 1.5063e-06 | 0.017057 | 0.017057 | 0.017057 | 0.98006 | -0.38414 | 0.97979 | -0.3895 | 4.686
100 | 0.010413 | 0.0026103 | -0.010412 | -0.0026099 | 8.7892e-07 | 4.4428e-07 | 0.015807 | 0.015807 | 0.015807 | 0.9802 | -0.38143 | 0.98011 | -0.38321 | 4.3427
101 | -0.030376 | -0.0076823 | 0.030416 | 0.0077075 | 4.0422e-05 | 2.5212e-05 | 0.045808 | 0.045808 | 0.045808 | 0.98724 | -0.24445 | 0.98868 | -0.21675 | 12.5847
102 | -0.0095644 | -0.0023972 | 0.0095879 | 0.0024085 | 2.3525e-05 | 1.1341e-05 | 0.014565 | 0.014563 | 0.014565 | 0.97717 | -0.44102 | 0.97979 | -0.3895 | 4.0013
103 | 0.026833 | 0.0067577 | -0.026824 | -0.006752 | 9.204e-06 | 5.704e-06 | 0.040731 | 0.040731 | 0.040731 | 0.98055 | -0.3739 | 0.98019 | -0.38108 | 11.1899
104 | -0.19135 | -0.048693 | 0.19141 | 0.048729 | 5.6929e-05 | 3.6217e-05 | 0.28606 | 0.28606 | 0.28606 | 0.99629 | -0.070469 | 0.99661 | -0.064299 | 26.196
105 | -0.19458 | -0.049523 | 0.19471 | 0.049607 | 0.00013185 | 8.3894e-05 | 0.29079 | 0.29079 | 0.29079 | 0.99661 | -0.064299 | 0.99735 | -0.050253 | 26.6293
106 | 0.0028704 | 0.00071928 | -0.0028703 | -0.00071937 | 6.7236e-08 | -8.4546e-08 | 0.0042825 | 0.0042825 | 0.0042825 | 0.99735 | -0.050253 | 0.99733 | -0.050745 | 1.1765
107 | -0.19758 | -0.050326 | 0.19781 | 0.050473 | 0.00023004 | 0.0001464 | 0.29507 | 0.29507 | 0.29507 | 0.99735 | -0.050253 | 0.99862 | -0.026148 | 27.0214
108 | -0.20032 | -0.051102 | 0.20044 | 0.051178 | 0.00011921 | 7.5876e-05 | 0.29881 | 0.29881 | 0.29881 | 0.99862 | -0.026148 | 0.99927 | -0.013834 | 27.364
109 | -0.20312 | -0.051849 | 0.20326 | 0.051935 | 0.00013587 | 8.6492e-05 | 0.3028 | 0.3028 | 0.3028 | 0.99927 | -0.013834 | 1 | 0 | 27.7291
110 | 0.032288 | 0.0081858 | -0.03227 | -0.0081744 | 1.8229e-05 | 1.1402e-05 | 0.048589 | 0.048589 | 0.048589 | 0.9895 | -0.20096 | 0.98889 | -0.21271 | 13.3486
111 | 0.03185 | 0.0080693 | -0.031848 | -0.0080677 | 2.5811e-06 | 1.6135e-06 | 0.047958 | 0.047958 | 0.047958 | 0.98889 | -0.21271 | 0.9888 | -0.2144 | 13.1752
112 | 0.030839 | 0.0078148 | -0.030836 | -0.0078126 | 3.4901e-06 | 2.1783e-06 | 0.046439 | 0.046439 | 0.046439 | 0.9888 | -0.2144 | 0.98868 | -0.21675 | 12.7581
113 | -0.0010357 | -0.00025956 | 0.0010358 | 0.00025788 | 1.307e-07 | -1.6833e-06 | 0.0015747 | 0.0015741 | 0.0015747 | 0.97864 | -0.41204 | 0.97878 | -0.40939 | 0.43262
114 | -0.0010358 | -0.00025788 | 0.0010358 | 0.00025762 | 2.0656e-08 | -2.6621e-07 | 0.0015741 | 0.001574 | 0.0015741 | 0.97878 | -0.40939 | 0.9788 | -0.40897 | 0.43244
115 | -0.0057474 | -0.0014382 | 0.0057484 | 0.0014384 | 1.0226e-06 | 2.0532e-07 | 0.0087367 | 0.0087365 | 0.0087367 | 0.9788 | -0.40897 | 0.97899 | -0.40523 | 2.4002
116 | 0.0047116 | 0.0011806 | -0.0047108 | -0.0011806 | 7.8673e-07 | -1.0364e-08 | 0.0071627 | 0.0071628 | 0.0071628 | 0.9788 | -0.40897 | 0.97862 | -0.41247 | 1.9678
117 | -0.0077645 | -0.0019437 | 0.0077646 | 0.0019437 | 6.3606e-08 | 2.5393e-08 | 0.011801 | 0.011801 | 0.011801 | 0.97899 | -0.40523 | 0.979 | -0.40506 | 3.242
118 | -0.0086356 | -0.002162 | 0.0086361 | 0.0021623 | 5.8095e-07 | 2.5872e-07 | 0.013125 | 0.013125 | 0.013125 | 0.979 | -0.40506 | 0.97907 | -0.40364 | 3.6057
119 | -0.010402 | -0.0026048 | 0.010412 | 0.0026099 | 1.013e-05 | 5.1224e-06 | 0.015808 | 0.015807 | 0.015808 | 0.97907 | -0.40364 | 0.98011 | -0.38321 | 4.3428
120 | 0.0014322 | 0.00035439 | -0.0014318 | -0.00035707 | 4.2967e-07 | -2.6748e-06 | 0.0021921 | 0.0021932 | 0.0021932 | 0.97147 | -0.55275 | 0.97115 | -0.55909 | 0.60252
121 | 0.0014318 | 0.00035707 | -0.0014317 | -0.00035733 | 4.3207e-08 | -2.6871e-07 | 0.0021932 | 0.0021933 | 0.0021933 | 0.97115 | -0.55909 | 0.97112 | -0.55973 | 0.60255
122 | 0.00079827 | 0.00019857 | -0.00079822 | -0.00019958 | 4.7332e-08 | -1.014e-06 | 0.0012226 | 0.001223 | 0.001223 | 0.97112 | -0.55973 | 0.97106 | -0.56097 | 0.33599
123 | 0.00079822 | 0.00019958 | -0.0007982 | -0.00020005 | 2.1648e-08 | -4.6352e-07 | 0.001223 | 0.0012232 | 0.0012232 | 0.97106 | -0.56097 | 0.97103 | -0.56154 | 0.33604
124 | -0.00066283 | -0.00016612 | 0.00066283 | 0.0001661 | 6.6641e-10 | -2.0809e-08 | 0.0010166 | 0.0010166 | 0.0010166 | 0.97024 | -0.57809 | 0.97024 | -0.57807 | 0.27927
125 | 0.0013427 | 0.00033633 | -0.0013427 | -0.00033651 | 2.3916e-08 | -1.8611e-07 | 0.0020179 | 0.002018 | 0.002018 | 0.9901 | -0.18947 | 0.99008 | -0.18984 | 0.55439

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.20627 | 0.052276

## res_load
| p_mw | q_mvar
0 | 0.0033026 | 0.0008277
1 | 0.0011571 | 0.00028999
2 | 0.0011742 | 0.00029429
3 | 0.002938 | 0.00073634
4 | 0.0011899 | 0.00029822
5 | 0.001467 | 0.00036767
6 | 0.0011195 | 0.00028058
7 | 0.0022406 | 0.00056155
8 | 0.00090255 | 0.0002262
9 | 0.00067869 | 0.0001701
10 | 0.00056203 | 0.00014086
11 | 0.00048229 | 0.00012087
12 | 0.00029919 | 7.4983e-05
13 | 0.0003001 | 7.5212e-05
14 | 0.00030065 | 7.535e-05
15 | 0.00039662 | 9.9402e-05
16 | 0.00081613 | 0.00020454
17 | 0.0019617 | 0.00049165
18 | 0.00044458 | 0.00011142
19 | 0.017514 | 0.0043895
20 | 0.0015924 | 0.0003991
21 | 0.0014385 | 0.00036052
22 | 0.0038169 | 0.00095659
23 | 0.0021053 | 0.00052765
24 | 0.0012608 | 0.00031599
25 | 0.0010378 | 0.0002601
26 | 0.00075955 | 0.00019036
27 | 0.0011965 | 0.00029987
28 | 0.0015537 | 0.0003894
29 | 0.004749 | 0.0011902
30 | 0.0016689 | 0.00041827
31 | 0.0047839 | 0.001199
32 | 0.0011029 | 0.00027642
33 | 0.0010624 | 0.00026627
34 | 0.0021979 | 0.00055084
35 | 0.0012278 | 0.00030771
36 | 0.00094888 | 0.00023781
37 | 0.00065277 | 0.0001636
38 | 0.0012394 | 0.00031062
39 | 0.001072 | 0.00026868
40 | 0.0014259 | 0.00035736
41 | 0.0016206 | 0.00040617
42 | 0.0021407 | 0.00053652
43 | 0.0015916 | 0.00039888
44 | 0.026416 | 0.0066204
45 | 0.0012137 | 0.00030418
46 | 0.0025252 | 0.00063287
47 | 0.0027466 | 0.00068836
48 | 0.002403 | 0.00060224
49 | 0.0045311 | 0.0011356
50 | 0.002403 | 0.00060224
51 | 0.0025097 | 0.00062898
52 | 0.0032055 | 0.00080338
53 | 0.0013161 | 0.00032984
54 | 0.00058535 | 0.0001467
55 | 0.0025097 | 0.00062898
56 | 0.0015224 | 0.00038155
57 | 0.0010077 | 0.00025255
58 | 0.0018388 | 0.00046085
59 | 0.0016775 | 0.00042042
60 | 0.0024198 | 0.00060647
61 | 0.0014826 | 0.00037157
62 | 0.00066305 | 0.00016618
63 | 0.0011253 | 0.00028204
64 | 0.0026313 | 0.00065946
65 | 0.00065816 | 0.00016495
66 | 0.0012028 | 0.00030145
67 | 0.00084843 | 0.00021264
68 | 0.0014255 | 0.00035727
69 | 0.0011125 | 0.00027882
70 | 0.0014087 | 0.00035306
71 | 0.0021882 | 0.00054841
72 | 0.0031694 | 0.00079432
73 | 0.0028703 | 0.00071937
74 | 0.0025105 | 0.00062919
75 | 0.0026779 | 0.00067115
76 | 0.001358 | 0.00034035
77 | 0.00064363 | 0.00016131
78 | 0.00041952 | 0.00010514
79 | 0.0010088 | 0.00025284
80 | 0.00041959 | 0.00010516
81 | 0.0015789 | 0.0003957
82 | 0.0010357 | 0.00025956
83 | 0.0020161 | 0.00050527
84 | 0.0047108 | 0.0011806
85 | 0.00087101 | 0.0002183
86 | 0.0017655 | 0.00044248
87 | 0.0016421 | 0.00041154
88 | 0.0010203 | 0.00025571
89 | 0.00063348 | 0.00015876
90 | 0.0034983 | 0.00087675
91 | 0.003619 | 0.00090699
92 | 0.0011282 | 0.00028275
93 | 0.0007982 | 0.00020005
94 | 0.00066283 | 0.00016612
95 | 0.0016985 | 0.00042569
96 | 0.0016235 | 0.00040689
97 | 0.0013427 | 0.00033651

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1