## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1321-1_1_2_node_138 | 0.4 | n |  | TRUE
1 | bus_LV_1321-1_1_2_node_14 | 0.4 | n |  | TRUE
2 | bus_LV_1321-1_1_2_node_139 | 0.4 | n |  | TRUE
3 | bus_LV_1321-1_1_2_node_17 | 0.4 | n |  | TRUE
4 | bus_LV_1321-1_1_2_node_140 | 0.4 | n |  | TRUE
5 | bus_LV_1321-1_1_2_node_143 | 0.4 | n |  | TRUE
6 | bus_LV_1321-1_1_2_node_196 | 0.4 | n |  | TRUE
7 | bus_LV_1321-1_1_2_node_158 | 0.4 | n |  | TRUE
8 | bus_LV_1321-1_1_2_node_141 | 0.4 | n |  | TRUE
9 | bus_LV_1321-1_1_2_node_142 | 0.4 | n |  | TRUE
10 | bus_LV_1321-1_1_2_node_150 | 0.4 | n |  | TRUE
11 | bus_LV_1321-1_1_2_node_204 | 0.4 | n |  | TRUE
12 | bus_LV_1321-1_1_2_node_145 | 0.4 | n |  | TRUE
13 | bus_LV_1321-1_1_2_node_203 | 0.4 | n |  | TRUE
14 | bus_LV_1321-1_1_2_node_144 | 0.4 | n |  | TRUE
15 | bus_LV_1321-1_1_2_node_146 | 0.4 | n |  | TRUE
16 | bus_LV_1321-1_1_2_node_157 | 0.4 | n |  | TRUE
17 | bus_LV_1321-1_1_2_node_148 | 0.4 | n |  | TRUE
18 | bus_LV_1321-1_1_2_node_154 | 0.4 | n |  | TRUE
19 | bus_LV_1321-1_1_2_node_155 | 0.4 | n |  | TRUE
20 | bus_LV_1321-1_1_2_node_152 | 0.4 | n |  | TRUE
21 | bus_LV_1321-1_1_2_node_156 | 0.4 | n |  | TRUE
22 | bus_LV_1321-1_1_2_node_151 | 0.4 | n |  | TRUE
23 | bus_LV_1321-1_1_2_node_153 | 0.4 | n |  | TRUE
24 | bus_LV_1321-1_1_2_node_159 | 0.4 | n |  | TRUE
25 | bus_MV_17_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1321-1_1_2_load_138 | 0 | 0.019293 | 0.0048353 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1321-1_1_2_load_196 | 6 | 0.013184 | 0.0033043 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1321-1_1_2_load_158 | 7 | 0.0026833 | 0.00067251 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1321-1_1_2_load_150 | 10 | 0.0036233 | 0.00090808 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1321-1_1_2_load_204 | 11 | 0.0088644 | 0.0022216 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1321-1_1_2_load_203 | 13 | 0.0077882 | 0.0019519 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1321-1_1_2_load_157 | 16 | 0.0019741 | 0.00049476 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1321-1_1_2_load_154 | 18 | 0.0023834 | 0.00059735 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1321-1_1_2_load_155 | 19 | 0.001653 | 0.00041427 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1321-1_1_2_load_152 | 20 | 0.0021983 | 0.00055094 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1321-1_1_2_load_156 | 21 | 0.037734 | 0.009457 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1321-1_1_2_load_151 | 22 | 0.0055862 | 0.0014 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1321-1_1_2_load_153 | 23 | 0.00090888 | 0.00022779 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1321-1_1_2_load_159 | 24 | 0.0031272 | 0.00078375 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1321-1_1_2_line_0 |  | 0 | 1 | 0.017398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1321-1_1_2_line_1 |  | 0 | 2 | 0.17493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1321-1_1_2_line_2 |  | 1 | 4 | 0.15575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1321-1_1_2_line_3 |  | 2 | 3 | 0.006116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1321-1_1_2_line_4 |  | 3 | 7 | 0.13206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1321-1_1_2_line_5 |  | 4 | 5 | 0.015926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1321-1_1_2_line_6 |  | 4 | 6 | 0.0072545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1321-1_1_2_line_7 |  | 5 | 13 | 0.020428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1321-1_1_2_line_8 |  | 5 | 9 | 0.030103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1321-1_1_2_line_9 |  | 7 | 24 | 0.040644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1321-1_1_2_line_10 |  | 8 | 9 | 0.093236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1321-1_1_2_line_11 |  | 8 | 10 | 0.016564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1321-1_1_2_line_12 |  | 9 | 11 | 0.001753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1321-1_1_2_line_13 |  | 9 | 12 | 0.063798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1321-1_1_2_line_14 |  | 10 | 22 | 0.027306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1321-1_1_2_line_15 |  | 12 | 17 | 0.059639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1321-1_1_2_line_16 |  | 12 | 18 | 0.010371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1321-1_1_2_line_17 |  | 14 | 15 | 0.024002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1321-1_1_2_line_18 |  | 14 | 16 | 0.080276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1321-1_1_2_line_19 |  | 15 | 19 | 0.013115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1321-1_1_2_line_20 |  | 15 | 20 | 0.01248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1321-1_1_2_line_21 |  | 17 | 21 | 0.004928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1321-1_1_2_line_22 |  | 18 | 23 | 0.015375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1321-1_1_2_line_23 |  | 20 | 23 | 0.0030576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1321-1_1_2_trafo_153 | 0.63 MVA 20/0.4 kV | 25 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21
0 | 2697329.3681 | 1223523.2678 | 2697321.8823 | 1223508.8797 | 2697321.3379 | 1223507.834
1 | 2697244.7402 | 1223351.4849 | 2697256.184 | 1223366.438 | 2697266.9053 | 1223382.4356 | 2697275.1892 | 1223398.5936 | 2697292.6594 | 1223443.9002 | 2697307.8144 | 1223480.952 | 2697319.5879 | 1223504.4723 | 2697321.3379 | 1223507.834
2 | 2697329.3681 | 1223523.2678 | 2697324.2866 | 1223538.5512 | 2697320.232 | 1223556.9091 | 2697323.0256 | 1223566.495 | 2697325.2278 | 1223576.527 | 2697326.0702 | 1223582.9898 | 2697328.0622 | 1223592.4291 | 2697327.8654 | 1223595.6504 | 2697326.0962 | 1223604.1164 | 2697325.4791 | 1223607.998 | 2697325.7542 | 1223612.5057 | 2697329.4329 | 1223620.8384 | 2697331.923 | 1223625.7938 | 2697332.6748 | 1223628.0521 | 2697333.3072 | 1223635.7568 | 2697334.2922 | 1223640.4541 | 2697336.31 | 1223643.6782 | 2697337.3458 | 1223647.5869 | 2697338.7676 | 1223650.1564 | 2697341.1666 | 1223651.4076 | 2697341.3412 | 1223638.8793 | 2697341.4805 | 1223630.3644
3 | 2697250.8714 | 1223351.3182 | 2697244.7402 | 1223351.4849
4 | 2697250.8714 | 1223351.3182 | 2697261.948 | 1223347.4409 | 2697266.6375 | 1223346.8504 | 2697271.1133 | 1223349.5921 | 2697273.9023 | 1223352.9734 | 2697313.0812 | 1223433.004 | 2697320.8749 | 1223447.9501
5 | 2697357.445 | 1223630.8814 | 2697341.4805 | 1223630.3644
6 | 2697341.4805 | 1223630.3644 | 2697341.7007 | 1223623.1132
7 | 2697357.445 | 1223630.8814 | 2697356.8682 | 1223651.2976
8 | 2697370.786 | 1223648.034 | 2697370.8038 | 1223645.5547 | 2697370.9587 | 1223631.4583 | 2697357.445 | 1223630.8814
9 | 2697345.9149 | 1223479.863 | 2697322.818 | 1223451.6764 | 2697320.8749 | 1223447.9501
10 | 2697370.786 | 1223648.034 | 2697372.0907 | 1223648.022 | 2697380.6085 | 1223648.4616 | 2697380.5204 | 1223658.4784 | 2697396.0793 | 1223663.3809 | 2697398.1646 | 1223674.5229 | 2697398.5461 | 1223694.7658 | 2697399.7676 | 1223720.2262
11 | 2697399.7676 | 1223720.2262 | 2697400.6456 | 1223736.7673
12 | 2697369.4551 | 1223649.1797 | 2697370.786 | 1223648.034
13 | 2697370.786 | 1223648.034 | 2697372.0907 | 1223648.022 | 2697380.6085 | 1223648.4616 | 2697380.5983 | 1223644.4475 | 2697395.8894 | 1223644.8646 | 2697395.9984 | 1223642.3757 | 2697397.3151 | 1223638.8503 | 2697399.8234 | 1223635.7446 | 2697403.2105 | 1223633.6207 | 2697407.1085 | 1223632.7172 | 2697411.0838 | 1223633.1159 | 2697414.4346 | 1223634.6051 | 2697417.1861 | 1223637.0185 | 2697421.189 | 1223633.8818
14 | 2697400.6456 | 1223736.7673 | 2697401.0022 | 1223743.4852 | 2697401.7113 | 1223759.0079 | 2697402.2593 | 1223764.0176
15 | 2697467.5525 | 1223668.632 | 2697466.553 | 1223665.2911 | 2697462.0012 | 1223658.8786 | 2697440.7337 | 1223644.5648 | 2697428.4761 | 1223635.3687 | 2697421.189 | 1223633.8818
16 | 2697421.189 | 1223633.8818 | 2697417.4642 | 1223624.2028 | 2697417.4642 | 1223624.2028
17 | 2697386.7014 | 1223582.0472 | 2697391.4108 | 1223582.0799 | 2697394.4882 | 1223592.3931 | 2697399.2569 | 1223599.465
18 | 2697386.7014 | 1223582.0472 | 2697387.365 | 1223553.5489 | 2697387.863 | 1223543.5166 | 2697389.4097 | 1223532.8898 | 2697392.1226 | 1223519.6025 | 2697394.8743 | 1223509.9629 | 2697397.679 | 1223503.115
19 | 2697399.2569 | 1223599.465 | 2697397.9458 | 1223592.4497 | 2697397.6871 | 1223586.4766
20 | 2697399.2569 | 1223599.465 | 2697405.866 | 1223605.7666 | 2697407.6491 | 1223608.6008
21 | 2697467.5525 | 1223668.632 | 2697472.3584 | 1223669.7226
22 | 2697409.2772 | 1223611.1889 | 2697417.4642 | 1223624.2028
23 | 2697407.6491 | 1223608.6008 | 2697409.2772 | 1223611.1889

## bus_geodata
| x | y | coords
0 | 2697321.3379 | 1223507.834
1 | 2697329.3681 | 1223523.2678
2 | 2697244.7402 | 1223351.4849
3 | 2697250.8715 | 1223351.3182
4 | 2697341.4805 | 1223630.3644
5 | 2697357.445 | 1223630.8814
6 | 2697341.7007 | 1223623.1132
7 | 2697320.8749 | 1223447.9501
8 | 2697399.7676 | 1223720.2262
9 | 2697370.786 | 1223648.034
10 | 2697400.6456 | 1223736.7673
11 | 2697369.4551 | 1223649.1797
12 | 2697421.189 | 1223633.8818
13 | 2697356.8682 | 1223651.2976
14 | 2697386.7014 | 1223582.0472
15 | 2697399.2569 | 1223599.465
16 | 2697397.679 | 1223503.115
17 | 2697467.5525 | 1223668.632
18 | 2697417.4642 | 1223624.2028
19 | 2697397.6871 | 1223586.4766
20 | 2697407.6491 | 1223608.6008
21 | 2697472.3584 | 1223669.7226
22 | 2697402.2593 | 1223764.0176
23 | 2697409.2772 | 1223611.1889
24 | 2697345.9149 | 1223479.863
25 | 2697399.2569 | 1223599.465

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.988 | -0.23112 | 0.019293 | 0.0048353
1 | 0.9884 | -0.22332 | 0 | 0
2 | 0.98707 | -0.24931 | 0 | 0
3 | 0.98703 | -0.24995 | 0 | 0
4 | 0.99199 | -0.15378 | 0 | 0
5 | 0.99255 | -0.14298 | 0 | 0
6 | 0.9919 | -0.15547 | 0.013184 | 0.0033043
7 | 0.98633 | -0.2637 | 0.0026833 | 0.00067251
8 | 0.99304 | -0.13363 | 0 | 0
9 | 0.99382 | -0.11846 | 0 | 0
10 | 0.9929 | -0.13633 | 0.0036233 | 0.00090808
11 | 0.99381 | -0.11874 | 0.0088644 | 0.0022216
12 | 0.99757 | -0.046484 | 0 | 0
13 | 0.99241 | -0.1458 | 0.0077882 | 0.0019519
14 | 0.9999 | -0.0019279 | 0 | 0
15 | 0.99994 | -0.0011006 | 0 | 0
16 | 0.99976 | -0.0046928 | 0.0019741 | 0.00049476
17 | 0.99552 | -0.085981 | 0 | 0
18 | 0.99853 | -0.02799 | 0.0023834 | 0.00059735
19 | 0.99992 | -0.0014786 | 0.001653 | 0.00041427
20 | 0.99998 | -0.00031069 | 0.0021983 | 0.00055094
21 | 0.99535 | -0.089252 | 0.037734 | 0.009457
22 | 0.99276 | -0.13903 | 0.0055862 | 0.0014
23 | 1 | 0 | -0.11246 | -0.028038
24 | 0.98621 | -0.26597 | 0.0031272 | 0.00078375
25 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.025113 | -0.006293 | 0.025122 | 0.0062988 | 9.3329e-06 | 5.7501e-06 | 0.037822 | 0.037822 | 0.037822 | 0.988 | -0.23112 | 0.9884 | -0.22332 | 10.3906
1 | 0.0058199 | 0.0014577 | -0.0058149 | -0.0014567 | 5.04e-06 | 9.8752e-07 | 0.008765 | 0.0087658 | 0.0087658 | 0.988 | -0.23112 | 0.98707 | -0.24931 | 2.4082
2 | -0.025122 | -0.0062988 | 0.025206 | 0.0063502 | 8.3548e-05 | 5.1467e-05 | 0.037822 | 0.037821 | 0.037822 | 0.9884 | -0.22332 | 0.99199 | -0.15378 | 10.3906
3 | 0.0058149 | 0.0014567 | -0.0058147 | -0.0014567 | 1.7623e-07 | 3.4614e-08 | 0.0087658 | 0.0087658 | 0.0087658 | 0.98707 | -0.24931 | 0.98703 | -0.24995 | 2.4082
4 | 0.0058147 | 0.0014567 | -0.0058109 | -0.001456 | 3.8054e-06 | 7.4882e-07 | 0.0087658 | 0.0087664 | 0.0087664 | 0.98703 | -0.24995 | 0.98633 | -0.2637 | 2.4083
5 | -0.038391 | -0.0096551 | 0.038411 | 0.0096676 | 1.9814e-05 | 1.2475e-05 | 0.0576 | 0.057599 | 0.0576 | 0.99199 | -0.15378 | 0.99255 | -0.14298 | 15.824
6 | 0.013185 | 0.0033049 | -0.013184 | -0.0033043 | 1.0642e-06 | 5.8744e-07 | 0.019778 | 0.019778 | 0.019778 | 0.99199 | -0.15378 | 0.9919 | -0.15547 | 5.4336
7 | 0.0077893 | 0.0019523 | -0.0077882 | -0.0019519 | 1.0446e-06 | 4.0459e-07 | 0.011678 | 0.011678 | 0.011678 | 0.99255 | -0.14298 | 0.99241 | -0.1458 | 3.2082
8 | -0.0462 | -0.01162 | 0.046254 | 0.011654 | 5.4177e-05 | 3.4284e-05 | 0.069277 | 0.069277 | 0.069277 | 0.99255 | -0.14298 | 0.99382 | -0.11846 | 19.0322
9 | 0.0031275 | 0.00078345 | -0.0031272 | -0.00078375 | 3.393e-07 | -3.0152e-07 | 0.0047182 | 0.0047184 | 0.0047184 | 0.98633 | -0.2637 | 0.98621 | -0.26597 | 1.2963
10 | -0.0092113 | -0.0023087 | 0.009218 | 0.0023118 | 6.6609e-06 | 3.0558e-06 | 0.013803 | 0.013802 | 0.013803 | 0.99304 | -0.13363 | 0.99382 | -0.11846 | 3.792
11 | 0.0092113 | 0.0023087 | -0.0092101 | -0.0023082 | 1.1834e-06 | 5.4312e-07 | 0.013803 | 0.013803 | 0.013803 | 0.99304 | -0.13363 | 0.9929 | -0.13633 | 3.792
12 | 0.0088645 | 0.0022217 | -0.0088644 | -0.0022216 | 1.158e-07 | 5.14e-08 | 0.013273 | 0.013273 | 0.013273 | 0.99382 | -0.11846 | 0.99381 | -0.11874 | 3.6463
13 | -0.064337 | -0.016188 | 0.064559 | 0.016329 | 0.0002221 | 0.00014132 | 0.096352 | 0.096351 | 0.096352 | 0.99382 | -0.11846 | 0.99757 | -0.046484 | 26.4703
14 | 0.0055869 | 0.0014001 | -0.0055862 | -0.0014 | 7.1785e-07 | 1.0631e-07 | 0.0083728 | 0.0083729 | 0.0083729 | 0.9929 | -0.13633 | 0.99276 | -0.13903 | 2.3003
15 | 0.037811 | 0.0095055 | -0.03774 | -0.0094607 | 7.1168e-05 | 4.4771e-05 | 0.056411 | 0.056411 | 0.056411 | 0.99757 | -0.046484 | 0.99552 | -0.085981 | 15.4975
16 | -0.10237 | -0.025834 | 0.10246 | 0.025892 | 9.0757e-05 | 5.7949e-05 | 0.15276 | 0.15276 | 0.15276 | 0.99757 | -0.046484 | 0.99853 | -0.02799 | 41.9676
17 | -0.0019744 | -0.00049387 | 0.0019744 | 0.0004936 | 7.7681e-08 | -2.6512e-07 | 0.0029378 | 0.0029377 | 0.0029378 | 0.9999 | -0.0019279 | 0.99994 | -0.0011006 | 0.8071
18 | 0.0019744 | 0.00049387 | -0.0019741 | -0.00049476 | 2.5985e-07 | -8.8649e-07 | 0.0029378 | 0.0029382 | 0.0029382 | 0.9999 | -0.0019279 | 0.99976 | -0.0046928 | 0.8072
19 | 0.001653 | 0.00041412 | -0.001653 | -0.00041427 | 2.9759e-08 | -1.53e-07 | 0.0024598 | 0.0024598 | 0.0024598 | 0.99994 | -0.0011006 | 0.99992 | -0.0014786 | 0.67578
20 | -0.0036274 | -0.00090773 | 0.0036276 | 0.00090765 | 1.3634e-07 | -7.646e-08 | 0.0053975 | 0.0053974 | 0.0053975 | 0.99994 | -0.0011006 | 0.99998 | -0.00031069 | 1.4828
21 | 0.03774 | 0.0094607 | -0.037734 | -0.009457 | 5.8807e-06 | 3.6996e-06 | 0.056411 | 0.056411 | 0.056411 | 0.99552 | -0.085981 | 0.99535 | -0.089252 | 15.4975
22 | -0.10484 | -0.02649 | 0.10499 | 0.02658 | 0.00014088 | 8.996e-05 | 0.15631 | 0.15631 | 0.15631 | 0.99853 | -0.02799 | 1 | 0 | 42.9434
23 | -0.0058259 | -0.0014586 | 0.005826 | 0.0014586 | 8.6161e-08 | 1.503e-08 | 0.0086686 | 0.0086686 | 0.0086686 | 0.99998 | -0.00031069 | 1 | 0 | 2.3815

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.11337 | 0.028266

## res_load
| p_mw | q_mvar
0 | 0.019293 | 0.0048353
1 | 0.013184 | 0.0033043
2 | 0.0026833 | 0.00067251
3 | 0.0036233 | 0.00090808
4 | 0.0088644 | 0.0022216
5 | 0.0077882 | 0.0019519
6 | 0.0019741 | 0.00049476
7 | 0.0023834 | 0.00059735
8 | 0.001653 | 0.00041427
9 | 0.0021983 | 0.00055094
10 | 0.037734 | 0.009457
11 | 0.0055862 | 0.0014
12 | 0.00090888 | 0.00022779
13 | 0.0031272 | 0.00078375

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1