## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1321-1_2_1_node_131 | 0.4 | n |  | TRUE
1 | bus_LV_1321-1_2_1_node_181 | 0.4 | n |  | TRUE
2 | bus_LV_1321-1_2_1_node_129 | 0.4 | n |  | TRUE
3 | bus_LV_1321-1_2_1_node_194 | 0.4 | n |  | TRUE
4 | bus_LV_1321-1_2_1_node_31 | 0.4 | n |  | TRUE
5 | bus_LV_1321-1_2_1_node_32 | 0.4 | n |  | TRUE
6 | bus_LV_1321-1_2_1_node_33 | 0.4 | n |  | TRUE
7 | bus_LV_1321-1_2_1_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_1321-1_2_1_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_1321-1_2_1_node_161 | 0.4 | n |  | TRUE
10 | bus_LV_1321-1_2_1_node_163 | 0.4 | n |  | TRUE
11 | bus_LV_1321-1_2_1_node_199 | 0.4 | n |  | TRUE
12 | bus_LV_1321-1_2_1_node_111 | 0.4 | n |  | TRUE
13 | bus_LV_1321-1_2_1_node_172 | 0.4 | n |  | TRUE
14 | bus_LV_1321-1_2_1_node_173 | 0.4 | n |  | TRUE
15 | bus_LV_1321-1_2_1_node_49 | 0.4 | n |  | TRUE
16 | bus_LV_1321-1_2_1_node_198 | 0.4 | n |  | TRUE
17 | bus_LV_1321-1_2_1_node_48 | 0.4 | n |  | TRUE
18 | bus_LV_1321-1_2_1_node_46 | 0.4 | n |  | TRUE
19 | bus_LV_1321-1_2_1_node_43 | 0.4 | n |  | TRUE
20 | bus_LV_1321-1_2_1_node_160 | 0.4 | n |  | TRUE
21 | bus_LV_1321-1_2_1_node_162 | 0.4 | n |  | TRUE
22 | bus_LV_1321-1_2_1_node_112 | 0.4 | n |  | TRUE
23 | bus_LV_1321-1_2_1_node_50 | 0.4 | n |  | TRUE
24 | bus_LV_1321-1_2_1_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_1321-1_2_1_node_39 | 0.4 | n |  | TRUE
26 | bus_LV_1321-1_2_1_node_40 | 0.4 | n |  | TRUE
27 | bus_LV_1321-1_2_1_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_1321-1_2_1_node_44 | 0.4 | n |  | TRUE
29 | bus_LV_1321-1_2_1_node_42 | 0.4 | n |  | TRUE
30 | bus_LV_1321-1_2_1_node_197 | 0.4 | n |  | TRUE
31 | bus_LV_1321-1_2_1_node_103 | 0.4 | n |  | TRUE
32 | bus_LV_1321-1_2_1_node_47 | 0.4 | n |  | TRUE
33 | bus_LV_1321-1_2_1_node_105 | 0.4 | n |  | TRUE
34 | bus_LV_1321-1_2_1_node_101 | 0.4 | n |  | TRUE
35 | bus_LV_1321-1_2_1_node_45 | 0.4 | n |  | TRUE
36 | bus_LV_1321-1_2_1_node_107 | 0.4 | n |  | TRUE
37 | bus_LV_1321-1_2_1_node_200 | 0.4 | n |  | TRUE
38 | bus_LV_1321-1_2_1_node_106 | 0.4 | n |  | TRUE
39 | bus_LV_1321-1_2_1_node_123 | 0.4 | n |  | TRUE
40 | bus_LV_1321-1_2_1_node_122 | 0.4 | n |  | TRUE
41 | bus_LV_1321-1_2_1_node_51 | 0.4 | n |  | TRUE
42 | bus_LV_1321-1_2_1_node_52 | 0.4 | n |  | TRUE
43 | bus_LV_1321-1_2_1_node_53 | 0.4 | n |  | TRUE
44 | bus_LV_1321-1_2_1_node_184 | 0.4 | n |  | TRUE
45 | bus_LV_1321-1_2_1_node_170 | 0.4 | n |  | TRUE
46 | bus_LV_1321-1_2_1_node_171 | 0.4 | n |  | TRUE
47 | bus_LV_1321-1_2_1_node_169 | 0.4 | n |  | TRUE
48 | bus_LV_1321-1_2_1_node_182 | 0.4 | n |  | TRUE
49 | bus_LV_1321-1_2_1_node_54 | 0.4 | n |  | TRUE
50 | bus_LV_1321-1_2_1_node_55 | 0.4 | n |  | TRUE
51 | bus_LV_1321-1_2_1_node_57 | 0.4 | n |  | TRUE
52 | bus_LV_1321-1_2_1_node_58 | 0.4 | n |  | TRUE
53 | bus_LV_1321-1_2_1_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_1321-1_2_1_node_108 | 0.4 | n |  | TRUE
55 | bus_LV_1321-1_2_1_node_109 | 0.4 | n |  | TRUE
56 | bus_LV_1321-1_2_1_node_60 | 0.4 | n |  | TRUE
57 | bus_LV_1321-1_2_1_node_61 | 0.4 | n |  | TRUE
58 | bus_LV_1321-1_2_1_node_62 | 0.4 | n |  | TRUE
59 | bus_LV_1321-1_2_1_node_63 | 0.4 | n |  | TRUE
60 | bus_LV_1321-1_2_1_node_64 | 0.4 | n |  | TRUE
61 | bus_LV_1321-1_2_1_node_86 | 0.4 | n |  | TRUE
62 | bus_LV_1321-1_2_1_node_66 | 0.4 | n |  | TRUE
63 | bus_LV_1321-1_2_1_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_1321-1_2_1_node_91 | 0.4 | n |  | TRUE
65 | bus_LV_1321-1_2_1_node_90 | 0.4 | n |  | TRUE
66 | bus_LV_1321-1_2_1_node_67 | 0.4 | n |  | TRUE
67 | bus_LV_1321-1_2_1_node_88 | 0.4 | n |  | TRUE
68 | bus_LV_1321-1_2_1_node_85 | 0.4 | n |  | TRUE
69 | bus_LV_1321-1_2_1_node_87 | 0.4 | n |  | TRUE
70 | bus_LV_1321-1_2_1_node_134 | 0.4 | n |  | TRUE
71 | bus_LV_1321-1_2_1_node_89 | 0.4 | n |  | TRUE
72 | bus_LV_1321-1_2_1_node_84 | 0.4 | n |  | TRUE
73 | bus_LV_1321-1_2_1_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_1321-1_2_1_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_1321-1_2_1_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_1321-1_2_1_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_1321-1_2_1_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_1321-1_2_1_node_79 | 0.4 | n |  | TRUE
79 | bus_LV_1321-1_2_1_node_76 | 0.4 | n |  | TRUE
80 | bus_LV_1321-1_2_1_node_83 | 0.4 | n |  | TRUE
81 | bus_LV_1321-1_2_1_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_1321-1_2_1_node_81 | 0.4 | n |  | TRUE
83 | bus_LV_1321-1_2_1_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_1321-1_2_1_node_74 | 0.4 | n |  | TRUE
85 | bus_LV_1321-1_2_1_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_1321-1_2_1_node_78 | 0.4 | n |  | TRUE
87 | bus_LV_1321-1_2_1_node_135 | 0.4 | n |  | TRUE
88 | bus_LV_1321-1_2_1_node_136 | 0.4 | n |  | TRUE
89 | bus_LV_1321-1_2_1_node_133 | 0.4 | n |  | TRUE
90 | bus_LV_1321-1_2_1_node_137 | 0.4 | n |  | TRUE
91 | bus_LV_1321-1_2_1_node_80 | 0.4 | n |  | TRUE
92 | bus_LV_1321-1_2_1_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_1321-1_2_1_node_179 | 0.4 | n |  | TRUE
94 | bus_LV_1321-1_2_1_node_93 | 0.4 | n |  | TRUE
95 | bus_LV_1321-1_2_1_node_94 | 0.4 | n |  | TRUE
96 | bus_LV_1321-1_2_1_node_95 | 0.4 | n |  | TRUE
97 | bus_LV_1321-1_2_1_node_96 | 0.4 | n |  | TRUE
98 | bus_LV_1321-1_2_1_node_97 | 0.4 | n |  | TRUE
99 | bus_LV_1321-1_2_1_node_98 | 0.4 | n |  | TRUE
100 | bus_LV_1321-1_2_1_node_99 | 0.4 | n |  | TRUE
101 | bus_LV_1321-1_2_1_node_110 | 0.4 | n |  | TRUE
102 | bus_LV_1321-1_2_1_node_132 | 0.4 | n |  | TRUE
103 | bus_LV_1321-1_2_1_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_1321-1_2_1_node_128 | 0.4 | n |  | TRUE
105 | bus_LV_1321-1_2_1_node_125 | 0.4 | n |  | TRUE
106 | bus_LV_1321-1_2_1_node_124 | 0.4 | n |  | TRUE
107 | bus_LV_1321-1_2_1_node_102 | 0.4 | n |  | TRUE
108 | bus_LV_1321-1_2_1_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_1321-1_2_1_node_127 | 0.4 | n |  | TRUE
110 | bus_LV_1321-1_2_1_node_126 | 0.4 | n |  | TRUE
111 | bus_LV_1321-1_2_1_node_117 | 0.4 | n |  | TRUE
112 | bus_LV_1321-1_2_1_node_118 | 0.4 | n |  | TRUE
113 | bus_LV_1321-1_2_1_node_119 | 0.4 | n |  | TRUE
114 | bus_LV_1321-1_2_1_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_1321-1_2_1_node_114 | 0.4 | n |  | TRUE
116 | bus_LV_1321-1_2_1_node_115 | 0.4 | n |  | TRUE
117 | bus_LV_1321-1_2_1_node_116 | 0.4 | n |  | TRUE
118 | bus_LV_1321-1_2_1_node_120 | 0.4 | n |  | TRUE
119 | bus_LV_1321-1_2_1_node_121 | 0.4 | n |  | TRUE
120 | bus_LV_1321-1_2_1_node_167 | 0.4 | n |  | TRUE
121 | bus_LV_1321-1_2_1_node_165 | 0.4 | n |  | TRUE
122 | bus_LV_1321-1_2_1_node_168 | 0.4 | n |  | TRUE
123 | bus_LV_1321-1_2_1_node_164 | 0.4 | n |  | TRUE
124 | bus_LV_1321-1_2_1_node_176 | 0.4 | n |  | TRUE
125 | bus_LV_1321-1_2_1_node_177 | 0.4 | n |  | TRUE
126 | bus_LV_1321-1_2_1_node_130 | 0.4 | n |  | TRUE
127 | bus_LV_1321-1_2_1_node_187 | 0.4 | n |  | TRUE
128 | bus_LV_1321-1_2_1_node_183 | 0.4 | n |  | TRUE
129 | bus_LV_1321-1_2_1_node_180 | 0.4 | n |  | TRUE
130 | bus_LV_1321-1_2_1_node_166 | 0.4 | n |  | TRUE
131 | bus_LV_1321-1_2_1_node_195 | 0.4 | n |  | TRUE
132 | bus_LV_1321-1_2_1_node_175 | 0.4 | n |  | TRUE
133 | bus_LV_1321-1_2_1_node_174 | 0.4 | n |  | TRUE
134 | bus_LV_1321-1_2_1_node_202 | 0.4 | n |  | TRUE
135 | bus_LV_1321-1_2_1_node_178 | 0.4 | n |  | TRUE
136 | bus_LV_1321-1_2_1_node_185 | 0.4 | n |  | TRUE
137 | bus_LV_1321-1_2_1_node_186 | 0.4 | n |  | TRUE
138 | bus_MV_0_node_197 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1321-1_2_1_load_194 | 3 | 7.3438e-05 | 1.8405e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1321-1_2_1_load_31 | 4 | 0.0018938 | 0.00047463 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1321-1_2_1_load_163 | 10 | 0.00025934 | 6.4998e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1321-1_2_1_load_199 | 11 | 0.00026249 | 6.5786e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1321-1_2_1_load_172 | 13 | 0.00037622 | 9.4289e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1321-1_2_1_load_198 | 16 | 0.00011904 | 2.9834e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1321-1_2_1_load_46 | 18 | 0.00071984 | 0.00018041 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1321-1_2_1_load_160 | 20 | 0.00022612 | 5.6671e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1321-1_2_1_load_162 | 21 | 0.00052162 | 0.00013073 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1321-1_2_1_load_112 | 22 | 0.00014315 | 3.5876e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1321-1_2_1_load_50 | 23 | 7.1679e-05 | 1.7964e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1321-1_2_1_load_38 | 24 | 0.00036827 | 9.2298e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1321-1_2_1_load_44 | 28 | 0.00043265 | 0.00010843 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1321-1_2_1_load_42 | 29 | 0.00035827 | 8.979e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1321-1_2_1_load_197 | 30 | 0.00061351 | 0.00015376 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1321-1_2_1_load_47 | 32 | 0.0002962 | 7.4234e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1321-1_2_1_load_105 | 33 | 0.00018768 | 4.7036e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1321-1_2_1_load_101 | 34 | 0.0001852 | 4.6416e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1321-1_2_1_load_200 | 37 | 0.00021198 | 5.3127e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1321-1_2_1_load_123 | 39 | 0.00091303 | 0.00022883 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1321-1_2_1_load_122 | 40 | 0.00032974 | 8.2641e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1321-1_2_1_load_51 | 41 | 0.0001293 | 3.2406e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1321-1_2_1_load_52 | 42 | 0.00060719 | 0.00015217 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1321-1_2_1_load_184 | 44 | 9.0386e-05 | 2.2653e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1321-1_2_1_load_169 | 47 | 0.00025472 | 6.3839e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1321-1_2_1_load_182 | 48 | 0.00034072 | 8.5392e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1321-1_2_1_load_54 | 49 | 0.0005811 | 0.00014564 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1321-1_2_1_load_55 | 50 | 0.0016838 | 0.00042201 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1321-1_2_1_load_58 | 52 | 0.00033191 | 8.3186e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1321-1_2_1_load_59 | 53 | 0.00047103 | 0.00011805 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1321-1_2_1_load_108 | 54 | 0.00025702 | 6.4415e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1321-1_2_1_load_109 | 55 | 0.00024244 | 6.0761e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1321-1_2_1_load_60 | 56 | 0.00029201 | 7.3184e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1321-1_2_1_load_61 | 57 | 0.00027196 | 6.8159e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1321-1_2_1_load_63 | 59 | 0.00030587 | 7.6657e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1321-1_2_1_load_64 | 60 | 0.00010608 | 2.6586e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1321-1_2_1_load_86 | 61 | 0.00042895 | 0.00010751 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1321-1_2_1_load_91 | 64 | 0.0002206 | 5.5287e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1321-1_2_1_load_90 | 65 | 0.0010118 | 0.00025359 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1321-1_2_1_load_88 | 67 | 0.00028168 | 7.0596e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1321-1_2_1_load_85 | 68 | 0.00086964 | 0.00021795 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1321-1_2_1_load_87 | 69 | 0.00045409 | 0.00011381 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1321-1_2_1_load_89 | 71 | 0.00023347 | 5.8512e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1321-1_2_1_load_84 | 72 | 0.00028812 | 7.221e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1321-1_2_1_load_68 | 73 | 0.00098954 | 0.000248 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1321-1_2_1_load_69 | 74 | 0.00085476 | 0.00021422 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1321-1_2_1_load_72 | 77 | 0.00070289 | 0.00017616 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1321-1_2_1_load_79 | 78 | 0.0028665 | 0.00071841 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1321-1_2_1_load_76 | 79 | 0.00033242 | 8.3313e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1321-1_2_1_load_83 | 80 | 0.0013484 | 0.00033795 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1321-1_2_1_load_77 | 81 | 0.00062098 | 0.00015563 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1321-1_2_1_load_73 | 83 | 0.00027618 | 6.9217e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1321-1_2_1_load_74 | 84 | 0.00046007 | 0.0001153 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1321-1_2_1_load_75 | 85 | 0.0012098 | 0.00030321 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1321-1_2_1_load_135 | 87 | 0.00025322 | 6.3462e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1321-1_2_1_load_136 | 88 | 0.00043466 | 0.00010894 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1321-1_2_1_load_137 | 90 | 0.0018859 | 0.00047266 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1321-1_2_1_load_80 | 91 | 0.0012499 | 0.00031325 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1321-1_2_1_load_82 | 92 | 0.00056067 | 0.00014052 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1321-1_2_1_load_179 | 93 | 0.0018391 | 0.00046091 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1321-1_2_1_load_93 | 94 | 0.0007089 | 0.00017767 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1321-1_2_1_load_94 | 95 | 0.00052018 | 0.00013037 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1321-1_2_1_load_96 | 97 | 0.0034401 | 0.00086218 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1321-1_2_1_load_99 | 100 | 0.00073588 | 0.00018443 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1321-1_2_1_load_110 | 101 | 0.00074788 | 0.00018744 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1321-1_2_1_load_132 | 102 | 0.00025836 | 6.4752e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1321-1_2_1_load_100 | 103 | 0.0013122 | 0.00032886 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1321-1_2_1_load_128 | 104 | 0.00037109 | 9.3004e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1321-1_2_1_load_125 | 105 | 0.00023636 | 5.9237e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1321-1_2_1_load_102 | 107 | 0.00029734 | 7.452e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1321-1_2_1_load_104 | 108 | 0.00079792 | 0.00019998 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1321-1_2_1_load_127 | 109 | 0.00033904 | 8.4972e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1321-1_2_1_load_126 | 110 | 0.00033577 | 8.4152e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1321-1_2_1_load_119 | 113 | 0.00021703 | 5.4392e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1321-1_2_1_load_113 | 114 | 9.7584e-05 | 2.4457e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1321-1_2_1_load_114 | 115 | 0.00027446 | 6.8786e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1321-1_2_1_load_115 | 116 | 0.00030547 | 7.6559e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1321-1_2_1_load_116 | 117 | 0.00015356 | 3.8485e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1321-1_2_1_load_120 | 118 | 0.00018568 | 4.6537e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1321-1_2_1_load_121 | 119 | 0.00051607 | 0.00012934 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1321-1_2_1_load_167 | 120 | 0.00022467 | 5.6307e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1321-1_2_1_load_165 | 121 | 0.00029485 | 7.3897e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1321-1_2_1_load_168 | 122 | 0.0005781 | 0.00014488 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1321-1_2_1_load_164 | 123 | 0.00047719 | 0.0001196 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1321-1_2_1_load_176 | 124 | 0.00046244 | 0.0001159 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1321-1_2_1_load_130 | 126 | 0.00028029 | 7.0247e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1321-1_2_1_load_187 | 127 | 0.00098879 | 0.00024781 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1321-1_2_1_load_183 | 128 | 0.00037496 | 9.3973e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1321-1_2_1_load_180 | 129 | 0.00098198 | 0.00024611 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1321-1_2_1_load_166 | 130 | 0.00014886 | 3.7308e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1321-1_2_1_load_195 | 131 | 0.00012255 | 3.0715e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1321-1_2_1_load_174 | 133 | 0.0011182 | 0.00028025 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1321-1_2_1_load_178 | 135 | 0.00014117 | 3.5381e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1321-1_2_1_load_185 | 136 | 0.00030143 | 7.5545e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1321-1_2_1_load_186 | 137 | 0.0010671 | 0.00026743 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1321-1_2_1_line_0 |  | 0 | 1 | 0.16885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1321-1_2_1_line_1 |  | 0 | 2 | 0.41357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1321-1_2_1_line_2 |  | 0 | 3 | 0.16124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1321-1_2_1_line_3 |  | 1 | 48 | 0.014949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1321-1_2_1_line_4 |  | 1 | 128 | 0.035466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1321-1_2_1_line_5 |  | 1 | 129 | 0.068438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1321-1_2_1_line_6 |  | 2 | 126 | 0.083912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1321-1_2_1_line_7 |  | 2 | 104 | 0.1146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1321-1_2_1_line_8 |  | 4 | 5 | 0.088727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1321-1_2_1_line_9 |  | 4 | 6 | 0.059324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1321-1_2_1_line_10 |  | 5 | 7 | 0.4985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1321-1_2_1_line_11 |  | 6 | 8 | 0.23591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1321-1_2_1_line_12 |  | 7 | 9 | 0.103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1321-1_2_1_line_13 |  | 7 | 10 | 0.040871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1321-1_2_1_line_14 |  | 8 | 11 | 0.009897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1321-1_2_1_line_15 |  | 8 | 12 | 0.32913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1321-1_2_1_line_16 |  | 9 | 20 | 0.085322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1321-1_2_1_line_17 |  | 10 | 21 | 0.02332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1321-1_2_1_line_18 |  | 12 | 22 | 0.038234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1321-1_2_1_line_19 |  | 12 | 23 | 0.076763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1321-1_2_1_line_20 |  | 13 | 14 | 0.26429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1321-1_2_1_line_21 |  | 14 | 132 | 0.15633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1321-1_2_1_line_22 |  | 15 | 16 | 0.12005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1321-1_2_1_line_23 |  | 15 | 17 | 0.011348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1321-1_2_1_line_24 |  | 17 | 23 | 0.015571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1321-1_2_1_line_25 |  | 17 | 32 | 0.08862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1321-1_2_1_line_26 |  | 18 | 19 | 0.10603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1321-1_2_1_line_27 |  | 19 | 35 | 0.016244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1321-1_2_1_line_28 |  | 19 | 29 | 0.074087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1321-1_2_1_line_29 |  | 22 | 111 | 0.021944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1321-1_2_1_line_30 |  | 24 | 25 | 0.22769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1321-1_2_1_line_31 |  | 25 | 26 | 0.26811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1321-1_2_1_line_32 |  | 25 | 27 | 0.040597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1321-1_2_1_line_33 |  | 26 | 28 | 0.048596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1321-1_2_1_line_34 |  | 26 | 29 | 0.040586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1321-1_2_1_line_35 |  | 27 | 30 | 0.064832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1321-1_2_1_line_36 |  | 27 | 31 | 0.07258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1321-1_2_1_line_37 |  | 28 | 32 | 0.0056094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1321-1_2_1_line_38 |  | 31 | 33 | 0.0073904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1321-1_2_1_line_39 |  | 31 | 34 | 0.03394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1321-1_2_1_line_40 |  | 33 | 98 | 0.041466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1321-1_2_1_line_41 |  | 34 | 107 | 0.011353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1321-1_2_1_line_42 |  | 35 | 36 | 0.070271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1321-1_2_1_line_43 |  | 36 | 37 | 0.03973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1321-1_2_1_line_44 |  | 36 | 38 | 0.1383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1321-1_2_1_line_45 |  | 38 | 54 | 0.044953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1321-1_2_1_line_46 |  | 38 | 55 | 0.016387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1321-1_2_1_line_47 |  | 38 | 52 | 0.023337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1321-1_2_1_line_48 |  | 39 | 40 | 0.037864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1321-1_2_1_line_49 |  | 40 | 54 | 0.016835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1321-1_2_1_line_50 |  | 41 | 42 | 0.44243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1321-1_2_1_line_51 |  | 42 | 43 | 0.020215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1321-1_2_1_line_52 |  | 43 | 44 | 0.027674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1321-1_2_1_line_53 |  | 44 | 48 | 0.025259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1321-1_2_1_line_54 |  | 45 | 46 | 0.009309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1321-1_2_1_line_55 |  | 45 | 47 | 0.27656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1321-1_2_1_line_56 |  | 46 | 131 | 0.27811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1321-1_2_1_line_57 |  | 47 | 122 | 0.020581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1321-1_2_1_line_58 |  | 49 | 50 | 0.0032511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1321-1_2_1_line_59 |  | 50 | 51 | 0.036669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1321-1_2_1_line_60 |  | 51 | 52 | 0.2264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1321-1_2_1_line_61 |  | 51 | 53 | 0.037427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1321-1_2_1_line_62 |  | 55 | 106 | 0.23107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1321-1_2_1_line_63 |  | 56 | 57 | 0.065225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1321-1_2_1_line_64 |  | 56 | 58 | 0.19231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1321-1_2_1_line_65 |  | 57 | 59 | 0.20035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1321-1_2_1_line_66 |  | 58 | 60 | 0.025187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1321-1_2_1_line_67 |  | 59 | 61 | 0.06527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1321-1_2_1_line_68 |  | 60 | 62 | 0.0058981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1321-1_2_1_line_69 |  | 61 | 69 | 0.025947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1321-1_2_1_line_70 |  | 62 | 66 | 0.05712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1321-1_2_1_line_71 |  | 62 | 67 | 0.011555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1321-1_2_1_line_72 |  | 63 | 64 | 0.13343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1321-1_2_1_line_73 |  | 63 | 65 | 0.29122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1321-1_2_1_line_74 |  | 64 | 70 | 0.24469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1321-1_2_1_line_75 |  | 66 | 68 | 0.02383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1321-1_2_1_line_76 |  | 67 | 71 | 0.014636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1321-1_2_1_line_77 |  | 68 | 72 | 0.0056686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1321-1_2_1_line_78 |  | 69 | 78 | 0.11102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1321-1_2_1_line_79 |  | 70 | 93 | 0.33064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1321-1_2_1_line_80 |  | 70 | 89 | 0.16136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1321-1_2_1_line_81 |  | 72 | 84 | 0.15704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1321-1_2_1_line_82 |  | 73 | 74 | 0.010349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1321-1_2_1_line_83 |  | 73 | 75 | 0.028589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1321-1_2_1_line_84 |  | 75 | 76 | 0.007696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1321-1_2_1_line_85 |  | 75 | 77 | 0.05509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1321-1_2_1_line_86 |  | 76 | 78 | 0.028855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1321-1_2_1_line_87 |  | 76 | 79 | 0.026924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1321-1_2_1_line_88 |  | 77 | 80 | 0.033568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1321-1_2_1_line_89 |  | 79 | 81 | 0.31227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1321-1_2_1_line_90 |  | 80 | 82 | 1.3228e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1321-1_2_1_line_91 |  | 81 | 86 | 0.040452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1321-1_2_1_line_92 |  | 82 | 91 | 0.026553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1321-1_2_1_line_93 |  | 83 | 84 | 0.033848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1321-1_2_1_line_94 |  | 84 | 85 | 0.021936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1321-1_2_1_line_95 |  | 86 | 87 | 0.026088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1321-1_2_1_line_96 |  | 86 | 88 | 0.025843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1321-1_2_1_line_97 |  | 87 | 89 | 0.05907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1321-1_2_1_line_98 |  | 88 | 90 | 0.043971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1321-1_2_1_line_99 |  | 89 | 102 | 0.0080335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1321-1_2_1_line_100 |  | 91 | 92 | 0.0057954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1321-1_2_1_line_101 |  | 94 | 95 | 0.011935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1321-1_2_1_line_102 |  | 94 | 96 | 0.028326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1321-1_2_1_line_103 |  | 95 | 97 | 0.026475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1321-1_2_1_line_104 |  | 96 | 98 | 0.099226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1321-1_2_1_line_105 |  | 96 | 99 | 0.19098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1321-1_2_1_line_106 |  | 96 | 100 | 0.010472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1321-1_2_1_line_107 |  | 98 | 101 | 0.041996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1321-1_2_1_line_108 |  | 99 | 102 | 0.017708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1321-1_2_1_line_109 |  | 100 | 103 | 0.04184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1321-1_2_1_line_110 |  | 101 | 104 | 0.032664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1321-1_2_1_line_111 |  | 105 | 106 | 0.077269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1321-1_2_1_line_112 |  | 106 | 110 | 0.019111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1321-1_2_1_line_113 |  | 107 | 108 | 0.0071849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1321-1_2_1_line_114 |  | 108 | 109 | 0.00015229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1321-1_2_1_line_115 |  | 110 | 124 | 0.0437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1321-1_2_1_line_116 |  | 111 | 112 | 0.23913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1321-1_2_1_line_117 |  | 111 | 113 | 0.015505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1321-1_2_1_line_118 |  | 112 | 120 | 0.14275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1321-1_2_1_line_119 |  | 112 | 121 | 0.18775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1321-1_2_1_line_120 |  | 113 | 119 | 0.020102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1321-1_2_1_line_121 |  | 114 | 115 | 0.26456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1321-1_2_1_line_122 |  | 114 | 116 | 0.0093806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1321-1_2_1_line_123 |  | 115 | 117 | 0.013829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1321-1_2_1_line_124 |  | 117 | 118 | 0.028703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1321-1_2_1_line_125 |  | 118 | 119 | 0.00042703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1321-1_2_1_line_126 |  | 120 | 122 | 0.022302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1321-1_2_1_line_127 |  | 121 | 123 | 0.027706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1321-1_2_1_line_128 |  | 123 | 130 | 0.026103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1321-1_2_1_line_129 |  | 124 | 125 | 0.030795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1321-1_2_1_line_130 |  | 125 | 135 | 0.033877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1321-1_2_1_line_131 |  | 125 | 133 | 0.021828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1321-1_2_1_line_132 |  | 126 | 127 | 0.049638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1321-1_2_1_line_133 |  | 128 | 136 | 0.02073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1321-1_2_1_line_134 |  | 132 | 134 | 0.18027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1321-1_2_1_line_135 |  | 134 | 135 | 0.22845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1321-1_2_1_line_136 |  | 136 | 137 | 0.026498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1321-1_2_1_trafo_197 | 0.63 MVA 20/0.4 kV | 138 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21
0 | 2698651.9882 | 1225007.1902 | 2698639.1707 | 1225016.0285 | 2698623.1666 | 1225025.9038 | 2698613.5632 | 1225040.7554 | 2698612.5505 | 1225052.9029 | 2698610.9201 | 1225077.6048 | 2698604.3404 | 1225106.2942 | 2698597.2988 | 1225138.6119 | 2698593.5896 | 1225155.6182
1 | 2698548.099 | 1225492.1294 | 2698554.3706 | 1225482.9044 | 2698568.2554 | 1225456.2595 | 2698578.3 | 1225446.3076 | 2698595.2751 | 1225440.9071 | 2698639.7628 | 1225420.1737 | 2698655.4155 | 1225396.227 | 2698654.836 | 1225379.5054 | 2698643.1329 | 1225359.6082 | 2698621.7575 | 1225336.3372 | 2698601.2438 | 1225312.7581 | 2698590.3563 | 1225287.5485 | 2698586.8487 | 1225237.4989 | 2698589.1653 | 1225214.3873 | 2698588.2644 | 1225192.8012 | 2698591.5707 | 1225164.8804 | 2698593.5896 | 1225155.6182
2 | 2698593.5896 | 1225155.6182 | 2698433.966 | 1225178.3859
3 | 2698651.9882 | 1225007.1902 | 2698666.7767 | 1225009.3728
4 | 2698651.9882 | 1225007.1902 | 2698655.396 | 1225019.3443 | 2698660.503 | 1225041.6088
5 | 2698651.9882 | 1225007.1902 | 2698653.6367 | 1225002.8922 | 2698661.6039 | 1224976.0605 | 2698671.4351 | 1224941.5901
6 | 2698548.099 | 1225492.1294 | 2698531.3253 | 1225485.836 | 2698501.7155 | 1225480.8868 | 2698471.241 | 1225479.1591 | 2698465.7987 | 1225478.8219
7 | 2698548.099 | 1225492.1294 | 2698537.6855 | 1225507.4235 | 2698538.3201 | 1225517.6303 | 2698545.7116 | 1225525.0135 | 2698565.9313 | 1225527.8726 | 2698582.9311 | 1225534.2365 | 2698599.5762 | 1225561.0761 | 2698602.1228 | 1225565.6876
8 | 2699584.2202 | 1225882.0017 | 2699577.2749 | 1225862.1044 | 2699579.8988 | 1225851.196 | 2699589.8989 | 1225837.1754 | 2699588.8279 | 1225828.2399 | 2699565.7887 | 1225808.6962
9 | 2699512.6601 | 1225792.5178 | 2699530.0543 | 1225791.9749 | 2699545.9177 | 1225791.8401 | 2699565.7887 | 1225808.6962
10 | 2699584.2202 | 1225882.0017 | 2699621.6842 | 1225859.657 | 2699647.0237 | 1225823.3772 | 2699692.188 | 1225745.6105 | 2699703.7251 | 1225733.0947 | 2699716.0705 | 1225723.0276 | 2699752.3701 | 1225693.8036 | 2699754.1058 | 1225688.8625 | 2699761.3444 | 1225668.2022 | 2699773.7725 | 1225643.7261 | 2699787.5622 | 1225624.8659 | 2699804.8719 | 1225599.5711 | 2699815.1625 | 1225576.427 | 2699821.169 | 1225556.0129 | 2699820.0598 | 1225517.7444 | 2699826.1673 | 1225488.1476 | 2699835.1754 | 1225473.2212
11 | 2699510.1635 | 1225571.0603 | 2699508.1004 | 1225597.3893 | 2699506.93 | 1225618.8519 | 2699501.0898 | 1225651.6002 | 2699495.1489 | 1225690.8292 | 2699480.4869 | 1225716.1246 | 2699478.9207 | 1225736.7801 | 2699503.4663 | 1225776.9306 | 2699512.6601 | 1225792.5178
12 | 2699835.1754 | 1225473.2212 | 2699846.0744 | 1225467.6 | 2699860.9178 | 1225466.8596 | 2699913.636 | 1225480.0205 | 2699934.7917 | 1225485.3574
13 | 2699835.1754 | 1225473.2212 | 2699839.8323 | 1225451.9061 | 2699841.3335 | 1225432.912
14 | 2699510.1635 | 1225571.0603 | 2699518.3917 | 1225565.5272
15 | 2699510.1635 | 1225571.0603 | 2699488.212 | 1225553.9142 | 2699462.9692 | 1225531.8097 | 2699418.3322 | 1225522.7907 | 2699370.0515 | 1225512.6549 | 2699214.2808 | 1225470.0811 | 2699208.7003 | 1225468.7204 | 2699204.2548 | 1225473.4052
16 | 2699934.7917 | 1225485.3574 | 2699938.8494 | 1225501.0813 | 2699940.8528 | 1225570.1355
17 | 2699849.6882 | 1225412.5944 | 2699842.3353 | 1225420.2363 | 2699841.3335 | 1225432.912
18 | 2699204.2548 | 1225473.4052 | 2699203.3004 | 1225437.8859 | 2699203.7637 | 1225435.2243
19 | 2699204.2548 | 1225473.4052 | 2699200.681 | 1225484.9206 | 2699188.2972 | 1225504.5951 | 2699172.4929 | 1225514.3277 | 2699161.5061 | 1225512.977 | 2699150.7917 | 1225507.9658
20 | 2699445.492 | 1226268.6175 | 2699483.5695 | 1226247.0383 | 2699505.9019 | 1226243.9873 | 2699565.5129 | 1226215.9306 | 2699625.3821 | 1226172.5011 | 2699658.7088 | 1226127.7711 | 2699660.9219 | 1226126.9729
21 | 2699445.492 | 1226268.6175 | 2699431.5244 | 1226283.7618 | 2699431.1387 | 1226306.8276 | 2699381.8995 | 1226381.1923 | 2699359.2638 | 1226387.9192
22 | 2699253.2882 | 1225547.5096 | 2699245.7071 | 1225550.6298 | 2699235.901 | 1225553.5017 | 2699225.2929 | 1225555.3596 | 2699214.5345 | 1225553.957 | 2699203.2271 | 1225549.1094 | 2699194.3705 | 1225543.6912 | 2699176.074 | 1225531.0105 | 2699146.3369 | 1225511.9013
23 | 2699135.7298 | 1225507.7883 | 2699146.3369 | 1225511.9013
24 | 2699135.7298 | 1225507.7883 | 2699146.9857 | 1225506.1857 | 2699150.7917 | 1225507.9658
25 | 2699135.7298 | 1225507.7883 | 2699114.7861 | 1225519.27 | 2699074.4735 | 1225566.9555 | 2699073.3473 | 1225568.9534
26 | 2699038.2441 | 1225726.9013 | 2699046.8351 | 1225744.1567 | 2699059.5728 | 1225760.992 | 2699070.1971 | 1225782.2509 | 2699074.4471 | 1225796.1094 | 2699078.2937 | 1225809.1495 | 2699083.0242 | 1225822.0991
27 | 2699037.4053 | 1225743.1213 | 2699038.2441 | 1225726.9013
28 | 2699038.2441 | 1225726.9013 | 2699038.8942 | 1225714.2697 | 2699054.3794 | 1225664.4692 | 2699053.7219 | 1225655.2066
29 | 2699207.5269 | 1225413.6055 | 2699203.7637 | 1225435.2243
30 | 2698797.5262 | 1225642.9622 | 2698829.7716 | 1225616.0892 | 2698843.813 | 1225603.3466 | 2698851.2632 | 1225595.7648 | 2698853.8341 | 1225570.1891 | 2698854.654 | 1225538.6466 | 2698852.8601 | 1225499.6887 | 2698846.8413 | 1225470.401 | 2698842.6386 | 1225454.1083 | 2698842.8569 | 1225440.9722
31 | 2698797.5262 | 1225642.9622 | 2698914.9106 | 1225669.3976 | 2698948.0237 | 1225669.6927 | 2698976.3613 | 1225663.9931 | 2699003.1578 | 1225652.0413 | 2699029.592 | 1225635.9027 | 2699046.7298 | 1225616.1737
32 | 2698757.9473 | 1225633.4317 | 2698797.5262 | 1225642.9622
33 | 2699046.7298 | 1225616.1737 | 2699070.5928 | 1225573.8399
34 | 2699046.7298 | 1225616.1737 | 2699051.4316 | 1225622.9457 | 2699053.7219 | 1225655.2066
35 | 2698757.9473 | 1225633.4317 | 2698765.9518 | 1225649.0759 | 2698782.318 | 1225667.9944 | 2698789.0894 | 1225676.6242 | 2698786.3598 | 1225681.6492 | 2698782.628 | 1225685.8458
36 | 2698757.9473 | 1225633.4317 | 2698738.0859 | 1225628.6543 | 2698686.1801 | 1225621.7663
37 | 2699070.5928 | 1225573.8399 | 2699073.3473 | 1225568.9534
38 | 2698686.1801 | 1225621.7663 | 2698678.9318 | 1225623.2084
39 | 2698686.1801 | 1225621.7663 | 2698684.6059 | 1225612.4557 | 2698680.9029 | 1225590.7008 | 2698679.4437 | 1225588.7577
40 | 2698638.2141 | 1225631.0445 | 2698654.1466 | 1225628.1398 | 2698678.9318 | 1225623.2084
41 | 2698679.4437 | 1225588.7577 | 2698673.3438 | 1225580.6349 | 2698672.6184 | 1225579.6855
42 | 2699037.4053 | 1225743.1213 | 2699036.5758 | 1225759.2413 | 2699040.036 | 1225813.249
43 | 2699040.036 | 1225813.249 | 2699045.171 | 1225819.9504 | 2699051.9283 | 1225829.3919 | 2699060.7172 | 1225838.8562 | 2699067.1866 | 1225840.9987
44 | 2699040.036 | 1225813.249 | 2699043.6151 | 1225869.2157 | 2699037.65 | 1225926.9359 | 2699033.9314 | 1225950.8246
45 | 2699033.9314 | 1225950.8246 | 2699022.2517 | 1225944.2366 | 2699011.5146 | 1225929.7586 | 2699003.7495 | 1225918.6931
46 | 2699033.9314 | 1225950.8246 | 2699027.7015 | 1225962.9853 | 2699027.0668 | 1225965.634
47 | 2699033.9314 | 1225950.8246 | 2699045.8216 | 1225957.9721 | 2699052.0836 | 1225965.0675
48 | 2698995.7634 | 1225903.9307 | 2698991.458 | 1225894.8776 | 2698974.5902 | 1225882.0322 | 2698971.7659 | 1225876.0259
49 | 2698995.7634 | 1225903.9307 | 2699000.7537 | 1225914.4241 | 2699003.7495 | 1225918.6931
50 | 2698723.9438 | 1224978.2792 | 2698733.8045 | 1224976.2467 | 2698737.4196 | 1224966.7665 | 2698743.734 | 1224954.1066 | 2698754.602 | 1224936.6409 | 2698771.8195 | 1224928.6209 | 2698797.6034 | 1224918.9084 | 2698842.219 | 1224902.6152 | 2698878.4445 | 1224888.818 | 2698895.1856 | 1224884.8377 | 2698911.0557 | 1224884.9014 | 2698930.086 | 1224890.0881 | 2698946.1826 | 1224900.6966 | 2698959.6637 | 1224909.4381 | 2698973.4271 | 1224913.5143 | 2698988.6587 | 1224914.5795 | 2699001.4736 | 1224914.5926 | 2699018.389 | 1224912.4391 | 2699041.8332 | 1224909.3825 | 2699063.7712 | 1224911.1711 | 2699075.9182 | 1224914.4089 | 2699121.7604 | 1224931.2161
51 | 2698704.0891 | 1224982.0803 | 2698721.9727 | 1224978.6855 | 2698723.9438 | 1224978.2792
52 | 2698704.0891 | 1224982.0803 | 2698704.6931 | 1224989.5512 | 2698692.6832 | 1225002.7282 | 2698690.5266 | 1225003.6618
53 | 2698666.7767 | 1225009.3728 | 2698674.6507 | 1225010.5349 | 2698690.5266 | 1225003.6618
54 | 2699078.0204 | 1224800.4952 | 2699079.6954 | 1224809.6519
55 | 2699079.6954 | 1224809.6519 | 2699103.9364 | 1224819.7849 | 2699111.6871 | 1224830.6551 | 2699120.8345 | 1224855.5476 | 2699131.8257 | 1224879.459 | 2699145.4382 | 1224904.4148 | 2699162.7196 | 1224929.4429 | 2699181.9056 | 1224949.8328 | 2699202.0733 | 1224972.274 | 2699217.9257 | 1224997.4786 | 2699226.1708 | 1225015.0509 | 2699226.9973 | 1225026.4173 | 2699227.8838 | 1225032.8589
56 | 2699078.0204 | 1224800.4952 | 2699077.5051 | 1224788.6336 | 2699031.5004 | 1224739.7885 | 2699021.6084 | 1224725.4247 | 2698988.2574 | 1224657.0874 | 2698978.0571 | 1224647.1107 | 2698924.3456 | 1224632.9298 | 2698918.4217 | 1224627.9945 | 2698914.6667 | 1224618.4919 | 2698914.8227 | 1224600.5794
57 | 2699227.8838 | 1225032.8589 | 2699228.4514 | 1225036.9825 | 2699231.1891 | 1225043.3216 | 2699240.0803 | 1225046.7056 | 2699240.0803 | 1225046.7056
58 | 2699247.9145 | 1226134.4004 | 2699245.2542 | 1226132.5316
59 | 2699221.0592 | 1226105.4088 | 2699237.7153 | 1226127.2357 | 2699245.2542 | 1226132.5316
60 | 2699221.0592 | 1226105.4088 | 2699217.7948 | 1226101.1291 | 2699193.135 | 1226079.6136 | 2699161.4776 | 1226066.7211 | 2699133.1253 | 1226059.7548 | 2699109.3317 | 1226037.1867 | 2699066.0392 | 1225980.8807 | 2699052.0836 | 1225965.0675
61 | 2699199.0786 | 1226076.8996 | 2699211.7317 | 1226088.2854 | 2699220.7074 | 1226098.7759 | 2699221.0592 | 1226105.4088
62 | 2699027.7281 | 1226169.4572 | 2699043.2724 | 1226168.3929 | 2699059.276 | 1226142.0291 | 2699054.6502 | 1226109.3285 | 2699022.5651 | 1226043.8027 | 2699022.9351 | 1225982.8759 | 2699027.0668 | 1225965.634
63 | 2698149.101 | 1225984.9378 | 2698206.9172 | 1226015.1296
64 | 2697988.7784 | 1225886.5117 | 2698028.0293 | 1225930.1673 | 2698067.2156 | 1225954.7083 | 2698141.4008 | 1225980.9167 | 2698149.101 | 1225984.9378
65 | 2698206.9172 | 1226015.1296 | 2698211.0581 | 1226017.292 | 2698279.1336 | 1226058.5011 | 2698338.6472 | 1226112.6454 | 2698367.401 | 1226133.7097
66 | 2697988.7784 | 1225886.5117 | 2697978.2104 | 1225909.3746
67 | 2698410.7263 | 1226179.717 | 2698401.7252 | 1226158.8547 | 2698367.401 | 1226133.7097
68 | 2697975.7356 | 1225914.7284 | 2697978.2104 | 1225909.3746
69 | 2698410.7263 | 1226179.717 | 2698418.54 | 1226197.8276 | 2698423.4254 | 1226201.6813
70 | 2697924.9046 | 1225920.4959 | 2697936.2932 | 1225909.8423 | 2697949.2194 | 1225907.1086 | 2697963.7596 | 1225914.5533 | 2697975.7356 | 1225914.7284
71 | 2697975.7356 | 1225914.7284 | 2697978.4005 | 1225920.4875 | 2697982.9888 | 1225922.9535
72 | 2697959.1819 | 1225734.4818 | 2698059.6924 | 1225756.2081 | 2698089.7669 | 1225761.8297
73 | 2697959.1819 | 1225734.4818 | 2697962.013 | 1225741.6557 | 2697993.0771 | 1225751.6966 | 2698029.4579 | 1225774.9569 | 2698069.6726 | 1225797.4356 | 2698104.6948 | 1225825.344 | 2698133.0857 | 1225842.9691 | 2698159.9633 | 1225862.6933 | 2698200.414 | 1225892.1975
74 | 2698327.0887 | 1225818.5202 | 2698256.9987 | 1225793.0888 | 2698089.7669 | 1225761.8297
75 | 2697924.9046 | 1225920.4959 | 2697922.0479 | 1225923.162 | 2697923.0185 | 1225928.6819 | 2697932.9908 | 1225938.9562
76 | 2697995.8805 | 1225929.882 | 2697982.9888 | 1225922.9535
77 | 2697936.9388 | 1225943.0239 | 2697932.9908 | 1225938.9562
78 | 2698423.4254 | 1226201.6813 | 2698445.608 | 1226219.1795 | 2698488.0041 | 1226262.5568 | 2698501.8606 | 1226279.7848
79 | 2698327.0887 | 1225818.5202 | 2698329.8829 | 1225796.2615 | 2698328.1461 | 1225760.9851 | 2698317.8011 | 1225720.3739 | 2698219.4008 | 1225589.2437 | 2698206.4808 | 1225576.399 | 2698182.186 | 1225562.2769 | 2698170.1976 | 1225551.3269 | 2698166.078 | 1225549.5677
80 | 2698478.2656 | 1225870.4461 | 2698464.0703 | 1225872.8797 | 2698327.0887 | 1225818.5202
81 | 2697936.9388 | 1225943.0239 | 2697890.604 | 1226093.0734
82 | 2698530.4839 | 1226336.9915 | 2698530.4839 | 1226336.9915 | 2698535.4167 | 1226346.0892
83 | 2698522.181 | 1226309.6343 | 2698530.4839 | 1226336.9915
84 | 2698519.9452 | 1226302.2697 | 2698522.181 | 1226309.6343
85 | 2698522.181 | 1226309.6343 | 2698545.4454 | 1226327.5991 | 2698565.2765 | 1226333.6096 | 2698569.9466 | 1226335.3232
86 | 2698519.9452 | 1226302.2697 | 2698501.8606 | 1226279.7848
87 | 2698519.9452 | 1226302.2697 | 2698520.2103 | 1226275.3468
88 | 2698569.9466 | 1226335.3232 | 2698578.0036 | 1226338.2794 | 2698586.98 | 1226348.769 | 2698591.4651 | 1226348.0316 | 2698592.9945 | 1226341.5763
89 | 2698520.2103 | 1226275.3468 | 2698520.9116 | 1226204.126 | 2698504.4404 | 1226107.8394 | 2698478.2492 | 1226062.8179 | 2698502.2163 | 1226032.4815 | 2698497.8902 | 1225992.937 | 2698504.4041 | 1225981.8843
90 | 2698592.9976 | 1226341.5635 | 2698592.9945 | 1226341.5763
91 | 2698496.6722 | 1225948.3736 | 2698511.8302 | 1225969.284 | 2698504.4041 | 1225981.8843
92 | 2698592.9976 | 1226341.5635 | 2698576.8249 | 1226320.5038
93 | 2697920.8625 | 1226107.8527 | 2697908.9819 | 1226100.1744 | 2697890.604 | 1226093.0734
94 | 2697890.604 | 1226093.0734 | 2697870.1424 | 1226085.1673
95 | 2698496.6722 | 1225948.3736 | 2698484.0593 | 1225925.5369
96 | 2698496.6722 | 1225948.3736 | 2698502.5529 | 1225947.1589 | 2698510.2898 | 1225946.4754 | 2698521.7435 | 1225950.2851
97 | 2698478.2656 | 1225870.4461 | 2698471.0769 | 1225885.6381 | 2698478.1964 | 1225914.9215 | 2698484.0593 | 1225925.5369
98 | 2698545.106 | 1225980.6987 | 2698548.8408 | 1225976.3018 | 2698543.6855 | 1225968.5108 | 2698534.4802 | 1225959.4407 | 2698525.664 | 1225951.5891 | 2698521.7435 | 1225950.2851
99 | 2698478.2656 | 1225870.4461 | 2698482.6269 | 1225863.6995
100 | 2698573.2951 | 1226315.9074 | 2698576.8249 | 1226320.5038
101 | 2698562.9676 | 1225690.7686 | 2698565.7112 | 1225694.4112 | 2698571.7874 | 1225698.5913
102 | 2698545.9256 | 1225668.1424 | 2698562.9676 | 1225690.7686
103 | 2698595.93 | 1225704.551 | 2698587.8122 | 1225699.4587 | 2698575.3666 | 1225701.0537 | 2698571.7874 | 1225698.5913
104 | 2698545.9256 | 1225668.1424 | 2698603.5924 | 1225644.4471 | 2698638.2141 | 1225631.0445
105 | 2698545.9256 | 1225668.1424 | 2698531.4233 | 1225685.4148 | 2698524.3443 | 1225725.9935 | 2698507.0617 | 1225775.1873 | 2698492.2403 | 1225848.8284
106 | 2698545.9256 | 1225668.1424 | 2698539.4428 | 1225659.918 | 2698539.4428 | 1225659.918
107 | 2698638.2141 | 1225631.0445 | 2698617.913 | 1225594.2817
108 | 2698492.2403 | 1225848.8284 | 2698482.6269 | 1225863.6995
109 | 2698536.7266 | 1225618.6299 | 2698535.5416 | 1225625.3841 | 2698539.3425 | 1225641.2585 | 2698539.4428 | 1225659.918
110 | 2698602.1228 | 1225565.6876 | 2698617.913 | 1225594.2817
111 | 2699027.7281 | 1226169.4572 | 2698959.1196 | 1226133.9124
112 | 2699027.7281 | 1226169.4572 | 2699039.229 | 1226184.7209
113 | 2698672.6184 | 1225579.6855 | 2698668.2565 | 1225573.9763
114 | 2698668.164 | 1225573.8552 | 2698668.2565 | 1225573.9763
115 | 2699039.229 | 1226184.7209 | 2699065.5266 | 1226219.6225
116 | 2699207.5269 | 1225413.6055 | 2699239.4448 | 1225376.0994 | 2699274.9115 | 1225310.4434 | 2699279.6563 | 1225249.2228 | 2699278.3344 | 1225195.3174
117 | 2699207.5269 | 1225413.6055 | 2699203.0683 | 1225412.2524 | 2699192.2602 | 1225411.354
118 | 2699278.3344 | 1225195.3174 | 2699277.6479 | 1225091.0752 | 2699273.4899 | 1225079.8756 | 2699258.4637 | 1225063.3575 | 2699256.031 | 1225059.8948
119 | 2699278.3344 | 1225195.3174 | 2699309.9696 | 1225156.6729 | 2699315.4908 | 1225137.9959 | 2699343.9167 | 1225098.5863 | 2699375.1324 | 1225064.227 | 2699388.0638 | 1225051.3559 | 2699392.1028 | 1225048.2794
120 | 2699192.2602 | 1225411.354 | 2699187.8414 | 1225410.9866 | 2699172.3988 | 1225413.6343
121 | 2698993.2466 | 1225265.8736 | 2698996.2039 | 1225268.1042 | 2699009.033 | 1225279.0588 | 2699021.7987 | 1225294.2821 | 2699040 | 1225324.5846 | 2699062.9248 | 1225364.9063 | 2699075.3234 | 1225389.8529 | 2699098.7542 | 1225423.9009 | 2699116.4225 | 1225449.7359 | 2699120.033 | 1225452.8428 | 2699123.9014 | 1225452.2957 | 2699127.8281 | 1225448.714 | 2699130.6518 | 1225437.6086 | 2699133.5204 | 1225424.269 | 2699134.4769 | 1225421.6265
122 | 2698985.7575 | 1225260.2248 | 2698993.2466 | 1225265.8736
123 | 2699143.4351 | 1225413.2339 | 2699140.8273 | 1225413.0381 | 2699136.5089 | 1225416.0128 | 2699134.4769 | 1225421.6265
124 | 2699171.978 | 1225413.7064 | 2699165.2042 | 1225414.8678 | 2699143.4351 | 1225413.2339
125 | 2699171.978 | 1225413.7064 | 2699172.3988 | 1225413.6343
126 | 2699256.031 | 1225059.8948 | 2699251.1679 | 1225052.9728 | 2699247.5909 | 1225047.8539 | 2699240.0803 | 1225046.7056
127 | 2699414.5754 | 1225032.0984 | 2699404.8765 | 1225038.5496 | 2699392.1028 | 1225048.2794
128 | 2699414.5754 | 1225032.0984 | 2699418.6559 | 1225029.3843 | 2699426.8775 | 1225026.097 | 2699435.9375 | 1225024.8252 | 2699439.0318 | 1225025.6365
129 | 2699079.0157 | 1226246.8224 | 2699073.901 | 1226230.7367 | 2699065.5266 | 1226219.6225
130 | 2699085.3677 | 1226280.0967 | 2699079.0157 | 1226246.8224
131 | 2699079.0157 | 1226246.8224 | 2699099.7953 | 1226253.5072
132 | 2698417.3072 | 1225470.5608 | 2698435.4822 | 1225476.9437 | 2698465.7987 | 1225478.8219
133 | 2698660.503 | 1225041.6088 | 2698661.2794 | 1225044.9936 | 2698663.1384 | 1225054.976 | 2698669.1727 | 1225058.7232 | 2698669.1727 | 1225058.7232
134 | 2699207.9268 | 1226472.678 | 2699231.2511 | 1226472.3555 | 2699257.038 | 1226467.1151 | 2699351.7223 | 1226402.3371 | 2699359.2638 | 1226387.9192
135 | 2699085.3677 | 1226280.0967 | 2699154.1829 | 1226376.4459 | 2699207.9268 | 1226472.678
136 | 2698669.1727 | 1225058.7232 | 2698684.841 | 1225058.5828 | 2698695.6667 | 1225058.8712

## bus_geodata
| x | y | coords
0 | 2698593.5896 | 1225155.6182
1 | 2698651.9882 | 1225007.1902
2 | 2698548.099 | 1225492.1294
3 | 2698433.966 | 1225178.3859
4 | 2699565.7887 | 1225808.6962
5 | 2699584.2202 | 1225882.0017
6 | 2699512.6601 | 1225792.5178
7 | 2699835.1754 | 1225473.2212
8 | 2699510.1635 | 1225571.0603
9 | 2699934.7917 | 1225485.3574
10 | 2699841.3335 | 1225432.912
11 | 2699518.3917 | 1225565.5272
12 | 2699204.2548 | 1225473.4052
13 | 2699660.9219 | 1226126.9729
14 | 2699445.492 | 1226268.6175
15 | 2699146.3369 | 1225511.9013
16 | 2699253.2882 | 1225547.5096
17 | 2699135.7298 | 1225507.7883
18 | 2699083.0242 | 1225822.0991
19 | 2699038.2441 | 1225726.9013
20 | 2699940.8528 | 1225570.1355
21 | 2699849.6882 | 1225412.5944
22 | 2699203.7637 | 1225435.2243
23 | 2699150.7917 | 1225507.9658
24 | 2698842.8569 | 1225440.9722
25 | 2698797.5262 | 1225642.9622
26 | 2699046.7298 | 1225616.1737
27 | 2698757.9473 | 1225633.4317
28 | 2699070.5928 | 1225573.8399
29 | 2699053.7219 | 1225655.2066
30 | 2698782.628 | 1225685.8458
31 | 2698686.1801 | 1225621.7663
32 | 2699073.3473 | 1225568.9534
33 | 2698678.9318 | 1225623.2084
34 | 2698679.4437 | 1225588.7577
35 | 2699037.4053 | 1225743.1213
36 | 2699040.036 | 1225813.249
37 | 2699067.1866 | 1225840.9987
38 | 2699033.9314 | 1225950.8246
39 | 2698971.7659 | 1225876.0259
40 | 2698995.7634 | 1225903.9307
41 | 2699121.7604 | 1224931.2161
42 | 2698723.9438 | 1224978.2792
43 | 2698704.0891 | 1224982.0803
44 | 2698690.5266 | 1225003.6618
45 | 2699079.6954 | 1224809.6519
46 | 2699078.0204 | 1224800.4952
47 | 2699227.8838 | 1225032.8589
48 | 2698666.7767 | 1225009.3728
49 | 2699247.9145 | 1226134.4004
50 | 2699245.2542 | 1226132.5316
51 | 2699221.0592 | 1226105.4088
52 | 2699052.0836 | 1225965.0675
53 | 2699199.0786 | 1226076.8996
54 | 2699003.7495 | 1225918.6931
55 | 2699027.0668 | 1225965.634
56 | 2698149.101 | 1225984.9378
57 | 2698206.9172 | 1226015.1296
58 | 2697988.7784 | 1225886.5117
59 | 2698367.401 | 1226133.7097
60 | 2697978.2104 | 1225909.3746
61 | 2698410.7263 | 1226179.717
62 | 2697975.7356 | 1225914.7284
63 | 2697959.1819 | 1225734.4818
64 | 2698089.7669 | 1225761.8297
65 | 2698200.414 | 1225892.1975
66 | 2697924.9046 | 1225920.4959
67 | 2697982.9888 | 1225922.9535
68 | 2697932.9908 | 1225938.9562
69 | 2698423.4254 | 1226201.6813
70 | 2698327.0887 | 1225818.5202
71 | 2697995.8805 | 1225929.882
72 | 2697936.9388 | 1225943.0239
73 | 2698530.4839 | 1226336.9915
74 | 2698535.4167 | 1226346.0892
75 | 2698522.181 | 1226309.6343
76 | 2698519.9452 | 1226302.2697
77 | 2698569.9466 | 1226335.3232
78 | 2698501.8606 | 1226279.7848
79 | 2698520.2103 | 1226275.3468
80 | 2698592.9945 | 1226341.5763
81 | 2698504.4041 | 1225981.8843
82 | 2698592.9976 | 1226341.5635
83 | 2697920.8625 | 1226107.8527
84 | 2697890.604 | 1226093.0734
85 | 2697870.1424 | 1226085.1673
86 | 2698496.6722 | 1225948.3736
87 | 2698484.0593 | 1225925.5369
88 | 2698521.7435 | 1225950.2851
89 | 2698478.2656 | 1225870.4461
90 | 2698545.106 | 1225980.6987
91 | 2698576.8249 | 1226320.5038
92 | 2698573.2951 | 1226315.9074
93 | 2698166.078 | 1225549.5677
94 | 2698562.9676 | 1225690.7686
95 | 2698571.7874 | 1225698.5913
96 | 2698545.9256 | 1225668.1424
97 | 2698595.93 | 1225704.551
98 | 2698638.2141 | 1225631.0445
99 | 2698492.2403 | 1225848.8284
100 | 2698539.4428 | 1225659.918
101 | 2698617.913 | 1225594.2817
102 | 2698482.6269 | 1225863.6995
103 | 2698536.7266 | 1225618.6299
104 | 2698602.1228 | 1225565.6876
105 | 2698959.1196 | 1226133.9124
106 | 2699027.7281 | 1226169.4572
107 | 2698672.6184 | 1225579.6855
108 | 2698668.2565 | 1225573.9763
109 | 2698668.164 | 1225573.8552
110 | 2699039.229 | 1226184.7209
111 | 2699207.5269 | 1225413.6055
112 | 2699278.3344 | 1225195.3174
113 | 2699192.2602 | 1225411.354
114 | 2698993.2466 | 1225265.8736
115 | 2699134.4769 | 1225421.6265
116 | 2698985.7575 | 1225260.2248
117 | 2699143.4351 | 1225413.2339
118 | 2699171.978 | 1225413.7064
119 | 2699172.3988 | 1225413.6343
120 | 2699256.031 | 1225059.8948
121 | 2699392.1028 | 1225048.2794
122 | 2699240.0803 | 1225046.7056
123 | 2699414.5754 | 1225032.0984
124 | 2699065.5266 | 1226219.6225
125 | 2699079.0157 | 1226246.8224
126 | 2698465.7987 | 1225478.8219
127 | 2698417.3072 | 1225470.5608
128 | 2698660.503 | 1225041.6088
129 | 2698671.4351 | 1224941.5901
130 | 2699439.0318 | 1225025.6365
131 | 2698914.8227 | 1224600.5794
132 | 2699359.2638 | 1226387.9192
133 | 2699099.7953 | 1226253.5072
134 | 2699207.9268 | 1226472.678
135 | 2699085.3677 | 1226280.0967
136 | 2698669.1727 | 1225058.7232
137 | 2698695.6667 | 1225058.8712
138 | 2698782.628 | 1225685.8458

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99046 | -0.18403 | 0 | 0
1 | 0.98986 | -0.19579 | 0 | 0
2 | 0.99196 | -0.15463 | 0 | 0
3 | 0.99045 | -0.18425 | 7.3438e-05 | 1.8405e-05
4 | 0.98874 | -0.21916 | 0.0018938 | 0.00047463
5 | 0.98866 | -0.22079 | 0 | 0
6 | 0.9889 | -0.21606 | 0 | 0
7 | 0.9882 | -0.2299 | 0 | 0
8 | 0.98952 | -0.20373 | 0 | 0
9 | 0.98818 | -0.23032 | 0 | 0
10 | 0.98817 | -0.23047 | 0.00025934 | 6.4998e-05
11 | 0.98952 | -0.20378 | 0.00026249 | 6.5786e-05
12 | 0.99048 | -0.18496 | 0 | 0
13 | 0.98854 | -0.22296 | 0.00037622 | 9.4289e-05
14 | 0.98863 | -0.22117 | 0 | 0
15 | 0.99108 | -0.17306 | 0 | 0
16 | 0.99107 | -0.17332 | 0.00011904 | 2.9834e-05
17 | 0.99108 | -0.17304 | 0 | 0
18 | 0.99111 | -0.17235 | 0.00071984 | 0.00018041
19 | 0.99118 | -0.17099 | 0 | 0
20 | 0.98816 | -0.23067 | 0.00022612 | 5.6671e-05
21 | 0.98816 | -0.23068 | 0.00052162 | 0.00013073
22 | 0.99034 | -0.18771 | 0.00014315 | 3.5876e-05
23 | 0.99098 | -0.17507 | 7.1679e-05 | 1.7964e-05
24 | 0.99613 | -0.074412 | 0.00036827 | 9.2298e-05
25 | 0.9962 | -0.072924 | 0 | 0
26 | 0.99207 | -0.15349 | 0 | 0
27 | 0.99684 | -0.060511 | 0 | 0
28 | 0.99171 | -0.16054 | 0.00043265 | 0.00010843
29 | 0.99175 | -0.15985 | 0.00035827 | 8.979e-05
30 | 1 | 0 | -0.055321 | -0.013564
31 | 0.99445 | -0.1064 | 0 | 0
32 | 0.99168 | -0.16132 | 0.0002962 | 7.4234e-05
33 | 0.99422 | -0.11087 | 0.00018768 | 4.7036e-05
34 | 0.9944 | -0.10737 | 0.0001852 | 4.6416e-05
35 | 0.99106 | -0.17323 | 0 | 0
36 | 0.99057 | -0.18291 | 0 | 0
37 | 0.99056 | -0.18306 | 0.00021198 | 5.3127e-05
38 | 0.98962 | -0.20145 | 0 | 0
39 | 0.98951 | -0.20364 | 0.00091303 | 0.00022883
40 | 0.98954 | -0.20302 | 0.00032974 | 8.2641e-05
41 | 0.98974 | -0.1982 | 0.0001293 | 3.2406e-05
42 | 0.98979 | -0.19713 | 0.00060719 | 0.00015217
43 | 0.98981 | -0.19686 | 0 | 0
44 | 0.98983 | -0.19649 | 9.0386e-05 | 2.2653e-05
45 | 0.98959 | -0.20258 | 0 | 0
46 | 0.98959 | -0.20261 | 0 | 0
47 | 0.98962 | -0.20191 | 0.00025472 | 6.3839e-05
48 | 0.98984 | -0.19611 | 0.00034072 | 8.5392e-05
49 | 0.98891 | -0.2153 | 0.0005811 | 0.00014564
50 | 0.98891 | -0.21526 | 0.0016838 | 0.00042201
51 | 0.98899 | -0.21378 | 0 | 0
52 | 0.98956 | -0.20272 | 0.00033191 | 8.3186e-05
53 | 0.98897 | -0.2141 | 0.00047103 | 0.00011805
54 | 0.98956 | -0.20265 | 0.00025702 | 6.4415e-05
55 | 0.98958 | -0.20231 | 0.00024244 | 6.0761e-05
56 | 0.97753 | -0.43582 | 0.00029201 | 7.3184e-05
57 | 0.97777 | -0.43102 | 0.00027196 | 6.8159e-05
58 | 0.97686 | -0.44895 | 0 | 0
59 | 0.97857 | -0.41529 | 0.00030587 | 7.6657e-05
60 | 0.97678 | -0.45067 | 0.00010608 | 2.6586e-05
61 | 0.97885 | -0.4098 | 0.00042895 | 0.00010751
62 | 0.97676 | -0.45106 | 0 | 0
63 | 0.98535 | -0.28277 | 0 | 0
64 | 0.98547 | -0.28032 | 0.0002206 | 5.5287e-05
65 | 0.98508 | -0.28809 | 0.0010118 | 0.00025359
66 | 0.97659 | -0.45431 | 0 | 0
67 | 0.97675 | -0.45117 | 0.00028168 | 7.0596e-05
68 | 0.97652 | -0.45566 | 0.00086964 | 0.00021795
69 | 0.97897 | -0.40741 | 0.00045409 | 0.00011381
70 | 0.98575 | -0.27483 | 0 | 0
71 | 0.97675 | -0.45123 | 0.00023347 | 5.8512e-05
72 | 0.97651 | -0.4559 | 0.00028812 | 7.221e-05
73 | 0.97966 | -0.39366 | 0.00098954 | 0.000248
74 | 0.97966 | -0.39382 | 0.00085476 | 0.00021422
75 | 0.97971 | -0.39271 | 0 | 0
76 | 0.97975 | -0.39191 | 0 | 0
77 | 0.97952 | -0.39657 | 0.00070289 | 0.00017616
78 | 0.97953 | -0.3963 | 0.0028665 | 0.00071841
79 | 0.9801 | -0.38502 | 0.00033242 | 8.3313e-05
80 | 0.97942 | -0.3985 | 0.0013484 | 0.00033795
81 | 0.98426 | -0.30362 | 0.00062098 | 0.00015563
82 | 0.97942 | -0.3985 | 0 | 0
83 | 0.97622 | -0.46167 | 0.00027618 | 6.9217e-05
84 | 0.97623 | -0.4615 | 0.00046007 | 0.0001153
85 | 0.9762 | -0.46198 | 0.0012098 | 0.00030321
86 | 0.98483 | -0.29267 | 0 | 0
87 | 0.98524 | -0.28453 | 0.00025322 | 6.3462e-05
88 | 0.98477 | -0.29375 | 0.00043466 | 0.00010894
89 | 0.98621 | -0.26584 | 0 | 0
90 | 0.98469 | -0.29524 | 0.0018859 | 0.00047266
91 | 0.97937 | -0.39937 | 0.0012499 | 0.00031325
92 | 0.97937 | -0.39943 | 0.00056067 | 0.00014052
93 | 0.98519 | -0.28577 | 0.0018391 | 0.00046091
94 | 0.99027 | -0.18699 | 0.0007089 | 0.00017767
95 | 0.99023 | -0.18783 | 0.00052018 | 0.00013037
96 | 0.99039 | -0.18464 | 0 | 0
97 | 0.99014 | -0.18945 | 0.0034401 | 0.00086218
98 | 0.99292 | -0.13587 | 0 | 0
99 | 0.9867 | -0.2562 | 0 | 0
100 | 0.99037 | -0.18502 | 0.00073588 | 0.00018443
101 | 0.99268 | -0.14063 | 0.00074788 | 0.00018744
102 | 0.98636 | -0.26286 | 0.00025836 | 6.4752e-05
103 | 0.99032 | -0.186 | 0.0013122 | 0.00032886
104 | 0.99251 | -0.1439 | 0.00037109 | 9.3004e-05
105 | 0.989 | -0.21378 | 0.00023636 | 5.9237e-05
106 | 0.98901 | -0.21345 | 0 | 0
107 | 0.99439 | -0.10765 | 0.00029734 | 7.452e-05
108 | 0.99438 | -0.1078 | 0.00079792 | 0.00019998
109 | 0.99438 | -0.1078 | 0.00033904 | 8.4972e-05
110 | 0.98897 | -0.21429 | 0.00033577 | 8.4152e-05
111 | 0.99026 | -0.18924 | 0 | 0
112 | 0.9898 | -0.19833 | 0 | 0
113 | 0.99023 | -0.18972 | 0.00021703 | 5.4392e-05
114 | 0.99008 | -0.1928 | 9.7584e-05 | 2.4457e-05
115 | 0.99018 | -0.19088 | 0.00027446 | 6.8786e-05
116 | 0.99007 | -0.19285 | 0.00030547 | 7.6559e-05
117 | 0.99018 | -0.19071 | 0.00015356 | 3.8485e-05
118 | 0.99021 | -0.19028 | 0.00018568 | 4.6537e-05
119 | 0.99021 | -0.19027 | 0.00051607 | 0.00012934
120 | 0.98965 | -0.20138 | 0.00022467 | 5.6307e-05
121 | 0.98964 | -0.20142 | 0.00029485 | 7.3897e-05
122 | 0.98963 | -0.20177 | 0.0005781 | 0.00014488
123 | 0.98963 | -0.20173 | 0.00047719 | 0.0001196
124 | 0.98889 | -0.21595 | 0.00046244 | 0.0001159
125 | 0.98884 | -0.21687 | 0 | 0
126 | 0.99186 | -0.15652 | 0.00028029 | 7.0247e-05
127 | 0.99182 | -0.1574 | 0.00098879 | 0.00024781
128 | 0.9898 | -0.19689 | 0.00037496 | 9.3973e-05
129 | 0.9898 | -0.19699 | 0.00098198 | 0.00024611
130 | 0.98962 | -0.2018 | 0.00014886 | 3.7308e-05
131 | 0.98956 | -0.20324 | 0.00012255 | 3.0715e-05
132 | 0.98869 | -0.22009 | 0 | 0
133 | 0.98882 | -0.2173 | 0.0011182 | 0.00028025
134 | 0.98875 | -0.21882 | 0 | 0
135 | 0.98883 | -0.2172 | 0.00014117 | 3.5381e-05
136 | 0.98978 | -0.1974 | 0.00030143 | 7.5545e-05
137 | 0.98975 | -0.1979 | 0.0010671 | 0.00026743
138 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0038954 | 0.00096631 | -0.0038933 | -0.00096709 | 2.1664e-06 | -7.854e-07 | 0.0058488 | 0.0058496 | 0.0058496 | 0.99046 | -0.18403 | 0.98986 | -0.19579 | 1.607
1 | -0.0039689 | -0.00098264 | 0.0039744 | 0.00098083 | 5.5043e-06 | -1.8081e-06 | 0.0059584 | 0.0059565 | 0.0059584 | 0.99046 | -0.18403 | 0.99196 | -0.15463 | 1.6369
2 | 7.3439e-05 | 1.6331e-05 | -7.3438e-05 | -1.8405e-05 | 7.3126e-10 | -2.0747e-06 | 0.00010963 | 0.00011033 | 0.00011033 | 0.99046 | -0.18403 | 0.99045 | -0.18425 | 0.030311
3 | 0.0011677 | 0.00028585 | -0.0011676 | -0.00028603 | 1.7225e-08 | -1.8113e-07 | 0.0017529 | 0.001753 | 0.001753 | 0.98986 | -0.19579 | 0.98984 | -0.19611 | 0.48158
4 | 0.0017436 | 0.00043598 | -0.0017435 | -0.00043638 | 9.1349e-08 | -3.9741e-07 | 0.0026207 | 0.0026209 | 0.0026209 | 0.98986 | -0.19579 | 0.9898 | -0.19689 | 0.72002
5 | 0.00098203 | 0.00024526 | -0.00098198 | -0.00024611 | 5.5919e-08 | -8.439e-07 | 0.0014759 | 0.0014763 | 0.0014763 | 0.98986 | -0.19579 | 0.9898 | -0.19699 | 0.40557
6 | 0.0012692 | 0.00031644 | -0.0012691 | -0.00031745 | 1.1402e-07 | -1.0102e-06 | 0.0019034 | 0.0019037 | 0.0019037 | 0.99196 | -0.15463 | 0.99186 | -0.15652 | 0.52301
7 | -0.0052436 | -0.0012973 | 0.0052463 | 0.0012975 | 2.6547e-06 | 2.1881e-07 | 0.0078599 | 0.0078594 | 0.0078599 | 0.99196 | -0.15463 | 0.99251 | -0.1439 | 2.1593
8 | 0.0010076 | 0.00024198 | -0.0010075 | -0.00024307 | 7.6163e-08 | -1.0891e-06 | 0.0015128 | 0.0015132 | 0.0015132 | 0.98874 | -0.21916 | 0.98866 | -0.22079 | 0.4157
9 | -0.0029014 | -0.00071661 | 0.0029018 | 0.00071612 | 4.2341e-07 | -4.9e-07 | 0.0043628 | 0.0043625 | 0.0043628 | 0.98874 | -0.21916 | 0.9889 | -0.21606 | 1.1986
10 | 0.0010075 | 0.00024307 | -0.0010071 | -0.00024919 | 4.2864e-07 | -6.1151e-06 | 0.0015132 | 0.0015154 | 0.0015154 | 0.98866 | -0.22079 | 0.9882 | -0.2299 | 0.41631
11 | -0.0029018 | -0.00071612 | 0.0029035 | 0.00071417 | 1.6832e-06 | -1.9513e-06 | 0.0043625 | 0.0043615 | 0.0043625 | 0.9889 | -0.21606 | 0.98952 | -0.20373 | 1.1985
12 | 0.00022613 | 5.4264e-05 | -0.00022612 | -5.558e-05 | 4.462e-09 | -1.3167e-06 | 0.00033966 | 0.00034012 | 0.00034012 | 0.9882 | -0.2299 | 0.98818 | -0.23032 | 0.093439
13 | 0.00078099 | 0.00019492 | -0.00078097 | -0.00019543 | 2.119e-08 | -5.1005e-07 | 0.0011757 | 0.0011759 | 0.0011759 | 0.9882 | -0.2299 | 0.98817 | -0.23047 | 0.32305
14 | 0.00026249 | 6.5659e-05 | -0.00026249 | -6.5786e-05 | 5.782e-10 | -1.2676e-07 | 0.00039468 | 0.00039472 | 0.00039472 | 0.98952 | -0.20373 | 0.98952 | -0.20378 | 0.10844
15 | -0.003166 | -0.00077983 | 0.0031688 | 0.00077738 | 2.791e-06 | -2.4457e-06 | 0.0047561 | 0.0047547 | 0.0047561 | 0.98952 | -0.20373 | 0.99048 | -0.18496 | 1.3066
16 | 0.00022612 | 5.558e-05 | -0.00022612 | -5.6671e-05 | 3.7054e-09 | -1.0907e-06 | 0.00034012 | 0.0003405 | 0.0003405 | 0.98818 | -0.23032 | 0.98816 | -0.23067 | 0.093544
17 | 0.00052163 | 0.00013044 | -0.00052162 | -0.00013073 | 5.3948e-09 | -2.9529e-07 | 0.00078538 | 0.00078548 | 0.00078548 | 0.98817 | -0.23047 | 0.98816 | -0.23068 | 0.21579
18 | 0.0039961 | 0.00098124 | -0.0039956 | -0.0009814 | 5.1554e-07 | -1.6208e-07 | 0.0059963 | 0.0059965 | 0.0059965 | 0.99048 | -0.18496 | 0.99034 | -0.18771 | 1.6474
19 | -0.0071649 | -0.0017586 | 0.0071682 | 0.0017598 | 3.3271e-06 | 1.1409e-06 | 0.010751 | 0.010751 | 0.010751 | 0.99048 | -0.18496 | 0.99098 | -0.17507 | 2.9536
20 | -0.00037622 | -9.4289e-05 | 0.00037625 | 9.092e-05 | 3.1717e-08 | -3.3683e-06 | 0.0005663 | 0.00056512 | 0.0005663 | 0.98854 | -0.22296 | 0.98863 | -0.22117 | 0.15558
21 | -0.00037625 | -9.092e-05 | 0.00037627 | 8.8928e-05 | 1.8699e-08 | -1.9927e-06 | 0.00056512 | 0.00056444 | 0.00056512 | 0.98863 | -0.22117 | 0.98869 | -0.22009 | 0.15525
22 | 0.00011904 | 2.8288e-05 | -0.00011904 | -2.9834e-05 | 1.4337e-09 | -1.546e-06 | 0.00017819 | 0.00017873 | 0.00017873 | 0.99108 | -0.17306 | 0.99107 | -0.17332 | 0.049101
23 | -0.00011904 | -2.8288e-05 | 0.00011904 | 2.8142e-05 | 1.3508e-10 | -1.4615e-07 | 0.00017819 | 0.00017814 | 0.00017819 | 0.99108 | -0.17306 | 0.99108 | -0.17304 | 0.048954
24 | 0.0072406 | 0.001778 | -0.0072399 | -0.0017777 | 6.8845e-07 | 2.3997e-07 | 0.010858 | 0.010858 | 0.010858 | 0.99108 | -0.17304 | 0.99098 | -0.17507 | 2.983
25 | -0.0073596 | -0.0018061 | 0.0073637 | 0.0018076 | 4.0476e-06 | 1.4478e-06 | 0.011036 | 0.011036 | 0.011036 | 0.99108 | -0.17304 | 0.99168 | -0.16132 | 3.032
26 | -0.00071984 | -0.00018041 | 0.00071988 | 0.00017907 | 4.642e-08 | -1.3368e-06 | 0.0010807 | 0.0010803 | 0.0010807 | 0.99111 | -0.17235 | 0.99118 | -0.17099 | 0.29691
27 | 0.0077071 | 0.0019117 | -0.0077062 | -0.0019114 | 8.145e-07 | 3.1194e-07 | 0.011563 | 0.011563 | 0.011563 | 0.99118 | -0.17099 | 0.99106 | -0.17323 | 3.1768
28 | -0.0084269 | -0.0020908 | 0.0084314 | 0.0020927 | 4.4412e-06 | 1.8869e-06 | 0.012644 | 0.012643 | 0.012644 | 0.99118 | -0.17099 | 0.99175 | -0.15985 | 3.4735
29 | 0.0038524 | 0.00094553 | -0.0038522 | -0.00094563 | 2.7506e-07 | -1.0629e-07 | 0.0057814 | 0.0057815 | 0.0057815 | 0.99034 | -0.18771 | 0.99026 | -0.18924 | 1.5883
30 | -0.00036827 | -9.2298e-05 | 0.0003683 | 8.935e-05 | 2.5791e-08 | -2.9477e-06 | 0.00055013 | 0.0005491 | 0.00055013 | 0.99613 | -0.074412 | 0.9962 | -0.072924 | 0.15113
31 | 0.016952 | 0.0042128 | -0.016888 | -0.0041751 | 6.4403e-05 | 3.7742e-05 | 0.025309 | 0.02531 | 0.02531 | 0.9962 | -0.072924 | 0.99207 | -0.15349 | 6.9533
32 | -0.01732 | -0.0043022 | 0.017331 | 0.0043081 | 1.0179e-05 | 5.9856e-06 | 0.025858 | 0.025858 | 0.025858 | 0.9962 | -0.072924 | 0.99684 | -0.060511 | 7.1038
33 | 0.0080955 | 0.0019914 | -0.0080928 | -0.0019903 | 2.6811e-06 | 1.0887e-06 | 0.012129 | 0.01213 | 0.01213 | 0.99207 | -0.15349 | 0.99171 | -0.16054 | 3.3323
34 | 0.0087923 | 0.0021836 | -0.0087896 | -0.0021825 | 2.6442e-06 | 1.1684e-06 | 0.013181 | 0.013181 | 0.013181 | 0.99207 | -0.15349 | 0.99175 | -0.15985 | 3.6211
35 | -0.053516 | -0.013465 | 0.053671 | 0.013564 | 0.00015522 | 9.8494e-05 | 0.079904 | 0.079903 | 0.079904 | 0.99684 | -0.060511 | 1 | 0 | 21.9516
36 | 0.036185 | 0.0091571 | -0.036106 | -0.0091071 | 7.9503e-05 | 4.9938e-05 | 0.054046 | 0.054047 | 0.054047 | 0.99684 | -0.060511 | 0.99445 | -0.1064 | 14.848
37 | 0.0076601 | 0.0018819 | -0.0076599 | -0.0018818 | 2.7724e-07 | 1.0506e-07 | 0.01148 | 0.01148 | 0.01148 | 0.99171 | -0.16054 | 0.99168 | -0.16132 | 3.154
38 | 0.034486 | 0.0087019 | -0.034479 | -0.0086972 | 7.3858e-06 | 4.631e-06 | 0.051623 | 0.051623 | 0.051623 | 0.99445 | -0.1064 | 0.99422 | -0.11087 | 14.1823
39 | 0.0016196 | 0.00040527 | -0.0016195 | -0.00040566 | 7.4742e-08 | -3.9249e-07 | 0.0024232 | 0.0024234 | 0.0024234 | 0.99445 | -0.1064 | 0.9944 | -0.10737 | 0.66576
40 | 0.034291 | 0.0086502 | -0.03425 | -0.0086245 | 4.099e-05 | 2.5697e-05 | 0.051343 | 0.051343 | 0.051343 | 0.99422 | -0.11087 | 0.99292 | -0.13587 | 14.1052
41 | 0.0014343 | 0.00035925 | -0.0014343 | -0.00035938 | 1.9612e-08 | -1.3473e-07 | 0.0021462 | 0.0021463 | 0.0021463 | 0.9944 | -0.10737 | 0.99439 | -0.10765 | 0.58964
42 | 0.0077062 | 0.0019114 | -0.0077027 | -0.0019101 | 3.5236e-06 | 1.3501e-06 | 0.011563 | 0.011564 | 0.011564 | 0.99106 | -0.17323 | 0.99057 | -0.18291 | 3.1768
43 | 0.00021198 | 5.2617e-05 | -0.00021198 | -5.3127e-05 | 1.5099e-09 | -5.1047e-07 | 0.00031826 | 0.00031844 | 0.00031844 | 0.99057 | -0.18291 | 0.99056 | -0.18306 | 0.087483
44 | 0.0074907 | 0.0018575 | -0.0074842 | -0.001855 | 6.5591e-06 | 2.4191e-06 | 0.011245 | 0.011246 | 0.011246 | 0.99057 | -0.18291 | 0.98962 | -0.20145 | 3.0896
45 | 0.0014999 | 0.00037469 | -0.0014998 | -0.00037521 | 8.5718e-08 | -5.2267e-07 | 0.0022549 | 0.0022551 | 0.0022551 | 0.98962 | -0.20145 | 0.98956 | -0.20265 | 0.61953
46 | 0.0029146 | 0.00071451 | -0.0029145 | -0.00071465 | 1.1772e-07 | -1.352e-07 | 0.0043768 | 0.0043769 | 0.0043769 | 0.98962 | -0.20145 | 0.98958 | -0.20231 | 1.2024
47 | 0.0030697 | 0.00076583 | -0.0030695 | -0.00076601 | 1.8634e-07 | -1.8056e-07 | 0.0046144 | 0.0046145 | 0.0046145 | 0.98962 | -0.20145 | 0.98956 | -0.20272 | 1.2677
48 | -0.00091303 | -0.00022883 | 0.00091305 | 0.00022836 | 2.6764e-08 | -4.6927e-07 | 0.001373 | 0.0013728 | 0.001373 | 0.98951 | -0.20364 | 0.98954 | -0.20302 | 0.3772
49 | -0.0012428 | -0.000311 | 0.0012428 | 0.0003108 | 2.2044e-08 | -2.0216e-07 | 0.0018687 | 0.0018686 | 0.0018687 | 0.98954 | -0.20302 | 0.98956 | -0.20265 | 0.51337
50 | -0.0001293 | -3.2406e-05 | 0.00012931 | 2.6724e-05 | 6.2077e-09 | -5.6822e-06 | 0.0001944 | 0.00019255 | 0.0001944 | 0.98974 | -0.1982 | 0.98979 | -0.19713 | 0.053406
51 | -0.00073649 | -0.0001789 | 0.0007365 | 0.00017865 | 9.2594e-09 | -2.539e-07 | 0.0011052 | 0.0011051 | 0.0011052 | 0.98979 | -0.19713 | 0.98981 | -0.19686 | 0.30363
52 | -0.0007365 | -0.00017865 | 0.00073652 | 0.0001783 | 1.2673e-08 | -3.476e-07 | 0.0011051 | 0.001105 | 0.0011051 | 0.98981 | -0.19686 | 0.98983 | -0.19649 | 0.30361
53 | -0.0008269 | -0.00020095 | 0.00082692 | 0.00020063 | 1.4584e-08 | -3.1535e-07 | 0.0012409 | 0.0012408 | 0.0012409 | 0.98983 | -0.19649 | 0.98984 | -0.19611 | 0.3409
54 | 0.00012256 | 2.7025e-05 | -0.00012256 | -2.7144e-05 | 1.1699e-10 | -1.1952e-07 | 0.00018305 | 0.00018309 | 0.00018309 | 0.98959 | -0.20258 | 0.98959 | -0.20261 | 0.050299
55 | -0.00012256 | -2.7025e-05 | 0.00012256 | 2.3474e-05 | 3.4546e-09 | -3.551e-06 | 0.00018305 | 0.00018201 | 0.00018305 | 0.98959 | -0.20258 | 0.98962 | -0.20191 | 0.050289
56 | 0.00012256 | 2.7144e-05 | -0.00012255 | -3.0715e-05 | 3.5183e-09 | -3.5707e-06 | 0.00018309 | 0.00018429 | 0.00018429 | 0.98959 | -0.20261 | 0.98956 | -0.20324 | 0.050628
57 | -0.00037728 | -8.7312e-05 | 0.00037728 | 8.7049e-05 | 2.4617e-09 | -2.6286e-07 | 0.00056481 | 0.00056473 | 0.00056481 | 0.98962 | -0.20191 | 0.98963 | -0.20177 | 0.15517
58 | -0.0005811 | -0.00014564 | 0.0005811 | 0.0001456 | 9.3211e-10 | -4.1115e-08 | 0.00087439 | 0.00087437 | 0.00087439 | 0.98891 | -0.2153 | 0.98891 | -0.21526 | 0.24022
59 | -0.0022649 | -0.0005676 | 0.0022651 | 0.00056724 | 1.5971e-07 | -3.6829e-07 | 0.003408 | 0.0034079 | 0.003408 | 0.98891 | -0.21526 | 0.98899 | -0.21378 | 0.93627
60 | -0.0027361 | -0.00068481 | 0.0027376 | 0.00068283 | 1.4382e-06 | -1.9863e-06 | 0.0041164 | 0.0041154 | 0.0041164 | 0.98899 | -0.21378 | 0.98956 | -0.20272 | 1.1309
61 | 0.00047104 | 0.00011758 | -0.00047103 | -0.00011805 | 7.048e-09 | -4.7574e-07 | 0.00070855 | 0.00070872 | 0.00070872 | 0.98899 | -0.21378 | 0.98897 | -0.2141 | 0.1947
62 | 0.002672 | 0.00065389 | -0.0026706 | -0.00065596 | 1.3953e-06 | -2.0739e-06 | 0.0040124 | 0.0040134 | 0.0040134 | 0.98958 | -0.20231 | 0.98901 | -0.21345 | 1.1026
63 | -0.004021 | -0.0010024 | 0.0040219 | 0.0010022 | 9.1575e-07 | -2.318e-07 | 0.006119 | 0.0061187 | 0.006119 | 0.97753 | -0.43582 | 0.97777 | -0.43102 | 1.681
64 | 0.003729 | 0.00092924 | -0.0037267 | -0.00093016 | 2.3224e-06 | -9.2284e-07 | 0.0056745 | 0.0056753 | 0.0056753 | 0.97753 | -0.43582 | 0.97686 | -0.44895 | 1.5592
65 | -0.0042939 | -0.0010704 | 0.0042971 | 0.0010699 | 3.2057e-06 | -4.6329e-07 | 0.0065325 | 0.0065316 | 0.0065325 | 0.97777 | -0.43102 | 0.97857 | -0.41529 | 1.7947
66 | 0.0037267 | 0.00093016 | -0.0037264 | -0.00093028 | 3.0423e-07 | -1.2059e-07 | 0.0056753 | 0.0056754 | 0.0056754 | 0.97686 | -0.44895 | 0.97678 | -0.45067 | 1.5592
67 | -0.0046029 | -0.0011465 | 0.0046041 | 0.0011465 | 1.1982e-06 | -5.3391e-08 | 0.0069967 | 0.0069964 | 0.0069967 | 0.97857 | -0.41529 | 0.97885 | -0.4098 | 1.9222
68 | 0.0036203 | 0.0009037 | -0.0036202 | -0.00090373 | 6.7244e-08 | -3.0789e-08 | 0.0055138 | 0.0055139 | 0.0055139 | 0.97678 | -0.45067 | 0.97676 | -0.45106 | 1.5148
69 | -0.0050331 | -0.001254 | 0.0050337 | 0.001254 | 5.692e-07 | 3.8092e-08 | 0.0076485 | 0.0076484 | 0.0076485 | 0.97885 | -0.4098 | 0.97897 | -0.40741 | 2.1012
70 | 0.0031051 | 0.00077495 | -0.0031046 | -0.00077535 | 4.7908e-07 | -4.082e-07 | 0.0047292 | 0.0047294 | 0.0047294 | 0.97676 | -0.45106 | 0.97659 | -0.45431 | 1.2993
71 | 0.00051515 | 0.00012878 | -0.00051515 | -0.00012893 | 2.6681e-09 | -1.4292e-07 | 0.00078468 | 0.00078473 | 0.00078473 | 0.97676 | -0.45106 | 0.97675 | -0.45117 | 0.21559
72 | -0.0010121 | -0.00025005 | 0.0010122 | 0.00024842 | 1.1664e-07 | -1.6251e-06 | 0.0015271 | 0.0015265 | 0.0015271 | 0.98535 | -0.28277 | 0.98547 | -0.28032 | 0.41954
73 | 0.0010121 | 0.00025005 | -0.0010118 | -0.00025359 | 2.549e-07 | -3.5453e-06 | 0.0015271 | 0.0015284 | 0.0015284 | 0.98535 | -0.28277 | 0.98508 | -0.28809 | 0.4199
74 | -0.0012328 | -0.00030371 | 0.0012331 | 0.00030079 | 3.1713e-07 | -2.9155e-06 | 0.0018596 | 0.0018585 | 0.0018596 | 0.98547 | -0.28032 | 0.98575 | -0.27483 | 0.51089
75 | 0.0031046 | 0.00077535 | -0.0031044 | -0.00077552 | 1.9989e-07 | -1.7022e-07 | 0.0047294 | 0.0047295 | 0.0047295 | 0.97659 | -0.45431 | 0.97652 | -0.45566 | 1.2993
76 | 0.00023347 | 5.8329e-05 | -0.00023347 | -5.8512e-05 | 6.9415e-10 | -1.8274e-07 | 0.0003556 | 0.00035567 | 0.00035567 | 0.97675 | -0.45117 | 0.97675 | -0.45123 | 0.097712
77 | 0.0022347 | 0.00055757 | -0.0022347 | -0.00055763 | 2.4637e-08 | -5.5149e-08 | 0.0034044 | 0.0034044 | 0.0034044 | 0.97652 | -0.45566 | 0.97651 | -0.4559 | 0.93528
78 | -0.0054878 | -0.0013678 | 0.0054906 | 0.0013683 | 2.8946e-06 | 4.5587e-07 | 0.0083386 | 0.0083381 | 0.0083386 | 0.97897 | -0.40741 | 0.97953 | -0.3963 | 2.2908
79 | 0.00184 | 0.00045731 | -0.0018391 | -0.00046091 | 9.5614e-07 | -3.6007e-06 | 0.0027762 | 0.0027777 | 0.0027777 | 0.98575 | -0.27483 | 0.98519 | -0.28577 | 0.7631
80 | -0.0030731 | -0.00075811 | 0.0030744 | 0.00075688 | 1.2996e-06 | -1.2262e-06 | 0.0046347 | 0.004634 | 0.0046347 | 0.98575 | -0.27483 | 0.98621 | -0.26584 | 1.2733
81 | 0.0019466 | 0.00048542 | -0.0019461 | -0.00048705 | 5.1797e-07 | -1.6325e-06 | 0.0029654 | 0.0029661 | 0.0029661 | 0.97651 | -0.4559 | 0.97623 | -0.4615 | 0.81486
82 | 0.00085477 | 0.0002141 | -0.00085476 | -0.00021422 | 6.5414e-09 | -1.2612e-07 | 0.0012983 | 0.0012983 | 0.0012983 | 0.97966 | -0.39366 | 0.97966 | -0.39382 | 0.35668
83 | -0.0018443 | -0.0004621 | 0.0018444 | 0.00046179 | 8.4126e-08 | -3.0615e-07 | 0.0028013 | 0.0028011 | 0.0028013 | 0.97966 | -0.39366 | 0.97971 | -0.39271 | 0.76958
84 | -0.0057073 | -0.0014288 | 0.0057076 | 0.0014289 | 2.1683e-07 | 4.1857e-08 | 0.0086679 | 0.0086679 | 0.0086679 | 0.97971 | -0.39271 | 0.97975 | -0.39191 | 2.3813
85 | 0.0038629 | 0.00096704 | -0.0038622 | -0.00096728 | 7.1108e-07 | -2.3848e-07 | 0.0058668 | 0.005867 | 0.005867 | 0.97971 | -0.39271 | 0.97952 | -0.39657 | 1.6118
86 | 0.0083589 | 0.0020875 | -0.0083571 | -0.0020867 | 1.7432e-06 | 7.5237e-07 | 0.012693 | 0.012693 | 0.012693 | 0.97975 | -0.39191 | 0.97953 | -0.3963 | 3.487
87 | -0.014066 | -0.0035163 | 0.014071 | 0.0035189 | 4.6067e-06 | 2.6091e-06 | 0.02136 | 0.02136 | 0.02136 | 0.97975 | -0.39191 | 0.9801 | -0.38502 | 5.8682
88 | 0.0031593 | 0.00079112 | -0.0031591 | -0.00079136 | 2.8994e-07 | -2.3692e-07 | 0.0047992 | 0.0047994 | 0.0047994 | 0.97952 | -0.39657 | 0.97942 | -0.3985 | 1.3185
89 | -0.014403 | -0.0036023 | 0.014459 | 0.0036341 | 5.5979e-05 | 3.1875e-05 | 0.021865 | 0.021864 | 0.021865 | 0.9801 | -0.38502 | 0.98426 | -0.30362 | 6.0069
90 | 0.0018106 | 0.00045341 | -0.0018106 | -0.00045341 | 3.6344e-11 | -1.47e-10 | 0.0027507 | 0.0027507 | 0.0027507 | 0.97942 | -0.3985 | 0.97942 | -0.3985 | 0.75569
91 | -0.01508 | -0.0037898 | 0.015088 | 0.0037943 | 7.8873e-06 | 4.5335e-06 | 0.022802 | 0.022802 | 0.022802 | 0.98426 | -0.30362 | 0.98483 | -0.29267 | 6.2644
92 | 0.0018106 | 0.00045341 | -0.0018106 | -0.00045369 | 7.5346e-08 | -2.8593e-07 | 0.0027507 | 0.0027508 | 0.0027508 | 0.97942 | -0.3985 | 0.97937 | -0.39937 | 0.75573
93 | -0.00027618 | -6.9217e-05 | 0.00027618 | 6.8795e-05 | 2.2486e-09 | -4.2176e-07 | 0.00042097 | 0.00042082 | 0.00042097 | 0.97622 | -0.46167 | 0.97623 | -0.4615 | 0.11565
94 | 0.0012098 | 0.00030295 | -0.0012098 | -0.00030321 | 2.7972e-08 | -2.5635e-07 | 0.001844 | 0.0018441 | 0.0018441 | 0.97623 | -0.4615 | 0.9762 | -0.46198 | 0.50662
95 | -0.017409 | -0.0043752 | 0.017416 | 0.0043792 | 6.7713e-06 | 4.0015e-06 | 0.026309 | 0.026308 | 0.026309 | 0.98483 | -0.29267 | 0.98524 | -0.28453 | 7.2276
96 | 0.0023209 | 0.00058087 | -0.0023207 | -0.00058113 | 1.1915e-07 | -2.5255e-07 | 0.0035064 | 0.0035065 | 0.0035065 | 0.98483 | -0.29267 | 0.98477 | -0.29375 | 0.96333
97 | -0.017669 | -0.0044426 | 0.017685 | 0.004452 | 1.5781e-05 | 9.3465e-06 | 0.026691 | 0.026691 | 0.026691 | 0.98524 | -0.28453 | 0.98621 | -0.26584 | 7.3327
98 | 0.0018861 | 0.00047219 | -0.0018859 | -0.00047266 | 1.3392e-07 | -4.7369e-07 | 0.0028497 | 0.0028499 | 0.0028499 | 0.98477 | -0.29375 | 0.98469 | -0.29524 | 0.78295
99 | -0.020759 | -0.0052089 | 0.020762 | 0.0052107 | 2.956e-06 | 1.7893e-06 | 0.031325 | 0.031325 | 0.031325 | 0.98621 | -0.26584 | 0.98636 | -0.26286 | 8.6056
100 | 0.00056067 | 0.00014045 | -0.00056067 | -0.00014052 | 1.577e-09 | -7.1917e-08 | 0.00085183 | 0.00085186 | 0.00085186 | 0.97937 | -0.39937 | 0.97937 | -0.39943 | 0.23403
101 | 0.0039607 | 0.00099232 | -0.0039606 | -0.00099237 | 1.5853e-07 | -5.2086e-08 | 0.0059514 | 0.0059515 | 0.0059515 | 0.99027 | -0.18699 | 0.99023 | -0.18783 | 1.635
102 | -0.0046696 | -0.00117 | 0.0046702 | 0.00117 | 5.2296e-07 | -2.9774e-08 | 0.0070166 | 0.0070165 | 0.0070166 | 0.99027 | -0.18699 | 0.99039 | -0.18464 | 1.9276
103 | 0.0034404 | 0.00086201 | -0.0034401 | -0.00086218 | 2.6535e-07 | -1.7072e-07 | 0.0051698 | 0.0051699 | 0.0051699 | 0.99023 | -0.18783 | 0.99014 | -0.18945 | 1.4203
104 | -0.027818 | -0.0070057 | 0.027883 | 0.0070461 | 6.5035e-05 | 4.0342e-05 | 0.041807 | 0.041806 | 0.041807 | 0.99039 | -0.18464 | 0.99292 | -0.13587 | 11.4854
105 | 0.021099 | 0.0053231 | -0.021027 | -0.0052795 | 7.2031e-05 | 4.3651e-05 | 0.031713 | 0.031714 | 0.031714 | 0.99039 | -0.18464 | 0.9867 | -0.2562 | 8.7127
106 | 0.0020482 | 0.00051268 | -0.0020481 | -0.00051279 | 3.7182e-08 | -1.1096e-07 | 0.003077 | 0.0030771 | 0.0030771 | 0.99039 | -0.18464 | 0.99037 | -0.18502 | 0.84535
107 | 0.0063676 | 0.0015784 | -0.0063661 | -0.0015781 | 1.4322e-06 | 3.7359e-07 | 0.0095364 | 0.0095366 | 0.0095366 | 0.99292 | -0.13587 | 0.99268 | -0.14063 | 2.62
108 | 0.021027 | 0.0052795 | -0.021021 | -0.0052754 | 6.6789e-06 | 4.0484e-06 | 0.031714 | 0.031714 | 0.031714 | 0.9867 | -0.2562 | 0.98636 | -0.26286 | 8.7127
109 | 0.0013122 | 0.00032836 | -0.0013122 | -0.00032886 | 6.0986e-08 | -4.9934e-07 | 0.0019714 | 0.0019716 | 0.0019716 | 0.99037 | -0.18502 | 0.99032 | -0.186 | 0.54166
110 | 0.0056182 | 0.0013906 | -0.0056174 | -0.0013905 | 8.6752e-07 | 1.33e-07 | 0.0084156 | 0.0084157 | 0.0084157 | 0.99268 | -0.14063 | 0.99251 | -0.1439 | 2.312
111 | -0.00023636 | -5.9237e-05 | 0.00023636 | 5.8247e-05 | 3.6608e-09 | -9.8921e-07 | 0.00035562 | 0.00035527 | 0.00035562 | 0.989 | -0.21378 | 0.98901 | -0.21345 | 0.097697
112 | 0.0024343 | 0.00059771 | -0.0024342 | -0.0005979 | 9.5907e-08 | -1.8386e-07 | 0.0036581 | 0.0036582 | 0.0036582 | 0.98901 | -0.21345 | 0.98897 | -0.21429 | 1.005
113 | 0.001137 | 0.00028486 | -0.001137 | -0.00028495 | 7.7991e-09 | -8.8213e-08 | 0.0017014 | 0.0017014 | 0.0017014 | 0.99439 | -0.10765 | 0.99438 | -0.1078 | 0.46741
114 | 0.00033904 | 8.497e-05 | -0.00033904 | -8.4972e-05 | 1.46e-11 | -1.9667e-09 | 0.00050735 | 0.00050735 | 0.00050735 | 0.99438 | -0.1078 | 0.99438 | -0.1078 | 0.13938
115 | 0.0020984 | 0.00051374 | -0.0020982 | -0.0005142 | 1.6293e-07 | -4.5642e-07 | 0.003153 | 0.0031532 | 0.0031532 | 0.98897 | -0.21429 | 0.98889 | -0.21595 | 0.86626
116 | 0.0021022 | 0.00051152 | -0.0021013 | -0.00051403 | 8.9205e-07 | -2.504e-06 | 0.0031535 | 0.0031545 | 0.0031545 | 0.99026 | -0.18924 | 0.9898 | -0.19833 | 0.86663
117 | 0.00175 | 0.00043411 | -0.0017499 | -0.00043428 | 4.0158e-08 | -1.7376e-07 | 0.002628 | 0.0026281 | 0.0026281 | 0.99026 | -0.18924 | 0.99023 | -0.18972 | 0.72201
118 | 0.0011802 | 0.00028624 | -0.0011801 | -0.00028797 | 1.6795e-07 | -1.727e-06 | 0.001771 | 0.0017716 | 0.0017716 | 0.9898 | -0.19833 | 0.98965 | -0.20138 | 0.4867
119 | 0.00092105 | 0.00022779 | -0.00092091 | -0.00023011 | 1.3486e-07 | -2.3265e-06 | 0.0013836 | 0.0013844 | 0.0013844 | 0.9898 | -0.19833 | 0.98964 | -0.20142 | 0.38034
120 | 0.0015329 | 0.00037989 | -0.0015329 | -0.00038012 | 3.9948e-08 | -2.3302e-07 | 0.002302 | 0.0023021 | 0.0023021 | 0.99023 | -0.18972 | 0.99021 | -0.19027 | 0.63244
121 | -0.00040306 | -0.0001009 | 0.00040309 | 9.7516e-05 | 3.6328e-08 | -3.3794e-06 | 0.00060572 | 0.00060454 | 0.00060572 | 0.99008 | -0.1928 | 0.99018 | -0.19088 | 0.16641
122 | 0.00030547 | 7.6438e-05 | -0.00030547 | -7.6559e-05 | 7.4138e-10 | -1.2016e-07 | 0.00045906 | 0.0004591 | 0.0004591 | 0.99008 | -0.1928 | 0.99007 | -0.19285 | 0.12613
123 | -0.00067755 | -0.0001663 | 0.00067756 | 0.00016613 | 5.3632e-09 | -1.7445e-07 | 0.001017 | 0.0010169 | 0.001017 | 0.99018 | -0.19088 | 0.99018 | -0.19071 | 0.27939
124 | -0.00083111 | -0.00020461 | 0.00083113 | 0.00020425 | 1.6754e-08 | -3.5849e-07 | 0.0012477 | 0.0012475 | 0.0012477 | 0.99018 | -0.19071 | 0.99021 | -0.19028 | 0.34277
125 | -0.0010168 | -0.00025079 | 0.0010168 | 0.00025079 | 3.7296e-10 | -5.2543e-09 | 0.0015266 | 0.0015266 | 0.0015266 | 0.99021 | -0.19028 | 0.99021 | -0.19027 | 0.41939
126 | 0.0009554 | 0.00023166 | -0.00095538 | -0.00023193 | 1.7194e-08 | -2.7555e-07 | 0.0014338 | 0.0014339 | 0.0014339 | 0.98965 | -0.20138 | 0.98963 | -0.20177 | 0.39393
127 | 0.00062606 | 0.00015622 | -0.00062605 | -0.00015657 | 9.203e-09 | -3.5009e-07 | 0.0009411 | 0.00094122 | 0.00094122 | 0.98964 | -0.20142 | 0.98963 | -0.20173 | 0.25858
128 | 0.00014886 | 3.6973e-05 | -0.00014886 | -3.7308e-05 | 4.9014e-10 | -3.3507e-07 | 0.00022371 | 0.00022383 | 0.00022383 | 0.98963 | -0.20173 | 0.98962 | -0.2018 | 0.061491
129 | 0.0016358 | 0.0003983 | -0.0016357 | -0.00039865 | 6.9739e-08 | -3.5043e-07 | 0.0024574 | 0.0024575 | 0.0024575 | 0.98889 | -0.21595 | 0.98884 | -0.21687 | 0.67514
130 | 0.00051749 | 0.00011867 | -0.00051749 | -0.0001191 | 7.6311e-09 | -4.2969e-07 | 0.00077497 | 0.00077511 | 0.00077511 | 0.98884 | -0.21687 | 0.98883 | -0.2172 | 0.21294
131 | 0.0011182 | 0.00027998 | -0.0011182 | -0.00028025 | 2.3177e-08 | -2.6518e-07 | 0.0016826 | 0.0016827 | 0.0016827 | 0.98884 | -0.21687 | 0.98882 | -0.2173 | 0.46229
132 | 0.00098883 | 0.0002472 | -0.00098879 | -0.00024781 | 4.0958e-08 | -6.1442e-07 | 0.0014832 | 0.0014835 | 0.0014835 | 0.99186 | -0.15652 | 0.99182 | -0.1574 | 0.40755
133 | 0.0013685 | 0.00034241 | -0.0013685 | -0.00034265 | 3.29e-08 | -2.4538e-07 | 0.0020572 | 0.0020573 | 0.0020573 | 0.9898 | -0.19689 | 0.98978 | -0.1974 | 0.56519
134 | -0.00037627 | -8.8928e-05 | 0.00037629 | 8.663e-05 | 2.1508e-08 | -2.2982e-06 | 0.00056444 | 0.00056368 | 0.00056444 | 0.98869 | -0.22009 | 0.98875 | -0.21882 | 0.15507
135 | -0.00037629 | -8.663e-05 | 0.00037632 | 8.3717e-05 | 2.7173e-08 | -2.9128e-06 | 0.00056368 | 0.00056273 | 0.00056368 | 0.98875 | -0.21882 | 0.98883 | -0.2172 | 0.15486
136 | 0.0010671 | 0.00026711 | -0.0010671 | -0.00026743 | 2.5572e-08 | -3.2419e-07 | 0.0016041 | 0.0016042 | 0.0016042 | 0.98978 | -0.1974 | 0.98975 | -0.1979 | 0.44073

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.055935 | 0.013718

## res_load
| p_mw | q_mvar
0 | 7.3438e-05 | 1.8405e-05
1 | 0.0018938 | 0.00047463
2 | 0.00025934 | 6.4998e-05
3 | 0.00026249 | 6.5786e-05
4 | 0.00037622 | 9.4289e-05
5 | 0.00011904 | 2.9834e-05
6 | 0.00071984 | 0.00018041
7 | 0.00022612 | 5.6671e-05
8 | 0.00052162 | 0.00013073
9 | 0.00014315 | 3.5876e-05
10 | 7.1679e-05 | 1.7964e-05
11 | 0.00036827 | 9.2298e-05
12 | 0.00043265 | 0.00010843
13 | 0.00035827 | 8.979e-05
14 | 0.00061351 | 0.00015376
15 | 0.0002962 | 7.4234e-05
16 | 0.00018768 | 4.7036e-05
17 | 0.0001852 | 4.6416e-05
18 | 0.00021198 | 5.3127e-05
19 | 0.00091303 | 0.00022883
20 | 0.00032974 | 8.2641e-05
21 | 0.0001293 | 3.2406e-05
22 | 0.00060719 | 0.00015217
23 | 9.0386e-05 | 2.2653e-05
24 | 0.00025472 | 6.3839e-05
25 | 0.00034072 | 8.5392e-05
26 | 0.0005811 | 0.00014564
27 | 0.0016838 | 0.00042201
28 | 0.00033191 | 8.3186e-05
29 | 0.00047103 | 0.00011805
30 | 0.00025702 | 6.4415e-05
31 | 0.00024244 | 6.0761e-05
32 | 0.00029201 | 7.3184e-05
33 | 0.00027196 | 6.8159e-05
34 | 0.00030587 | 7.6657e-05
35 | 0.00010608 | 2.6586e-05
36 | 0.00042895 | 0.00010751
37 | 0.0002206 | 5.5287e-05
38 | 0.0010118 | 0.00025359
39 | 0.00028168 | 7.0596e-05
40 | 0.00086964 | 0.00021795
41 | 0.00045409 | 0.00011381
42 | 0.00023347 | 5.8512e-05
43 | 0.00028812 | 7.221e-05
44 | 0.00098954 | 0.000248
45 | 0.00085476 | 0.00021422
46 | 0.00070289 | 0.00017616
47 | 0.0028665 | 0.00071841
48 | 0.00033242 | 8.3313e-05
49 | 0.0013484 | 0.00033795
50 | 0.00062098 | 0.00015563
51 | 0.00027618 | 6.9217e-05
52 | 0.00046007 | 0.0001153
53 | 0.0012098 | 0.00030321
54 | 0.00025322 | 6.3462e-05
55 | 0.00043466 | 0.00010894
56 | 0.0018859 | 0.00047266
57 | 0.0012499 | 0.00031325
58 | 0.00056067 | 0.00014052
59 | 0.0018391 | 0.00046091
60 | 0.0007089 | 0.00017767
61 | 0.00052018 | 0.00013037
62 | 0.0034401 | 0.00086218
63 | 0.00073588 | 0.00018443
64 | 0.00074788 | 0.00018744
65 | 0.00025836 | 6.4752e-05
66 | 0.0013122 | 0.00032886
67 | 0.00037109 | 9.3004e-05
68 | 0.00023636 | 5.9237e-05
69 | 0.00029734 | 7.452e-05
70 | 0.00079792 | 0.00019998
71 | 0.00033904 | 8.4972e-05
72 | 0.00033577 | 8.4152e-05
73 | 0.00021703 | 5.4392e-05
74 | 9.7584e-05 | 2.4457e-05
75 | 0.00027446 | 6.8786e-05
76 | 0.00030547 | 7.6559e-05
77 | 0.00015356 | 3.8485e-05
78 | 0.00018568 | 4.6537e-05
79 | 0.00051607 | 0.00012934
80 | 0.00022467 | 5.6307e-05
81 | 0.00029485 | 7.3897e-05
82 | 0.0005781 | 0.00014488
83 | 0.00047719 | 0.0001196
84 | 0.00046244 | 0.0001159
85 | 0.00028029 | 7.0247e-05
86 | 0.00098879 | 0.00024781
87 | 0.00037496 | 9.3973e-05
88 | 0.00098198 | 0.00024611
89 | 0.00014886 | 3.7308e-05
90 | 0.00012255 | 3.0715e-05
91 | 0.0011182 | 0.00028025
92 | 0.00014117 | 3.5381e-05
93 | 0.00030143 | 7.5545e-05
94 | 0.0010671 | 0.00026743

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1