## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1321-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1321-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1321-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1321-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1321-4_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1321-4_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1321-4_0_4_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1321-4_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1321-4_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1321-4_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1321-4_0_4_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_1321-4_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1321-4_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1321-4_0_4_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_1321-4_0_4_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_1321-4_0_4_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_1321-4_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1321-4_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1321-4_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1321-4_0_4_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1321-4_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1321-4_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1321-4_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1321-4_0_4_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1321-4_0_4_node_51 | 0.4 | n |  | TRUE
25 | bus_LV_1321-4_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1321-4_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1321-4_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1321-4_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1321-4_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1321-4_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1321-4_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1321-4_0_4_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_1321-4_0_4_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_1321-4_0_4_node_45 | 0.4 | n |  | TRUE
35 | bus_LV_1321-4_0_4_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_1321-4_0_4_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_1321-4_0_4_node_38 | 0.4 | n |  | TRUE
38 | bus_LV_1321-4_0_4_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_1321-4_0_4_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_1321-4_0_4_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_1321-4_0_4_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1321-4_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_1321-4_0_4_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_1321-4_0_4_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_1321-4_0_4_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_1321-4_0_4_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_1321-4_0_4_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_1321-4_0_4_node_49 | 0.4 | n |  | TRUE
49 | bus_LV_1321-4_0_4_node_50 | 0.4 | n |  | TRUE
50 | bus_MV_15_0_node_160 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1321-4_0_4_load_0 | 0 | 0.0065593 | 0.0016439 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1321-4_0_4_load_3 | 3 | 0.0022945 | 0.00057506 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1321-4_0_4_load_5 | 4 | 0.0079172 | 0.0019842 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1321-4_0_4_load_11 | 6 | 0.003006 | 0.00075338 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1321-4_0_4_load_7 | 7 | 0.0020242 | 0.00050731 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1321-4_0_4_load_6 | 9 | 0.010391 | 0.0026042 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1321-4_0_4_load_32 | 10 | 0.073185 | 0.018342 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1321-4_0_4_load_19 | 13 | 0.0062924 | 0.001577 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1321-4_0_4_load_20 | 14 | 0.0042301 | 0.0010602 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1321-4_0_4_load_14 | 18 | 0.010329 | 0.0025888 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1321-4_0_4_load_13 | 20 | 0.0018173 | 0.00045546 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1321-4_0_4_load_17 | 22 | 0.00239 | 0.00059898 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1321-4_0_4_load_51 | 24 | 0.0025884 | 0.00064873 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1321-4_0_4_load_22 | 25 | 0.0042956 | 0.0010766 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1321-4_0_4_load_23 | 26 | 0.0072934 | 0.0018279 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1321-4_0_4_load_24 | 27 | 0.014772 | 0.0037023 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1321-4_0_4_load_27 | 30 | 0.014696 | 0.0036832 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1321-4_0_4_load_30 | 32 | 0.0058404 | 0.0014637 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1321-4_0_4_load_45 | 34 | 0.0039536 | 0.00099086 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1321-4_0_4_load_46 | 35 | 0.018646 | 0.0046732 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1321-4_0_4_load_34 | 38 | 0.019458 | 0.0048767 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1321-4_0_4_load_47 | 39 | 0.021835 | 0.0054723 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1321-4_0_4_load_35 | 40 | 0.01101 | 0.0027594 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1321-4_0_4_load_37 | 41 | 0.010214 | 0.0025599 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1321-4_0_4_load_39 | 42 | 0.012943 | 0.0032438 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1321-4_0_4_load_40 | 44 | 0.020346 | 0.0050992 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1321-4_0_4_load_48 | 47 | 0.038014 | 0.0095273 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1321-4_0_4_load_50 | 49 | 0.030858 | 0.0077339 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1321-4_0_4_line_0 |  | 0 | 1 | 0.037078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1321-4_0_4_line_1 |  | 0 | 2 | 0.034804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1321-4_0_4_line_2 |  | 1 | 3 | 0.011849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1321-4_0_4_line_3 |  | 2 | 4 | 0.0027097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1321-4_0_4_line_4 |  | 4 | 8 | 0.017068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1321-4_0_4_line_5 |  | 5 | 6 | 0.031889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1321-4_0_4_line_6 |  | 5 | 7 | 0.037259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1321-4_0_4_line_7 |  | 6 | 11 | 0.035132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1321-4_0_4_line_8 |  | 7 | 12 | 0.0049296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1321-4_0_4_line_9 |  | 8 | 13 | 0.035516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1321-4_0_4_line_10 |  | 8 | 14 | 0.019844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1321-4_0_4_line_11 |  | 8 | 12 | 0.025432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1321-4_0_4_line_12 |  | 9 | 10 | 0.0064063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1321-4_0_4_line_13 |  | 10 | 15 | 0.025599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1321-4_0_4_line_14 |  | 11 | 20 | 0.042317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1321-4_0_4_line_15 |  | 13 | 19 | 0.010121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1321-4_0_4_line_16 |  | 14 | 17 | 0.0071007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1321-4_0_4_line_17 |  | 15 | 36 | 0.014755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1321-4_0_4_line_18 |  | 16 | 17 | 0.044523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1321-4_0_4_line_19 |  | 16 | 18 | 0.017237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1321-4_0_4_line_20 |  | 19 | 25 | 0.016921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1321-4_0_4_line_21 |  | 19 | 26 | 0.035967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1321-4_0_4_line_22 |  | 20 | 21 | 0.0083945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1321-4_0_4_line_23 |  | 21 | 22 | 0.046811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1321-4_0_4_line_24 |  | 21 | 23 | 0.045306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1321-4_0_4_line_25 |  | 23 | 24 | 0.018031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1321-4_0_4_line_26 |  | 25 | 27 | 0.016483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1321-4_0_4_line_27 |  | 26 | 28 | 0.04127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1321-4_0_4_line_28 |  | 28 | 29 | 0.035123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1321-4_0_4_line_29 |  | 29 | 30 | 0.032122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1321-4_0_4_line_30 |  | 30 | 31 | 0.040829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1321-4_0_4_line_31 |  | 31 | 32 | 0.035608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1321-4_0_4_line_32 |  | 31 | 33 | 0.035593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1321-4_0_4_line_33 |  | 33 | 34 | 0.019737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1321-4_0_4_line_34 |  | 34 | 35 | 0.033585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_1321-4_0_4_line_35 |  | 35 | 37 | 0.035569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1321-4_0_4_line_36 |  | 36 | 37 | 0.046385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1321-4_0_4_line_37 |  | 36 | 38 | 0.01173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1321-4_0_4_line_38 |  | 37 | 39 | 0.041542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1321-4_0_4_line_39 |  | 38 | 40 | 0.038979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1321-4_0_4_line_40 |  | 39 | 43 | 0.022909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1321-4_0_4_line_41 |  | 40 | 41 | 0.0092404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1321-4_0_4_line_42 |  | 41 | 42 | 0.027926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1321-4_0_4_line_43 |  | 43 | 45 | 0.067497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1321-4_0_4_line_44 |  | 44 | 45 | 0.026364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1321-4_0_4_line_45 |  | 45 | 46 | 0.029513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1321-4_0_4_line_46 |  | 46 | 47 | 0.009668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1321-4_0_4_line_47 |  | 47 | 48 | 0.032289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1321-4_0_4_line_48 |  | 48 | 49 | 0.007231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1321-4_0_4_trafo_33 | 0.63 MVA 20/0.4 kV | 50 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2696439.6097 | 1225767.9777 | 2696424.8107 | 1225795.5354 | 2696420.1288 | 1225798.9561
1 | 2696392.0259 | 1225819.4882 | 2696420.1288 | 1225798.9561
2 | 2696439.6097 | 1225767.9777 | 2696441.5691 | 1225769.177 | 2696450.9408 | 1225767.3316
3 | 2696392.0259 | 1225819.4882 | 2696389.3465 | 1225819.0844
4 | 2696373.5882 | 1225812.8849 | 2696379.7132 | 1225816.2198 | 2696383.4262 | 1225817.7477 | 2696387.1476 | 1225818.7531 | 2696389.3465 | 1225819.0844
5 | 2696407.0887 | 1225754.1299 | 2696388.5249 | 1225757.1647 | 2696375.7738 | 1225760.072
6 | 2696407.0887 | 1225754.1299 | 2696388.6061 | 1225786.4812
7 | 2696345.0097 | 1225775.64 | 2696361.7274 | 1225763.4686 | 2696365.821 | 1225762.5676 | 2696373.8906 | 1225760.5301 | 2696375.0022 | 1225760.2479 | 2696375.7738 | 1225760.072
8 | 2696386.1608 | 1225790.7615 | 2696388.6061 | 1225786.4812
9 | 2696373.5882 | 1225812.8849 | 2696370.7867 | 1225817.7986 | 2696362.5932 | 1225832.1651 | 2696355.9908 | 1225843.7344
10 | 2696373.5882 | 1225812.8849 | 2696365.285 | 1225808.2805 | 2696360.3799 | 1225817.3939
11 | 2696386.1608 | 1225790.7615 | 2696373.5882 | 1225812.8849
12 | 2696434.5595 | 1225837.6881 | 2696437.9267 | 1225843.1381
13 | 2696451.3814 | 1225864.9156 | 2696437.9267 | 1225843.1381
14 | 2696345.0097 | 1225775.64 | 2696326.8291 | 1225783.1066 | 2696311.5896 | 1225789.6758 | 2696306.535 | 1225793.032
15 | 2696350.9743 | 1225852.5248 | 2696355.9908 | 1225843.7344
16 | 2696357.0147 | 1225823.6464 | 2696360.3799 | 1225817.3939
17 | 2696451.3814 | 1225864.9156 | 2696457.2759 | 1225868.9029 | 2696464.836 | 1225870.2264
18 | 2696345.5217 | 1225832.0219 | 2696333.544 | 1225822.5768 | 2696340.19 | 1225814.8122 | 2696354.8418 | 1225822.9886 | 2696357.0147 | 1225823.6464
19 | 2696345.5217 | 1225832.0219 | 2696338.6966 | 1225842.8859 | 2696335.2447 | 1225845.6256
20 | 2696350.9743 | 1225852.5248 | 2696360.2657 | 1225866.6662
21 | 2696350.9743 | 1225852.5248 | 2696333.1503 | 1225883.7645
22 | 2696299.5417 | 1225797.6754 | 2696306.535 | 1225793.032
23 | 2696299.5417 | 1225797.6754 | 2696269.7561 | 1225787.6642 | 2696256.7784 | 1225779.3958
24 | 2696299.5417 | 1225797.6754 | 2696291.1308 | 1225810.9599 | 2696285.7861 | 1225827.7966 | 2696286.4652 | 1225839.705
25 | 2696286.4652 | 1225839.705 | 2696277.17 | 1225824.2547
26 | 2696369.3167 | 1225880.4418 | 2696360.2657 | 1225866.6662
27 | 2696310.5081 | 1225918.2613 | 2696331.7708 | 1225886.1825 | 2696333.1503 | 1225883.7645
28 | 2696310.5081 | 1225918.2613 | 2696310.0792 | 1225928.3616 | 2696313.6511 | 1225938.1264 | 2696328.2625 | 1225938.4853
29 | 2696328.2625 | 1225938.4853 | 2696333.9156 | 1225930.6935 | 2696355.1347 | 1225923.2232
30 | 2696392.3665 | 1225921.033 | 2696381.2593 | 1225914.0259 | 2696355.1347 | 1225923.2232
31 | 2696392.3665 | 1225921.033 | 2696415.1395 | 1225912.2623 | 2696425.5085 | 1225908.018
32 | 2696392.3665 | 1225921.033 | 2696368.7162 | 1225930.1343 | 2696371.6579 | 1225939.9556
33 | 2696371.6579 | 1225939.9556 | 2696381.992 | 1225932.4398 | 2696388.4805 | 1225929.9252
34 | 2696388.4805 | 1225929.9252 | 2696419.796 | 1225917.7893
35 | 2696452.9613 | 1225904.9365 | 2696419.796 | 1225917.7893
36 | 2696452.9613 | 1225904.9365 | 2696444.7498 | 1225885.345 | 2696456.8967 | 1225876.391 | 2696464.836 | 1225870.2264
37 | 2696464.836 | 1225870.2264 | 2696470.8982 | 1225868.0786 | 2696475.2444 | 1225865.0476
38 | 2696452.9613 | 1225904.9365 | 2696491.6833 | 1225889.8909
39 | 2696475.2444 | 1225865.0476 | 2696476.7722 | 1225863.982 | 2696488.9785 | 1225851.3709 | 2696501.0095 | 1225835.9417
40 | 2696513.0373 | 1225881.5937 | 2696491.6833 | 1225889.8909
41 | 2696501.0095 | 1225835.9417 | 2696501.6843 | 1225835.0764 | 2696505.9951 | 1225828.1679
42 | 2696505.9951 | 1225828.1679 | 2696512.9557 | 1225817.0129 | 2696518.2991 | 1225803.2351
43 | 2696492.2937 | 1225926.0114 | 2696523.5758 | 1225913.821 | 2696520.2138 | 1225901.8802 | 2696513.0373 | 1225881.5937
44 | 2696492.2937 | 1225926.0114 | 2696467.5654 | 1225935.1524
45 | 2696475.5023 | 1225941.3279 | 2696489.9459 | 1225936.1361 | 2696495.2756 | 1225933.8098 | 2696492.2937 | 1225926.0114
46 | 2696475.5023 | 1225941.3279 | 2696478.8807 | 1225950.3892
47 | 2696478.8807 | 1225950.3892 | 2696460.6096 | 1225977.0121
48 | 2696463.5273 | 1225983.6307 | 2696460.6096 | 1225977.0121

## bus_geodata
| x | y | coords
0 | 2696420.1288 | 1225798.9561
1 | 2696439.6097 | 1225767.9777
2 | 2696392.0259 | 1225819.4882
3 | 2696450.9408 | 1225767.3316
4 | 2696389.3465 | 1225819.0844
5 | 2696407.0887 | 1225754.1299
6 | 2696375.7738 | 1225760.072
7 | 2696388.6061 | 1225786.4812
8 | 2696373.5882 | 1225812.8849
9 | 2696434.5595 | 1225837.6881
10 | 2696437.9267 | 1225843.1381
11 | 2696345.0097 | 1225775.64
12 | 2696386.1608 | 1225790.7615
13 | 2696355.9908 | 1225843.7344
14 | 2696360.3799 | 1225817.3939
15 | 2696451.3814 | 1225864.9156
16 | 2696345.5217 | 1225832.0219
17 | 2696357.0147 | 1225823.6464
18 | 2696335.2447 | 1225845.6256
19 | 2696350.9743 | 1225852.5248
20 | 2696306.535 | 1225793.032
21 | 2696299.5417 | 1225797.6754
22 | 2696256.7784 | 1225779.3958
23 | 2696286.4652 | 1225839.705
24 | 2696277.17 | 1225824.2547
25 | 2696360.2657 | 1225866.6662
26 | 2696333.1503 | 1225883.7645
27 | 2696369.3167 | 1225880.4418
28 | 2696310.5081 | 1225918.2613
29 | 2696328.2625 | 1225938.4853
30 | 2696355.1347 | 1225923.2232
31 | 2696392.3665 | 1225921.033
32 | 2696425.5085 | 1225908.018
33 | 2696371.6579 | 1225939.9556
34 | 2696388.4805 | 1225929.9252
35 | 2696419.796 | 1225917.7893
36 | 2696464.836 | 1225870.2264
37 | 2696452.9613 | 1225904.9365
38 | 2696475.2444 | 1225865.0476
39 | 2696491.6833 | 1225889.8909
40 | 2696501.0095 | 1225835.9417
41 | 2696505.9951 | 1225828.1679
42 | 2696518.2991 | 1225803.2351
43 | 2696513.0373 | 1225881.5937
44 | 2696467.5654 | 1225935.1524
45 | 2696492.2937 | 1225926.0114
46 | 2696475.5023 | 1225941.3279
47 | 2696478.8807 | 1225950.3892
48 | 2696460.6096 | 1225977.0121
49 | 2696463.5273 | 1225983.6307
50 | 2696456.8967 | 1225876.391

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97169 | -0.54567 | 0.0065593 | 0.0016439
1 | 0.97161 | -0.54724 | 0 | 0
2 | 0.97198 | -0.53998 | 0 | 0
3 | 0.97159 | -0.54774 | 0.0022945 | 0.00057506
4 | 0.972 | -0.53953 | 0.0079172 | 0.0019842
5 | 0.97159 | -0.54763 | 0 | 0
6 | 0.9713 | -0.5534 | 0.003006 | 0.00075338
7 | 0.97194 | -0.54088 | 0.0020242 | 0.00050731
8 | 0.97227 | -0.53425 | 0 | 0
9 | 0.998 | -0.038526 | 0.010391 | 0.0026042
10 | 0.99806 | -0.037362 | 0.073185 | 0.018342
11 | 0.97108 | -0.55782 | 0 | 0
12 | 0.97199 | -0.53981 | 0 | 0
13 | 0.9737 | -0.50603 | 0.0062924 | 0.001577
14 | 0.972 | -0.53958 | 0.0042301 | 0.0010602
15 | 1 | 0 | -0.37323 | -0.094814
16 | 0.9715 | -0.54943 | 0 | 0
17 | 0.97193 | -0.54094 | 0 | 0
18 | 0.97134 | -0.55272 | 0.010329 | 0.0025888
19 | 0.97417 | -0.49683 | 0 | 0
20 | 0.97081 | -0.56314 | 0.0018173 | 0.00045546
21 | 0.97077 | -0.56391 | 0 | 0
22 | 0.97067 | -0.56598 | 0.00239 | 0.00059898
23 | 0.97066 | -0.56608 | 0 | 0
24 | 0.97062 | -0.56695 | 0.0025884 | 0.00064873
25 | 0.97387 | -0.50275 | 0.0042956 | 0.0010766
26 | 0.97647 | -0.45166 | 0.0072934 | 0.0018279
27 | 0.97364 | -0.50723 | 0.014772 | 0.0037023
28 | 0.97938 | -0.39463 | 0 | 0
29 | 0.98187 | -0.34635 | 0 | 0
30 | 0.98414 | -0.30241 | 0.014696 | 0.0036832
31 | 0.98758 | -0.23613 | 0 | 0
32 | 0.98739 | -0.23985 | 0.0058404 | 0.0014637
33 | 0.99077 | -0.17503 | 0 | 0
34 | 0.99254 | -0.14131 | 0.0039536 | 0.00099086
35 | 0.99411 | -0.11155 | 0.018646 | 0.0046732
36 | 0.99871 | -0.024349 | 0 | 0
37 | 0.99542 | -0.086708 | 0 | 0
38 | 0.99814 | -0.035348 | 0.019458 | 0.0048767
39 | 0.99116 | -0.16821 | 0.021835 | 0.0054723
40 | 0.99693 | -0.058677 | 0.01101 | 0.0027594
41 | 0.99673 | -0.06243 | 0.010214 | 0.0025599
42 | 0.99641 | -0.068774 | 0.012943 | 0.0032438
43 | 0.98927 | -0.20455 | 0 | 0
44 | 0.98321 | -0.32208 | 0.020346 | 0.0050992
45 | 0.9837 | -0.31241 | 0 | 0
46 | 0.98183 | -0.34909 | 0 | 0
47 | 0.98121 | -0.36114 | 0.038014 | 0.0095273
48 | 0.98029 | -0.37919 | 0 | 0
49 | 0.98008 | -0.38324 | 0.030858 | 0.0077339
50 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0022947 | 0.00057459 | -0.0022946 | -0.00057494 | 1.7169e-07 | -3.4937e-07 | 0.0035139 | 0.003514 | 0.003514 | 0.97169 | -0.54567 | 0.97161 | -0.54724 | 0.96539
1 | -0.008854 | -0.0022185 | 0.0088564 | 0.0022196 | 2.3993e-06 | 1.1043e-06 | 0.013559 | 0.013558 | 0.013559 | 0.97169 | -0.54567 | 0.97198 | -0.53998 | 3.7249
2 | 0.0022946 | 0.00057494 | -0.0022945 | -0.00057506 | 5.487e-08 | -1.1163e-07 | 0.003514 | 0.0035141 | 0.0035141 | 0.97161 | -0.54724 | 0.97159 | -0.54774 | 0.96541
3 | -0.0088564 | -0.0022196 | 0.0088566 | 0.0022197 | 1.8679e-07 | 8.5963e-08 | 0.013558 | 0.013558 | 0.013558 | 0.97198 | -0.53998 | 0.972 | -0.53953 | 3.7248
4 | -0.016774 | -0.004204 | 0.016778 | 0.0042064 | 4.2204e-06 | 2.4894e-06 | 0.025679 | 0.025679 | 0.025679 | 0.972 | -0.53953 | 0.97227 | -0.53425 | 7.0546
5 | 0.0098084 | 0.002458 | -0.0098057 | -0.0024566 | 2.6984e-06 | 1.3322e-06 | 0.015022 | 0.015022 | 0.015022 | 0.97159 | -0.54763 | 0.9713 | -0.5534 | 4.1269
6 | -0.0098084 | -0.002458 | 0.0098115 | 0.0024595 | 3.1527e-06 | 1.5562e-06 | 0.015022 | 0.015021 | 0.015022 | 0.97159 | -0.54763 | 0.97194 | -0.54088 | 4.1268
7 | 0.0067997 | 0.0017033 | -0.0067982 | -0.0017028 | 1.4295e-06 | 4.8016e-07 | 0.010417 | 0.010417 | 0.010417 | 0.9713 | -0.5534 | 0.97108 | -0.55782 | 2.8618
8 | -0.011836 | -0.0029668 | 0.011836 | 0.0029672 | 6.0699e-07 | 3.2738e-07 | 0.01812 | 0.01812 | 0.01812 | 0.97194 | -0.54088 | 0.97199 | -0.53981 | 4.9782
9 | -0.043187 | -0.01083 | 0.043245 | 0.010866 | 5.8188e-05 | 3.6799e-05 | 0.066098 | 0.066098 | 0.066098 | 0.97227 | -0.53425 | 0.9737 | -0.50603 | 18.1589
10 | 0.01457 | 0.0036544 | -0.014566 | -0.0036523 | 3.7004e-06 | 2.1222e-06 | 0.022299 | 0.022299 | 0.022299 | 0.97227 | -0.53425 | 0.972 | -0.53958 | 6.1262
11 | 0.011839 | 0.0029689 | -0.011836 | -0.0029672 | 3.1315e-06 | 1.6888e-06 | 0.01812 | 0.01812 | 0.01812 | 0.97227 | -0.53425 | 0.97199 | -0.53981 | 4.9781
12 | -0.010391 | -0.0026042 | 0.010392 | 0.0026045 | 5.7664e-07 | 2.8534e-07 | 0.015493 | 0.015493 | 0.015493 | 0.998 | -0.038526 | 0.99806 | -0.037362 | 4.2563
13 | -0.083576 | -0.020946 | 0.083725 | 0.021041 | 0.00014904 | 9.5053e-05 | 0.1246 | 0.1246 | 0.1246 | 0.99806 | -0.037362 | 1 | 0 | 34.2321
14 | 0.0067982 | 0.0017028 | -0.0067965 | -0.0017022 | 1.7219e-06 | 5.7866e-07 | 0.010417 | 0.010417 | 0.010417 | 0.97108 | -0.55782 | 0.97081 | -0.56314 | 2.8618
15 | -0.049538 | -0.012444 | 0.04956 | 0.012457 | 2.1758e-05 | 1.3799e-05 | 0.075714 | 0.075714 | 0.075714 | 0.9737 | -0.50603 | 0.97417 | -0.49683 | 20.8006
16 | 0.010336 | 0.0025921 | -0.010335 | -0.0025918 | 6.6673e-07 | 3.387e-07 | 0.015824 | 0.015824 | 0.015824 | 0.972 | -0.53958 | 0.97193 | -0.54094 | 4.3472
17 | 0.28786 | 0.073772 | -0.28752 | -0.073556 | 0.0003393 | 0.00021658 | 0.42891 | 0.42891 | 0.42891 | 1 | 0 | 0.99871 | -0.024349 | 39.2779
18 | -0.010331 | -0.0025896 | 0.010335 | 0.0025918 | 4.1806e-06 | 2.1241e-06 | 0.015824 | 0.015824 | 0.015824 | 0.9715 | -0.54943 | 0.97193 | -0.54094 | 4.3472
19 | 0.010331 | 0.0025896 | -0.010329 | -0.0025888 | 1.6185e-06 | 8.2247e-07 | 0.015824 | 0.015824 | 0.015824 | 0.9715 | -0.54943 | 0.97134 | -0.55272 | 4.3473
20 | 0.019076 | 0.0047839 | -0.019071 | -0.0047807 | 5.388e-06 | 3.2377e-06 | 0.02914 | 0.02914 | 0.02914 | 0.97417 | -0.49683 | 0.97387 | -0.50275 | 8.0055
21 | -0.068636 | -0.017241 | 0.068784 | 0.017336 | 0.00014829 | 9.4455e-05 | 0.10485 | 0.10485 | 0.10485 | 0.97417 | -0.49683 | 0.97647 | -0.45166 | 28.8061
22 | 0.0049792 | 0.0012467 | -0.004979 | -0.0012467 | 1.8333e-07 | 1.3544e-08 | 0.0076315 | 0.0076315 | 0.0076315 | 0.97081 | -0.56314 | 0.97077 | -0.56391 | 2.0966
23 | 0.0023902 | 0.00059855 | -0.00239 | -0.00059898 | 2.3562e-07 | -4.2789e-07 | 0.0036635 | 0.0036638 | 0.0036638 | 0.97077 | -0.56391 | 0.97067 | -0.56598 | 1.0065
24 | 0.0025888 | 0.00064818 | -0.0025886 | -0.00064857 | 2.6751e-07 | -3.8887e-07 | 0.003968 | 0.0039682 | 0.0039682 | 0.97077 | -0.56391 | 0.97066 | -0.56608 | 1.0902
25 | 0.0025886 | 0.00064857 | -0.0025884 | -0.00064873 | 1.0647e-07 | -1.5472e-07 | 0.0039682 | 0.0039682 | 0.0039682 | 0.97066 | -0.56608 | 0.97062 | -0.56695 | 1.0902
26 | 0.014775 | 0.0037041 | -0.014772 | -0.0037023 | 3.1505e-06 | 1.8113e-06 | 0.022576 | 0.022577 | 0.022577 | 0.97387 | -0.50275 | 0.97364 | -0.50723 | 6.2024
27 | -0.076078 | -0.019164 | 0.076286 | 0.019296 | 0.00020813 | 0.00013269 | 0.11597 | 0.11597 | 0.11597 | 0.97647 | -0.45166 | 0.97938 | -0.39463 | 31.8594
28 | -0.076286 | -0.019296 | 0.076463 | 0.019409 | 0.00017713 | 0.00011292 | 0.11597 | 0.11597 | 0.11597 | 0.97938 | -0.39463 | 0.98187 | -0.34635 | 31.8593
29 | -0.076463 | -0.019409 | 0.076625 | 0.019512 | 0.000162 | 0.00010327 | 0.11597 | 0.11597 | 0.11597 | 0.98187 | -0.34635 | 0.98414 | -0.30241 | 31.8593
30 | -0.091321 | -0.023196 | 0.091614 | 0.023382 | 0.00029238 | 0.0001866 | 0.13819 | 0.13819 | 0.13819 | 0.98414 | -0.30241 | 0.98758 | -0.23613 | 37.9638
31 | 0.0058414 | 0.0014639 | -0.0058404 | -0.0014637 | 1.0344e-06 | 2.0649e-07 | 0.0088014 | 0.0088016 | 0.0088016 | 0.98758 | -0.23613 | 0.98739 | -0.23985 | 2.418
32 | -0.097455 | -0.024846 | 0.097743 | 0.02503 | 0.00028838 | 0.00018411 | 0.14699 | 0.14699 | 0.14699 | 0.98758 | -0.23613 | 0.99077 | -0.17503 | 40.3817
33 | -0.097743 | -0.02503 | 0.097903 | 0.025132 | 0.00015991 | 0.00010209 | 0.14699 | 0.14699 | 0.14699 | 0.99077 | -0.17503 | 0.99254 | -0.14131 | 40.3816
34 | -0.10186 | -0.026123 | 0.102 | 0.026217 | 0.00014725 | 9.3369e-05 | 0.15292 | 0.15292 | 0.15292 | 0.99254 | -0.14131 | 0.99411 | -0.11155 | 21.005
35 | -0.12065 | -0.03089 | 0.1208 | 0.030982 | 0.00014538 | 9.1656e-05 | 0.18083 | 0.18083 | 0.18083 | 0.99411 | -0.11155 | 0.99542 | -0.086708 | 16.5591
36 | 0.23382 | 0.060069 | -0.23311 | -0.05962 | 0.0007058 | 0.0004499 | 0.3489 | 0.3489 | 0.3489 | 0.99871 | -0.024349 | 0.99542 | -0.086708 | 31.9503
37 | 0.0537 | 0.013486 | -0.053672 | -0.013468 | 2.8166e-05 | 1.7873e-05 | 0.080019 | 0.080019 | 0.080019 | 0.99871 | -0.024349 | 0.99814 | -0.035348 | 21.9832
38 | 0.11232 | 0.028638 | -0.11188 | -0.028357 | 0.00044006 | 0.0002811 | 0.16807 | 0.16807 | 0.16807 | 0.99542 | -0.086708 | 0.99116 | -0.16821 | 46.1736
39 | 0.034213 | 0.0085917 | -0.034175 | -0.0085678 | 3.8036e-05 | 2.3834e-05 | 0.051011 | 0.051011 | 0.051011 | 0.99814 | -0.035348 | 0.99693 | -0.058677 | 14.0141
40 | 0.090042 | 0.022885 | -0.089885 | -0.022784 | 0.00015725 | 0.00010034 | 0.13529 | 0.13529 | 0.13529 | 0.99116 | -0.16821 | 0.98927 | -0.20455 | 37.1681
41 | 0.023165 | 0.0058084 | -0.023161 | -0.0058058 | 4.1429e-06 | 2.531e-06 | 0.034577 | 0.034577 | 0.034577 | 0.99693 | -0.058677 | 0.99673 | -0.06243 | 9.4992
42 | 0.012947 | 0.0032459 | -0.012943 | -0.0032438 | 3.9124e-06 | 2.1401e-06 | 0.019329 | 0.019329 | 0.019329 | 0.99673 | -0.06243 | 0.99641 | -0.068774 | 5.3101
43 | 0.089885 | 0.022784 | -0.089421 | -0.022489 | 0.0004633 | 0.00029565 | 0.13529 | 0.13529 | 0.13529 | 0.98927 | -0.20455 | 0.9837 | -0.31241 | 37.1682
44 | -0.020346 | -0.0050992 | 0.020355 | 0.0051049 | 9.3739e-06 | 5.6648e-06 | 0.030792 | 0.030792 | 0.030792 | 0.98321 | -0.32208 | 0.9837 | -0.31241 | 8.4594
45 | 0.069066 | 0.017384 | -0.068945 | -0.017307 | 0.00012086 | 7.6975e-05 | 0.1045 | 0.1045 | 0.1045 | 0.9837 | -0.31241 | 0.98183 | -0.34909 | 28.7089
46 | 0.068945 | 0.017307 | -0.068905 | -0.017281 | 3.9592e-05 | 2.5216e-05 | 0.1045 | 0.1045 | 0.1045 | 0.98183 | -0.34909 | 0.98121 | -0.36114 | 28.7089
47 | 0.030891 | 0.0077542 | -0.030864 | -0.0077376 | 2.6578e-05 | 1.6603e-05 | 0.046851 | 0.046851 | 0.046851 | 0.98121 | -0.36114 | 0.98029 | -0.37919 | 12.8712
48 | 0.030864 | 0.0077376 | -0.030858 | -0.0077339 | 5.9521e-06 | 3.7182e-06 | 0.046851 | 0.046851 | 0.046851 | 0.98029 | -0.37919 | 0.98008 | -0.38324 | 12.8712

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37323 | 0.094814

## res_load
| p_mw | q_mvar
0 | 0.0065593 | 0.0016439
1 | 0.0022945 | 0.00057506
2 | 0.0079172 | 0.0019842
3 | 0.003006 | 0.00075338
4 | 0.0020242 | 0.00050731
5 | 0.010391 | 0.0026042
6 | 0.073185 | 0.018342
7 | 0.0062924 | 0.001577
8 | 0.0042301 | 0.0010602
9 | 0.010329 | 0.0025888
10 | 0.0018173 | 0.00045546
11 | 0.00239 | 0.00059898
12 | 0.0025884 | 0.00064873
13 | 0.0042956 | 0.0010766
14 | 0.0072934 | 0.0018279
15 | 0.014772 | 0.0037023
16 | 0.014696 | 0.0036832
17 | 0.0058404 | 0.0014637
18 | 0.0039536 | 0.00099086
19 | 0.018646 | 0.0046732
20 | 0.019458 | 0.0048767
21 | 0.021835 | 0.0054723
22 | 0.01101 | 0.0027594
23 | 0.010214 | 0.0025599
24 | 0.012943 | 0.0032438
25 | 0.020346 | 0.0050992
26 | 0.038014 | 0.0095273
27 | 0.030858 | 0.0077339

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1