## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1331-4_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1331-4_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1331-4_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1331-4_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1331-4_0_2_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1331-4_0_2_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_1331-4_0_2_node_45 | 0.4 | n |  | TRUE
7 | bus_LV_1331-4_0_2_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1331-4_0_2_node_54 | 0.4 | n |  | TRUE
9 | bus_LV_1331-4_0_2_node_51 | 0.4 | n |  | TRUE
10 | bus_LV_1331-4_0_2_node_63 | 0.4 | n |  | TRUE
11 | bus_LV_1331-4_0_2_node_41 | 0.4 | n |  | TRUE
12 | bus_LV_1331-4_0_2_node_42 | 0.4 | n |  | TRUE
13 | bus_LV_1331-4_0_2_node_44 | 0.4 | n |  | TRUE
14 | bus_LV_1331-4_0_2_node_62 | 0.4 | n |  | TRUE
15 | bus_LV_1331-4_0_2_node_52 | 0.4 | n |  | TRUE
16 | bus_LV_1331-4_0_2_node_53 | 0.4 | n |  | TRUE
17 | bus_LV_1331-4_0_2_node_58 | 0.4 | n |  | TRUE
18 | bus_LV_1331-4_0_2_node_64 | 0.4 | n |  | TRUE
19 | bus_LV_1331-4_0_2_node_55 | 0.4 | n |  | TRUE
20 | bus_LV_1331-4_0_2_node_56 | 0.4 | n |  | TRUE
21 | bus_LV_1331-4_0_2_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_1331-4_0_2_node_60 | 0.4 | n |  | TRUE
23 | bus_LV_1331-4_0_2_node_61 | 0.4 | n |  | TRUE
24 | bus_LV_1331-4_0_2_node_66 | 0.4 | n |  | TRUE
25 | bus_LV_1331-4_0_2_node_65 | 0.4 | n |  | TRUE
26 | bus_LV_1331-4_0_2_node_67 | 0.4 | n |  | TRUE
27 | bus_LV_1331-4_0_2_node_68 | 0.4 | n |  | TRUE
28 | bus_LV_1331-4_0_2_node_69 | 0.4 | n |  | TRUE
29 | bus_MV_4_0_node_115 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1331-4_0_2_load_0 | 0 | 0.012751 | 0.0031957 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1331-4_0_2_load_2 | 2 | 0.021296 | 0.0053373 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1331-4_0_2_load_3 | 3 | 0.010093 | 0.0025296 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1331-4_0_2_load_40 | 5 | 0.015485 | 0.0038809 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1331-4_0_2_load_45 | 6 | 0.018089 | 0.0045334 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1331-4_0_2_load_51 | 9 | 0.0041597 | 0.0010425 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1331-4_0_2_load_63 | 10 | 0.0051507 | 0.0012909 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1331-4_0_2_load_41 | 11 | 0.021595 | 0.0054123 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1331-4_0_2_load_62 | 14 | 0.0065847 | 0.0016503 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1331-4_0_2_load_53 | 16 | 0.016306 | 0.0040868 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1331-4_0_2_load_58 | 17 | 0.032506 | 0.0081468 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1331-4_0_2_load_64 | 18 | 0.0028826 | 0.00072245 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1331-4_0_2_load_55 | 19 | 0.0092158 | 0.0023097 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1331-4_0_2_load_56 | 20 | 0.0099577 | 0.0024956 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1331-4_0_2_load_59 | 21 | 0.021398 | 0.0053629 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1331-4_0_2_load_60 | 22 | 0.021393 | 0.0053615 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1331-4_0_2_load_61 | 23 | 0.021397 | 0.0053627 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1331-4_0_2_load_66 | 24 | 0.0067435 | 0.0016901 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1331-4_0_2_load_65 | 25 | 0.0018939 | 0.00047465 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1331-4_0_2_load_69 | 28 | 0.0078312 | 0.0019627 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1331-4_0_2_line_0 |  | 0 | 1 | 0.019855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_1331-4_0_2_line_1 |  | 1 | 2 | 0.04136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1331-4_0_2_line_2 |  | 1 | 3 | 0.016737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1331-4_0_2_line_3 |  | 1 | 4 | 0.045182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1331-4_0_2_line_4 |  | 2 | 5 | 0.032086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1331-4_0_2_line_5 |  | 3 | 6 | 0.015007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1331-4_0_2_line_6 |  | 4 | 10 | 0.024838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1331-4_0_2_line_7 |  | 5 | 11 | 0.021731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1331-4_0_2_line_8 |  | 7 | 8 | 0.034929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1331-4_0_2_line_9 |  | 7 | 9 | 0.010435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1331-4_0_2_line_10 |  | 8 | 18 | 0.013714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1331-4_0_2_line_11 |  | 8 | 10 | 0.010698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1331-4_0_2_line_12 |  | 9 | 15 | 0.052319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1331-4_0_2_line_13 |  | 11 | 12 | 0.083271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1331-4_0_2_line_14 |  | 12 | 13 | 0.061783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1331-4_0_2_line_15 |  | 13 | 14 | 0.075237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1331-4_0_2_line_16 |  | 14 | 19 | 0.058881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1331-4_0_2_line_17 |  | 15 | 16 | 0.043551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1331-4_0_2_line_18 |  | 16 | 17 | 0.017662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1331-4_0_2_line_19 |  | 17 | 21 | 0.0033165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1331-4_0_2_line_20 |  | 18 | 24 | 0.03033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1331-4_0_2_line_21 |  | 19 | 20 | 0.025942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1331-4_0_2_line_22 |  | 21 | 22 | 0.020874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1331-4_0_2_line_23 |  | 22 | 23 | 0.007535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1331-4_0_2_line_24 |  | 24 | 25 | 0.020865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1331-4_0_2_line_25 |  | 25 | 26 | 0.044292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1331-4_0_2_line_26 |  | 26 | 27 | 0.060956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1331-4_0_2_line_27 |  | 27 | 28 | 0.093345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1331-4_0_2_trafo_0 | 0.63 MVA 20/0.4 kV | 29 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2676037.2956 | 1214401.126 | 2676043.821 | 1214393.3153 | 2676043.185 | 1214383.6592
1 | 2676037.2956 | 1214401.126 | 2676056.7471 | 1214401.1629 | 2676065.1692 | 1214402.4489 | 2676075.8896 | 1214410.4691
2 | 2676037.2956 | 1214401.126 | 2676041.991 | 1214417.1906
3 | 2676014.9779 | 1214425.7128 | 2676014.4964 | 1214412.8428 | 2676014.4561 | 1214403.503 | 2676037.2956 | 1214401.126
4 | 2676075.8896 | 1214410.4691 | 2676101.3502 | 1214429.5168 | 2676101.5541 | 1214429.7213
5 | 2676047.9662 | 1214430.9347 | 2676042.6156 | 1214419.3277 | 2676041.991 | 1214417.1906
6 | 2676014.9779 | 1214425.7128 | 2676007.3116 | 1214415.1861 | 2676006.174 | 1214403.4254
7 | 2676101.5541 | 1214429.7213 | 2676113.2667 | 1214441.4654 | 2676115.8572 | 1214445.91
8 | 2676005.1441 | 1214392.7774 | 2676005.2034 | 1214382.1714 | 2676007.7937 | 1214370.2412 | 2676014.0254 | 1214359.8473
9 | 2676014.0254 | 1214359.8473 | 2676013.4148 | 1214349.4306
10 | 2676005.1441 | 1214392.7774 | 2675991.43 | 1214392.7808
11 | 2676005.1441 | 1214392.7774 | 2676006.174 | 1214403.4254
12 | 2676008.5636 | 1214297.3598 | 2676010.7132 | 1214313.4419 | 2676012.5095 | 1214333.9891 | 2676013.4148 | 1214349.4306
13 | 2676148.065 | 1214522.6173 | 2676145.4372 | 1214516.0685 | 2676119.9783 | 1214452.9807 | 2676115.8572 | 1214445.91
14 | 2676206.1551 | 1214501.1456 | 2676179.9781 | 1214510.9285 | 2676158.3394 | 1214519.213 | 2676148.065 | 1214522.6173
15 | 2676206.1551 | 1214501.1456 | 2676208.0805 | 1214483.0363 | 2676222.727 | 1214427.9233
16 | 2676222.727 | 1214427.9233 | 2676187.5327 | 1214380.7186
17 | 2676008.5636 | 1214297.3598 | 2676028.9531 | 1214289.9927 | 2676036.5959 | 1214290.4571 | 2676044.2157 | 1214302.4565
18 | 2676044.2157 | 1214302.4565 | 2676053.6839 | 1214317.3666
19 | 2676055.4618 | 1214320.1663 | 2676053.6839 | 1214317.3666
20 | 2675991.43 | 1214392.7808 | 2675973.4936 | 1214392.7853 | 2675969.0585 | 1214392.1395 | 2675967.0285 | 1214388.7225 | 2675966.1199 | 1214384.8915
21 | 2676166.9863 | 1214396.5561 | 2676187.5327 | 1214380.7186
22 | 2676055.4618 | 1214320.1663 | 2676066.6516 | 1214337.7877
23 | 2676070.6909 | 1214344.1486 | 2676066.6516 | 1214337.7877
24 | 2675961.3049 | 1214364.5895 | 2675966.1199 | 1214384.8915
25 | 2675945.6529 | 1214323.3083 | 2675951.1886 | 1214333.552 | 2675955.8958 | 1214347.4209 | 2675961.125 | 1214363.8313 | 2675961.3049 | 1214364.5895
26 | 2675945.6529 | 1214323.3083 | 2675917.074 | 1214343.9243 | 2675897.5285 | 1214360.7975
27 | 2675897.5285 | 1214360.7975 | 2675957.2115 | 1214432.5701

## bus_geodata
| x | y | coords
0 | 2676043.185 | 1214383.6592
1 | 2676037.2956 | 1214401.126
2 | 2676075.8896 | 1214410.4691
3 | 2676041.991 | 1214417.1906
4 | 2676014.9779 | 1214425.7128
5 | 2676101.5541 | 1214429.7213
6 | 2676047.9662 | 1214430.9347
7 | 2676014.0254 | 1214359.8473
8 | 2676005.1441 | 1214392.7774
9 | 2676013.4148 | 1214349.4306
10 | 2676006.174 | 1214403.4254
11 | 2676115.8572 | 1214445.91
12 | 2676148.065 | 1214522.6173
13 | 2676206.1551 | 1214501.1456
14 | 2676222.727 | 1214427.9233
15 | 2676008.5636 | 1214297.3598
16 | 2676044.2157 | 1214302.4565
17 | 2676053.6839 | 1214317.3666
18 | 2675991.43 | 1214392.7808
19 | 2676187.5327 | 1214380.7186
20 | 2676166.9863 | 1214396.5561
21 | 2676055.4618 | 1214320.1663
22 | 2676066.6516 | 1214337.7877
23 | 2676070.6909 | 1214344.1486
24 | 2675966.1199 | 1214384.8915
25 | 2675961.3049 | 1214364.5895
26 | 2675945.6529 | 1214323.3083
27 | 2675897.5285 | 1214360.7975
28 | 2675957.2115 | 1214432.5701
29 | 2676043.1402 | 1214382.9777

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.25935 | -0.066019
1 | 0.99767 | -0.044054 | 0 | 0
2 | 0.99449 | -0.10519 | 0.021296 | 0.0053373
3 | 0.99725 | -0.052317 | 0.010093 | 0.0025296
4 | 0.9947 | -0.10027 | 0 | 0
5 | 0.99264 | -0.1408 | 0.015485 | 0.0038809
6 | 0.997 | -0.057076 | 0.018089 | 0.0045334
7 | 0.9879 | -0.22997 | 0 | 0
8 | 0.99171 | -0.15716 | 0 | 0
9 | 0.98676 | -0.25183 | 0.0041597 | 0.0010425
10 | 0.99307 | -0.13131 | 0.0051507 | 0.0012909
11 | 0.9917 | -0.15902 | 0.021595 | 0.0054123
12 | 0.98972 | -0.19712 | 0 | 0
13 | 0.98826 | -0.22549 | 0 | 0
14 | 0.98647 | -0.26014 | 0.0065847 | 0.0016503
15 | 0.98126 | -0.35825 | 0 | 0
16 | 0.97668 | -0.44775 | 0.016306 | 0.0040868
17 | 0.97509 | -0.47901 | 0.032506 | 0.0081468
18 | 0.99147 | -0.16187 | 0.0028826 | 0.00072245
19 | 0.98544 | -0.28038 | 0.0092158 | 0.0023097
20 | 0.9852 | -0.28502 | 0.0099577 | 0.0024956
21 | 0.97489 | -0.48291 | 0.021398 | 0.0053629
22 | 0.97406 | -0.49931 | 0.021393 | 0.0053615
23 | 0.97391 | -0.50227 | 0.021397 | 0.0053627
24 | 0.99101 | -0.17073 | 0.0067435 | 0.0016901
25 | 0.99082 | -0.17434 | 0.0018939 | 0.00047465
26 | 0.99051 | -0.1805 | 0 | 0
27 | 0.99007 | -0.18899 | 0 | 0
28 | 0.9894 | -0.202 | 0.0078312 | 0.0019627
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.2577 | 0.066019 | -0.25715 | -0.065669 | 0.00054885 | 0.00035074 | 0.38397 | 0.38397 | 0.38397 | 1 | 0 | 0.99767 | -0.044054 | 52.7427
1 | 0.084677 | 0.021428 | -0.084429 | -0.02127 | 0.00024767 | 0.00015797 | 0.12637 | 0.12637 | 0.12637 | 0.99767 | -0.044054 | 0.99449 | -0.10519 | 34.7162
2 | 0.028197 | 0.0070724 | -0.028186 | -0.0070655 | 1.1102e-05 | 6.8867e-06 | 0.042058 | 0.042058 | 0.042058 | 0.99767 | -0.044054 | 0.99725 | -0.052317 | 11.5543
3 | 0.14427 | 0.037168 | -0.14388 | -0.036917 | 0.00039358 | 0.00025072 | 0.21554 | 0.21554 | 0.21554 | 0.99767 | -0.044054 | 0.9947 | -0.10027 | 29.6077
4 | 0.063133 | 0.015933 | -0.063025 | -0.015864 | 0.00010746 | 6.8356e-05 | 0.094502 | 0.094503 | 0.094503 | 0.99449 | -0.10519 | 0.99264 | -0.1408 | 25.9622
5 | 0.018093 | 0.0045359 | -0.018089 | -0.0045334 | 4.1018e-06 | 2.4294e-06 | 0.026997 | 0.026997 | 0.026997 | 0.99725 | -0.052317 | 0.997 | -0.057076 | 7.4168
6 | 0.14388 | 0.036917 | -0.14367 | -0.03678 | 0.00021637 | 0.00013783 | 0.21554 | 0.21554 | 0.21554 | 0.9947 | -0.10027 | 0.99307 | -0.13131 | 29.6077
7 | 0.047541 | 0.011983 | -0.047499 | -0.011957 | 4.1416e-05 | 2.6225e-05 | 0.07129 | 0.07129 | 0.07129 | 0.99264 | -0.1408 | 0.9917 | -0.15902 | 19.5852
8 | -0.11855 | -0.030249 | 0.11897 | 0.030517 | 0.00041854 | 0.00026741 | 0.17875 | 0.17875 | 0.17875 | 0.9879 | -0.22997 | 0.99171 | -0.15716 | 49.1084
9 | 0.11855 | 0.030249 | -0.11842 | -0.030169 | 0.00012503 | 7.9887e-05 | 0.17875 | 0.17875 | 0.17875 | 0.9879 | -0.22997 | 0.98676 | -0.25183 | 49.1085
10 | 0.019374 | 0.0048614 | -0.01937 | -0.0048588 | 4.3467e-06 | 2.605e-06 | 0.029072 | 0.029073 | 0.029073 | 0.99171 | -0.15716 | 0.99147 | -0.16187 | 7.987
11 | -0.13834 | -0.035378 | 0.13851 | 0.035489 | 0.00017327 | 0.00011075 | 0.20783 | 0.20783 | 0.20783 | 0.99171 | -0.15716 | 0.99307 | -0.13131 | 57.0953
12 | 0.11426 | 0.029127 | -0.11368 | -0.028754 | 0.00058368 | 0.00037289 | 0.17248 | 0.17248 | 0.17248 | 0.98676 | -0.25183 | 0.98126 | -0.35825 | 47.3853
13 | 0.025904 | 0.0065449 | -0.025857 | -0.0065158 | 4.7221e-05 | 2.9149e-05 | 0.038887 | 0.038887 | 0.038887 | 0.9917 | -0.15902 | 0.98972 | -0.19712 | 10.6833
14 | 0.025857 | 0.0065158 | -0.025822 | -0.0064941 | 3.5036e-05 | 2.163e-05 | 0.038887 | 0.038888 | 0.038888 | 0.98972 | -0.19712 | 0.98826 | -0.22549 | 10.6834
15 | 0.025822 | 0.0064941 | -0.025779 | -0.0064678 | 4.2667e-05 | 2.6344e-05 | 0.038888 | 0.038888 | 0.038888 | 0.98826 | -0.22549 | 0.98647 | -0.26014 | 10.6835
16 | 0.019194 | 0.0048175 | -0.019176 | -0.0048064 | 1.8513e-05 | 1.1097e-05 | 0.028955 | 0.028956 | 0.028956 | 0.98647 | -0.26014 | 0.98544 | -0.28038 | 7.9548
17 | 0.11368 | 0.028754 | -0.11319 | -0.028443 | 0.00048587 | 0.00031041 | 0.17248 | 0.17248 | 0.17248 | 0.98126 | -0.35825 | 0.97668 | -0.44775 | 47.3853
18 | 0.096887 | 0.024357 | -0.096743 | -0.024265 | 0.00014437 | 9.2177e-05 | 0.14764 | 0.14764 | 0.14764 | 0.97668 | -0.44775 | 0.97509 | -0.47901 | 40.5602
19 | 0.064237 | 0.016118 | -0.064225 | -0.01611 | 1.1953e-05 | 7.6084e-06 | 0.098034 | 0.098034 | 0.098034 | 0.97509 | -0.47901 | 0.97489 | -0.48291 | 26.9323
20 | 0.016487 | 0.0041363 | -0.016481 | -0.0041323 | 6.9651e-06 | 4.0667e-06 | 0.024746 | 0.024746 | 0.024746 | 0.99147 | -0.16187 | 0.99101 | -0.17073 | 6.7985
21 | 0.0099599 | 0.0024967 | -0.0099577 | -0.0024956 | 2.2005e-06 | 1.0779e-06 | 0.01504 | 0.01504 | 0.01504 | 0.98544 | -0.28038 | 0.9852 | -0.28502 | 4.1318
22 | 0.042827 | 0.010747 | -0.042793 | -0.010726 | 3.3453e-05 | 2.115e-05 | 0.065373 | 0.065373 | 0.065373 | 0.97489 | -0.48291 | 0.97406 | -0.49931 | 17.9596
23 | 0.021401 | 0.0053646 | -0.021397 | -0.0053627 | 3.0201e-06 | 1.8391e-06 | 0.032693 | 0.032693 | 0.032693 | 0.97406 | -0.49931 | 0.97391 | -0.50227 | 8.9815
24 | 0.0097371 | 0.0024422 | -0.0097354 | -0.0024414 | 1.6727e-06 | 8.0172e-07 | 0.014621 | 0.014621 | 0.014621 | 0.99101 | -0.17073 | 0.99082 | -0.17434 | 4.0168
25 | 0.0078415 | 0.0019667 | -0.0078392 | -0.0019658 | 2.3037e-06 | 9.0408e-07 | 0.011777 | 0.011777 | 0.011777 | 0.99082 | -0.17434 | 0.99051 | -0.1805 | 3.2355
26 | 0.0078392 | 0.0019658 | -0.007836 | -0.0019646 | 3.1705e-06 | 1.2449e-06 | 0.011777 | 0.011777 | 0.011777 | 0.99051 | -0.1805 | 0.99007 | -0.18899 | 3.2355
27 | 0.007836 | 0.0019646 | -0.0078312 | -0.0019627 | 4.8555e-06 | 1.9079e-06 | 0.011777 | 0.011778 | 0.011778 | 0.99007 | -0.18899 | 0.9894 | -0.202 | 3.2356

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2721 | 0.069215

## res_load
| p_mw | q_mvar
0 | 0.012751 | 0.0031957
1 | 0.021296 | 0.0053373
2 | 0.010093 | 0.0025296
3 | 0.015485 | 0.0038809
4 | 0.018089 | 0.0045334
5 | 0.0041597 | 0.0010425
6 | 0.0051507 | 0.0012909
7 | 0.021595 | 0.0054123
8 | 0.0065847 | 0.0016503
9 | 0.016306 | 0.0040868
10 | 0.032506 | 0.0081468
11 | 0.0028826 | 0.00072245
12 | 0.0092158 | 0.0023097
13 | 0.0099577 | 0.0024956
14 | 0.021398 | 0.0053629
15 | 0.021393 | 0.0053615
16 | 0.021397 | 0.0053627
17 | 0.0067435 | 0.0016901
18 | 0.0018939 | 0.00047465
19 | 0.0078312 | 0.0019627

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1