## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1342-11_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1342-11_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1342-11_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1342-11_0_6_node_128 | 0.4 | n |  | TRUE
4 | bus_LV_1342-11_0_6_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_1342-11_0_6_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_1342-11_0_6_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_1342-11_0_6_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_1342-11_0_6_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_1342-11_0_6_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1342-11_0_6_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1342-11_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1342-11_0_6_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1342-11_0_6_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1342-11_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1342-11_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1342-11_0_6_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1342-11_0_6_node_120 | 0.4 | n |  | TRUE
18 | bus_LV_1342-11_0_6_node_119 | 0.4 | n |  | TRUE
19 | bus_LV_1342-11_0_6_node_125 | 0.4 | n |  | TRUE
20 | bus_LV_1342-11_0_6_node_124 | 0.4 | n |  | TRUE
21 | bus_LV_1342-11_0_6_node_118 | 0.4 | n |  | TRUE
22 | bus_LV_1342-11_0_6_node_76 | 0.4 | n |  | TRUE
23 | bus_LV_1342-11_0_6_node_77 | 0.4 | n |  | TRUE
24 | bus_LV_1342-11_0_6_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1342-11_0_6_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1342-11_0_6_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1342-11_0_6_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1342-11_0_6_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1342-11_0_6_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1342-11_0_6_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1342-11_0_6_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1342-11_0_6_node_126 | 0.4 | n |  | TRUE
33 | bus_LV_1342-11_0_6_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_1342-11_0_6_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1342-11_0_6_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1342-11_0_6_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_1342-11_0_6_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1342-11_0_6_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1342-11_0_6_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_1342-11_0_6_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_1342-11_0_6_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1342-11_0_6_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_1342-11_0_6_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_1342-11_0_6_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_1342-11_0_6_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_1342-11_0_6_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_1342-11_0_6_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_1342-11_0_6_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_1342-11_0_6_node_71 | 0.4 | n |  | TRUE
50 | bus_LV_1342-11_0_6_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_1342-11_0_6_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_1342-11_0_6_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_1342-11_0_6_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_1342-11_0_6_node_72 | 0.4 | n |  | TRUE
55 | bus_LV_1342-11_0_6_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_1342-11_0_6_node_39 | 0.4 | n |  | TRUE
57 | bus_LV_1342-11_0_6_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_1342-11_0_6_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_1342-11_0_6_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_1342-11_0_6_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_1342-11_0_6_node_99 | 0.4 | n |  | TRUE
62 | bus_LV_1342-11_0_6_node_86 | 0.4 | n |  | TRUE
63 | bus_LV_1342-11_0_6_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_1342-11_0_6_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_1342-11_0_6_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_1342-11_0_6_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_1342-11_0_6_node_55 | 0.4 | n |  | TRUE
68 | bus_LV_1342-11_0_6_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_1342-11_0_6_node_60 | 0.4 | n |  | TRUE
70 | bus_LV_1342-11_0_6_node_59 | 0.4 | n |  | TRUE
71 | bus_LV_1342-11_0_6_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_1342-11_0_6_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_1342-11_0_6_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_1342-11_0_6_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_1342-11_0_6_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_1342-11_0_6_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_1342-11_0_6_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_1342-11_0_6_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_1342-11_0_6_node_87 | 0.4 | n |  | TRUE
80 | bus_LV_1342-11_0_6_node_88 | 0.4 | n |  | TRUE
81 | bus_LV_1342-11_0_6_node_62 | 0.4 | n |  | TRUE
82 | bus_LV_1342-11_0_6_node_63 | 0.4 | n |  | TRUE
83 | bus_LV_1342-11_0_6_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_1342-11_0_6_node_65 | 0.4 | n |  | TRUE
85 | bus_LV_1342-11_0_6_node_66 | 0.4 | n |  | TRUE
86 | bus_LV_1342-11_0_6_node_98 | 0.4 | n |  | TRUE
87 | bus_LV_1342-11_0_6_node_111 | 0.4 | n |  | TRUE
88 | bus_LV_1342-11_0_6_node_97 | 0.4 | n |  | TRUE
89 | bus_LV_1342-11_0_6_node_100 | 0.4 | n |  | TRUE
90 | bus_LV_1342-11_0_6_node_89 | 0.4 | n |  | TRUE
91 | bus_LV_1342-11_0_6_node_85 | 0.4 | n |  | TRUE
92 | bus_LV_1342-11_0_6_node_112 | 0.4 | n |  | TRUE
93 | bus_LV_1342-11_0_6_node_117 | 0.4 | n |  | TRUE
94 | bus_LV_1342-11_0_6_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_1342-11_0_6_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_1342-11_0_6_node_82 | 0.4 | n |  | TRUE
97 | bus_LV_1342-11_0_6_node_79 | 0.4 | n |  | TRUE
98 | bus_LV_1342-11_0_6_node_101 | 0.4 | n |  | TRUE
99 | bus_LV_1342-11_0_6_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_1342-11_0_6_node_73 | 0.4 | n |  | TRUE
101 | bus_LV_1342-11_0_6_node_96 | 0.4 | n |  | TRUE
102 | bus_LV_1342-11_0_6_node_90 | 0.4 | n |  | TRUE
103 | bus_LV_1342-11_0_6_node_81 | 0.4 | n |  | TRUE
104 | bus_LV_1342-11_0_6_node_92 | 0.4 | n |  | TRUE
105 | bus_LV_1342-11_0_6_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_1342-11_0_6_node_84 | 0.4 | n |  | TRUE
107 | bus_LV_1342-11_0_6_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_1342-11_0_6_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_1342-11_0_6_node_94 | 0.4 | n |  | TRUE
110 | bus_LV_1342-11_0_6_node_91 | 0.4 | n |  | TRUE
111 | bus_LV_1342-11_0_6_node_102 | 0.4 | n |  | TRUE
112 | bus_LV_1342-11_0_6_node_121 | 0.4 | n |  | TRUE
113 | bus_LV_1342-11_0_6_node_123 | 0.4 | n |  | TRUE
114 | bus_LV_1342-11_0_6_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_1342-11_0_6_node_104 | 0.4 | n |  | TRUE
116 | bus_LV_1342-11_0_6_node_122 | 0.4 | n |  | TRUE
117 | bus_LV_1342-11_0_6_node_107 | 0.4 | n |  | TRUE
118 | bus_LV_1342-11_0_6_node_105 | 0.4 | n |  | TRUE
119 | bus_LV_1342-11_0_6_node_106 | 0.4 | n |  | TRUE
120 | bus_LV_1342-11_0_6_node_108 | 0.4 | n |  | TRUE
121 | bus_LV_1342-11_0_6_node_110 | 0.4 | n |  | TRUE
122 | bus_LV_1342-11_0_6_node_116 | 0.4 | n |  | TRUE
123 | bus_LV_1342-11_0_6_node_115 | 0.4 | n |  | TRUE
124 | bus_LV_1342-11_0_6_node_113 | 0.4 | n |  | TRUE
125 | bus_LV_1342-11_0_6_node_114 | 0.4 | n |  | TRUE
126 | bus_MV_18_0_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1342-11_0_6_load_0 | 0 | 0.00080778 | 0.00020245 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1342-11_0_6_load_1 | 1 | 0.001596 | 0.00039999 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1342-11_0_6_load_2 | 2 | 0.0014441 | 0.00036193 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1342-11_0_6_load_128 | 3 | 0.003769 | 0.00094461 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1342-11_0_6_load_13 | 4 | 0.00083447 | 0.00020914 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1342-11_0_6_load_14 | 5 | 0.0058242 | 0.0014597 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1342-11_0_6_load_15 | 6 | 0.0038937 | 0.00097586 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1342-11_0_6_load_12 | 7 | 0.00073113 | 0.00018324 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1342-11_0_6_load_5 | 10 | 0.0011303 | 0.00028328 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1342-11_0_6_load_9 | 11 | 0.0011885 | 0.00029787 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1342-11_0_6_load_7 | 12 | 0.00064666 | 0.00016207 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1342-11_0_6_load_6 | 13 | 0.00097073 | 0.00024329 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1342-11_0_6_load_8 | 14 | 0.0012967 | 0.00032498 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1342-11_0_6_load_10 | 15 | 0.0015832 | 0.0003968 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1342-11_0_6_load_11 | 16 | 0.0019468 | 0.00048792 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1342-11_0_6_load_120 | 17 | 0.0013175 | 0.00033019 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1342-11_0_6_load_119 | 18 | 0.0096172 | 0.0024103 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1342-11_0_6_load_125 | 19 | 0.0078646 | 0.0019711 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1342-11_0_6_load_124 | 20 | 0.0066829 | 0.0016749 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1342-11_0_6_load_118 | 21 | 0.011452 | 0.0028702 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1342-11_0_6_load_76 | 22 | 0.0055152 | 0.0013822 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1342-11_0_6_load_77 | 23 | 0.0052099 | 0.0013057 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1342-11_0_6_load_16 | 24 | 0.003283 | 0.00082279 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1342-11_0_6_load_17 | 25 | 0.0064586 | 0.0016187 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1342-11_0_6_load_19 | 27 | 0.006551 | 0.0016418 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1342-11_0_6_load_20 | 28 | 0.0052927 | 0.0013265 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1342-11_0_6_load_21 | 29 | 0.0047589 | 0.0011927 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1342-11_0_6_load_27 | 30 | 0.0059618 | 0.0014942 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1342-11_0_6_load_126 | 32 | 0.0038755 | 0.00097129 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1342-11_0_6_load_32 | 33 | 0.0028488 | 0.00071399 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1342-11_0_6_load_29 | 34 | 0.0029805 | 0.00074699 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1342-11_0_6_load_22 | 35 | 0.0029096 | 0.00072923 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1342-11_0_6_load_23 | 36 | 0.004073 | 0.0010208 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1342-11_0_6_load_24 | 37 | 0.0054715 | 0.0013713 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1342-11_0_6_load_25 | 38 | 0.003574 | 0.00089573 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1342-11_0_6_load_26 | 39 | 0.0032938 | 0.0008255 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1342-11_0_6_load_28 | 43 | 0.0036854 | 0.00092364 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1342-11_0_6_load_30 | 44 | 0.0080964 | 0.0020291 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1342-11_0_6_load_33 | 45 | 0.003141 | 0.00078722 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1342-11_0_6_load_36 | 46 | 0.0057202 | 0.0014336 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1342-11_0_6_load_71 | 49 | 0.0073719 | 0.0018476 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1342-11_0_6_load_44 | 50 | 0.0087023 | 0.002181 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1342-11_0_6_load_45 | 51 | 0.0055355 | 0.0013873 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1342-11_0_6_load_51 | 52 | 0.0051178 | 0.0012827 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1342-11_0_6_load_48 | 53 | 0.0069103 | 0.0017319 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1342-11_0_6_load_72 | 54 | 0.00395 | 0.00098996 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1342-11_0_6_load_38 | 55 | 0.011958 | 0.0029969 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1342-11_0_6_load_39 | 56 | 0.0035521 | 0.00089024 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1342-11_0_6_load_40 | 57 | 0.0045102 | 0.0011304 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1342-11_0_6_load_41 | 58 | 0.0051321 | 0.0012862 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1342-11_0_6_load_42 | 59 | 0.0030194 | 0.00075675 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1342-11_0_6_load_49 | 60 | 0.0073491 | 0.0018419 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1342-11_0_6_load_99 | 61 | 0.0059714 | 0.0014966 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1342-11_0_6_load_46 | 63 | 0.0030088 | 0.00075408 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1342-11_0_6_load_47 | 64 | 0.0047398 | 0.0011879 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1342-11_0_6_load_56 | 65 | 0.011751 | 0.002945 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1342-11_0_6_load_54 | 66 | 0.0055045 | 0.0013795 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1342-11_0_6_load_55 | 67 | 0.0038853 | 0.00097375 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1342-11_0_6_load_53 | 68 | 0.0042392 | 0.0010625 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1342-11_0_6_load_60 | 69 | 0.0034128 | 0.00085534 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1342-11_0_6_load_52 | 71 | 0.0053427 | 0.001339 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1342-11_0_6_load_67 | 72 | 0.0027162 | 0.00068073 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1342-11_0_6_load_68 | 73 | 0.0029331 | 0.0007351 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1342-11_0_6_load_69 | 74 | 0.0033437 | 0.000838 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1342-11_0_6_load_57 | 76 | 0.0059699 | 0.0014962 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1342-11_0_6_load_58 | 77 | 0.0028265 | 0.00070838 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1342-11_0_6_load_61 | 78 | 0.0078952 | 0.0019787 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1342-11_0_6_load_87 | 79 | 0.0034972 | 0.00087649 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1342-11_0_6_load_88 | 80 | 0.0058409 | 0.0014639 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1342-11_0_6_load_62 | 81 | 0.0049835 | 0.001249 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1342-11_0_6_load_63 | 82 | 0.0081784 | 0.0020497 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1342-11_0_6_load_64 | 83 | 0.0052909 | 0.001326 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1342-11_0_6_load_66 | 85 | 0.0085235 | 0.0021362 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1342-11_0_6_load_98 | 86 | 0.0065677 | 0.001646 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1342-11_0_6_load_111 | 87 | 0.0063854 | 0.0016003 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1342-11_0_6_load_97 | 88 | 0.0061583 | 0.0015434 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1342-11_0_6_load_100 | 89 | 0.0047281 | 0.001185 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1342-11_0_6_load_89 | 90 | 0.0024169 | 0.00060574 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1342-11_0_6_load_85 | 91 | 0.0048967 | 0.0012272 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1342-11_0_6_load_112 | 92 | 0.010921 | 0.002737 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1342-11_0_6_load_117 | 93 | 0.0092378 | 0.0023152 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1342-11_0_6_load_83 | 95 | 0.0029849 | 0.0007481 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1342-11_0_6_load_82 | 96 | 0.0034837 | 0.0008731 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1342-11_0_6_load_79 | 97 | 0.0024929 | 0.00062479 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1342-11_0_6_load_101 | 98 | 0.0050202 | 0.0012582 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1342-11_0_6_load_80 | 99 | 0.0023506 | 0.00058913 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1342-11_0_6_load_73 | 100 | 0.0030357 | 0.00076081 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1342-11_0_6_load_96 | 101 | 0.0048113 | 0.0012058 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1342-11_0_6_load_90 | 102 | 0.0035821 | 0.00089775 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1342-11_0_6_load_81 | 103 | 0.0031468 | 0.00078865 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1342-11_0_6_load_92 | 104 | 0.0056014 | 0.0014038 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1342-11_0_6_load_84 | 106 | 0.0032102 | 0.00080454 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1342-11_0_6_load_103 | 108 | 0.0040862 | 0.0010241 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1342-11_0_6_load_94 | 109 | 0.00881 | 0.002208 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1342-11_0_6_load_91 | 110 | 0.0078155 | 0.0019587 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1342-11_0_6_load_102 | 111 | 0.0038817 | 0.00097284 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1342-11_0_6_load_121 | 112 | 0.004324 | 0.0010837 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1342-11_0_6_load_123 | 113 | 0.0029761 | 0.00074587 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1342-11_0_6_load_104 | 115 | 0.0067982 | 0.0017038 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1342-11_0_6_load_122 | 116 | 0.0069632 | 0.0017451 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1342-11_0_6_load_107 | 117 | 0.0040007 | 0.0010027 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1342-11_0_6_load_105 | 118 | 0.0046948 | 0.0011766 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1342-11_0_6_load_106 | 119 | 0.0045826 | 0.0011485 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1342-11_0_6_load_108 | 120 | 0.0053944 | 0.001352 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1342-11_0_6_load_116 | 122 | 0.0075978 | 0.0019042 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1342-11_0_6_load_115 | 123 | 0.0053177 | 0.0013327 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1342-11_0_6_load_113 | 124 | 0.0054234 | 0.0013592 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1342-11_0_6_load_114 | 125 | 0.011697 | 0.0029315 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 59 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1342-11_0_6_line_0 |  | 0 | 1 | 0.015517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1342-11_0_6_line_1 |  | 1 | 2 | 0.011879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1342-11_0_6_line_2 |  | 2 | 8 | 0.026085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1342-11_0_6_line_3 |  | 3 | 4 | 0.24329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1342-11_0_6_line_4 |  | 4 | 16 | 0.12254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1342-11_0_6_line_5 |  | 5 | 6 | 0.02322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1342-11_0_6_line_6 |  | 5 | 7 | 0.11945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1342-11_0_6_line_7 |  | 6 | 22 | 0.021996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1342-11_0_6_line_8 |  | 7 | 10 | 0.029242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1342-11_0_6_line_9 |  | 8 | 9 | 0.020805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1342-11_0_6_line_10 |  | 8 | 10 | 0.035521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1342-11_0_6_line_11 |  | 9 | 11 | 0.015561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1342-11_0_6_line_12 |  | 9 | 12 | 0.011757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1342-11_0_6_line_13 |  | 12 | 13 | 0.023751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1342-11_0_6_line_14 |  | 13 | 14 | 0.01611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1342-11_0_6_line_15 |  | 15 | 16 | 0.05219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1342-11_0_6_line_16 |  | 16 | 17 | 0.16486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1342-11_0_6_line_17 |  | 17 | 18 | 0.0027817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1342-11_0_6_line_18 |  | 18 | 121 | 0.028775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1342-11_0_6_line_19 |  | 19 | 20 | 0.0045427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1342-11_0_6_line_20 |  | 19 | 21 | 0.053125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1342-11_0_6_line_21 |  | 20 | 118 | 0.0010224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1342-11_0_6_line_22 |  | 21 | 122 | 0.018934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1342-11_0_6_line_23 |  | 21 | 121 | 0.035133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1342-11_0_6_line_24 |  | 22 | 23 | 0.0054882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1342-11_0_6_line_25 |  | 23 | 94 | 0.012257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1342-11_0_6_line_26 |  | 24 | 25 | 0.012939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1342-11_0_6_line_27 |  | 24 | 26 | 0.014545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1342-11_0_6_line_28 |  | 25 | 27 | 0.018433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1342-11_0_6_line_29 |  | 26 | 28 | 0.031214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1342-11_0_6_line_30 |  | 26 | 29 | 0.01577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1342-11_0_6_line_31 |  | 27 | 30 | 0.0021946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1342-11_0_6_line_32 |  | 28 | 31 | 0.025285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1342-11_0_6_line_33 |  | 29 | 32 | 0.031413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1342-11_0_6_line_34 |  | 31 | 33 | 0.0075496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1342-11_0_6_line_35 |  | 31 | 34 | 0.02902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1342-11_0_6_line_36 |  | 33 | 45 | 0.012543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1342-11_0_6_line_37 |  | 34 | 43 | 0.0098409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1342-11_0_6_line_38 |  | 35 | 36 | 0.010827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1342-11_0_6_line_39 |  | 35 | 37 | 0.023641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1342-11_0_6_line_40 |  | 36 | 38 | 0.0005328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1342-11_0_6_line_41 |  | 37 | 39 | 0.0062215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1342-11_0_6_line_42 |  | 39 | 40 | 0.011656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1342-11_0_6_line_43 |  | 40 | 41 | 0.032314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1342-11_0_6_line_44 |  | 40 | 42 | 0.011542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1342-11_0_6_line_45 |  | 41 | 48 | 0.007814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_1342-11_0_6_line_46 |  | 41 | 49 | 0.038227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1342-11_0_6_line_47 |  | 42 | 46 | 0.018169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1342-11_0_6_line_48 |  | 42 | 45 | 0.02922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1342-11_0_6_line_49 |  | 43 | 44 | 0.003411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1342-11_0_6_line_50 |  | 46 | 47 | 0.049527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1342-11_0_6_line_51 |  | 47 | 50 | 0.020954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1342-11_0_6_line_52 |  | 47 | 51 | 0.020559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1342-11_0_6_line_53 |  | 48 | 52 | 0.019215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1342-11_0_6_line_54 |  | 48 | 53 | 0.019411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_1342-11_0_6_line_55 |  | 49 | 54 | 0.023703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1342-11_0_6_line_56 |  | 51 | 63 | 0.029297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1342-11_0_6_line_57 |  | 52 | 69 | 0.025149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1342-11_0_6_line_58 |  | 53 | 60 | 0.016625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_1342-11_0_6_line_59 |  | 54 | 100 | 0.01117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1342-11_0_6_line_60 |  | 55 | 56 | 0.022681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_1342-11_0_6_line_61 |  | 55 | 57 | 0.00024711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_1342-11_0_6_line_62 |  | 56 | 58 | 0.015916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_1342-11_0_6_line_63 |  | 57 | 59 | 0.021039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_1342-11_0_6_line_64 |  | 58 | 60 | 0.022356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_1342-11_0_6_line_65 |  | 59 | 61 | 0.023559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_1342-11_0_6_line_66 |  | 61 | 62 | 0.041731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_1342-11_0_6_line_67 |  | 62 | 107 | 0.033205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_1342-11_0_6_line_68 |  | 62 | 106 | 0.017663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1342-11_0_6_line_69 |  | 63 | 64 | 0.00043861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1342-11_0_6_line_70 |  | 64 | 65 | 0.048632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1342-11_0_6_line_71 |  | 65 | 67 | 0.0058157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1342-11_0_6_line_72 |  | 66 | 67 | 0.0061804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1342-11_0_6_line_73 |  | 66 | 68 | 0.008757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1342-11_0_6_line_74 |  | 68 | 71 | 0.011386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1342-11_0_6_line_75 |  | 69 | 70 | 0.014814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1342-11_0_6_line_76 |  | 70 | 78 | 0.015368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1342-11_0_6_line_77 |  | 70 | 76 | 0.0068171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1342-11_0_6_line_78 |  | 72 | 73 | 0.0015762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1342-11_0_6_line_79 |  | 72 | 74 | 0.020004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1342-11_0_6_line_80 |  | 74 | 75 | 0.010413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1342-11_0_6_line_81 |  | 75 | 96 | 0.012484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1342-11_0_6_line_82 |  | 75 | 97 | 0.01793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1342-11_0_6_line_83 |  | 76 | 77 | 0.024186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1342-11_0_6_line_84 |  | 78 | 79 | 0.0026249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1342-11_0_6_line_85 |  | 79 | 80 | 0.019141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1342-11_0_6_line_86 |  | 80 | 110 | 0.0068421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1342-11_0_6_line_87 |  | 81 | 82 | 0.013374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1342-11_0_6_line_88 |  | 81 | 83 | 0.021051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1342-11_0_6_line_89 |  | 82 | 84 | 0.021693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1342-11_0_6_line_90 |  | 83 | 85 | 0.0042818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1342-11_0_6_line_91 |  | 84 | 89 | 0.028712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1342-11_0_6_line_92 |  | 84 | 90 | 0.0094415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1342-11_0_6_line_93 |  | 85 | 91 | 0.018314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1342-11_0_6_line_94 |  | 86 | 87 | 0.0069717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1342-11_0_6_line_95 |  | 86 | 88 | 0.019145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1342-11_0_6_line_96 |  | 87 | 92 | 0.012597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1342-11_0_6_line_97 |  | 88 | 101 | 0.014569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1342-11_0_6_line_98 |  | 90 | 94 | 0.013673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1342-11_0_6_line_99 |  | 91 | 95 | 0.02822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1342-11_0_6_line_100 |  | 92 | 93 | 0.01264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1342-11_0_6_line_101 |  | 93 | 123 | 0.013352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1342-11_0_6_line_102 |  | 94 | 102 | 0.010378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1342-11_0_6_line_103 |  | 95 | 106 | 0.00082385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1342-11_0_6_line_104 |  | 96 | 98 | 0.012853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1342-11_0_6_line_105 |  | 97 | 99 | 0.0015328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1342-11_0_6_line_106 |  | 99 | 103 | 0.019647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1342-11_0_6_line_107 |  | 103 | 104 | 0.0040381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1342-11_0_6_line_108 |  | 104 | 105 | 0.016302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1342-11_0_6_line_109 |  | 105 | 109 | 0.025781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1342-11_0_6_line_110 |  | 105 | 107 | 0.03488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1342-11_0_6_line_111 |  | 107 | 108 | 0.015576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_1342-11_0_6_line_112 |  | 108 | 115 | 0.00026018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_1342-11_0_6_line_113 |  | 109 | 111 | 0.01507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1342-11_0_6_line_114 |  | 112 | 113 | 0.021841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1342-11_0_6_line_115 |  | 112 | 114 | 0.01734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1342-11_0_6_line_116 |  | 114 | 116 | 0.0082957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1342-11_0_6_line_117 |  | 114 | 117 | 0.024102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1342-11_0_6_line_118 |  | 115 | 118 | 0.021461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_1342-11_0_6_line_119 |  | 117 | 119 | 0.015721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1342-11_0_6_line_120 |  | 119 | 120 | 0.020508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1342-11_0_6_line_121 |  | 120 | 121 | 0.011129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1342-11_0_6_line_122 |  | 122 | 125 | 0.012532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1342-11_0_6_line_123 |  | 123 | 124 | 0.0037892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1342-11_0_6_line_124 |  | 124 | 125 | 0.015243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1342-11_0_6_trafo_42 | 0.63 MVA 20/0.4 kV | 126 | 59 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2709493.5165 | 1226148.1514 | 2709488.412 | 1226133.4983
1 | 2709484.5043 | 1226122.2805 | 2709488.412 | 1226133.4983
2 | 2709475.9231 | 1226097.647 | 2709484.5043 | 1226122.2805
3 | 2709342.1838 | 1226485.9248 | 2709584.5035 | 1226464.1996
4 | 2709251.1782 | 1226403.8571 | 2709342.1838 | 1226485.9248
5 | 2709270.8017 | 1226085.7706 | 2709284.9552 | 1226085.0275 | 2709293.9897 | 1226084.5562
6 | 2709293.9897 | 1226084.5562 | 2709413.3839 | 1226081.0048
7 | 2709248.868 | 1226087.3937 | 2709264.8742 | 1226086.0818 | 2709270.8017 | 1226085.7706
8 | 2709413.3839 | 1226081.0048 | 2709413.4892 | 1226081.0085 | 2709441.7618 | 1226088.0506
9 | 2709496.7826 | 1226097.1415 | 2709475.9231 | 1226097.647
10 | 2709475.9231 | 1226097.647 | 2709465.9354 | 1226094.0717 | 2709441.7618 | 1226088.0506
11 | 2709496.7826 | 1226097.1415 | 2709499.5204 | 1226086.3949 | 2709500.744 | 1226082.0939
12 | 2709496.7826 | 1226097.1415 | 2709508.5277 | 1226096.6171
13 | 2709532.1223 | 1226094.1879 | 2709519.0006 | 1226096.1496 | 2709508.5277 | 1226096.6171
14 | 2709548.0569 | 1226091.816 | 2709545.4889 | 1226092.1897 | 2709532.1223 | 1226094.1879
15 | 2709251.1782 | 1226403.8571 | 2709223.7244 | 1226448.2432
16 | 2709152.7366 | 1226271.6191 | 2709251.1782 | 1226403.8571
17 | 2709152.7366 | 1226271.6191 | 2709150.2702 | 1226270.333
18 | 2709124.7552 | 1226257.0283 | 2709150.2702 | 1226270.333
19 | 2709124.3296 | 1226191.8048 | 2709120.2214 | 1226189.8662
20 | 2709124.3296 | 1226191.8048 | 2709153.1887 | 1226236.408
21 | 2709120.2214 | 1226189.8662 | 2709119.2968 | 1226189.4299
22 | 2709168.3234 | 1226225.0306 | 2709153.1887 | 1226236.408
23 | 2709124.7552 | 1226257.0283 | 2709134.7736 | 1226250.2514 | 2709153.1887 | 1226236.408
24 | 2709248.868 | 1226087.3937 | 2709243.3982 | 1226087.842
25 | 2709231.1826 | 1226088.8431 | 2709243.3982 | 1226087.842
26 | 2709040.7737 | 1225918.7068 | 2709045.8516 | 1225907.7192 | 2709046.2015 | 1225906.9618
27 | 2709034.6718 | 1225931.9104 | 2709040.7737 | 1225918.7068
28 | 2709053.9321 | 1225890.2285 | 2709046.2015 | 1225906.9618
29 | 2709034.6718 | 1225931.9104 | 2709050.067 | 1225936.2624 | 2709064.7091 | 1225940.3992
30 | 2709034.6718 | 1225931.9104 | 2709020.4541 | 1225928.6697 | 2709019.3803 | 1225928.1631
31 | 2709054.8525 | 1225888.2362 | 2709053.9321 | 1225890.2285
32 | 2709089.0415 | 1225947.2738 | 2709064.7091 | 1225940.3992
33 | 2708990.9787 | 1225914.7411 | 2709014.3728 | 1225925.8006 | 2709019.3803 | 1225928.1631
34 | 2709089.0415 | 1225947.2738 | 2709096.3548 | 1225949.1478
35 | 2709089.0415 | 1225947.2738 | 2709100.3465 | 1225920.5468
36 | 2709108.5056 | 1225952.2613 | 2709096.3548 | 1225949.1478
37 | 2709105.8195 | 1225912.5689 | 2709102.0954 | 1225916.4122 | 2709100.3465 | 1225920.5468
38 | 2709163.6776 | 1225922.7947 | 2709167.7029 | 1225912.7437
39 | 2709163.6776 | 1225922.7947 | 2709154.8883 | 1225944.7409
40 | 2709167.7029 | 1225912.7437 | 2709167.901 | 1225912.2491
41 | 2709152.5753 | 1225950.5165 | 2709154.8883 | 1225944.7409
42 | 2709148.2419 | 1225961.3366 | 2709152.5753 | 1225950.5165
43 | 2709148.2419 | 1225961.3366 | 2709168.8112 | 1225966.7512 | 2709175.489 | 1225968.5084 | 2709179.5787 | 1225969.5842
44 | 2709136.8113 | 1225959.5144 | 2709148.2419 | 1225961.3366
45 | 2709179.5787 | 1225969.5842 | 2709176.2869 | 1225976.6736
46 | 2709179.5787 | 1225969.5842 | 2709195.9208 | 1225935.0267
47 | 2709136.8113 | 1225959.5144 | 2709129.8812 | 1225976.3102
48 | 2709136.8113 | 1225959.5144 | 2709108.5056 | 1225952.2613
49 | 2709108.1931 | 1225910.1192 | 2709105.8195 | 1225912.5689
50 | 2709104.8718 | 1226017.5836 | 2709112.2514 | 1226001.34 | 2709122.9093 | 1225993.2071 | 2709129.8812 | 1225976.3102
51 | 2709104.8718 | 1226017.5836 | 2709124.1601 | 1226025.7704
52 | 2709104.8718 | 1226017.5836 | 2709085.8032 | 1226009.8976
53 | 2709176.2869 | 1225976.6736 | 2709193.2 | 1225985.7939
54 | 2709176.2869 | 1225976.6736 | 2709174.6293 | 1225980.2348 | 2709168.0988 | 1225994.2735
55 | 2709195.9208 | 1225935.0267 | 2709206.0537 | 1225913.5991
56 | 2709058.6304 | 1225998.945 | 2709085.8032 | 1226009.8976
57 | 2709215.336 | 1225997.7305 | 2709193.2 | 1225985.7939
58 | 2709168.0988 | 1225994.2735 | 2709161.0867 | 1226009.3476
59 | 2709210.8289 | 1225903.5014 | 2709206.0537 | 1225913.5991
60 | 2709135.3782 | 1226064.6134 | 2709140.5848 | 1226053.4209 | 2709144.9448 | 1226044.0482
61 | 2709135.2739 | 1226064.8375 | 2709135.3782 | 1226064.6134
62 | 2709144.9448 | 1226044.0482 | 2709151.6576 | 1226029.6175
63 | 2709126.4 | 1226083.9134 | 2709135.2739 | 1226064.8375
64 | 2709161.0867 | 1226009.3476 | 2709151.6576 | 1226029.6175
65 | 2709126.4 | 1226083.9134 | 2709116.463 | 1226105.2745
66 | 2709098.8612 | 1226143.1123 | 2709116.463 | 1226105.2745
67 | 2709098.8612 | 1226143.1123 | 2709093.0491 | 1226154.9257 | 2709091.5604 | 1226158.3788 | 2709085.5661 | 1226173.5136
68 | 2709098.8612 | 1226143.1123 | 2709107.4747 | 1226143.0813 | 2709116.4485 | 1226141.9127
69 | 2709058.6304 | 1225998.945 | 2709058.2236 | 1225998.7811
70 | 2709058.2236 | 1225998.7811 | 2709036.3192 | 1226042.2012
71 | 2709036.3192 | 1226042.2012 | 2709030.8472 | 1226044.1708
72 | 2709025.032 | 1226046.2638 | 2709030.8472 | 1226044.1708
73 | 2709016.7925 | 1226049.2295 | 2709025.032 | 1226046.2638
74 | 2709006.0793 | 1226053.0854 | 2709016.7925 | 1226049.2295
75 | 2709228.375 | 1226004.7617 | 2709215.336 | 1225997.7305
76 | 2709228.375 | 1226004.7617 | 2709222.1932 | 1226018.8315
77 | 2709228.375 | 1226004.7617 | 2709231.1193 | 1225998.5214
78 | 2709026.2033 | 1226111.0264 | 2709024.7079 | 1226111.5246
79 | 2709026.2033 | 1226111.0264 | 2709045.1815 | 1226104.7029
80 | 2709055.0601 | 1226101.4114 | 2709045.1815 | 1226104.7029
81 | 2709055.0601 | 1226101.4114 | 2709066.9035 | 1226097.4649
82 | 2709055.0601 | 1226101.4114 | 2709060.5668 | 1226118.4751
83 | 2709231.1193 | 1225998.5214 | 2709237.0629 | 1225985.0063 | 2709246.2049 | 1225982.7254
84 | 2709222.1932 | 1226018.8315 | 2709221.1373 | 1226021.2347
85 | 2709213.4377 | 1226038.759 | 2709221.1373 | 1226021.2347
86 | 2709213.4377 | 1226038.759 | 2709210.6854 | 1226045.0231
87 | 2709181.3672 | 1226113.2273 | 2709191.2 | 1226104.1616
88 | 2709181.3672 | 1226113.2273 | 2709165.8906 | 1226127.4964
89 | 2709208.1447 | 1226090.7217 | 2709199.509 | 1226096.501 | 2709191.2 | 1226104.1616
90 | 2709161.8807 | 1226128.9979 | 2709165.8906 | 1226127.4964 | 2709165.8906 | 1226127.4964
91 | 2709208.1447 | 1226090.7217 | 2709204.5463 | 1226083.5392 | 2709185.3905 | 1226075.7507
92 | 2709208.1447 | 1226090.7217 | 2709217.555 | 1226089.9544
93 | 2709161.8807 | 1226128.9979 | 2709144.7297 | 1226135.42
94 | 2709224.4 | 1226182.8756 | 2709229.9727 | 1226178.6864
95 | 2709229.9727 | 1226178.6864 | 2709245.2761 | 1226167.1822
96 | 2709224.4 | 1226182.8756 | 2709214.3306 | 1226190.4452
97 | 2709256.8555 | 1226158.3428 | 2709253.9815 | 1226160.6379 | 2709245.2761 | 1226167.1822
98 | 2709231.1826 | 1226088.8431 | 2709217.555 | 1226089.9544
99 | 2709117.2654 | 1226141.8063 | 2709117.8031 | 1226141.7363 | 2709142.6212 | 1226136.2095 | 2709144.7297 | 1226135.42
100 | 2709204.2269 | 1226198.0405 | 2709214.3306 | 1226190.4452
101 | 2709204.2269 | 1226198.0405 | 2709193.554 | 1226206.0638
102 | 2709231.1826 | 1226088.8431 | 2709229.9561 | 1226078.5377
103 | 2709117.2654 | 1226141.8063 | 2709116.4485 | 1226141.9127
104 | 2709079.0975 | 1226093.4015 | 2709066.9035 | 1226097.4649
105 | 2709060.5668 | 1226118.4751 | 2709061.0375 | 1226119.9339
106 | 2709067.0714 | 1226138.6314 | 2709061.0375 | 1226119.9339
107 | 2709068.3116 | 1226142.4744 | 2709067.0714 | 1226138.6314
108 | 2709073.3182 | 1226157.9886 | 2709068.3116 | 1226142.4744
109 | 2709073.3182 | 1226157.9886 | 2709048.98 | 1226166.4909
110 | 2709073.3182 | 1226157.9886 | 2709076.8054 | 1226156.7738 | 2709080.8883 | 1226156.971 | 2709087.3727 | 1226157.279 | 2709091.5604 | 1226158.3788 | 2709085.5661 | 1226173.5136
111 | 2709085.5661 | 1226173.5136 | 2709099.653 | 1226180.1607
112 | 2709099.8883 | 1226180.2718 | 2709099.653 | 1226180.1607
113 | 2709034.2 | 1226167.3168 | 2709044.5277 | 1226168.0463 | 2709048.98 | 1226166.4909
114 | 2709051.7722 | 1226245.5366 | 2709042.6222 | 1226265.3681
115 | 2709059.0365 | 1226229.792 | 2709051.7722 | 1226245.5366
116 | 2709059.0365 | 1226229.792 | 2709062.5738 | 1226222.2882
117 | 2709059.0365 | 1226229.792 | 2709082.0492 | 1226236.9568
118 | 2709119.2968 | 1226189.4299 | 2709099.8883 | 1226180.2718
119 | 2709096.858 | 1226242.1337 | 2709093.8272 | 1226240.6267 | 2709086.854 | 1226238.4528 | 2709082.0492 | 1226236.9568
120 | 2709096.858 | 1226242.1337 | 2709110.7543 | 1226249.0434 | 2709115.0878 | 1226251.5148
121 | 2709124.7552 | 1226257.0283 | 2709115.0878 | 1226251.5148
122 | 2709168.3234 | 1226225.0306 | 2709178.3408 | 1226217.5001
123 | 2709190.5251 | 1226208.3407 | 2709193.554 | 1226206.0638
124 | 2709190.5251 | 1226208.3407 | 2709178.3408 | 1226217.5001

## bus_geodata
| x | y | coords
0 | 2709493.5165 | 1226148.1514
1 | 2709488.412 | 1226133.4983
2 | 2709484.5043 | 1226122.2805
3 | 2709584.5035 | 1226464.1996
4 | 2709342.1838 | 1226485.9248
5 | 2709293.9897 | 1226084.5562
6 | 2709270.8017 | 1226085.7706
7 | 2709413.3839 | 1226081.0048
8 | 2709475.9231 | 1226097.647
9 | 2709496.7826 | 1226097.1415
10 | 2709441.7618 | 1226088.0506
11 | 2709500.744 | 1226082.0939
12 | 2709508.5277 | 1226096.6171
13 | 2709532.1223 | 1226094.1879
14 | 2709548.0569 | 1226091.816
15 | 2709223.7244 | 1226448.2432
16 | 2709251.1782 | 1226403.8571
17 | 2709152.7366 | 1226271.6191
18 | 2709150.2702 | 1226270.333
19 | 2709124.3296 | 1226191.8048
20 | 2709120.2214 | 1226189.8662
21 | 2709153.1887 | 1226236.408
22 | 2709248.868 | 1226087.3937
23 | 2709243.3982 | 1226087.842
24 | 2709040.7737 | 1225918.7068
25 | 2709046.2015 | 1225906.9618
26 | 2709034.6718 | 1225931.9104
27 | 2709053.9321 | 1225890.2285
28 | 2709064.7091 | 1225940.3992
29 | 2709019.3803 | 1225928.1631
30 | 2709054.8525 | 1225888.2362
31 | 2709089.0415 | 1225947.2738
32 | 2708990.9787 | 1225914.7411
33 | 2709096.3548 | 1225949.1478
34 | 2709100.3465 | 1225920.5468
35 | 2709163.6776 | 1225922.7947
36 | 2709167.7029 | 1225912.7437
37 | 2709154.8883 | 1225944.7409
38 | 2709167.901 | 1225912.2491
39 | 2709152.5753 | 1225950.5165
40 | 2709148.2419 | 1225961.3366
41 | 2709179.5787 | 1225969.5842
42 | 2709136.8113 | 1225959.5144
43 | 2709105.8195 | 1225912.5689
44 | 2709108.1931 | 1225910.1192
45 | 2709108.5056 | 1225952.2613
46 | 2709129.8812 | 1225976.3102
47 | 2709104.8718 | 1226017.5836
48 | 2709176.2869 | 1225976.6736
49 | 2709195.9208 | 1225935.0267
50 | 2709124.1601 | 1226025.7704
51 | 2709085.8032 | 1226009.8976
52 | 2709193.2 | 1225985.7939
53 | 2709168.0988 | 1225994.2735
54 | 2709206.0537 | 1225913.5991
55 | 2709135.3782 | 1226064.6134
56 | 2709144.9448 | 1226044.0482
57 | 2709135.2739 | 1226064.8375
58 | 2709151.6576 | 1226029.6175
59 | 2709126.4 | 1226083.9134
60 | 2709161.0867 | 1226009.3476
61 | 2709116.463 | 1226105.2745
62 | 2709098.8612 | 1226143.1123
63 | 2709058.6304 | 1225998.945
64 | 2709058.2236 | 1225998.7811
65 | 2709036.3192 | 1226042.2012
66 | 2709025.032 | 1226046.2638
67 | 2709030.8472 | 1226044.1708
68 | 2709016.7925 | 1226049.2295
69 | 2709215.336 | 1225997.7305
70 | 2709228.375 | 1226004.7617
71 | 2709006.0793 | 1226053.0854
72 | 2709026.2033 | 1226111.0264
73 | 2709024.7079 | 1226111.5246
74 | 2709045.1815 | 1226104.7029
75 | 2709055.0601 | 1226101.4114
76 | 2709231.1193 | 1225998.5214
77 | 2709246.2049 | 1225982.7254
78 | 2709222.1932 | 1226018.8315
79 | 2709221.1373 | 1226021.2347
80 | 2709213.4377 | 1226038.759
81 | 2709181.3672 | 1226113.2273
82 | 2709191.2 | 1226104.1616
83 | 2709165.8906 | 1226127.4964
84 | 2709208.1447 | 1226090.7217
85 | 2709161.8807 | 1226128.9979
86 | 2709229.9727 | 1226178.6864
87 | 2709224.4 | 1226182.8756
88 | 2709245.2761 | 1226167.1822
89 | 2709185.3905 | 1226075.7507
90 | 2709217.555 | 1226089.9544
91 | 2709144.7297 | 1226135.42
92 | 2709214.3306 | 1226190.4452
93 | 2709204.2269 | 1226198.0405
94 | 2709231.1826 | 1226088.8431
95 | 2709117.2654 | 1226141.8063
96 | 2709066.9035 | 1226097.4649
97 | 2709060.5668 | 1226118.4751
98 | 2709079.0975 | 1226093.4015
99 | 2709061.0375 | 1226119.9339
100 | 2709210.8289 | 1225903.5014
101 | 2709256.8555 | 1226158.3428
102 | 2709229.9561 | 1226078.5377
103 | 2709067.0714 | 1226138.6314
104 | 2709068.3116 | 1226142.4744
105 | 2709073.3182 | 1226157.9886
106 | 2709116.4485 | 1226141.9127
107 | 2709085.5661 | 1226173.5136
108 | 2709099.653 | 1226180.1607
109 | 2709048.98 | 1226166.4909
110 | 2709210.6854 | 1226045.0231
111 | 2709034.2 | 1226167.3168
112 | 2709051.7722 | 1226245.5366
113 | 2709042.6222 | 1226265.3681
114 | 2709059.0365 | 1226229.792
115 | 2709099.8883 | 1226180.2718
116 | 2709062.5738 | 1226222.2882
117 | 2709082.0492 | 1226236.9568
118 | 2709119.2968 | 1226189.4299
119 | 2709096.858 | 1226242.1337
120 | 2709115.0878 | 1226251.5149
121 | 2709124.7552 | 1226257.0283
122 | 2709168.3234 | 1226225.0306
123 | 2709193.554 | 1226206.0638
124 | 2709190.5251 | 1226208.3407
125 | 2709178.3408 | 1226217.5001
126 | 2709098.8612 | 1226143.1123

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98349 | -0.31795 | 0.00080778 | 0.00020245
1 | 0.9835 | -0.31773 | 0.001596 | 0.00039999
2 | 0.98353 | -0.31721 | 0.0014441 | 0.00036193
3 | 0.97876 | -0.40963 | 0.003769 | 0.00094461
4 | 0.97961 | -0.39294 | 0.00083447 | 0.00020914
5 | 0.98521 | -0.28444 | 0.0058242 | 0.0014597
6 | 0.98554 | -0.27792 | 0.0038937 | 0.00097586
7 | 0.98413 | -0.30553 | 0.00073113 | 0.00018324
8 | 0.98362 | -0.3154 | 0 | 0
9 | 0.98354 | -0.31694 | 0 | 0
10 | 0.98388 | -0.31031 | 0.0011303 | 0.00028328
11 | 0.98353 | -0.31727 | 0.0011885 | 0.00029787
12 | 0.98351 | -0.31756 | 0.00064666 | 0.00016207
13 | 0.98346 | -0.31853 | 0.00097073 | 0.00024329
14 | 0.98344 | -0.31891 | 0.0012967 | 0.00032498
15 | 0.98006 | -0.38418 | 0.0015832 | 0.0003968
16 | 0.98013 | -0.38268 | 0.0019468 | 0.00048792
17 | 0.98137 | -0.35833 | 0.0013175 | 0.00033019
18 | 0.9814 | -0.35786 | 0.0096172 | 0.0024103
19 | 0.98997 | -0.1915 | 0.0078646 | 0.0019711
20 | 0.99027 | -0.18582 | 0.0066829 | 0.0016749
21 | 0.98344 | -0.31791 | 0.011452 | 0.0028702
22 | 0.98594 | -0.27021 | 0.0055152 | 0.0013822
23 | 0.98606 | -0.26775 | 0.0052099 | 0.0013057
24 | 0.98208 | -0.34503 | 0.003283 | 0.00082279
25 | 0.98185 | -0.34946 | 0.0064586 | 0.0016187
26 | 0.98238 | -0.33918 | 0 | 0
27 | 0.98164 | -0.35364 | 0.006551 | 0.0016418
28 | 0.98327 | -0.32178 | 0.0052927 | 0.0013265
29 | 0.98225 | -0.34164 | 0.0047589 | 0.0011927
30 | 0.98163 | -0.35387 | 0.0059618 | 0.0014942
31 | 0.98411 | -0.3053 | 0 | 0
32 | 0.98214 | -0.34384 | 0.0038755 | 0.00097129
33 | 0.98447 | -0.29838 | 0.0028488 | 0.00071399
34 | 0.98372 | -0.31301 | 0.0029805 | 0.00074699
35 | 0.98733 | -0.24287 | 0.0029096 | 0.00072923
36 | 0.98725 | -0.24435 | 0.004073 | 0.0010208
37 | 0.98756 | -0.2384 | 0.0054715 | 0.0013713
38 | 0.98725 | -0.24438 | 0.003574 | 0.00089573
39 | 0.98765 | -0.23662 | 0.0032938 | 0.0008255
40 | 0.98785 | -0.2326 | 0 | 0
41 | 0.99187 | -0.15517 | 0 | 0
42 | 0.98662 | -0.25641 | 0 | 0
43 | 0.98361 | -0.3151 | 0.0036854 | 0.00092364
44 | 0.98358 | -0.3156 | 0.0080964 | 0.0020291
45 | 0.98509 | -0.28625 | 0.003141 | 0.00078722
46 | 0.98564 | -0.27544 | 0.0057202 | 0.0014336
47 | 0.98323 | -0.3224 | 0 | 0
48 | 0.99241 | -0.14486 | 0 | 0
49 | 0.99137 | -0.1649 | 0.0073719 | 0.0018476
50 | 0.98306 | -0.32569 | 0.0087023 | 0.002181
51 | 0.98239 | -0.33873 | 0.0055355 | 0.0013873
52 | 0.99166 | -0.15928 | 0.0051178 | 0.0012827
53 | 0.99355 | -0.12296 | 0.0069103 | 0.0017319
54 | 0.99122 | -0.16784 | 0.00395 | 0.00098996
55 | 0.99849 | -0.028587 | 0.011958 | 0.0029969
56 | 0.997 | -0.056967 | 0.0035521 | 0.00089024
57 | 0.99851 | -0.028261 | 0.0045102 | 0.0011304
58 | 0.99597 | -0.0766 | 0.0051321 | 0.0012862
59 | 1 | 0 | -0.53107 | -0.13528
60 | 0.99456 | -0.10357 | 0.0073491 | 0.0018419
61 | 0.99789 | -0.040035 | 0.0059714 | 0.0014966
62 | 0.99422 | -0.1099 | 0 | 0
63 | 0.98135 | -0.3591 | 0.0030088 | 0.00075408
64 | 0.98133 | -0.35939 | 0.0047398 | 0.0011879
65 | 0.97995 | -0.38647 | 0.011751 | 0.002945
66 | 0.97976 | -0.39016 | 0.0055045 | 0.0013795
67 | 0.97985 | -0.38847 | 0.0038853 | 0.00097375
68 | 0.97969 | -0.39169 | 0.0042392 | 0.0010625
69 | 0.9908 | -0.1759 | 0.0034128 | 0.00085534
70 | 0.99035 | -0.18481 | 0 | 0
71 | 0.97963 | -0.39279 | 0.0053427 | 0.001339
72 | 0.98925 | -0.20589 | 0.0027162 | 0.00068073
73 | 0.98924 | -0.20597 | 0.0029331 | 0.0007351
74 | 0.98935 | -0.20387 | 0.0033437 | 0.000838
75 | 0.98944 | -0.20221 | 0 | 0
76 | 0.99029 | -0.18588 | 0.0059699 | 0.0014962
77 | 0.99023 | -0.18709 | 0.0028265 | 0.00070838
78 | 0.98999 | -0.19165 | 0.0078952 | 0.0019787
79 | 0.98995 | -0.19246 | 0.0034972 | 0.00087649
80 | 0.98971 | -0.19711 | 0.0058409 | 0.0014639
81 | 0.98857 | -0.21905 | 0.0049835 | 0.001249
82 | 0.98796 | -0.23079 | 0.0081784 | 0.0020497
83 | 0.98962 | -0.19874 | 0.0052909 | 0.001326
84 | 0.98715 | -0.24668 | 0 | 0
85 | 0.98985 | -0.19421 | 0.0085235 | 0.0021362
86 | 0.97908 | -0.40321 | 0.0065677 | 0.001646
87 | 0.97919 | -0.40099 | 0.0063854 | 0.0016003
88 | 0.97888 | -0.40703 | 0.0061583 | 0.0015434
89 | 0.98702 | -0.24911 | 0.0047281 | 0.001185
90 | 0.98683 | -0.25281 | 0.0024169 | 0.00060574
91 | 0.991 | -0.17209 | 0.0048967 | 0.0012272
92 | 0.97947 | -0.39551 | 0.010921 | 0.002737
93 | 0.97988 | -0.38752 | 0.0092378 | 0.0023152
94 | 0.98641 | -0.2611 | 0 | 0
95 | 0.99288 | -0.13566 | 0.0029849 | 0.0007481
96 | 0.98934 | -0.2041 | 0.0034837 | 0.0008731
97 | 0.98973 | -0.19662 | 0.0024929 | 0.00062479
98 | 0.98928 | -0.20525 | 0.0050202 | 0.0012582
99 | 0.98975 | -0.19608 | 0.0023506 | 0.00058913
100 | 0.99119 | -0.16844 | 0.0030357 | 0.00076081
101 | 0.97882 | -0.40831 | 0.0048113 | 0.0012058
102 | 0.98637 | -0.26176 | 0.0035821 | 0.00089775
103 | 0.99016 | -0.18827 | 0.0031468 | 0.00078865
104 | 0.99025 | -0.18644 | 0.0056014 | 0.0014038
105 | 0.99071 | -0.17744 | 0 | 0
106 | 0.99294 | -0.13456 | 0.0032102 | 0.00080454
107 | 0.99211 | -0.15035 | 0 | 0
108 | 0.99133 | -0.16535 | 0.0040862 | 0.0010241
109 | 0.99042 | -0.18325 | 0.00881 | 0.002208
110 | 0.98966 | -0.19806 | 0.0078155 | 0.0019587
111 | 0.99036 | -0.18429 | 0.0038817 | 0.00097284
112 | 0.98048 | -0.37581 | 0.004324 | 0.0010837
113 | 0.98042 | -0.37699 | 0.0029761 | 0.00074587
114 | 0.9806 | -0.37352 | 0 | 0
115 | 0.99132 | -0.1656 | 0.0067982 | 0.0017038
116 | 0.98054 | -0.37456 | 0.0069632 | 0.0017451
117 | 0.98092 | -0.36729 | 0.0040007 | 0.0010027
118 | 0.99031 | -0.18492 | 0.0046948 | 0.0011766
119 | 0.98118 | -0.36209 | 0.0045826 | 0.0011485
120 | 0.98161 | -0.35361 | 0.0053944 | 0.001352
121 | 0.9819 | -0.34792 | 0 | 0
122 | 0.98214 | -0.34323 | 0.0075978 | 0.0019042
123 | 0.98042 | -0.37684 | 0.0053177 | 0.0013327
124 | 0.9806 | -0.37344 | 0.0054234 | 0.0013592
125 | 0.98137 | -0.35831 | 0.011697 | 0.0029315
126 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00080778 | -0.00020245 | 0.00080779 | 0.00020226 | 8.691e-09 | -1.9134e-07 | 0.0012222 | 0.0012221 | 0.0012222 | 0.98349 | -0.31795 | 0.9835 | -0.31773 | 0.33576
1 | -0.0024038 | -0.00060224 | 0.0024038 | 0.00060213 | 5.8915e-08 | -1.1304e-07 | 0.0036367 | 0.0036367 | 0.0036367 | 0.9835 | -0.31773 | 0.98353 | -0.31721 | 0.99911
2 | -0.0038479 | -0.00096406 | 0.0038483 | 0.00096394 | 3.3151e-07 | -1.1891e-07 | 0.0058215 | 0.0058214 | 0.0058215 | 0.98353 | -0.31721 | 0.98362 | -0.3154 | 1.5993
3 | -0.003769 | -0.00094461 | 0.003772 | 0.00094347 | 2.995e-06 | -1.1435e-06 | 0.0057301 | 0.005729 | 0.0057301 | 0.97876 | -0.40963 | 0.97961 | -0.39294 | 1.5742
4 | -0.0046065 | -0.0011526 | 0.0046088 | 0.0011525 | 2.2494e-06 | -1.0403e-07 | 0.0069966 | 0.006996 | 0.0069966 | 0.97961 | -0.39294 | 0.98013 | -0.38268 | 1.9221
5 | -0.015651 | -0.0039241 | 0.015656 | 0.0039269 | 4.8657e-06 | 2.8183e-06 | 0.023639 | 0.023639 | 0.023639 | 0.98521 | -0.28444 | 0.98554 | -0.27792 | 6.4942
6 | 0.0098267 | 0.0024644 | -0.0098168 | -0.0024596 | 9.868e-06 | 4.7961e-06 | 0.014842 | 0.014843 | 0.014843 | 0.98521 | -0.28444 | 0.98413 | -0.30553 | 4.0777
7 | -0.019549 | -0.0049028 | 0.019557 | 0.0049071 | 7.1867e-06 | 4.3191e-06 | 0.029518 | 0.029518 | 0.029518 | 0.98554 | -0.27792 | 0.98594 | -0.27021 | 8.1093
8 | 0.0090857 | 0.0022764 | -0.0090836 | -0.0022754 | 2.0694e-06 | 9.5298e-07 | 0.013737 | 0.013738 | 0.013738 | 0.98413 | -0.30553 | 0.98388 | -0.31031 | 3.7741
9 | 0.0041031 | 0.0010274 | -0.0041028 | -0.0010275 | 3.0057e-07 | -7.1691e-08 | 0.0062069 | 0.006207 | 0.006207 | 0.98362 | -0.3154 | 0.98354 | -0.31694 | 1.7052
10 | -0.0079514 | -0.0019914 | 0.0079533 | 0.0019922 | 1.9271e-06 | 7.8239e-07 | 0.012028 | 0.012028 | 0.012028 | 0.98362 | -0.3154 | 0.98388 | -0.31031 | 3.3045
11 | 0.0011886 | 0.00029769 | -0.0011885 | -0.00029787 | 1.8868e-08 | -1.8541e-07 | 0.0017981 | 0.0017982 | 0.0017982 | 0.98354 | -0.31694 | 0.98353 | -0.31727 | 0.494
12 | 0.0029143 | 0.00072982 | -0.0029142 | -0.00072991 | 8.5699e-08 | -9.4353e-08 | 0.0044089 | 0.0044089 | 0.0044089 | 0.98354 | -0.31694 | 0.98351 | -0.31756 | 1.2112
13 | 0.0022676 | 0.00056785 | -0.0022674 | -0.00056808 | 1.0482e-07 | -2.343e-07 | 0.0034306 | 0.0034307 | 0.0034307 | 0.98351 | -0.31756 | 0.98346 | -0.31853 | 0.94249
14 | 0.0012967 | 0.00032479 | -0.0012967 | -0.00032498 | 2.3254e-08 | -1.8954e-07 | 0.0019619 | 0.001962 | 0.001962 | 0.98346 | -0.31853 | 0.98344 | -0.31891 | 0.53901
15 | -0.0015832 | -0.0003968 | 0.0015833 | 0.00039621 | 1.1308e-07 | -5.8534e-07 | 0.0024038 | 0.0024036 | 0.0024038 | 0.98006 | -0.38418 | 0.98013 | -0.38268 | 0.66039
16 | -0.0081389 | -0.0020366 | 0.0081484 | 0.0020406 | 9.4365e-06 | 3.959e-06 | 0.012355 | 0.012354 | 0.012355 | 0.98013 | -0.38268 | 0.98137 | -0.35833 | 3.3943
17 | -0.0094658 | -0.0023708 | 0.0094661 | 0.0023709 | 2.1486e-07 | 1.0237e-07 | 0.014352 | 0.014352 | 0.014352 | 0.98137 | -0.35833 | 0.9814 | -0.35786 | 3.9429
18 | -0.019083 | -0.0047812 | 0.019092 | 0.0047866 | 9.0337e-06 | 5.4178e-06 | 0.028934 | 0.028934 | 0.028934 | 0.9814 | -0.35786 | 0.9819 | -0.34792 | 7.9489
19 | -0.1419 | -0.036004 | 0.14194 | 0.036029 | 3.8807e-05 | 2.472e-05 | 0.21345 | 0.21345 | 0.21345 | 0.98997 | -0.1915 | 0.99027 | -0.18582 | 29.3202
20 | 0.13404 | 0.034033 | -0.13323 | -0.033516 | 0.00080992 | 0.00051767 | 0.20163 | 0.20163 | 0.20163 | 0.98997 | -0.1915 | 0.98344 | -0.31791 | 55.3929
21 | -0.14863 | -0.037704 | 0.14863 | 0.037708 | 6.3832e-06 | 4.0458e-06 | 0.22349 | 0.22349 | 0.22349 | 0.99027 | -0.18582 | 0.99031 | -0.18492 | 20.4664
22 | 0.074349 | 0.018722 | -0.074259 | -0.018665 | 8.9907e-05 | 5.73e-05 | 0.11253 | 0.11253 | 0.11253 | 0.98344 | -0.31791 | 0.98214 | -0.34323 | 30.914
23 | 0.047428 | 0.011923 | -0.04736 | -0.01188 | 6.7873e-05 | 4.2994e-05 | 0.071775 | 0.071775 | 0.071775 | 0.98344 | -0.31791 | 0.9819 | -0.34792 | 19.7185
24 | -0.025072 | -0.0062893 | 0.025075 | 0.0062912 | 2.9471e-06 | 1.8161e-06 | 0.037841 | 0.037841 | 0.037841 | 0.98594 | -0.27021 | 0.98606 | -0.26775 | 10.396
25 | -0.030285 | -0.0075969 | 0.030294 | 0.0076029 | 9.6005e-06 | 5.9879e-06 | 0.045703 | 0.045703 | 0.045703 | 0.98606 | -0.26775 | 0.98641 | -0.2611 | 12.5559
26 | 0.018978 | 0.0047584 | -0.018974 | -0.004756 | 4.012e-06 | 2.404e-06 | 0.028755 | 0.028756 | 0.028756 | 0.98208 | -0.34503 | 0.98185 | -0.34946 | 7.8999
27 | -0.022261 | -0.0055812 | 0.022267 | 0.005585 | 6.2056e-06 | 3.7875e-06 | 0.03373 | 0.03373 | 0.03373 | 0.98208 | -0.34503 | 0.98238 | -0.33918 | 9.2664
28 | 0.012515 | 0.0031374 | -0.012513 | -0.003136 | 2.4868e-06 | 1.3585e-06 | 0.018967 | 0.018968 | 0.018968 | 0.98185 | -0.34946 | 0.98164 | -0.35364 | 5.2109
29 | -0.030903 | -0.0077493 | 0.030928 | 0.0077653 | 2.5648e-05 | 1.6019e-05 | 0.04681 | 0.04681 | 0.04681 | 0.98238 | -0.33918 | 0.98327 | -0.32178 | 12.86
30 | 0.0086358 | 0.0021643 | -0.0086348 | -0.0021638 | 1.0119e-06 | 4.4796e-07 | 0.013081 | 0.013081 | 0.013081 | 0.98238 | -0.33918 | 0.98225 | -0.34164 | 3.5936
31 | 0.0059618 | 0.0014942 | -0.0059618 | -0.0014942 | 6.7215e-08 | 1.5274e-08 | 0.0090373 | 0.0090373 | 0.0090373 | 0.98164 | -0.35364 | 0.98163 | -0.35387 | 2.4828
32 | -0.036221 | -0.0090918 | 0.03625 | 0.0091097 | 2.8495e-05 | 1.7916e-05 | 0.05482 | 0.05482 | 0.05482 | 0.98327 | -0.32178 | 0.98411 | -0.3053 | 15.0604
33 | 0.0038759 | 0.00097115 | -0.0038755 | -0.00097129 | 4.0612e-07 | -1.3766e-07 | 0.0058715 | 0.0058716 | 0.0058716 | 0.98225 | -0.34164 | 0.98214 | -0.34384 | 1.6131
34 | -0.051019 | -0.012813 | 0.051036 | 0.012824 | 1.6852e-05 | 1.0689e-05 | 0.077152 | 0.077152 | 0.077152 | 0.98411 | -0.3053 | 0.98447 | -0.29838 | 21.1956
35 | 0.014769 | 0.0037036 | -0.014764 | -0.0037005 | 5.4274e-06 | 3.1049e-06 | 0.022332 | 0.022332 | 0.022332 | 0.98411 | -0.3053 | 0.98372 | -0.31301 | 6.1353
36 | -0.053884 | -0.013538 | 0.053916 | 0.013558 | 3.1211e-05 | 1.9816e-05 | 0.081458 | 0.081458 | 0.081458 | 0.98447 | -0.29838 | 0.98509 | -0.28625 | 22.3786
37 | 0.011783 | 0.0029535 | -0.011782 | -0.0029529 | 1.1724e-06 | 6.254e-07 | 0.017824 | 0.017824 | 0.017824 | 0.98372 | -0.31301 | 0.98361 | -0.3151 | 4.8967
38 | 0.0076476 | 0.0019167 | -0.0076471 | -0.0019165 | 5.3937e-07 | 2.0674e-07 | 0.011526 | 0.011526 | 0.011526 | 0.98733 | -0.24287 | 0.98725 | -0.24435 | 3.1665
39 | -0.010557 | -0.002646 | 0.010559 | 0.0026471 | 2.2443e-06 | 1.134e-06 | 0.015911 | 0.015911 | 0.015911 | 0.98733 | -0.24287 | 0.98756 | -0.2384 | 4.3712
40 | 0.003574 | 0.00089573 | -0.003574 | -0.00089573 | 5.798e-09 | -3.102e-09 | 0.0053869 | 0.0053869 | 0.0053869 | 0.98725 | -0.24435 | 0.98725 | -0.24438 | 1.4799
41 | -0.016031 | -0.0040184 | 0.016032 | 0.0040192 | 1.3613e-06 | 7.9161e-07 | 0.024155 | 0.024155 | 0.024155 | 0.98756 | -0.2384 | 0.98765 | -0.23662 | 6.636
42 | -0.019326 | -0.0048447 | 0.01933 | 0.0048469 | 3.7058e-06 | 2.2225e-06 | 0.029118 | 0.029118 | 0.029118 | 0.98765 | -0.23662 | 0.98785 | -0.2326 | 7.9994
43 | -0.13532 | -0.034154 | 0.13582 | 0.034477 | 0.00050389 | 0.00032207 | 0.20392 | 0.20392 | 0.20392 | 0.98785 | -0.2326 | 0.99187 | -0.15517 | 56.0215
44 | 0.11599 | 0.029308 | -0.11586 | -0.029223 | 0.00013225 | 8.4493e-05 | 0.1748 | 0.1748 | 0.1748 | 0.98785 | -0.2326 | 0.98662 | -0.25641 | 48.0222
45 | -0.15019 | -0.038079 | 0.15026 | 0.038126 | 7.4482e-05 | 4.7467e-05 | 0.22547 | 0.22547 | 0.22547 | 0.99187 | -0.15517 | 0.99241 | -0.14486 | 30.9711
46 | 0.014365 | 0.0036023 | -0.014359 | -0.0035986 | 6.6583e-06 | 3.7682e-06 | 0.021552 | 0.021552 | 0.021552 | 0.99187 | -0.15517 | 0.99137 | -0.1649 | 5.9208
47 | 0.058719 | 0.014826 | -0.058665 | -0.014792 | 5.3484e-05 | 3.3998e-05 | 0.088598 | 0.088598 | 0.088598 | 0.98662 | -0.25641 | 0.98564 | -0.27544 | 24.3402
48 | 0.057138 | 0.014397 | -0.057057 | -0.014345 | 8.1424e-05 | 5.1739e-05 | 0.086202 | 0.086203 | 0.086203 | 0.98662 | -0.25641 | 0.98509 | -0.28625 | 23.682
49 | 0.0080966 | 0.0020292 | -0.0080964 | -0.0020291 | 1.9191e-07 | 7.9526e-08 | 0.012249 | 0.012249 | 0.012249 | 0.98361 | -0.3151 | 0.98358 | -0.3156 | 3.365
50 | 0.052945 | 0.013359 | -0.052826 | -0.013283 | 0.00011875 | 7.5372e-05 | 0.079963 | 0.079963 | 0.079963 | 0.98564 | -0.27544 | 0.98323 | -0.3224 | 21.9679
51 | 0.0087036 | 0.0021816 | -0.0087023 | -0.002181 | 1.3634e-06 | 6.0684e-07 | 0.013172 | 0.013172 | 0.013172 | 0.98323 | -0.3224 | 0.98306 | -0.32569 | 3.6188
52 | 0.044123 | 0.011102 | -0.044088 | -0.01108 | 3.4393e-05 | 2.1751e-05 | 0.066791 | 0.066791 | 0.066791 | 0.98323 | -0.3224 | 0.98239 | -0.33873 | 18.3492
53 | 0.042462 | 0.010674 | -0.042433 | -0.010655 | 2.9219e-05 | 1.8452e-05 | 0.063679 | 0.063679 | 0.063679 | 0.99241 | -0.14486 | 0.99166 | -0.15928 | 17.4941
54 | -0.19272 | -0.0488 | 0.19293 | 0.048929 | 0.00020286 | 0.00012908 | 0.28915 | 0.28915 | 0.28915 | 0.99241 | -0.14486 | 0.99355 | -0.12296 | 26.4788
55 | 0.0069867 | 0.001751 | -0.0069858 | -0.0017507 | 9.7752e-07 | 3.2004e-07 | 0.010487 | 0.010487 | 0.010487 | 0.99137 | -0.1649 | 0.99122 | -0.16784 | 2.881
56 | 0.038553 | 0.0096926 | -0.038515 | -0.009669 | 3.7478e-05 | 2.3615e-05 | 0.058406 | 0.058406 | 0.058406 | 0.98239 | -0.33873 | 0.98135 | -0.3591 | 16.0457
57 | 0.037315 | 0.0093726 | -0.037285 | -0.009354 | 2.9575e-05 | 1.8604e-05 | 0.055999 | 0.055999 | 0.055999 | 0.99166 | -0.15928 | 0.9908 | -0.1759 | 15.3844
58 | -0.19984 | -0.050661 | 0.20002 | 0.05078 | 0.00018641 | 0.00011865 | 0.2995 | 0.2995 | 0.2995 | 0.99355 | -0.12296 | 0.99456 | -0.10357 | 27.4265
59 | 0.0030358 | 0.00076073 | -0.0030357 | -0.00076081 | 8.6994e-08 | -8.8297e-08 | 0.0045573 | 0.0045573 | 0.0045573 | 0.99122 | -0.16784 | 0.99119 | -0.16844 | 1.252
60 | 0.21682 | 0.055287 | -0.21653 | -0.055098 | 0.00029664 | 0.00018896 | 0.32346 | 0.32346 | 0.32346 | 0.99849 | -0.028587 | 0.997 | -0.056967 | 29.621
61 | -0.22878 | -0.058284 | 0.22879 | 0.058286 | 3.5976e-06 | 2.2928e-06 | 0.34128 | 0.34128 | 0.34128 | 0.99849 | -0.028587 | 0.99851 | -0.028261 | 31.2528
62 | 0.21298 | 0.054208 | -0.21277 | -0.054079 | 0.00020138 | 0.00012826 | 0.31816 | 0.31816 | 0.31816 | 0.997 | -0.056967 | 0.99597 | -0.0766 | 29.1355
63 | -0.2333 | -0.059416 | 0.23361 | 0.059619 | 0.00031849 | 0.00020301 | 0.348 | 0.348 | 0.348 | 0.99851 | -0.028261 | 1 | 0 | 31.8683
64 | 0.20764 | 0.052793 | -0.20737 | -0.052622 | 0.0002694 | 0.00017155 | 0.31049 | 0.31049 | 0.31049 | 0.99597 | -0.0766 | 0.99456 | -0.10357 | 28.4334
65 | 0.2958 | 0.075665 | -0.29523 | -0.0753 | 0.00057196 | 0.00036513 | 0.4407 | 0.4407 | 0.4407 | 1 | 0 | 0.99789 | -0.040035 | 40.3575
66 | 0.28926 | 0.073803 | -0.28829 | -0.073182 | 0.00097261 | 0.00062084 | 0.4318 | 0.4318 | 0.4318 | 0.99789 | -0.040035 | 0.99422 | -0.1099 | 39.5421
67 | 0.20875 | 0.053066 | -0.20835 | -0.052808 | 0.00040584 | 0.00025845 | 0.3127 | 0.3127 | 0.3127 | 0.99422 | -0.1099 | 0.99211 | -0.15035 | 28.6353
68 | 0.079536 | 0.020116 | -0.079442 | -0.020056 | 9.3961e-05 | 5.9906e-05 | 0.1191 | 0.1191 | 0.1191 | 0.99422 | -0.1099 | 0.99294 | -0.13456 | 32.7208
69 | 0.035506 | 0.0089149 | -0.035506 | -0.0089146 | 4.7685e-07 | 2.9965e-07 | 0.053844 | 0.053844 | 0.053844 | 0.98135 | -0.3591 | 0.98133 | -0.35939 | 14.7924
70 | 0.030766 | 0.0077268 | -0.030727 | -0.007702 | 3.9701e-05 | 2.4795e-05 | 0.046657 | 0.046657 | 0.046657 | 0.98133 | -0.35939 | 0.97995 | -0.38647 | 12.818
71 | 0.018976 | 0.0047569 | -0.018974 | -0.0047558 | 1.8107e-06 | 1.0856e-06 | 0.028814 | 0.028814 | 0.028814 | 0.97995 | -0.38647 | 0.97985 | -0.38847 | 7.916
72 | -0.015087 | -0.0037814 | 0.015089 | 0.0037821 | 1.2169e-06 | 7.0097e-07 | 0.022914 | 0.022914 | 0.022914 | 0.97976 | -0.39016 | 0.97985 | -0.38847 | 6.2951
73 | 0.0095829 | 0.0024018 | -0.0095822 | -0.0024015 | 6.956e-07 | 3.3491e-07 | 0.014554 | 0.014554 | 0.014554 | 0.97976 | -0.39016 | 0.97969 | -0.39169 | 3.9984
74 | 0.005343 | 0.001339 | -0.0053427 | -0.001339 | 2.812e-07 | 3.6607e-08 | 0.0081153 | 0.0081154 | 0.0081154 | 0.97969 | -0.39169 | 0.97963 | -0.39279 | 2.2295
75 | 0.033872 | 0.0084987 | -0.033858 | -0.0084896 | 1.4378e-05 | 9.011e-06 | 0.050874 | 0.050874 | 0.050874 | 0.9908 | -0.1759 | 0.99035 | -0.18481 | 13.9763
76 | 0.025061 | 0.0062851 | -0.025053 | -0.00628 | 8.1719e-06 | 5.0323e-06 | 0.037656 | 0.037656 | 0.037656 | 0.99035 | -0.18481 | 0.98999 | -0.19165 | 10.3451
77 | 0.008797 | 0.0022046 | -0.0087966 | -0.0022044 | 4.4662e-07 | 1.9813e-07 | 0.013218 | 0.013218 | 0.013218 | 0.99035 | -0.18481 | 0.99029 | -0.18588 | 3.6312
78 | 0.0029331 | 0.00073509 | -0.0029331 | -0.0007351 | 1.1506e-08 | -1.2873e-08 | 0.0044119 | 0.0044119 | 0.0044119 | 0.98925 | -0.20589 | 0.98924 | -0.20597 | 1.2121
79 | -0.0056493 | -0.0014158 | 0.0056498 | 0.0014159 | 5.4166e-07 | 8.9811e-08 | 0.0084975 | 0.0084974 | 0.0084975 | 0.98925 | -0.20589 | 0.98935 | -0.20387 | 2.3345
80 | -0.0089934 | -0.0022539 | 0.0089942 | 0.0022542 | 7.1441e-07 | 3.235e-07 | 0.013526 | 0.013526 | 0.013526 | 0.98935 | -0.20387 | 0.98944 | -0.20221 | 3.716
81 | 0.008505 | 0.0021316 | -0.0085042 | -0.0021313 | 7.6588e-07 | 3.2984e-07 | 0.012791 | 0.012791 | 0.012791 | 0.98944 | -0.20221 | 0.98934 | -0.2041 | 3.5139
82 | -0.017499 | -0.0043859 | 0.017504 | 0.0043886 | 4.6568e-06 | 2.75e-06 | 0.026317 | 0.026317 | 0.026317 | 0.98944 | -0.20221 | 0.98973 | -0.19662 | 7.23
83 | 0.0028266 | 0.00070817 | -0.0028265 | -0.00070838 | 1.6362e-07 | -2.0644e-07 | 0.0042472 | 0.0042473 | 0.0042473 | 0.99029 | -0.18588 | 0.99023 | -0.18709 | 1.1668
84 | 0.017158 | 0.0043013 | -0.017157 | -0.0043009 | 6.5467e-07 | 3.8524e-07 | 0.025789 | 0.025789 | 0.025789 | 0.98999 | -0.19165 | 0.98995 | -0.19246 | 7.085
85 | 0.01366 | 0.0034244 | -0.013657 | -0.0034227 | 3.0261e-06 | 1.6907e-06 | 0.020533 | 0.020533 | 0.020533 | 0.98995 | -0.19246 | 0.98971 | -0.19711 | 5.6408
86 | 0.0078158 | 0.0019589 | -0.0078155 | -0.0019587 | 3.543e-07 | 1.3883e-07 | 0.011751 | 0.011751 | 0.011751 | 0.98971 | -0.19711 | 0.98966 | -0.19806 | 3.2283
87 | 0.049283 | 0.012393 | -0.049256 | -0.012376 | 2.761e-05 | 1.7499e-05 | 0.074197 | 0.074197 | 0.074197 | 0.98857 | -0.21905 | 0.98796 | -0.23079 | 20.3838
88 | -0.054267 | -0.013642 | 0.05432 | 0.013676 | 5.269e-05 | 3.3451e-05 | 0.081698 | 0.081698 | 0.081698 | 0.98857 | -0.21905 | 0.98962 | -0.19874 | 22.4446
89 | 0.041077 | 0.010326 | -0.041046 | -0.010306 | 3.1148e-05 | 1.9657e-05 | 0.061879 | 0.061879 | 0.061879 | 0.98796 | -0.23079 | 0.98715 | -0.24668 | 16.9998
90 | -0.05961 | -0.015002 | 0.059623 | 0.01501 | 1.2906e-05 | 8.2049e-06 | 0.089654 | 0.089654 | 0.089654 | 0.98962 | -0.19874 | 0.98985 | -0.19421 | 24.6302
91 | 0.0047287 | 0.001185 | -0.0047281 | -0.001185 | 5.4706e-07 | -1.6899e-08 | 0.0071279 | 0.0071281 | 0.0071281 | 0.98715 | -0.24668 | 0.98702 | -0.24911 | 1.9583
92 | 0.036317 | 0.0091214 | -0.036307 | -0.0091147 | 1.0614e-05 | 6.6721e-06 | 0.054751 | 0.054752 | 0.054752 | 0.98715 | -0.24668 | 0.98683 | -0.25281 | 15.0416
93 | -0.068147 | -0.017146 | 0.068219 | 0.017192 | 7.2107e-05 | 4.5913e-05 | 0.10247 | 0.10247 | 0.10247 | 0.98985 | -0.19421 | 0.991 | -0.17209 | 28.1503
94 | -0.01754 | -0.0043963 | 0.017541 | 0.0043974 | 1.8578e-06 | 1.1013e-06 | 0.026657 | 0.026657 | 0.026657 | 0.97908 | -0.40321 | 0.97919 | -0.40099 | 7.3234
95 | 0.010972 | 0.0027503 | -0.01097 | -0.0027492 | 1.9964e-06 | 1.037e-06 | 0.016675 | 0.016675 | 0.016675 | 0.97908 | -0.40321 | 0.97888 | -0.40703 | 4.5812
96 | -0.023927 | -0.0059977 | 0.023933 | 0.0060016 | 6.2455e-06 | 3.8386e-06 | 0.03636 | 0.03636 | 0.03636 | 0.97919 | -0.40099 | 0.97947 | -0.39551 | 9.9891
97 | 0.0048116 | 0.0012058 | -0.0048113 | -0.0012058 | 2.9227e-07 | 3.921e-09 | 0.0073142 | 0.0073142 | 0.0073142 | 0.97888 | -0.40703 | 0.97882 | -0.40831 | 2.0094
98 | 0.03389 | 0.008509 | -0.033877 | -0.0085006 | 1.3392e-05 | 8.3965e-06 | 0.051107 | 0.051107 | 0.051107 | 0.98683 | -0.25281 | 0.98641 | -0.2611 | 14.0404
99 | -0.073116 | -0.018419 | 0.073243 | 0.018501 | 0.00012763 | 8.1317e-05 | 0.10982 | 0.10982 | 0.10982 | 0.991 | -0.17209 | 0.99288 | -0.13566 | 30.1702
100 | -0.034854 | -0.0087386 | 0.034867 | 0.0087469 | 1.329e-05 | 8.3467e-06 | 0.052951 | 0.052951 | 0.052951 | 0.97947 | -0.39551 | 0.97988 | -0.38752 | 14.5471
101 | -0.044105 | -0.011062 | 0.044127 | 0.011076 | 2.2463e-05 | 1.4208e-05 | 0.06698 | 0.06698 | 0.06698 | 0.97988 | -0.38752 | 0.98042 | -0.37684 | 18.401
102 | 0.0035822 | 0.00089769 | -0.0035821 | -0.00089775 | 1.1364e-07 | -5.974e-08 | 0.0054038 | 0.0054038 | 0.0054038 | 0.98641 | -0.2611 | 0.98637 | -0.26176 | 1.4846
103 | -0.076228 | -0.019249 | 0.076232 | 0.019251 | 4.0357e-06 | 2.5722e-06 | 0.11429 | 0.11429 | 0.11429 | 0.99288 | -0.13566 | 0.99294 | -0.13456 | 31.3991
104 | 0.0050205 | 0.0012582 | -0.0050202 | -0.0012582 | 2.7483e-07 | 1.0851e-08 | 0.0075511 | 0.0075511 | 0.0075511 | 0.98934 | -0.2041 | 0.98928 | -0.20525 | 2.0745
105 | -0.019997 | -0.0050134 | 0.019997 | 0.0050137 | 5.1958e-07 | 3.1283e-07 | 0.030065 | 0.030065 | 0.030065 | 0.98973 | -0.19662 | 0.98975 | -0.19608 | 8.2596
106 | -0.022348 | -0.0056028 | 0.022356 | 0.0056079 | 8.3172e-06 | 5.0704e-06 | 0.033599 | 0.033599 | 0.033599 | 0.98975 | -0.19608 | 0.99016 | -0.18827 | 9.2305
107 | -0.025503 | -0.0063966 | 0.025505 | 0.0063979 | 2.2245e-06 | 1.3717e-06 | 0.038328 | 0.038328 | 0.038328 | 0.99016 | -0.18827 | 0.99025 | -0.18644 | 10.5296
108 | -0.031107 | -0.0078018 | 0.03112 | 0.0078101 | 1.3358e-05 | 8.3393e-06 | 0.046745 | 0.046745 | 0.046745 | 0.99025 | -0.18644 | 0.99071 | -0.17744 | 12.842
109 | 0.012695 | 0.0031827 | -0.012692 | -0.0031808 | 3.5152e-06 | 1.9178e-06 | 0.019068 | 0.019068 | 0.019068 | 0.99071 | -0.17744 | 0.99042 | -0.18325 | 5.2386
110 | -0.043815 | -0.010993 | 0.043872 | 0.011029 | 5.6655e-05 | 3.5809e-05 | 0.065813 | 0.065813 | 0.065813 | 0.99071 | -0.17744 | 0.99211 | -0.15035 | 18.0805
111 | 0.16447 | 0.041779 | -0.16436 | -0.041704 | 0.00011868 | 7.535e-05 | 0.24688 | 0.24688 | 0.24688 | 0.99211 | -0.15035 | 0.99133 | -0.16535 | 22.6085
112 | 0.16027 | 0.04068 | -0.16027 | -0.040679 | 1.8851e-06 | 1.1964e-06 | 0.24075 | 0.24075 | 0.24075 | 0.99133 | -0.16535 | 0.99132 | -0.1656 | 22.0468
113 | 0.0038819 | 0.00097277 | -0.0038817 | -0.00097284 | 1.9222e-07 | -7.0902e-08 | 0.0058321 | 0.0058322 | 0.0058322 | 0.99042 | -0.18325 | 0.99036 | -0.18429 | 1.6023
114 | 0.0029762 | 0.0007457 | -0.0029761 | -0.00074587 | 1.6709e-07 | -1.685e-07 | 0.0045168 | 0.0045169 | 0.0045169 | 0.98048 | -0.37581 | 0.98042 | -0.37699 | 1.2409
115 | -0.0073002 | -0.0018294 | 0.007301 | 0.0018297 | 7.9813e-07 | 2.9209e-07 | 0.011079 | 0.011079 | 0.011079 | 0.98048 | -0.37581 | 0.9806 | -0.37352 | 3.0437
116 | 0.0069635 | 0.0017453 | -0.0069632 | -0.0017451 | 3.4736e-07 | 1.1767e-07 | 0.010567 | 0.010567 | 0.010567 | 0.9806 | -0.37352 | 0.98054 | -0.37456 | 2.903
117 | -0.014265 | -0.003575 | 0.014269 | 0.0035774 | 4.2348e-06 | 2.4061e-06 | 0.021646 | 0.021646 | 0.021646 | 0.9806 | -0.37352 | 0.98092 | -0.36729 | 5.9467
118 | 0.15347 | 0.038975 | -0.15333 | -0.038885 | 0.00014258 | 9.0425e-05 | 0.23055 | 0.23055 | 0.23055 | 0.99132 | -0.1656 | 0.99031 | -0.18492 | 21.1124
119 | -0.01827 | -0.00458 | 0.018274 | 0.0045827 | 4.5284e-06 | 2.6996e-06 | 0.027715 | 0.027715 | 0.027715 | 0.98092 | -0.36729 | 0.98118 | -0.36209 | 7.6139
120 | -0.022857 | -0.0057312 | 0.022866 | 0.0057369 | 9.2411e-06 | 5.6551e-06 | 0.034664 | 0.034664 | 0.034664 | 0.98118 | -0.36209 | 0.98161 | -0.35361 | 9.5232
121 | -0.02826 | -0.0070888 | 0.028268 | 0.0070936 | 7.6598e-06 | 4.7616e-06 | 0.042842 | 0.042842 | 0.042842 | 0.98161 | -0.35361 | 0.9819 | -0.34792 | 11.7697
122 | 0.066661 | 0.016761 | -0.066613 | -0.01673 | 4.7955e-05 | 3.0533e-05 | 0.10102 | 0.10102 | 0.10102 | 0.98214 | -0.34323 | 0.98137 | -0.35831 | 27.7516
123 | -0.049445 | -0.012409 | 0.049453 | 0.012414 | 8.0037e-06 | 5.0746e-06 | 0.07505 | 0.07505 | 0.07505 | 0.98042 | -0.37684 | 0.9806 | -0.37344 | 20.6182
124 | -0.054877 | -0.013773 | 0.054916 | 0.013799 | 3.9645e-05 | 2.518e-05 | 0.08328 | 0.08328 | 0.08328 | 0.9806 | -0.37344 | 0.98137 | -0.35831 | 22.8792

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53409 | 0.13604

## res_load
| p_mw | q_mvar
0 | 0.00080778 | 0.00020245
1 | 0.001596 | 0.00039999
2 | 0.0014441 | 0.00036193
3 | 0.003769 | 0.00094461
4 | 0.00083447 | 0.00020914
5 | 0.0058242 | 0.0014597
6 | 0.0038937 | 0.00097586
7 | 0.00073113 | 0.00018324
8 | 0.0011303 | 0.00028328
9 | 0.0011885 | 0.00029787
10 | 0.00064666 | 0.00016207
11 | 0.00097073 | 0.00024329
12 | 0.0012967 | 0.00032498
13 | 0.0015832 | 0.0003968
14 | 0.0019468 | 0.00048792
15 | 0.0013175 | 0.00033019
16 | 0.0096172 | 0.0024103
17 | 0.0078646 | 0.0019711
18 | 0.0066829 | 0.0016749
19 | 0.011452 | 0.0028702
20 | 0.0055152 | 0.0013822
21 | 0.0052099 | 0.0013057
22 | 0.003283 | 0.00082279
23 | 0.0064586 | 0.0016187
24 | 0.006551 | 0.0016418
25 | 0.0052927 | 0.0013265
26 | 0.0047589 | 0.0011927
27 | 0.0059618 | 0.0014942
28 | 0.0038755 | 0.00097129
29 | 0.0028488 | 0.00071399
30 | 0.0029805 | 0.00074699
31 | 0.0029096 | 0.00072923
32 | 0.004073 | 0.0010208
33 | 0.0054715 | 0.0013713
34 | 0.003574 | 0.00089573
35 | 0.0032938 | 0.0008255
36 | 0.0036854 | 0.00092364
37 | 0.0080964 | 0.0020291
38 | 0.003141 | 0.00078722
39 | 0.0057202 | 0.0014336
40 | 0.0073719 | 0.0018476
41 | 0.0087023 | 0.002181
42 | 0.0055355 | 0.0013873
43 | 0.0051178 | 0.0012827
44 | 0.0069103 | 0.0017319
45 | 0.00395 | 0.00098996
46 | 0.011958 | 0.0029969
47 | 0.0035521 | 0.00089024
48 | 0.0045102 | 0.0011304
49 | 0.0051321 | 0.0012862
50 | 0.0030194 | 0.00075675
51 | 0.0073491 | 0.0018419
52 | 0.0059714 | 0.0014966
53 | 0.0030088 | 0.00075408
54 | 0.0047398 | 0.0011879
55 | 0.011751 | 0.002945
56 | 0.0055045 | 0.0013795
57 | 0.0038853 | 0.00097375
58 | 0.0042392 | 0.0010625
59 | 0.0034128 | 0.00085534
60 | 0.0053427 | 0.001339
61 | 0.0027162 | 0.00068073
62 | 0.0029331 | 0.0007351
63 | 0.0033437 | 0.000838
64 | 0.0059699 | 0.0014962
65 | 0.0028265 | 0.00070838
66 | 0.0078952 | 0.0019787
67 | 0.0034972 | 0.00087649
68 | 0.0058409 | 0.0014639
69 | 0.0049835 | 0.001249
70 | 0.0081784 | 0.0020497
71 | 0.0052909 | 0.001326
72 | 0.0085235 | 0.0021362
73 | 0.0065677 | 0.001646
74 | 0.0063854 | 0.0016003
75 | 0.0061583 | 0.0015434
76 | 0.0047281 | 0.001185
77 | 0.0024169 | 0.00060574
78 | 0.0048967 | 0.0012272
79 | 0.010921 | 0.002737
80 | 0.0092378 | 0.0023152
81 | 0.0029849 | 0.0007481
82 | 0.0034837 | 0.0008731
83 | 0.0024929 | 0.00062479
84 | 0.0050202 | 0.0012582
85 | 0.0023506 | 0.00058913
86 | 0.0030357 | 0.00076081
87 | 0.0048113 | 0.0012058
88 | 0.0035821 | 0.00089775
89 | 0.0031468 | 0.00078865
90 | 0.0056014 | 0.0014038
91 | 0.0032102 | 0.00080454
92 | 0.0040862 | 0.0010241
93 | 0.00881 | 0.002208
94 | 0.0078155 | 0.0019587
95 | 0.0038817 | 0.00097284
96 | 0.004324 | 0.0010837
97 | 0.0029761 | 0.00074587
98 | 0.0067982 | 0.0017038
99 | 0.0069632 | 0.0017451
100 | 0.0040007 | 0.0010027
101 | 0.0046948 | 0.0011766
102 | 0.0045826 | 0.0011485
103 | 0.0053944 | 0.001352
104 | 0.0075978 | 0.0019042
105 | 0.0053177 | 0.0013327
106 | 0.0054234 | 0.0013592
107 | 0.011697 | 0.0029315

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1