## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1345-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1345-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1345-2_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1345-2_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1345-2_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1345-2_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1345-2_0_3_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1345-2_0_3_node_37 | 0.4 | n |  | TRUE
8 | bus_LV_1345-2_0_3_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1345-2_0_3_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1345-2_0_3_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1345-2_0_3_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_1345-2_0_3_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_1345-2_0_3_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1345-2_0_3_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_1345-2_0_3_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_1345-2_0_3_node_46 | 0.4 | n |  | TRUE
17 | bus_LV_1345-2_0_3_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1345-2_0_3_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_1345-2_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1345-2_0_3_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_1345-2_0_3_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_1345-2_0_3_node_47 | 0.4 | n |  | TRUE
23 | bus_LV_1345-2_0_3_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_1345-2_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1345-2_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_1345-2_0_3_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_1345-2_0_3_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_1345-2_0_3_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1345-2_0_3_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_1345-2_0_3_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_1345-2_0_3_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_1345-2_0_3_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_1345-2_0_3_node_129 | 0.4 | n |  | TRUE
34 | bus_LV_1345-2_0_3_node_128 | 0.4 | n |  | TRUE
35 | bus_LV_1345-2_0_3_node_54 | 0.4 | n |  | TRUE
36 | bus_LV_1345-2_0_3_node_55 | 0.4 | n |  | TRUE
37 | bus_LV_1345-2_0_3_node_56 | 0.4 | n |  | TRUE
38 | bus_LV_1345-2_0_3_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_1345-2_0_3_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_1345-2_0_3_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_1345-2_0_3_node_58 | 0.4 | n |  | TRUE
42 | bus_LV_1345-2_0_3_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_1345-2_0_3_node_62 | 0.4 | n |  | TRUE
44 | bus_LV_1345-2_0_3_node_48 | 0.4 | n |  | TRUE
45 | bus_LV_1345-2_0_3_node_136 | 0.4 | n |  | TRUE
46 | bus_LV_1345-2_0_3_node_168 | 0.4 | n |  | TRUE
47 | bus_LV_1345-2_0_3_node_59 | 0.4 | n |  | TRUE
48 | bus_LV_1345-2_0_3_node_60 | 0.4 | n |  | TRUE
49 | bus_LV_1345-2_0_3_node_61 | 0.4 | n |  | TRUE
50 | bus_LV_1345-2_0_3_node_180 | 0.4 | n |  | TRUE
51 | bus_LV_1345-2_0_3_node_123 | 0.4 | n |  | TRUE
52 | bus_LV_1345-2_0_3_node_101 | 0.4 | n |  | TRUE
53 | bus_LV_1345-2_0_3_node_102 | 0.4 | n |  | TRUE
54 | bus_LV_1345-2_0_3_node_103 | 0.4 | n |  | TRUE
55 | bus_LV_1345-2_0_3_node_104 | 0.4 | n |  | TRUE
56 | bus_LV_1345-2_0_3_node_108 | 0.4 | n |  | TRUE
57 | bus_LV_1345-2_0_3_node_105 | 0.4 | n |  | TRUE
58 | bus_LV_1345-2_0_3_node_106 | 0.4 | n |  | TRUE
59 | bus_LV_1345-2_0_3_node_107 | 0.4 | n |  | TRUE
60 | bus_LV_1345-2_0_3_node_110 | 0.4 | n |  | TRUE
61 | bus_LV_1345-2_0_3_node_111 | 0.4 | n |  | TRUE
62 | bus_LV_1345-2_0_3_node_170 | 0.4 | n |  | TRUE
63 | bus_LV_1345-2_0_3_node_130 | 0.4 | n |  | TRUE
64 | bus_LV_1345-2_0_3_node_131 | 0.4 | n |  | TRUE
65 | bus_LV_1345-2_0_3_node_132 | 0.4 | n |  | TRUE
66 | bus_LV_1345-2_0_3_node_133 | 0.4 | n |  | TRUE
67 | bus_LV_1345-2_0_3_node_137 | 0.4 | n |  | TRUE
68 | bus_LV_1345-2_0_3_node_134 | 0.4 | n |  | TRUE
69 | bus_LV_1345-2_0_3_node_135 | 0.4 | n |  | TRUE
70 | bus_LV_1345-2_0_3_node_140 | 0.4 | n |  | TRUE
71 | bus_LV_1345-2_0_3_node_138 | 0.4 | n |  | TRUE
72 | bus_LV_1345-2_0_3_node_141 | 0.4 | n |  | TRUE
73 | bus_LV_1345-2_0_3_node_142 | 0.4 | n |  | TRUE
74 | bus_LV_1345-2_0_3_node_143 | 0.4 | n |  | TRUE
75 | bus_LV_1345-2_0_3_node_169 | 0.4 | n |  | TRUE
76 | bus_LV_1345-2_0_3_node_171 | 0.4 | n |  | TRUE
77 | bus_LV_1345-2_0_3_node_181 | 0.4 | n |  | TRUE
78 | bus_LV_1345-2_0_3_node_183 | 0.4 | n |  | TRUE
79 | bus_LV_1345-2_0_3_node_184 | 0.4 | n |  | TRUE
80 | bus_LV_1345-2_0_3_node_182 | 0.4 | n |  | TRUE
81 | bus_MV_20_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1345-2_0_3_load_0 | 0 | 0.013579 | 0.0034031 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1345-2_0_3_load_1 | 1 | 0.02187 | 0.0054812 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1345-2_0_3_load_2 | 2 | 0.0039388 | 0.00098716 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1345-2_0_3_load_3 | 3 | 0.0075047 | 0.0018809 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1345-2_0_3_load_4 | 4 | 0.0072381 | 0.001814 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1345-2_0_3_load_5 | 5 | 0.0041687 | 0.0010448 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1345-2_0_3_load_37 | 7 | 0.0039171 | 0.00098172 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1345-2_0_3_load_10 | 8 | 0.012721 | 0.0031883 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1345-2_0_3_load_13 | 9 | 0.0057974 | 0.001453 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1345-2_0_3_load_14 | 10 | 0.0034818 | 0.00087261 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1345-2_0_3_load_15 | 11 | 0.0011473 | 0.00028753 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1345-2_0_3_load_16 | 12 | 0.0017731 | 0.00044438 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1345-2_0_3_load_17 | 13 | 0.0018978 | 0.00047563 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1345-2_0_3_load_20 | 14 | 0.00022901 | 5.7395e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1345-2_0_3_load_19 | 15 | 0.0014375 | 0.00036027 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1345-2_0_3_load_46 | 16 | 0.0038186 | 0.00095704 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1345-2_0_3_load_24 | 19 | 0.0011361 | 0.00028474 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1345-2_0_3_load_25 | 20 | 0.0011907 | 0.00029842 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1345-2_0_3_load_32 | 21 | 0.00084564 | 0.00021194 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1345-2_0_3_load_26 | 23 | 0.0053486 | 0.0013405 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1345-2_0_3_load_27 | 24 | 0.032468 | 0.0081371 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1345-2_0_3_load_28 | 25 | 0.0057749 | 0.0014473 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1345-2_0_3_load_30 | 26 | 0.0057753 | 0.0014474 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1345-2_0_3_load_31 | 28 | 0.0045964 | 0.001152 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1345-2_0_3_load_33 | 29 | 0.00072781 | 0.00018241 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1345-2_0_3_load_34 | 30 | 0.0065463 | 0.0016407 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1345-2_0_3_load_129 | 33 | 0.0069184 | 0.0017339 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1345-2_0_3_load_128 | 34 | 0.0045646 | 0.001144 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1345-2_0_3_load_54 | 35 | 0.015526 | 0.0038913 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1345-2_0_3_load_55 | 36 | 0.0029339 | 0.0007353 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1345-2_0_3_load_39 | 39 | 0.00022418 | 5.6186e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1345-2_0_3_load_40 | 40 | 0.011297 | 0.0028314 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1345-2_0_3_load_42 | 42 | 0.005775 | 0.0014474 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1345-2_0_3_load_62 | 43 | 0.00022418 | 5.6185e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1345-2_0_3_load_48 | 44 | 0.0019933 | 0.00049956 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1345-2_0_3_load_59 | 47 | 0.00022417 | 5.6182e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1345-2_0_3_load_180 | 50 | 0.0056155 | 0.0014074 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1345-2_0_3_load_123 | 51 | 0.0049566 | 0.0012422 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1345-2_0_3_load_101 | 52 | 0.00071113 | 0.00017823 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1345-2_0_3_load_102 | 53 | 0.00017108 | 4.2876e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1345-2_0_3_load_108 | 56 | 0.0009583 | 0.00024017 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1345-2_0_3_load_105 | 57 | 0.00060923 | 0.00015269 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1345-2_0_3_load_106 | 58 | 0.0004619 | 0.00011576 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1345-2_0_3_load_107 | 59 | 0.00030726 | 7.7006e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1345-2_0_3_load_110 | 60 | 0.0011244 | 0.0002818 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1345-2_0_3_load_111 | 61 | 0.0016635 | 0.00041691 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1345-2_0_3_load_170 | 62 | 0.0015356 | 0.00038485 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1345-2_0_3_load_131 | 64 | 0.0032273 | 0.00080883 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1345-2_0_3_load_132 | 65 | 0.0021317 | 0.00053425 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1345-2_0_3_load_133 | 66 | 0.0011826 | 0.00029638 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1345-2_0_3_load_137 | 67 | 0.0034793 | 0.00087201 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1345-2_0_3_load_134 | 68 | 0.0010919 | 0.00027365 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1345-2_0_3_load_135 | 69 | 0.00071444 | 0.00017906 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1345-2_0_3_load_140 | 70 | 0.0026731 | 0.00066995 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1345-2_0_3_load_138 | 71 | 0.0063183 | 0.0015835 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1345-2_0_3_load_141 | 72 | 0.0058612 | 0.001469 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1345-2_0_3_load_142 | 73 | 0.0046389 | 0.0011626 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1345-2_0_3_load_143 | 74 | 0.045832 | 0.011487 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1345-2_0_3_load_171 | 76 | 0.0011123 | 0.00027877 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1345-2_0_3_load_183 | 78 | 0.0015394 | 0.00038581 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1345-2_0_3_load_184 | 79 | 0.0010554 | 0.00026452 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1345-2_0_3_load_182 | 80 | 0.0002392 | 5.995e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1345-2_0_3_line_0 |  | 0 | 1 | 0.019862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1345-2_0_3_line_1 |  | 0 | 2 | 0.018712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1345-2_0_3_line_2 |  | 1 | 3 | 0.016025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1345-2_0_3_line_3 |  | 2 | 4 | 0.036359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1345-2_0_3_line_4 |  | 2 | 5 | 0.037992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1345-2_0_3_line_5 |  | 4 | 6 | 0.027295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1345-2_0_3_line_6 |  | 5 | 7 | 0.0040778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1345-2_0_3_line_7 |  | 6 | 9 | 0.024353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1345-2_0_3_line_8 |  | 6 | 8 | 0.0332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1345-2_0_3_line_9 |  | 7 | 38 | 0.046451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1345-2_0_3_line_10 |  | 9 | 10 | 0.026237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1345-2_0_3_line_11 |  | 11 | 12 | 0.022855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1345-2_0_3_line_12 |  | 11 | 13 | 0.060609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1345-2_0_3_line_13 |  | 12 | 14 | 0.20711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1345-2_0_3_line_14 |  | 13 | 15 | 0.015569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1345-2_0_3_line_15 |  | 15 | 16 | 0.0014592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1345-2_0_3_line_16 |  | 16 | 22 | 0.007023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1345-2_0_3_line_17 |  | 17 | 18 | 0.006231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1345-2_0_3_line_18 |  | 17 | 19 | 0.0336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1345-2_0_3_line_19 |  | 17 | 20 | 0.0096282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1345-2_0_3_line_20 |  | 18 | 21 | 0.032299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1345-2_0_3_line_21 |  | 19 | 22 | 0.00432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1345-2_0_3_line_22 |  | 21 | 29 | 0.039816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1345-2_0_3_line_23 |  | 22 | 44 | 0.039389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1345-2_0_3_line_24 |  | 23 | 24 | 0.023538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1345-2_0_3_line_25 |  | 23 | 25 | 0.02218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1345-2_0_3_line_26 |  | 25 | 26 | 0.0028349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1345-2_0_3_line_27 |  | 26 | 27 | 0.025803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1345-2_0_3_line_28 |  | 27 | 42 | 0.0034643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1345-2_0_3_line_29 |  | 27 | 28 | 0.048318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1345-2_0_3_line_30 |  | 29 | 30 | 0.079924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1345-2_0_3_line_31 |  | 30 | 31 | 0.040266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1345-2_0_3_line_32 |  | 31 | 35 | 0.044394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1345-2_0_3_line_33 |  | 31 | 36 | 0.044272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1345-2_0_3_line_34 |  | 31 | 37 | 0.010927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1345-2_0_3_line_35 |  | 32 | 33 | 0.098872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1345-2_0_3_line_36 |  | 32 | 34 | 0.062248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1345-2_0_3_line_37 |  | 33 | 63 | 0.014243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1345-2_0_3_line_38 |  | 34 | 40 | 0.03008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1345-2_0_3_line_39 |  | 36 | 45 | 0.019342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1345-2_0_3_line_40 |  | 37 | 46 | 0.00395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1345-2_0_3_line_41 |  | 38 | 39 | 0.035361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1345-2_0_3_line_42 |  | 38 | 40 | 0.035149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_1345-2_0_3_line_43 |  | 39 | 41 | 0.023605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1345-2_0_3_line_44 |  | 41 | 47 | 0.022334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1345-2_0_3_line_45 |  | 41 | 48 | 0.071959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1345-2_0_3_line_46 |  | 42 | 43 | 0.0028247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1345-2_0_3_line_47 |  | 43 | 47 | 0.032596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1345-2_0_3_line_48 |  | 45 | 70 | 0.018868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1345-2_0_3_line_49 |  | 45 | 69 | 0.060547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_1345-2_0_3_line_50 |  | 46 | 75 | 0.14696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1345-2_0_3_line_51 |  | 46 | 76 | 0.002306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1345-2_0_3_line_52 |  | 48 | 49 | 0.09885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1345-2_0_3_line_53 |  | 48 | 50 | 0.023697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1345-2_0_3_line_54 |  | 49 | 51 | 0.15191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1345-2_0_3_line_55 |  | 50 | 77 | 0.004549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1345-2_0_3_line_56 |  | 52 | 53 | 0.018192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1345-2_0_3_line_57 |  | 53 | 54 | 0.0087962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1345-2_0_3_line_58 |  | 54 | 55 | 0.072826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1345-2_0_3_line_59 |  | 55 | 56 | 0.2213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1345-2_0_3_line_60 |  | 55 | 57 | 0.0018281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1345-2_0_3_line_61 |  | 56 | 60 | 0.019829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1345-2_0_3_line_62 |  | 57 | 58 | 0.0023837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1345-2_0_3_line_63 |  | 58 | 59 | 0.012637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1345-2_0_3_line_64 |  | 60 | 61 | 0.0005438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1345-2_0_3_line_65 |  | 61 | 62 | 0.010404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1345-2_0_3_line_66 |  | 62 | 75 | 0.01966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1345-2_0_3_line_67 |  | 63 | 64 | 0.013194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_1345-2_0_3_line_68 |  | 63 | 65 | 0.023216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1345-2_0_3_line_69 |  | 64 | 66 | 0.0083099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_1345-2_0_3_line_70 |  | 65 | 67 | 0.022561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1345-2_0_3_line_71 |  | 66 | 68 | 0.020119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_1345-2_0_3_line_72 |  | 67 | 71 | 0.021895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1345-2_0_3_line_73 |  | 68 | 69 | 0.0070165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_1345-2_0_3_line_74 |  | 71 | 72 | 2.8869e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1345-2_0_3_line_75 |  | 72 | 73 | 0.0068461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1345-2_0_3_line_76 |  | 73 | 74 | 0.0089284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1345-2_0_3_line_77 |  | 77 | 78 | 0.011235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1345-2_0_3_line_78 |  | 77 | 79 | 0.032435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1345-2_0_3_line_79 |  | 79 | 80 | 0.0063595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1345-2_0_3_trafo_37 | 0.63 MVA 20/0.4 kV | 81 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2716276.8249 | 1225845.0363 | 2716295.9569 | 1225839.6993
1 | 2716260.1225 | 1225853.4721 | 2716276.8249 | 1225845.0363
2 | 2716311.3927 | 1225835.3933 | 2716295.9569 | 1225839.6993
3 | 2716260.1225 | 1225853.4721 | 2716265.9193 | 1225863.7489 | 2716272.3824 | 1225875.2396 | 2716277.1995 | 1225885.5454
4 | 2716260.1225 | 1225853.4721 | 2716242.7907 | 1225822.3428 | 2716241.4948 | 1225820.3667
5 | 2716293.4609 | 1225907.0761 | 2716286.0777 | 1225899.6038 | 2716281.1161 | 1225893.9247 | 2716277.1995 | 1225885.5454
6 | 2716239.2585 | 1225816.9568 | 2716241.4948 | 1225820.3667
7 | 2716293.4609 | 1225907.0761 | 2716282.7196 | 1225910.4133 | 2716270.5439 | 1225915.2608
8 | 2716293.4609 | 1225907.0761 | 2716325.2344 | 1225897.4472
9 | 2716207.0192 | 1225786.105 | 2716215.9375 | 1225788.759 | 2716224.8468 | 1225794.9823 | 2716239.2585 | 1225816.9568
10 | 2716246.168 | 1225924.9655 | 2716270.5439 | 1225915.2608
11 | 2715987.0711 | 1225537.1396 | 2715993.0467 | 1225539.5847 | 2716007.5262 | 1225547.2833
12 | 2716062.7731 | 1225572.0089 | 2716051.5348 | 1225567.502 | 2716027.2622 | 1225557.7768 | 2716007.5262 | 1225547.2833
13 | 2715987.0711 | 1225537.1396 | 2715826.9894 | 1225668.5412
14 | 2716076.2767 | 1225579.6577 | 2716066.5452 | 1225573.5216 | 2716062.7731 | 1225572.0089
15 | 2716076.2767 | 1225579.6577 | 2716077.511 | 1225580.436
16 | 2716083.4516 | 1225584.1818 | 2716077.511 | 1225580.436
17 | 2716113.1924 | 1225616.3757 | 2716109.6913 | 1225611.2146
18 | 2716109.6913 | 1225611.2146 | 2716103.3603 | 1225601.8616 | 2716086.6818 | 1225587.0503
19 | 2716109.6913 | 1225611.2146 | 2716119.1348 | 1225609.3375
20 | 2716113.1924 | 1225616.3757 | 2716144.8386 | 1225609.9147
21 | 2716083.4516 | 1225584.1818 | 2716086.6818 | 1225587.0503
22 | 2716144.8386 | 1225609.9147 | 2716183.8496 | 1225601.9501
23 | 2716083.4516 | 1225584.1818 | 2716072.2889 | 1225585.7764 | 2716044.6792 | 1225591.6314
24 | 2716210.9129 | 1225909.6694 | 2716210.2698 | 1225913.1002 | 2716193.5175 | 1225924.1113
25 | 2716210.9129 | 1225909.6694 | 2716211.6073 | 1225905.9652 | 2716202.0878 | 1225890.2054
26 | 2716200.6221 | 1225887.7788 | 2716202.0878 | 1225890.2054
27 | 2716187.2811 | 1225865.6924 | 2716200.6221 | 1225887.7788
28 | 2716187.2811 | 1225865.6924 | 2716185.4901 | 1225862.727
29 | 2716187.2811 | 1225865.6924 | 2716146.382 | 1225891.4199
30 | 2716262.159 | 1225585.9663 | 2716192.8264 | 1225600.1174 | 2716183.8496 | 1225601.9501
31 | 2716301.6119 | 1225577.9139 | 2716262.159 | 1225585.9663
32 | 2716301.6119 | 1225577.9139 | 2716312.5799 | 1225575.0371 | 2716344.9227 | 1225568.2112
33 | 2716301.6119 | 1225577.9139 | 2716306.4305 | 1225595.9554 | 2716308.8633 | 1225601.0624 | 2716320.3971 | 1225617.3303
34 | 2716298.9757 | 1225567.3097 | 2716301.6119 | 1225577.9139
35 | 2716132.9128 | 1225684.4576 | 2716187.8841 | 1225702.0998 | 2716200.8212 | 1225704.3763 | 2716228.4913 | 1225700.0689
36 | 2716132.9128 | 1225684.4576 | 2716141.7589 | 1225692.7589 | 2716163.198 | 1225717.8523 | 2716174.1035 | 1225731.0394
37 | 2716241.9722 | 1225695.473 | 2716228.4913 | 1225700.0689
38 | 2716174.1035 | 1225731.0394 | 2716188.0137 | 1225747.8599 | 2716192.813 | 1225754.5737
39 | 2716331.584 | 1225633.1091 | 2716320.3971 | 1225617.3303
40 | 2716298.0193 | 1225563.477 | 2716298.9757 | 1225567.3097
41 | 2716207.0192 | 1225786.105 | 2716196.7479 | 1225788.2728 | 2716186.7001 | 1225794.1368 | 2716176.2596 | 1225802.2619
42 | 2716207.0192 | 1225786.105 | 2716205.1735 | 1225776.1724 | 2716200.9524 | 1225765.9599 | 2716192.813 | 1225754.5737
43 | 2716155.6316 | 1225813.2896 | 2716169.0679 | 1225807.8587 | 2716176.2596 | 1225802.2619
44 | 2716155.6316 | 1225813.2896 | 2716167.1781 | 1225832.4073
45 | 2716155.6316 | 1225813.2896 | 2716144.4441 | 1225816.5626 | 2716112.2016 | 1225823.2386 | 2716097.8787 | 1225799.9078
46 | 2716184.0298 | 1225860.3091 | 2716185.4901 | 1225862.727
47 | 2716167.1781 | 1225832.4073 | 2716184.0298 | 1225860.3091
48 | 2716331.584 | 1225633.1091 | 2716337.7074 | 1225628.6364 | 2716342.8897 | 1225623.8229 | 2716345.4661 | 1225620.49
49 | 2716331.584 | 1225633.1091 | 2716283.0816 | 1225667.7658 | 2716282.3063 | 1225668.2884
50 | 2716298.0193 | 1225563.477 | 2716310.327 | 1225561.894 | 2716314.6298 | 1225565.214 | 2716328.5992 | 1225561.6399 | 2716333.5647 | 1225551.6292 | 2716365.1307 | 1225546.2866 | 2716355.2128 | 1225538.5089 | 2716344.7978 | 1225530.1655 | 2716337.9082 | 1225526.8949 | 2716330.8234 | 1225525.4664 | 2716313.3561 | 1225525.6585 | 2716300.1814 | 1225526.9799
51 | 2716298.0193 | 1225563.477 | 2716295.7246 | 1225563.2492
52 | 2716051.2821 | 1225854.3856 | 2716060.5304 | 1225841.3003 | 2716071.3065 | 1225833.8491 | 2716081.079 | 1225830.0368 | 2716088.1868 | 1225828.3296 | 2716112.2016 | 1225823.2386 | 2716097.8787 | 1225799.9078
53 | 2716097.8787 | 1225799.9078 | 2716085.3513 | 1225779.7927
54 | 2716051.2821 | 1225854.3856 | 2716162.7438 | 1225946.8317 | 2716167.8317 | 1225951.7766
55 | 2716082.9465 | 1225775.9313 | 2716085.3513 | 1225779.7927
56 | 2716135.7158 | 1225389.9308 | 2716143.4039 | 1225393.4262 | 2716144.4204 | 1225396.5151 | 2716142.2779 | 1225402.6462
57 | 2716139.3763 | 1225410.95 | 2716142.2779 | 1225402.6462
58 | 2716067.6336 | 1225419.4571 | 2716074.0907 | 1225416.5363 | 2716084.3896 | 1225414.1464 | 2716107.0045 | 1225410.1512 | 2716133.7542 | 1225410.3287 | 2716139.3763 | 1225410.95
59 | 2716067.6336 | 1225419.4571 | 2716068.7561 | 1225425.2724 | 2716085.5768 | 1225446.9505 | 2716098.9028 | 1225461.1881 | 2716111.6445 | 1225469.621 | 2716133.5144 | 1225480.078 | 2716152.974 | 1225491.2553 | 2716177.567 | 1225509.0379 | 2716196.8798 | 1225519.9567 | 2716217.5185 | 1225524.7189 | 2716240.4791 | 1225529.0151 | 2716249.8651 | 1225529.4896
60 | 2716067.6336 | 1225419.4571 | 2716067.2854 | 1225417.6624
61 | 2716269.6626 | 1225529.2467 | 2716258.4102 | 1225529.9216 | 2716249.8651 | 1225529.4896
62 | 2716067.2854 | 1225417.6624 | 2716066.8315 | 1225415.3223
63 | 2716066.8315 | 1225415.3223 | 2716066.2349 | 1225412.2465 | 2716062.6122 | 1225403.4605
64 | 2716269.6626 | 1225529.2467 | 2716270.2055 | 1225529.2141
65 | 2716270.2055 | 1225529.2141 | 2716280.5912 | 1225528.5912
66 | 2716300.1814 | 1225526.9799 | 2716289.309 | 1225528.0683 | 2716280.5912 | 1225528.5912
67 | 2716241.9722 | 1225695.473 | 2716252.9133 | 1225688.0989
68 | 2716241.9722 | 1225695.473 | 2716253.935 | 1225715.3697
69 | 2716252.9133 | 1225688.0989 | 2716259.8042 | 1225683.4545
70 | 2716253.935 | 1225715.3697 | 2716265.5603 | 1225734.7051
71 | 2716276.4879 | 1225672.2099 | 2716259.8042 | 1225683.4545
72 | 2716265.5603 | 1225734.7051 | 2716276.8422 | 1225753.4693
73 | 2716276.4879 | 1225672.2099 | 2716282.3063 | 1225668.2884
74 | 2716276.8571 | 1225753.4941 | 2716276.8422 | 1225753.4693
75 | 2716280.3847 | 1225759.3613 | 2716276.8571 | 1225753.4941
76 | 2716284.9853 | 1225767.0132 | 2716280.3847 | 1225759.3613
77 | 2716082.9465 | 1225775.9313 | 2716077.0042 | 1225766.3967
78 | 2716082.9465 | 1225775.9313 | 2716079.3861 | 1225778.0858 | 2716055.1842 | 1225792.7029
79 | 2716055.1842 | 1225792.7029 | 2716049.7405 | 1225795.9907

## bus_geodata
| x | y | coords
0 | 2716276.8249 | 1225845.0363
1 | 2716295.9569 | 1225839.6993
2 | 2716260.1225 | 1225853.4721
3 | 2716311.3927 | 1225835.3933
4 | 2716277.1995 | 1225885.5454
5 | 2716241.4948 | 1225820.3667
6 | 2716293.4609 | 1225907.0761
7 | 2716239.2584 | 1225816.9568
8 | 2716325.2344 | 1225897.4472
9 | 2716270.5439 | 1225915.2608
10 | 2716246.168 | 1225924.9655
11 | 2716007.5262 | 1225547.2833
12 | 2715987.0711 | 1225537.1396
13 | 2716062.7731 | 1225572.0089
14 | 2715826.9894 | 1225668.5412
15 | 2716076.2767 | 1225579.6577
16 | 2716077.511 | 1225580.436
17 | 2716109.6913 | 1225611.2146
18 | 2716113.1924 | 1225616.3757
19 | 2716086.6818 | 1225587.0503
20 | 2716119.1348 | 1225609.3375
21 | 2716144.8386 | 1225609.9147
22 | 2716083.4516 | 1225584.1818
23 | 2716210.9129 | 1225909.6694
24 | 2716193.5175 | 1225924.1113
25 | 2716202.0878 | 1225890.2054
26 | 2716200.6221 | 1225887.7788
27 | 2716187.2811 | 1225865.6924
28 | 2716146.382 | 1225891.4199
29 | 2716183.8496 | 1225601.9501
30 | 2716262.159 | 1225585.9663
31 | 2716301.6119 | 1225577.9139
32 | 2716132.9128 | 1225684.4576
33 | 2716228.4913 | 1225700.0689
34 | 2716174.1035 | 1225731.0394
35 | 2716344.9227 | 1225568.2112
36 | 2716320.3971 | 1225617.3303
37 | 2716298.9757 | 1225567.3097
38 | 2716207.0192 | 1225786.105
39 | 2716176.2596 | 1225802.2619
40 | 2716192.813 | 1225754.5737
41 | 2716155.6316 | 1225813.2896
42 | 2716185.4901 | 1225862.727
43 | 2716184.0298 | 1225860.3091
44 | 2716044.6792 | 1225591.6314
45 | 2716331.584 | 1225633.1091
46 | 2716298.0193 | 1225563.477
47 | 2716167.1781 | 1225832.4073
48 | 2716097.8787 | 1225799.9078
49 | 2716051.2821 | 1225854.3856
50 | 2716085.3513 | 1225779.7927
51 | 2716167.8317 | 1225951.7766
52 | 2716135.7158 | 1225389.9308
53 | 2716142.2779 | 1225402.6462
54 | 2716139.3763 | 1225410.95
55 | 2716067.6336 | 1225419.4571
56 | 2716249.8651 | 1225529.4896
57 | 2716067.2854 | 1225417.6624
58 | 2716066.8315 | 1225415.3223
59 | 2716062.6122 | 1225403.4605
60 | 2716269.6626 | 1225529.2467
61 | 2716270.2055 | 1225529.2141
62 | 2716280.5912 | 1225528.5912
63 | 2716241.9722 | 1225695.473
64 | 2716252.9133 | 1225688.0989
65 | 2716253.935 | 1225715.3697
66 | 2716259.8042 | 1225683.4545
67 | 2716265.5603 | 1225734.7051
68 | 2716276.4879 | 1225672.2099
69 | 2716282.3063 | 1225668.2884
70 | 2716345.4661 | 1225620.49
71 | 2716276.8422 | 1225753.4693
72 | 2716276.8571 | 1225753.4941
73 | 2716280.3847 | 1225759.3613
74 | 2716284.9853 | 1225767.0132
75 | 2716300.1814 | 1225526.9799
76 | 2716295.7246 | 1225563.2492
77 | 2716082.9465 | 1225775.9313
78 | 2716077.0042 | 1225766.3967
79 | 2716055.1842 | 1225792.7029
80 | 2716049.7405 | 1225795.9907
81 | 2716260.1225 | 1225853.4721

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99634 | -0.070392 | 0.013579 | 0.0034031
1 | 0.99581 | -0.080642 | 0.02187 | 0.0054812
2 | 0.99707 | -0.05629 | 0.0039388 | 0.00098716
3 | 0.9957 | -0.082756 | 0.0075047 | 0.0018809
4 | 0.9961 | -0.074949 | 0.0072381 | 0.001814
5 | 0.9997 | -0.0057094 | 0.0041687 | 0.0010448
6 | 0.99555 | -0.085505 | 0 | 0
7 | 1 | 0 | -0.31003 | -0.078992
8 | 0.99517 | -0.092935 | 0.012721 | 0.0031883
9 | 0.99535 | -0.08948 | 0.0057974 | 0.001453
10 | 0.99526 | -0.091088 | 0.0034818 | 0.00087261
11 | 0.97037 | -0.57206 | 0.0011473 | 0.00028753
12 | 0.97033 | -0.57291 | 0.0017731 | 0.00044438
13 | 0.97055 | -0.56852 | 0.0018978 | 0.00047563
14 | 0.97028 | -0.5738 | 0.00022901 | 5.7395e-05
15 | 0.97062 | -0.56706 | 0.0014375 | 0.00036027
16 | 0.97063 | -0.56688 | 0.0038186 | 0.00095704
17 | 0.97117 | -0.55621 | 0 | 0
18 | 0.97126 | -0.55452 | 0 | 0
19 | 0.97075 | -0.56456 | 0.0011361 | 0.00028474
20 | 0.97116 | -0.55642 | 0.0011907 | 0.00029842
21 | 0.9717 | -0.54579 | 0.00084564 | 0.00021194
22 | 0.9707 | -0.56554 | 0 | 0
23 | 0.98577 | -0.27291 | 0.0053486 | 0.0013405
24 | 0.98507 | -0.28663 | 0.032468 | 0.0081371
25 | 0.98654 | -0.25788 | 0.0057749 | 0.0014473
26 | 0.98666 | -0.25567 | 0.0057753 | 0.0014474
27 | 0.98783 | -0.23289 | 0 | 0
28 | 0.98762 | -0.23685 | 0.0045964 | 0.001152
29 | 0.97227 | -0.53442 | 0.00072781 | 0.00018241
30 | 0.97348 | -0.51056 | 0.0065463 | 0.0016407
31 | 0.97434 | -0.49372 | 0 | 0
32 | 0.98692 | -0.24871 | 0 | 0
33 | 0.98076 | -0.36798 | 0.0069184 | 0.0017339
34 | 0.9908 | -0.17438 | 0.0045646 | 0.001144
35 | 0.97369 | -0.50638 | 0.015526 | 0.0038913
36 | 0.97627 | -0.45562 | 0.0029339 | 0.0007353
37 | 0.97425 | -0.49546 | 0 | 0
38 | 0.99519 | -0.090992 | 0 | 0
39 | 0.99279 | -0.13705 | 0.00022418 | 5.6186e-05
40 | 0.99274 | -0.13745 | 0.011297 | 0.0028314
41 | 0.99119 | -0.16783 | 0 | 0
42 | 0.988 | -0.22955 | 0.005775 | 0.0014474
43 | 0.98815 | -0.22653 | 0.00022418 | 5.6185e-05
44 | 0.97063 | -0.567 | 0.0019933 | 0.00049956
45 | 0.97717 | -0.43799 | 0 | 0
46 | 0.97422 | -0.49609 | 0 | 0
47 | 0.98995 | -0.19171 | 0.00022417 | 5.6182e-05
48 | 0.99031 | -0.18497 | 0 | 0
49 | 0.98986 | -0.1937 | 0 | 0
50 | 0.99012 | -0.18853 | 0.0056155 | 0.0014074
51 | 0.98917 | -0.20711 | 0.0049566 | 0.0012422
52 | 0.97238 | -0.53243 | 0.00071113 | 0.00017823
53 | 0.97239 | -0.53219 | 0.00017108 | 4.2876e-05
54 | 0.9724 | -0.53204 | 0 | 0
55 | 0.97246 | -0.53086 | 0 | 0
56 | 0.97292 | -0.52161 | 0.0009583 | 0.00024017
57 | 0.97246 | -0.5309 | 0.00060923 | 0.00015269
58 | 0.97245 | -0.53094 | 0.0004619 | 0.00011576
59 | 0.97245 | -0.53101 | 0.00030726 | 7.7006e-05
60 | 0.97298 | -0.52043 | 0.0011244 | 0.0002818
61 | 0.97299 | -0.52039 | 0.0016635 | 0.00041691
62 | 0.97304 | -0.51924 | 0.0015356 | 0.00038485
63 | 0.97991 | -0.38439 | 0 | 0
64 | 0.97955 | -0.39143 | 0.0032273 | 0.00080883
65 | 0.97844 | -0.4132 | 0.0021317 | 0.00053425
66 | 0.97934 | -0.39563 | 0.0011826 | 0.00029638
67 | 0.97705 | -0.4404 | 0.0034793 | 0.00087201
68 | 0.97883 | -0.40558 | 0.0010919 | 0.00027365
69 | 0.97865 | -0.40898 | 0.00071444 | 0.00017906
70 | 0.97712 | -0.43891 | 0.0026731 | 0.00066995
71 | 0.97578 | -0.46548 | 0.0063183 | 0.0015835
72 | 0.97578 | -0.46551 | 0.0058612 | 0.001469
73 | 0.97545 | -0.47184 | 0.0046389 | 0.0011626
74 | 0.97507 | -0.47934 | 0.045832 | 0.011487
75 | 0.97318 | -0.5165 | 0 | 0
76 | 0.97421 | -0.49613 | 0.0011123 | 0.00027877
77 | 0.99011 | -0.18876 | 0 | 0
78 | 0.99009 | -0.18907 | 0.0015394 | 0.00038581
79 | 0.99007 | -0.18951 | 0.0010554 | 0.00026452
80 | 0.99007 | -0.18954 | 0.0002392 | 5.995e-05
81 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.02939 | 0.0073713 | -0.029376 | -0.0073623 | 1.4352e-05 | 8.9267e-06 | 0.043896 | 0.043896 | 0.043896 | 0.99634 | -0.070392 | 0.99581 | -0.080642 | 12.0593
1 | -0.042969 | -0.010774 | 0.042998 | 0.010793 | 2.8899e-05 | 1.8251e-05 | 0.064175 | 0.064175 | 0.064175 | 0.99634 | -0.070392 | 0.99707 | -0.05629 | 17.6305
2 | 0.0075055 | 0.0018811 | -0.0075047 | -0.0018809 | 7.5589e-07 | 2.7532e-07 | 0.011215 | 0.011215 | 0.011215 | 0.99581 | -0.080642 | 0.9957 | -0.082756 | 3.0812
3 | 0.029282 | 0.0073539 | -0.029256 | -0.0073377 | 2.6045e-05 | 1.6195e-05 | 0.043706 | 0.043706 | 0.043706 | 0.99707 | -0.05629 | 0.9961 | -0.074949 | 12.0072
4 | -0.076219 | -0.019134 | 0.076403 | 0.019251 | 0.00018437 | 0.0001175 | 0.11376 | 0.11376 | 0.11376 | 0.99707 | -0.05629 | 0.9997 | -0.0057094 | 31.2526
5 | 0.022018 | 0.0055237 | -0.022007 | -0.0055169 | 1.1075e-05 | 6.7329e-06 | 0.032894 | 0.032894 | 0.032894 | 0.9961 | -0.074949 | 0.99555 | -0.085505 | 9.0367
6 | -0.080572 | -0.020296 | 0.080594 | 0.02031 | 2.2007e-05 | 1.4031e-05 | 0.11996 | 0.11996 | 0.11996 | 0.9997 | -0.0057094 | 1 | 0 | 32.9572
7 | 0.0092812 | 0.0023262 | -0.0092795 | -0.0023254 | 1.7575e-06 | 8.0819e-07 | 0.013872 | 0.013872 | 0.013872 | 0.99555 | -0.085505 | 0.99535 | -0.08948 | 3.8111
8 | 0.012726 | 0.0031907 | -0.012721 | -0.0031883 | 4.5046e-06 | 2.4514e-06 | 0.019021 | 0.019021 | 0.019021 | 0.99555 | -0.085505 | 0.99517 | -0.092935 | 5.2257
9 | 0.22779 | 0.058682 | -0.22678 | -0.05804 | 0.001004 | 0.00064133 | 0.33952 | 0.33952 | 0.33952 | 1 | 0 | 0.99519 | -0.090992 | 46.6371
10 | 0.003482 | 0.00087244 | -0.0034818 | -0.00087261 | 2.6661e-07 | -1.7035e-07 | 0.0052055 | 0.0052056 | 0.0052056 | 0.99535 | -0.08948 | 0.99526 | -0.091088 | 1.4301
11 | 0.0020022 | 0.00049899 | -0.0020021 | -0.00049922 | 8.0741e-08 | -2.3065e-07 | 0.0030692 | 0.0030693 | 0.0030693 | 0.97037 | -0.57206 | 0.97033 | -0.57291 | 0.84323
12 | -0.0031494 | -0.00078652 | 0.00315 | 0.00078611 | 5.2987e-07 | -4.0975e-07 | 0.0048285 | 0.0048282 | 0.0048285 | 0.97037 | -0.57206 | 0.97055 | -0.56852 | 1.3265
13 | 0.00022902 | 5.4843e-05 | -0.00022901 | -5.7395e-05 | 9.5545e-09 | -2.552e-06 | 0.0003503 | 0.0003512 | 0.0003512 | 0.97033 | -0.57291 | 0.97028 | -0.5738 | 0.096485
14 | -0.0050478 | -0.0012617 | 0.0050481 | 0.0012618 | 3.4956e-07 | 3.1307e-08 | 0.0077379 | 0.0077378 | 0.0077379 | 0.97055 | -0.56852 | 0.97062 | -0.56706 | 2.1258
15 | -0.0064856 | -0.001622 | 0.0064857 | 0.0016221 | 5.4083e-08 | 1.6577e-08 | 0.0099415 | 0.0099415 | 0.0099415 | 0.97062 | -0.56706 | 0.97063 | -0.56688 | 2.7312
16 | -0.010304 | -0.0025791 | 0.010305 | 0.0025794 | 6.5709e-07 | 3.3373e-07 | 0.015796 | 0.015796 | 0.015796 | 0.97063 | -0.56688 | 0.9707 | -0.56554 | 4.3395
17 | -0.014631 | -0.003665 | 0.014632 | 0.0036656 | 1.1742e-06 | 6.7438e-07 | 0.022417 | 0.022417 | 0.022417 | 0.97117 | -0.55621 | 0.97126 | -0.55452 | 6.1585
18 | 0.01344 | 0.0033667 | -0.013435 | -0.0033636 | 5.3431e-06 | 3.004e-06 | 0.020593 | 0.020593 | 0.020593 | 0.97117 | -0.55621 | 0.97075 | -0.56456 | 5.6573
19 | 0.0011907 | 0.00029831 | -0.0011907 | -0.00029842 | 1.2017e-08 | -1.1145e-07 | 0.0018243 | 0.0018244 | 0.0018244 | 0.97117 | -0.55621 | 0.97116 | -0.55642 | 0.50121
20 | -0.014632 | -0.0036656 | 0.014638 | 0.0036691 | 6.0865e-06 | 3.4955e-06 | 0.022417 | 0.022417 | 0.022417 | 0.97126 | -0.55452 | 0.9717 | -0.54579 | 6.1585
21 | 0.012299 | 0.0030789 | -0.012298 | -0.0030786 | 5.7569e-07 | 3.1504e-07 | 0.018851 | 0.018851 | 0.018851 | 0.97075 | -0.56456 | 0.9707 | -0.56554 | 5.1789
22 | -0.015484 | -0.0038811 | 0.015492 | 0.0038859 | 8.3948e-06 | 4.8792e-06 | 0.023712 | 0.023712 | 0.023712 | 0.9717 | -0.54579 | 0.97227 | -0.53442 | 6.5142
23 | 0.0019934 | 0.00049916 | -0.0019933 | -0.00049956 | 1.3792e-07 | -3.9861e-07 | 0.0030556 | 0.0030558 | 0.0030558 | 0.9707 | -0.56554 | 0.97063 | -0.567 | 0.8395
24 | 0.032489 | 0.0081504 | -0.032468 | -0.0081371 | 2.1231e-05 | 1.3288e-05 | 0.049044 | 0.049045 | 0.049045 | 0.98577 | -0.27291 | 0.98507 | -0.28663 | 13.4738
25 | -0.037837 | -0.0094909 | 0.037865 | 0.009508 | 2.7136e-05 | 1.7084e-05 | 0.057118 | 0.057118 | 0.057118 | 0.98577 | -0.27291 | 0.98654 | -0.25788 | 15.6918
26 | -0.043639 | -0.010955 | 0.043644 | 0.010958 | 4.6067e-06 | 2.9121e-06 | 0.065828 | 0.065828 | 0.065828 | 0.98654 | -0.25788 | 0.98666 | -0.25567 | 18.0848
27 | -0.049419 | -0.012406 | 0.049473 | 0.01244 | 5.376e-05 | 3.4077e-05 | 0.074538 | 0.074538 | 0.074538 | 0.98666 | -0.25567 | 0.98783 | -0.23289 | 20.4776
28 | -0.05407 | -0.013592 | 0.054079 | 0.013597 | 8.6212e-06 | 5.4732e-06 | 0.081463 | 0.081463 | 0.081463 | 0.98783 | -0.23289 | 0.988 | -0.22955 | 22.38
29 | 0.0045973 | 0.0011519 | -0.0045964 | -0.001152 | 8.6896e-07 | -6.2298e-08 | 0.0069251 | 0.0069253 | 0.0069253 | 0.98783 | -0.23289 | 0.98762 | -0.23685 | 1.9025
30 | -0.01622 | -0.0040684 | 0.016239 | 0.0040792 | 1.8471e-05 | 1.0829e-05 | 0.024825 | 0.024825 | 0.024825 | 0.97227 | -0.53442 | 0.97348 | -0.51056 | 6.8202
31 | -0.022785 | -0.0057198 | 0.022803 | 0.0057311 | 1.832e-05 | 1.1223e-05 | 0.034831 | 0.034831 | 0.034831 | 0.97348 | -0.51056 | 0.97434 | -0.49372 | 9.5691
32 | 0.015536 | 0.0038967 | -0.015526 | -0.0038913 | 9.3727e-06 | 5.446e-06 | 0.023727 | 0.023728 | 0.023728 | 0.97434 | -0.49372 | 0.97369 | -0.50638 | 6.5186
33 | -0.047005 | -0.011797 | 0.04709 | 0.011851 | 8.5568e-05 | 5.4211e-05 | 0.071792 | 0.071792 | 0.071792 | 0.97434 | -0.49372 | 0.97627 | -0.45562 | 19.723
34 | 0.0086655 | 0.0021692 | -0.0086648 | -0.0021688 | 7.1756e-07 | 3.2316e-07 | 0.013233 | 0.013233 | 0.013233 | 0.97434 | -0.49372 | 0.97425 | -0.49546 | 3.6355
35 | 0.13544 | 0.034509 | -0.13466 | -0.034016 | 0.00077458 | 0.00049322 | 0.20441 | 0.20441 | 0.20441 | 0.98692 | -0.24871 | 0.98076 | -0.36798 | 28.078
36 | -0.13544 | -0.034509 | 0.13592 | 0.03482 | 0.00048766 | 0.00031051 | 0.20441 | 0.20441 | 0.20441 | 0.98692 | -0.24871 | 0.9908 | -0.17438 | 28.0778
37 | 0.12774 | 0.032282 | -0.12764 | -0.032218 | 0.00010042 | 6.3907e-05 | 0.19391 | 0.19391 | 0.19391 | 0.98076 | -0.36798 | 0.97991 | -0.38439 | 26.6361
38 | -0.14049 | -0.035964 | 0.14074 | 0.036124 | 0.00025172 | 0.00016032 | 0.21126 | 0.21126 | 0.21126 | 0.9908 | -0.17438 | 0.99274 | -0.13745 | 29.0194
39 | -0.050024 | -0.012586 | 0.050066 | 0.012613 | 4.2186e-05 | 2.6757e-05 | 0.076263 | 0.076263 | 0.076263 | 0.97627 | -0.45562 | 0.97717 | -0.43799 | 20.9515
40 | 0.0086648 | 0.0021688 | -0.0086645 | -0.0021687 | 2.5939e-07 | 1.1683e-07 | 0.013233 | 0.013233 | 0.013233 | 0.97425 | -0.49546 | 0.97422 | -0.49609 | 3.6355
41 | 0.074402 | 0.018866 | -0.074237 | -0.018762 | 0.00016434 | 0.00010472 | 0.11132 | 0.11132 | 0.11132 | 0.99519 | -0.090992 | 0.99279 | -0.13705 | 30.5836
42 | 0.15238 | 0.039174 | -0.15204 | -0.038955 | 0.00034319 | 0.00021873 | 0.22819 | 0.22819 | 0.22819 | 0.99519 | -0.090992 | 0.99274 | -0.13745 | 31.3454
43 | 0.074013 | 0.018705 | -0.073904 | -0.018636 | 0.00010904 | 6.9482e-05 | 0.11099 | 0.11099 | 0.11099 | 0.99279 | -0.13705 | 0.99119 | -0.16783 | 30.4913
44 | 0.06048 | 0.01527 | -0.060411 | -0.015226 | 6.9105e-05 | 4.394e-05 | 0.090835 | 0.090835 | 0.090835 | 0.99119 | -0.16783 | 0.98995 | -0.19171 | 24.9548
45 | 0.013424 | 0.0033661 | -0.013413 | -0.00336 | 1.096e-05 | 6.0877e-06 | 0.020153 | 0.020153 | 0.020153 | 0.99119 | -0.16783 | 0.99031 | -0.18497 | 5.5367
46 | -0.059854 | -0.015044 | 0.059863 | 0.01505 | 8.6108e-06 | 5.4747e-06 | 0.090161 | 0.090161 | 0.090161 | 0.988 | -0.22955 | 0.98815 | -0.22653 | 24.7695
47 | -0.060087 | -0.015106 | 0.060187 | 0.01517 | 0.00010011 | 6.3652e-05 | 0.090499 | 0.090499 | 0.090499 | 0.98815 | -0.22653 | 0.98995 | -0.19171 | 24.8623
48 | 0.0026733 | 0.00066979 | -0.0026731 | -0.00066995 | 1.1725e-07 | -1.6132e-07 | 0.0040707 | 0.0040708 | 0.0040708 | 0.97717 | -0.43799 | 0.97712 | -0.43891 | 1.1184
49 | -0.052739 | -0.013283 | 0.052813 | 0.013328 | 7.3264e-05 | 4.537e-05 | 0.080334 | 0.080333 | 0.080334 | 0.97717 | -0.43799 | 0.97865 | -0.40898 | 11.0349
50 | 0.0075522 | 0.00189 | -0.0075449 | -0.0018871 | 7.3324e-06 | 2.8648e-06 | 0.011534 | 0.011535 | 0.011535 | 0.97422 | -0.49609 | 0.97318 | -0.5165 | 3.1689
51 | 0.0011123 | 0.00027874 | -0.0011123 | -0.00027877 | 2.496e-09 | -2.7116e-08 | 0.0016989 | 0.0016989 | 0.0016989 | 0.97422 | -0.49609 | 0.97421 | -0.49613 | 0.46674
52 | 0.0049619 | 0.0012424 | -0.0049598 | -0.0012423 | 2.0604e-06 | 4.7411e-08 | 0.0074552 | 0.0074556 | 0.0074556 | 0.99031 | -0.18497 | 0.98986 | -0.1937 | 2.0483
53 | 0.008451 | 0.0021176 | -0.0084496 | -0.002117 | 1.4329e-06 | 6.1223e-07 | 0.012698 | 0.012698 | 0.012698 | 0.99031 | -0.18497 | 0.99012 | -0.18853 | 3.4886
54 | 0.0049598 | 0.0012423 | -0.0049566 | -0.0012422 | 3.1667e-06 | 7.5415e-08 | 0.0074556 | 0.0074563 | 0.0074563 | 0.98986 | -0.1937 | 0.98917 | -0.20711 | 2.0484
55 | 0.0028341 | 0.00070964 | -0.0028341 | -0.00070968 | 3.0944e-08 | -3.8701e-08 | 0.0042591 | 0.0042591 | 0.0042591 | 0.99012 | -0.18853 | 0.99011 | -0.18876 | 1.1701
56 | -0.00071113 | -0.00017823 | 0.00071113 | 0.000178 | 8.0782e-09 | -2.205e-07 | 0.0010882 | 0.0010881 | 0.0010882 | 0.97238 | -0.53243 | 0.97239 | -0.53219 | 0.29896
57 | -0.00088221 | -0.00022088 | 0.00088222 | 0.00022078 | 6.0109e-09 | -1.0527e-07 | 0.0013499 | 0.0013499 | 0.0013499 | 0.97239 | -0.53219 | 0.9724 | -0.53204 | 0.37086
58 | -0.00088222 | -0.00022078 | 0.00088227 | 0.0002199 | 4.9753e-08 | -8.7163e-07 | 0.0013499 | 0.0013496 | 0.0013499 | 0.9724 | -0.53204 | 0.97246 | -0.53086 | 0.37085
59 | -0.0022607 | -0.00056516 | 0.0022617 | 0.00056304 | 9.9243e-07 | -2.1117e-06 | 0.0034587 | 0.0034577 | 0.0034587 | 0.97246 | -0.53086 | 0.97292 | -0.52161 | 0.95018
60 | 0.0013784 | 0.00034525 | -0.0013784 | -0.00034527 | 3.0494e-09 | -2.0729e-08 | 0.0021091 | 0.0021091 | 0.0021091 | 0.97246 | -0.53086 | 0.97246 | -0.5309 | 0.57942
61 | -0.00322 | -0.00080322 | 0.0032201 | 0.00080309 | 1.8023e-07 | -1.3091e-07 | 0.0049233 | 0.0049232 | 0.0049233 | 0.97292 | -0.52161 | 0.97298 | -0.52043 | 1.3526
62 | 0.00076916 | 0.00019258 | -0.00076916 | -0.00019261 | 1.238e-09 | -2.8781e-08 | 0.0011769 | 0.0011769 | 0.0011769 | 0.97246 | -0.5309 | 0.97245 | -0.53094 | 0.32332
63 | 0.00030726 | 7.685e-05 | -0.00030726 | -7.7006e-05 | 1.0474e-09 | -1.5611e-07 | 0.0004701 | 0.00047016 | 0.00047016 | 0.97245 | -0.53094 | 0.97245 | -0.53101 | 0.12916
64 | -0.0043445 | -0.0010849 | 0.0043445 | 0.0010849 | 8.9982e-09 | -9.9457e-10 | 0.0066428 | 0.0066428 | 0.0066428 | 0.97298 | -0.52043 | 0.97299 | -0.52039 | 1.8249
65 | -0.006008 | -0.0015018 | 0.0060084 | 0.0015019 | 3.2929e-07 | 8.1514e-08 | 0.0091868 | 0.0091868 | 0.0091868 | 0.97299 | -0.52039 | 0.97304 | -0.51924 | 2.5239
66 | -0.0075439 | -0.0018867 | 0.0075449 | 0.0018871 | 9.8096e-07 | 3.8357e-07 | 0.011535 | 0.011535 | 0.011535 | 0.97304 | -0.51924 | 0.97318 | -0.5165 | 3.169
67 | 0.059095 | 0.014927 | -0.059075 | -0.014915 | 1.994e-05 | 1.2429e-05 | 0.089778 | 0.089779 | 0.089779 | 0.97991 | -0.38439 | 0.97955 | -0.39143 | 12.3322
68 | 0.068549 | 0.017291 | -0.068454 | -0.017231 | 9.4405e-05 | 6.0127e-05 | 0.10413 | 0.10413 | 0.10413 | 0.97991 | -0.38439 | 0.97844 | -0.4132 | 28.6079
69 | 0.055848 | 0.014106 | -0.055836 | -0.014099 | 1.1225e-05 | 6.9746e-06 | 0.084876 | 0.084876 | 0.084876 | 0.97955 | -0.39143 | 0.97934 | -0.39563 | 11.6588
70 | 0.066323 | 0.016696 | -0.066237 | -0.016642 | 8.6118e-05 | 5.4833e-05 | 0.10089 | 0.10089 | 0.10089 | 0.97844 | -0.4132 | 0.97705 | -0.4404 | 27.7173
71 | 0.054654 | 0.013803 | -0.054628 | -0.013786 | 2.6038e-05 | 1.6158e-05 | 0.083079 | 0.08308 | 0.08308 | 0.97934 | -0.39563 | 0.97883 | -0.40558 | 11.412
72 | 0.062757 | 0.01577 | -0.062682 | -0.015722 | 7.5026e-05 | 4.7743e-05 | 0.095592 | 0.095592 | 0.095592 | 0.97705 | -0.4404 | 0.97578 | -0.46548 | 26.2615
73 | 0.053536 | 0.013513 | -0.053527 | -0.013507 | 8.7213e-06 | 5.4053e-06 | 0.08142 | 0.08142 | 0.08142 | 0.97883 | -0.40558 | 0.97865 | -0.40898 | 11.184
74 | 0.056364 | 0.014138 | -0.056364 | -0.014138 | 7.9989e-08 | 5.083e-08 | 0.085957 | 0.085957 | 0.085957 | 0.97578 | -0.46548 | 0.97578 | -0.46551 | 23.6145
75 | 0.050503 | 0.012669 | -0.050487 | -0.01266 | 1.5229e-05 | 9.6609e-06 | 0.077019 | 0.077019 | 0.077019 | 0.97578 | -0.46551 | 0.97545 | -0.47184 | 21.159
76 | 0.045849 | 0.011497 | -0.045832 | -0.011487 | 1.6379e-05 | 1.0371e-05 | 0.069942 | 0.069942 | 0.069942 | 0.97545 | -0.47184 | 0.97507 | -0.47934 | 19.215
77 | 0.0015394 | 0.00038568 | -0.0015394 | -0.00038581 | 2.255e-08 | -1.3006e-07 | 0.0023135 | 0.0023136 | 0.0023136 | 0.99011 | -0.18876 | 0.99009 | -0.18907 | 0.63559
78 | 0.0012947 | 0.000324 | -0.0012946 | -0.00032438 | 4.6044e-08 | -3.8766e-07 | 0.0019456 | 0.0019457 | 0.0019457 | 0.99011 | -0.18876 | 0.99007 | -0.18951 | 0.53454
79 | 0.0002392 | 5.9868e-05 | -0.0002392 | -5.995e-05 | 3.0818e-10 | -8.1587e-08 | 0.00035948 | 0.00035951 | 0.00035951 | 0.99007 | -0.18951 | 0.99007 | -0.18954 | 0.098766

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31395 | 0.079974

## res_load
| p_mw | q_mvar
0 | 0.013579 | 0.0034031
1 | 0.02187 | 0.0054812
2 | 0.0039388 | 0.00098716
3 | 0.0075047 | 0.0018809
4 | 0.0072381 | 0.001814
5 | 0.0041687 | 0.0010448
6 | 0.0039171 | 0.00098172
7 | 0.012721 | 0.0031883
8 | 0.0057974 | 0.001453
9 | 0.0034818 | 0.00087261
10 | 0.0011473 | 0.00028753
11 | 0.0017731 | 0.00044438
12 | 0.0018978 | 0.00047563
13 | 0.00022901 | 5.7395e-05
14 | 0.0014375 | 0.00036027
15 | 0.0038186 | 0.00095704
16 | 0.0011361 | 0.00028474
17 | 0.0011907 | 0.00029842
18 | 0.00084564 | 0.00021194
19 | 0.0053486 | 0.0013405
20 | 0.032468 | 0.0081371
21 | 0.0057749 | 0.0014473
22 | 0.0057753 | 0.0014474
23 | 0.0045964 | 0.001152
24 | 0.00072781 | 0.00018241
25 | 0.0065463 | 0.0016407
26 | 0.0069184 | 0.0017339
27 | 0.0045646 | 0.001144
28 | 0.015526 | 0.0038913
29 | 0.0029339 | 0.0007353
30 | 0.00022418 | 5.6186e-05
31 | 0.011297 | 0.0028314
32 | 0.005775 | 0.0014474
33 | 0.00022418 | 5.6185e-05
34 | 0.0019933 | 0.00049956
35 | 0.00022417 | 5.6182e-05
36 | 0.0056155 | 0.0014074
37 | 0.0049566 | 0.0012422
38 | 0.00071113 | 0.00017823
39 | 0.00017108 | 4.2876e-05
40 | 0.0009583 | 0.00024017
41 | 0.00060923 | 0.00015269
42 | 0.0004619 | 0.00011576
43 | 0.00030726 | 7.7006e-05
44 | 0.0011244 | 0.0002818
45 | 0.0016635 | 0.00041691
46 | 0.0015356 | 0.00038485
47 | 0.0032273 | 0.00080883
48 | 0.0021317 | 0.00053425
49 | 0.0011826 | 0.00029638
50 | 0.0034793 | 0.00087201
51 | 0.0010919 | 0.00027365
52 | 0.00071444 | 0.00017906
53 | 0.0026731 | 0.00066995
54 | 0.0063183 | 0.0015835
55 | 0.0058612 | 0.001469
56 | 0.0046389 | 0.0011626
57 | 0.045832 | 0.011487
58 | 0.0011123 | 0.00027877
59 | 0.0015394 | 0.00038581
60 | 0.0010554 | 0.00026452
61 | 0.0002392 | 5.995e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1