## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1347-6_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1347-6_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1347-6_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1347-6_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1347-6_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1347-6_0_5_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_1347-6_0_5_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1347-6_0_5_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1347-6_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1347-6_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1347-6_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1347-6_0_5_node_123 | 0.4 | n |  | TRUE
12 | bus_LV_1347-6_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1347-6_0_5_node_125 | 0.4 | n |  | TRUE
14 | bus_LV_1347-6_0_5_node_124 | 0.4 | n |  | TRUE
15 | bus_LV_1347-6_0_5_node_104 | 0.4 | n |  | TRUE
16 | bus_LV_1347-6_0_5_node_122 | 0.4 | n |  | TRUE
17 | bus_LV_1347-6_0_5_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1347-6_0_5_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1347-6_0_5_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1347-6_0_5_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1347-6_0_5_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_1347-6_0_5_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1347-6_0_5_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1347-6_0_5_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1347-6_0_5_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1347-6_0_5_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_1347-6_0_5_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1347-6_0_5_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1347-6_0_5_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_1347-6_0_5_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1347-6_0_5_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_1347-6_0_5_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1347-6_0_5_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_1347-6_0_5_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_1347-6_0_5_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_1347-6_0_5_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_1347-6_0_5_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_1347-6_0_5_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1347-6_0_5_node_41 | 0.4 | n |  | TRUE
40 | bus_LV_1347-6_0_5_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_1347-6_0_5_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1347-6_0_5_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_1347-6_0_5_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_1347-6_0_5_node_61 | 0.4 | n |  | TRUE
45 | bus_LV_1347-6_0_5_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_1347-6_0_5_node_45 | 0.4 | n |  | TRUE
47 | bus_LV_1347-6_0_5_node_50 | 0.4 | n |  | TRUE
48 | bus_LV_1347-6_0_5_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_1347-6_0_5_node_52 | 0.4 | n |  | TRUE
50 | bus_LV_1347-6_0_5_node_54 | 0.4 | n |  | TRUE
51 | bus_LV_1347-6_0_5_node_70 | 0.4 | n |  | TRUE
52 | bus_LV_1347-6_0_5_node_68 | 0.4 | n |  | TRUE
53 | bus_LV_1347-6_0_5_node_53 | 0.4 | n |  | TRUE
54 | bus_LV_1347-6_0_5_node_62 | 0.4 | n |  | TRUE
55 | bus_LV_1347-6_0_5_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_1347-6_0_5_node_77 | 0.4 | n |  | TRUE
57 | bus_LV_1347-6_0_5_node_42 | 0.4 | n |  | TRUE
58 | bus_LV_1347-6_0_5_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_1347-6_0_5_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_1347-6_0_5_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_1347-6_0_5_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_1347-6_0_5_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_1347-6_0_5_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_1347-6_0_5_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_1347-6_0_5_node_73 | 0.4 | n |  | TRUE
66 | bus_LV_1347-6_0_5_node_69 | 0.4 | n |  | TRUE
67 | bus_LV_1347-6_0_5_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_1347-6_0_5_node_78 | 0.4 | n |  | TRUE
69 | bus_LV_1347-6_0_5_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_1347-6_0_5_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_1347-6_0_5_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_1347-6_0_5_node_146 | 0.4 | n |  | TRUE
73 | bus_LV_1347-6_0_5_node_147 | 0.4 | n |  | TRUE
74 | bus_LV_1347-6_0_5_node_64 | 0.4 | n |  | TRUE
75 | bus_LV_1347-6_0_5_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_1347-6_0_5_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_1347-6_0_5_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_1347-6_0_5_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_1347-6_0_5_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_1347-6_0_5_node_74 | 0.4 | n |  | TRUE
81 | bus_LV_1347-6_0_5_node_75 | 0.4 | n |  | TRUE
82 | bus_LV_1347-6_0_5_node_76 | 0.4 | n |  | TRUE
83 | bus_LV_1347-6_0_5_node_91 | 0.4 | n |  | TRUE
84 | bus_LV_1347-6_0_5_node_141 | 0.4 | n |  | TRUE
85 | bus_LV_1347-6_0_5_node_138 | 0.4 | n |  | TRUE
86 | bus_LV_1347-6_0_5_node_142 | 0.4 | n |  | TRUE
87 | bus_LV_1347-6_0_5_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_1347-6_0_5_node_86 | 0.4 | n |  | TRUE
89 | bus_LV_1347-6_0_5_node_99 | 0.4 | n |  | TRUE
90 | bus_LV_1347-6_0_5_node_100 | 0.4 | n |  | TRUE
91 | bus_LV_1347-6_0_5_node_80 | 0.4 | n |  | TRUE
92 | bus_LV_1347-6_0_5_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_1347-6_0_5_node_82 | 0.4 | n |  | TRUE
94 | bus_LV_1347-6_0_5_node_83 | 0.4 | n |  | TRUE
95 | bus_LV_1347-6_0_5_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_1347-6_0_5_node_85 | 0.4 | n |  | TRUE
97 | bus_LV_1347-6_0_5_node_96 | 0.4 | n |  | TRUE
98 | bus_LV_1347-6_0_5_node_97 | 0.4 | n |  | TRUE
99 | bus_LV_1347-6_0_5_node_98 | 0.4 | n |  | TRUE
100 | bus_LV_1347-6_0_5_node_101 | 0.4 | n |  | TRUE
101 | bus_LV_1347-6_0_5_node_87 | 0.4 | n |  | TRUE
102 | bus_LV_1347-6_0_5_node_88 | 0.4 | n |  | TRUE
103 | bus_LV_1347-6_0_5_node_89 | 0.4 | n |  | TRUE
104 | bus_LV_1347-6_0_5_node_90 | 0.4 | n |  | TRUE
105 | bus_LV_1347-6_0_5_node_92 | 0.4 | n |  | TRUE
106 | bus_LV_1347-6_0_5_node_93 | 0.4 | n |  | TRUE
107 | bus_LV_1347-6_0_5_node_139 | 0.4 | n |  | TRUE
108 | bus_LV_1347-6_0_5_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_1347-6_0_5_node_95 | 0.4 | n |  | TRUE
110 | bus_LV_1347-6_0_5_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_1347-6_0_5_node_127 | 0.4 | n |  | TRUE
112 | bus_LV_1347-6_0_5_node_128 | 0.4 | n |  | TRUE
113 | bus_LV_1347-6_0_5_node_126 | 0.4 | n |  | TRUE
114 | bus_LV_1347-6_0_5_node_102 | 0.4 | n |  | TRUE
115 | bus_LV_1347-6_0_5_node_105 | 0.4 | n |  | TRUE
116 | bus_LV_1347-6_0_5_node_106 | 0.4 | n |  | TRUE
117 | bus_LV_1347-6_0_5_node_112 | 0.4 | n |  | TRUE
118 | bus_LV_1347-6_0_5_node_118 | 0.4 | n |  | TRUE
119 | bus_LV_1347-6_0_5_node_109 | 0.4 | n |  | TRUE
120 | bus_LV_1347-6_0_5_node_111 | 0.4 | n |  | TRUE
121 | bus_LV_1347-6_0_5_node_107 | 0.4 | n |  | TRUE
122 | bus_LV_1347-6_0_5_node_108 | 0.4 | n |  | TRUE
123 | bus_LV_1347-6_0_5_node_110 | 0.4 | n |  | TRUE
124 | bus_LV_1347-6_0_5_node_113 | 0.4 | n |  | TRUE
125 | bus_LV_1347-6_0_5_node_114 | 0.4 | n |  | TRUE
126 | bus_LV_1347-6_0_5_node_117 | 0.4 | n |  | TRUE
127 | bus_LV_1347-6_0_5_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_1347-6_0_5_node_121 | 0.4 | n |  | TRUE
129 | bus_LV_1347-6_0_5_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_1347-6_0_5_node_116 | 0.4 | n |  | TRUE
131 | bus_LV_1347-6_0_5_node_119 | 0.4 | n |  | TRUE
132 | bus_LV_1347-6_0_5_node_129 | 0.4 | n |  | TRUE
133 | bus_LV_1347-6_0_5_node_130 | 0.4 | n |  | TRUE
134 | bus_LV_1347-6_0_5_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_1347-6_0_5_node_132 | 0.4 | n |  | TRUE
136 | bus_LV_1347-6_0_5_node_133 | 0.4 | n |  | TRUE
137 | bus_LV_1347-6_0_5_node_144 | 0.4 | n |  | TRUE
138 | bus_LV_1347-6_0_5_node_134 | 0.4 | n |  | TRUE
139 | bus_LV_1347-6_0_5_node_145 | 0.4 | n |  | TRUE
140 | bus_LV_1347-6_0_5_node_152 | 0.4 | n |  | TRUE
141 | bus_LV_1347-6_0_5_node_135 | 0.4 | n |  | TRUE
142 | bus_LV_1347-6_0_5_node_136 | 0.4 | n |  | TRUE
143 | bus_LV_1347-6_0_5_node_137 | 0.4 | n |  | TRUE
144 | bus_LV_1347-6_0_5_node_140 | 0.4 | n |  | TRUE
145 | bus_LV_1347-6_0_5_node_143 | 0.4 | n |  | TRUE
146 | bus_LV_1347-6_0_5_node_148 | 0.4 | n |  | TRUE
147 | bus_LV_1347-6_0_5_node_149 | 0.4 | n |  | TRUE
148 | bus_LV_1347-6_0_5_node_150 | 0.4 | n |  | TRUE
149 | bus_LV_1347-6_0_5_node_151 | 0.4 | n |  | TRUE
150 | bus_MV_21_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1347-6_0_5_load_0 | 0 | 0.0018717 | 0.00046909 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1347-6_0_5_load_1 | 1 | 0.0004496 | 0.00011268 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1347-6_0_5_load_2 | 2 | 0.0006811 | 0.0001707 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1347-6_0_5_load_4 | 4 | 0.0021643 | 0.00054243 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1347-6_0_5_load_11 | 7 | 0.0045411 | 0.0011381 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1347-6_0_5_load_5 | 8 | 0.00042185 | 0.00010573 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1347-6_0_5_load_6 | 9 | 0.0049329 | 0.0012363 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1347-6_0_5_load_7 | 10 | 0.00083928 | 0.00021034 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1347-6_0_5_load_123 | 11 | 0.0041719 | 0.0010456 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1347-6_0_5_load_8 | 12 | 0.00062703 | 0.00015715 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1347-6_0_5_load_125 | 13 | 0.01429 | 0.0035814 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1347-6_0_5_load_124 | 14 | 0.016054 | 0.0040235 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1347-6_0_5_load_122 | 16 | 0.004277 | 0.0010719 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1347-6_0_5_load_12 | 17 | 0.0030112 | 0.00075468 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1347-6_0_5_load_16 | 19 | 0.00064993 | 0.00016289 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1347-6_0_5_load_23 | 21 | 0.014023 | 0.0035146 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1347-6_0_5_load_22 | 22 | 0.022038 | 0.0055233 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1347-6_0_5_load_18 | 23 | 0.0017472 | 0.0004379 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1347-6_0_5_load_19 | 24 | 0.0028266 | 0.00070842 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1347-6_0_5_load_21 | 25 | 0.00052247 | 0.00013094 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1347-6_0_5_load_20 | 27 | 0.00058736 | 0.00014721 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1347-6_0_5_load_25 | 28 | 0.016617 | 0.0041645 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1347-6_0_5_load_26 | 30 | 0.0082713 | 0.002073 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1347-6_0_5_load_35 | 31 | 0.0049954 | 0.001252 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1347-6_0_5_load_31 | 32 | 0.010553 | 0.0026449 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1347-6_0_5_load_29 | 33 | 0.0030637 | 0.00076783 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1347-6_0_5_load_27 | 35 | 0.0073326 | 0.0018377 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1347-6_0_5_load_28 | 36 | 0.0033052 | 0.00082836 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1347-6_0_5_load_41 | 39 | 0.0058719 | 0.0014716 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1347-6_0_5_load_38 | 40 | 0.0071715 | 0.0017973 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1347-6_0_5_load_36 | 41 | 0.0030926 | 0.00077508 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1347-6_0_5_load_37 | 42 | 0.011738 | 0.0029419 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1347-6_0_5_load_39 | 43 | 0.0014217 | 0.00035632 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1347-6_0_5_load_61 | 44 | 0.0034588 | 0.00086685 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1347-6_0_5_load_44 | 45 | 0.017024 | 0.0042666 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1347-6_0_5_load_50 | 47 | 0.0020295 | 0.00050865 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1347-6_0_5_load_54 | 50 | 0.0032369 | 0.00081124 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1347-6_0_5_load_70 | 51 | 0.0062322 | 0.0015619 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1347-6_0_5_load_68 | 52 | 0.0035033 | 0.00087801 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1347-6_0_5_load_62 | 54 | 0.0040124 | 0.0010056 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1347-6_0_5_load_77 | 56 | 0.0029755 | 0.00074574 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1347-6_0_5_load_42 | 57 | 0.0089071 | 0.0022323 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1347-6_0_5_load_48 | 58 | 0.011835 | 0.0029662 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1347-6_0_5_load_51 | 59 | 0.008162 | 0.0020456 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1347-6_0_5_load_55 | 61 | 0.0054786 | 0.0013731 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1347-6_0_5_load_47 | 62 | 0.0026834 | 0.00067253 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1347-6_0_5_load_46 | 63 | 0.0038668 | 0.00096911 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1347-6_0_5_load_73 | 65 | 0.0037195 | 0.00093221 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1347-6_0_5_load_69 | 66 | 0.0065299 | 0.0016365 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1347-6_0_5_load_63 | 67 | 0.0085917 | 0.0021533 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1347-6_0_5_load_78 | 68 | 0.0053294 | 0.0013357 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1347-6_0_5_load_58 | 70 | 0.0039908 | 0.0010002 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1347-6_0_5_load_59 | 71 | 0.0056935 | 0.0014269 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1347-6_0_5_load_147 | 73 | 0.01283 | 0.0032155 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1347-6_0_5_load_64 | 74 | 0.005672 | 0.0014215 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1347-6_0_5_load_67 | 75 | 0.0058959 | 0.0014776 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1347-6_0_5_load_66 | 76 | 0.0030942 | 0.00077549 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1347-6_0_5_load_65 | 77 | 0.0043687 | 0.0010949 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1347-6_0_5_load_71 | 78 | 0.0032152 | 0.0008058 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1347-6_0_5_load_72 | 79 | 0.0035724 | 0.00089533 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1347-6_0_5_load_75 | 81 | 0.0082303 | 0.0020627 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1347-6_0_5_load_76 | 82 | 0.004454 | 0.0011163 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1347-6_0_5_load_141 | 84 | 0.0032168 | 0.0008062 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1347-6_0_5_load_138 | 85 | 0.0069569 | 0.0017436 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1347-6_0_5_load_142 | 86 | 0.0057557 | 0.0014425 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1347-6_0_5_load_79 | 87 | 0.0043444 | 0.0010888 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1347-6_0_5_load_99 | 89 | 0.0029327 | 0.000735 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1347-6_0_5_load_100 | 90 | 0.0094615 | 0.0023713 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1347-6_0_5_load_80 | 91 | 0.0032871 | 0.00082384 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1347-6_0_5_load_81 | 92 | 0.0059395 | 0.0014886 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1347-6_0_5_load_82 | 93 | 0.0038345 | 0.00096101 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1347-6_0_5_load_83 | 94 | 0.0057042 | 0.0014296 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1347-6_0_5_load_84 | 95 | 0.0068159 | 0.0017082 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1347-6_0_5_load_85 | 96 | 0.0027687 | 0.00069389 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1347-6_0_5_load_97 | 98 | 0.0037558 | 0.0009413 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1347-6_0_5_load_87 | 101 | 0.0048675 | 0.0012199 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1347-6_0_5_load_88 | 102 | 0.0053424 | 0.0013389 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1347-6_0_5_load_89 | 103 | 0.006406 | 0.0016055 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1347-6_0_5_load_90 | 104 | 0.0027339 | 0.00068518 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1347-6_0_5_load_92 | 105 | 0.0038837 | 0.00097335 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1347-6_0_5_load_139 | 107 | 0.0063909 | 0.0016017 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1347-6_0_5_load_94 | 108 | 0.0038518 | 0.00096534 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1347-6_0_5_load_95 | 109 | 0.0040403 | 0.0010126 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1347-6_0_5_load_103 | 110 | 0.0044906 | 0.0011255 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1347-6_0_5_load_127 | 111 | 0.011685 | 0.0029286 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1347-6_0_5_load_128 | 112 | 0.0018245 | 0.00045727 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1347-6_0_5_load_126 | 113 | 0.016036 | 0.004019 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1347-6_0_5_load_102 | 114 | 0.0014264 | 0.0003575 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1347-6_0_5_load_105 | 115 | 0.003972 | 0.00099547 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1347-6_0_5_load_106 | 116 | 0.0026944 | 0.00067527 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1347-6_0_5_load_112 | 117 | 0.0040613 | 0.0010179 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1347-6_0_5_load_118 | 118 | 0.004186 | 0.0010491 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1347-6_0_5_load_111 | 120 | 0.0022789 | 0.00057113 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1347-6_0_5_load_107 | 121 | 0.0031923 | 0.00080007 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1347-6_0_5_load_108 | 122 | 0.0037094 | 0.00092967 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1347-6_0_5_load_110 | 123 | 0.0041331 | 0.0010359 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1347-6_0_5_load_113 | 124 | 0.00024406 | 6.1166e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1347-6_0_5_load_117 | 126 | 9.6768e-05 | 2.4252e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1347-6_0_5_load_115 | 127 | 0.00024158 | 6.0546e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1347-6_0_5_load_121 | 128 | 0.0035525 | 0.00089034 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1347-6_0_5_load_116 | 130 | 0.0042548 | 0.0010664 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1347-6_0_5_load_119 | 131 | 0.00020294 | 5.0862e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1347-6_0_5_load_130 | 133 | 0.0014824 | 0.00037152 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1347-6_0_5_load_131 | 134 | 0.0013626 | 0.00034149 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1347-6_0_5_load_132 | 135 | 0.00072489 | 0.00018167 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1347-6_0_5_load_133 | 136 | 0.0012453 | 0.00031209 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1347-6_0_5_load_144 | 137 | 0.0006044 | 0.00015148 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1347-6_0_5_load_134 | 138 | 0.0025157 | 0.00063051 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1347-6_0_5_load_152 | 140 | 0.0087247 | 0.0021866 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1347-6_0_5_load_135 | 141 | 0.0025275 | 0.00063345 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1347-6_0_5_load_136 | 142 | 0.0027543 | 0.00069028 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1347-6_0_5_load_137 | 143 | 0.0025363 | 0.00063565 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1347-6_0_5_load_140 | 144 | 0.013683 | 0.0034294 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1347-6_0_5_load_143 | 145 | 0.004007 | 0.0010043 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1347-6_0_5_load_148 | 146 | 0.0038042 | 0.00095343 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1347-6_0_5_load_150 | 148 | 0.0028693 | 0.00071912 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 65 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1347-6_0_5_line_0 |  | 0 | 1 | 0.0082437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1347-6_0_5_line_1 |  | 0 | 2 | 0.0419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1347-6_0_5_line_2 |  | 1 | 3 | 0.04594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1347-6_0_5_line_3 |  | 2 | 4 | 0.0081164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1347-6_0_5_line_4 |  | 3 | 8 | 0.0038268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1347-6_0_5_line_5 |  | 3 | 9 | 0.018547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1347-6_0_5_line_6 |  | 4 | 10 | 0.0076179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1347-6_0_5_line_7 |  | 5 | 6 | 0.037785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1347-6_0_5_line_8 |  | 5 | 7 | 0.022757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1347-6_0_5_line_9 |  | 6 | 13 | 0.035196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1347-6_0_5_line_10 |  | 6 | 14 | 0.044033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1347-6_0_5_line_11 |  | 7 | 11 | 0.022418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1347-6_0_5_line_12 |  | 7 | 9 | 0.12911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1347-6_0_5_line_13 |  | 10 | 12 | 0.01374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1347-6_0_5_line_14 |  | 11 | 16 | 0.022884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1347-6_0_5_line_15 |  | 14 | 15 | 0.045143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1347-6_0_5_line_16 |  | 15 | 99 | 0.026378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1347-6_0_5_line_17 |  | 16 | 128 | 0.015845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1347-6_0_5_line_18 |  | 17 | 18 | 0.032945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1347-6_0_5_line_19 |  | 18 | 19 | 0.042925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1347-6_0_5_line_20 |  | 19 | 20 | 0.042303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1347-6_0_5_line_21 |  | 20 | 23 | 0.031783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1347-6_0_5_line_22 |  | 20 | 24 | 0.023321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1347-6_0_5_line_23 |  | 21 | 22 | 0.012254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1347-6_0_5_line_24 |  | 22 | 27 | 9.5999e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1347-6_0_5_line_25 |  | 23 | 25 | 0.014284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1347-6_0_5_line_26 |  | 24 | 26 | 0.056671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1347-6_0_5_line_27 |  | 25 | 27 | 0.020201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1347-6_0_5_line_28 |  | 26 | 28 | 0.030205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1347-6_0_5_line_29 |  | 28 | 29 | 0.035801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1347-6_0_5_line_30 |  | 29 | 32 | 0.02688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1347-6_0_5_line_31 |  | 29 | 33 | 0.016115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1347-6_0_5_line_32 |  | 30 | 31 | 0.013648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1347-6_0_5_line_33 |  | 31 | 34 | 0.012176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1347-6_0_5_line_34 |  | 32 | 37 | 0.0081049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1347-6_0_5_line_35 |  | 33 | 36 | 0.0076517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1347-6_0_5_line_36 |  | 34 | 41 | 0.014055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1347-6_0_5_line_37 |  | 34 | 42 | 0.04399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1347-6_0_5_line_38 |  | 34 | 37 | 0.039757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1347-6_0_5_line_39 |  | 35 | 36 | 0.0023582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1347-6_0_5_line_40 |  | 37 | 38 | 0.011312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_1347-6_0_5_line_41 |  | 38 | 39 | 0.011441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1347-6_0_5_line_42 |  | 38 | 40 | 0.011531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1347-6_0_5_line_43 |  | 40 | 43 | 0.048571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1347-6_0_5_line_44 |  | 42 | 44 | 0.020447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1347-6_0_5_line_45 |  | 43 | 48 | 0.031564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1347-6_0_5_line_46 |  | 44 | 47 | 0.032598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1347-6_0_5_line_47 |  | 45 | 46 | 0.0053713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1347-6_0_5_line_48 |  | 46 | 59 | 0.005111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1347-6_0_5_line_49 |  | 46 | 60 | 0.023916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1347-6_0_5_line_50 |  | 47 | 58 | 0.0012526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1347-6_0_5_line_51 |  | 47 | 55 | 0.03576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1347-6_0_5_line_52 |  | 48 | 49 | 0.009247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1347-6_0_5_line_53 |  | 48 | 50 | 0.03426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1347-6_0_5_line_54 |  | 49 | 51 | 0.01612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1347-6_0_5_line_55 |  | 49 | 52 | 0.055139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1347-6_0_5_line_56 |  | 50 | 56 | 0.017214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_1347-6_0_5_line_57 |  | 51 | 65 | 0.013562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_1347-6_0_5_line_58 |  | 52 | 66 | 0.0032757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1347-6_0_5_line_59 |  | 53 | 54 | 0.017423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1347-6_0_5_line_60 |  | 53 | 55 | 0.014373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1347-6_0_5_line_61 |  | 54 | 67 | 0.0090277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1347-6_0_5_line_62 |  | 55 | 57 | 0.035648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1347-6_0_5_line_63 |  | 56 | 68 | 0.038352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_1347-6_0_5_line_64 |  | 58 | 63 | 0.02835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1347-6_0_5_line_65 |  | 60 | 61 | 0.0058699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1347-6_0_5_line_66 |  | 60 | 62 | 0.031668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1347-6_0_5_line_67 |  | 61 | 64 | 0.012426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1347-6_0_5_line_68 |  | 62 | 63 | 0.016224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1347-6_0_5_line_69 |  | 64 | 69 | 0.008379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1347-6_0_5_line_70 |  | 64 | 70 | 0.053603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1347-6_0_5_line_71 |  | 65 | 78 | 0.038498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1347-6_0_5_line_72 |  | 67 | 74 | 0.033348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1347-6_0_5_line_73 |  | 68 | 87 | 0.026635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_1347-6_0_5_line_74 |  | 69 | 71 | 0.0090863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1347-6_0_5_line_75 |  | 70 | 72 | 0.029622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1347-6_0_5_line_76 |  | 72 | 73 | 0.064582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1347-6_0_5_line_77 |  | 74 | 75 | 0.017996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1347-6_0_5_line_78 |  | 75 | 76 | 0.018054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1347-6_0_5_line_79 |  | 76 | 77 | 0.005205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1347-6_0_5_line_80 |  | 78 | 79 | 0.023981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1347-6_0_5_line_81 |  | 79 | 80 | 0.0056343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1347-6_0_5_line_82 |  | 80 | 81 | 0.017329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1347-6_0_5_line_83 |  | 80 | 82 | 0.017184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1347-6_0_5_line_84 |  | 81 | 83 | 0.019389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1347-6_0_5_line_85 |  | 82 | 84 | 0.035097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1347-6_0_5_line_86 |  | 83 | 85 | 0.018848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1347-6_0_5_line_87 |  | 84 | 86 | 0.0098979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1347-6_0_5_line_88 |  | 85 | 107 | 0.014721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1347-6_0_5_line_89 |  | 86 | 145 | 0.030946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1347-6_0_5_line_90 |  | 87 | 88 | 0.0092664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_1347-6_0_5_line_91 |  | 88 | 89 | 0.024557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_1347-6_0_5_line_92 |  | 88 | 90 | 0.056898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1347-6_0_5_line_93 |  | 89 | 100 | 0.017985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_1347-6_0_5_line_94 |  | 91 | 92 | 0.027218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1347-6_0_5_line_95 |  | 91 | 93 | 6.6726e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1347-6_0_5_line_96 |  | 92 | 94 | 0.032937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1347-6_0_5_line_97 |  | 93 | 95 | 0.00095039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1347-6_0_5_line_98 |  | 94 | 96 | 0.03586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1347-6_0_5_line_99 |  | 96 | 97 | 0.022743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1347-6_0_5_line_100 |  | 97 | 98 | 0.014404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_1347-6_0_5_line_101 |  | 97 | 99 | 0.011018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_1347-6_0_5_line_102 |  | 98 | 100 | 0.026859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_1347-6_0_5_line_103 |  | 99 | 110 | 0.027271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_1347-6_0_5_line_104 |  | 100 | 114 | 0.013704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1347-6_0_5_line_105 |  | 101 | 102 | 0.017957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1347-6_0_5_line_106 |  | 101 | 103 | 0.00341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1347-6_0_5_line_107 |  | 102 | 104 | 0.01117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1347-6_0_5_line_108 |  | 104 | 105 | 0.00029327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1347-6_0_5_line_109 |  | 105 | 106 | 0.04136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1347-6_0_5_line_110 |  | 106 | 108 | 0.0092822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1347-6_0_5_line_111 |  | 106 | 109 | 0.023054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1347-6_0_5_line_112 |  | 107 | 144 | 0.013633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1347-6_0_5_line_113 |  | 108 | 110 | 0.011937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1347-6_0_5_line_114 |  | 109 | 111 | 0.033729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1347-6_0_5_line_115 |  | 111 | 112 | 0.032248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1347-6_0_5_line_116 |  | 111 | 113 | 0.044598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1347-6_0_5_line_117 |  | 112 | 132 | 0.031165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1347-6_0_5_line_118 |  | 114 | 115 | 0.0066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1347-6_0_5_line_119 |  | 115 | 116 | 0.018576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1347-6_0_5_line_120 |  | 116 | 120 | 0.03929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1347-6_0_5_line_121 |  | 117 | 118 | 0.0048213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1347-6_0_5_line_122 |  | 117 | 119 | 0.020256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1347-6_0_5_line_123 |  | 119 | 120 | 0.012197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1347-6_0_5_line_124 |  | 119 | 121 | 0.013914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1347-6_0_5_line_125 |  | 121 | 122 | 0.0049825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1347-6_0_5_line_126 |  | 122 | 123 | 0.019475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1347-6_0_5_line_127 |  | 123 | 124 | 0.025382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1347-6_0_5_line_128 |  | 124 | 125 | 0.03084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1347-6_0_5_line_129 |  | 125 | 126 | 0.014418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1347-6_0_5_line_130 |  | 125 | 127 | 0.014421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1347-6_0_5_line_131 |  | 126 | 129 | 0.0094656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1347-6_0_5_line_132 |  | 127 | 130 | 0.030332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1347-6_0_5_line_133 |  | 129 | 131 | 0.024589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1347-6_0_5_line_134 |  | 132 | 133 | 0.010418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1347-6_0_5_line_135 |  | 132 | 134 | 0.011627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1347-6_0_5_line_136 |  | 133 | 135 | 0.036914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1347-6_0_5_line_137 |  | 134 | 136 | 0.012459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1347-6_0_5_line_138 |  | 135 | 137 | 0.077881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1347-6_0_5_line_139 |  | 136 | 138 | 0.018211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1347-6_0_5_line_140 |  | 137 | 139 | 0.016898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1347-6_0_5_line_141 |  | 138 | 141 | 0.01222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1347-6_0_5_line_142 |  | 139 | 140 | 0.096522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1347-6_0_5_line_143 |  | 140 | 149 | 0.073305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1347-6_0_5_line_144 |  | 141 | 142 | 0.017331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1347-6_0_5_line_145 |  | 142 | 143 | 0.012598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_1347-6_0_5_line_146 |  | 146 | 147 | 0.059887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1347-6_0_5_line_147 |  | 147 | 148 | 0.034459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_1347-6_0_5_line_148 |  | 148 | 149 | 0.040121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1347-6_0_5_trafo_73 | 0.63 MVA 20/0.4 kV | 150 | 65 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2713202.8846 | 1229220.1476 | 2713199.3452 | 1229212.7024
1 | 2713202.8846 | 1229220.1476 | 2713220.8737 | 1229257.9889
2 | 2713200.1768 | 1229169.04 | 2713205.0981 | 1229183.6005 | 2713205.6119 | 1229199.9896 | 2713199.3452 | 1229212.7024
3 | 2713220.8737 | 1229257.9889 | 2713224.3584 | 1229265.3191
4 | 2713200.1768 | 1229169.04 | 2713197.833 | 1229166.015
5 | 2713200.1768 | 1229169.04 | 2713212.2215 | 1229158.539 | 2713214.4596 | 1229157.2807
6 | 2713224.3584 | 1229265.3191 | 2713224.3584 | 1229265.3191 | 2713226.3387 | 1229272.6751
7 | 2713339.7604 | 1229120.4718 | 2713376.4382 | 1229110.9746
8 | 2713339.7604 | 1229120.4718 | 2713331.7017 | 1229107.119 | 2713330.2233 | 1229100.1126
9 | 2713376.4382 | 1229110.9746 | 2713377.2819 | 1229123.9562 | 2713373.2056 | 1229145.7621
10 | 2713376.4382 | 1229110.9746 | 2713418.851 | 1229099.139
11 | 2713328.7692 | 1229077.7595 | 2713329.8877 | 1229098.5223 | 2713330.2233 | 1229100.1126
12 | 2713330.2233 | 1229100.1126 | 2713214.4596 | 1229157.2807
13 | 2713229.9104 | 1229285.9424 | 2713226.3387 | 1229272.6751
14 | 2713328.7692 | 1229077.7595 | 2713327.5382 | 1229054.9088
15 | 2713462.3328 | 1229087.005 | 2713418.851 | 1229099.139
16 | 2713487.3315 | 1229078.3753 | 2713462.3328 | 1229087.005
17 | 2713326.6859 | 1229039.0871 | 2713327.5382 | 1229054.9088
18 | 2713945.8397 | 1228932.9508 | 2713953.8279 | 1228964.9132
19 | 2713945.8397 | 1228932.9508 | 2713933.6698 | 1228934.4744 | 2713911.4554 | 1228933.7817 | 2713903.4055 | 1228936.3007
20 | 2713861.5588 | 1228936.9399 | 2713871.7611 | 1228936.4571 | 2713880.4848 | 1228935.6235 | 2713898.1283 | 1228937.952 | 2713903.4055 | 1228936.3007
21 | 2713861.5588 | 1228936.9399 | 2713869.8294 | 1228967.6283
22 | 2713861.5588 | 1228936.9399 | 2713840.4903 | 1228946.9396
23 | 2713883.783 | 1228999.2404 | 2713885.1132 | 1229002.1747 | 2713890.8061 | 1229009.1876
24 | 2713883.783 | 1228999.2404 | 2713883.7434 | 1228999.153
25 | 2713875.4027 | 1228980.7539 | 2713870.382 | 1228969.6786 | 2713869.8294 | 1228967.6283
26 | 2713789.2932 | 1228971.2392 | 2713840.4903 | 1228946.9396
27 | 2713883.7434 | 1228999.153 | 2713875.4027 | 1228980.7539
28 | 2713789.2932 | 1228971.2392 | 2713759.3059 | 1228974.8581
29 | 2713723.7628 | 1228979.1476 | 2713759.3059 | 1228974.8581
30 | 2713723.7628 | 1228979.1476 | 2713727.0169 | 1228989.6846 | 2713733.5173 | 1229000.8731 | 2713735.3815 | 1229003.1103
31 | 2713723.7628 | 1228979.1476 | 2713720.9743 | 1228963.2754
32 | 2713779.1715 | 1229026.8545 | 2713788.7843 | 1229017.1668
33 | 2713770.5949 | 1229035.4979 | 2713779.1715 | 1229026.8545
34 | 2713740.57 | 1229009.3367 | 2713735.3815 | 1229003.1103
35 | 2713719.6503 | 1228955.7392 | 2713720.9743 | 1228963.2754
36 | 2713770.5949 | 1229035.4979 | 2713780.8273 | 1229045.1331
37 | 2713770.5949 | 1229035.4979 | 2713760.5805 | 1229046.7595 | 2713755.895 | 1229056.7665 | 2713762.662 | 1229073.3059
38 | 2713770.5949 | 1229035.4979 | 2713740.57 | 1229009.3367
39 | 2713719.2422 | 1228953.4165 | 2713719.6503 | 1228955.7392
40 | 2713740.57 | 1229009.3367 | 2713733.3924 | 1229018.0952
41 | 2713733.3924 | 1229018.0952 | 2713731.2834 | 1229026.528 | 2713730.1044 | 1229029.0103
42 | 2713733.3924 | 1229018.0952 | 2713723.2325 | 1229023.5486
43 | 2713723.2325 | 1229023.5486 | 2713680.4371 | 1229046.5199
44 | 2713770.4047 | 1229092.2299 | 2713762.662 | 1229073.3059
45 | 2713660.2873 | 1229070.227 | 2713675.6435 | 1229049.093 | 2713680.4371 | 1229046.5199
46 | 2713770.9272 | 1229124.2395 | 2713772.9805 | 1229098.5256 | 2713770.4047 | 1229092.2299
47 | 2713824.1563 | 1229083.8934 | 2713820.1431 | 1229080.3234
48 | 2713827.616 | 1229080.1233 | 2713824.1563 | 1229083.8934
49 | 2713824.1563 | 1229083.8934 | 2713833.7429 | 1229092.5947 | 2713842.4501 | 1229099.3332
50 | 2713770.9272 | 1229124.2395 | 2713772.1719 | 1229124.0994
51 | 2713770.9272 | 1229124.2395 | 2713761.5049 | 1229123.581 | 2713735.1539 | 1229121.6756
52 | 2713660.2873 | 1229070.227 | 2713654.6974 | 1229077.6036
53 | 2713660.2873 | 1229070.227 | 2713628.3392 | 1229057.8562
54 | 2713654.6974 | 1229077.6036 | 2713644.9681 | 1229090.4559
55 | 2713654.6974 | 1229077.6036 | 2713667.261 | 1229082.4252 | 2713675.0525 | 1229091.8814 | 2713678.7944 | 1229109.8001 | 2713677.6811 | 1229120.8689
56 | 2713612.2866 | 1229051.6404 | 2713628.3392 | 1229057.8562
57 | 2713638.3028 | 1229101.9904 | 2713639.2803 | 1229097.9693 | 2713644.9681 | 1229090.4559
58 | 2713677.3533 | 1229124.1281 | 2713677.6811 | 1229120.8689
59 | 2713721.0966 | 1229118.4933 | 2713714.3825 | 1229134.5711
60 | 2713735.1539 | 1229121.6756 | 2713721.0966 | 1229118.4933
61 | 2713714.3825 | 1229134.5711 | 2713710.9037 | 1229142.9016
62 | 2713735.1539 | 1229121.6756 | 2713730.7202 | 1229086.3042
63 | 2713612.2866 | 1229051.6404 | 2713589.1458 | 1229042.68 | 2713576.3769 | 1229038.1856
64 | 2713798.8419 | 1229115.5368 | 2713789.8572 | 1229120.2986 | 2713781.309 | 1229123.0706 | 2713772.1719 | 1229124.0994
65 | 2713842.4501 | 1229099.3332 | 2713848.0112 | 1229101.2122
66 | 2713842.4501 | 1229099.3332 | 2713836.386 | 1229105.7443 | 2713829.7874 | 1229108.0087 | 2713814.1703 | 1229110.8153
67 | 2713860.1646 | 1229102.2857 | 2713854.4759 | 1229102.9439 | 2713850.1604 | 1229101.9383 | 2713848.0112 | 1229101.2122
68 | 2713798.8419 | 1229115.5368 | 2713804.4571 | 1229112.5608 | 2713814.1703 | 1229110.8153
69 | 2713860.1646 | 1229102.2857 | 2713868.2276 | 1229099.9271
70 | 2713860.1646 | 1229102.2857 | 2713848.1901 | 1229154.5345
71 | 2713629.2089 | 1229139.3985 | 2713638.3028 | 1229101.9904
72 | 2713698.0531 | 1229173.6743 | 2713710.9037 | 1229142.9016
73 | 2713576.3769 | 1229038.1856 | 2713551.2525 | 1229029.3424
74 | 2713868.2276 | 1229099.9271 | 2713876.1439 | 1229095.7309 | 2713876.2553 | 1229095.6706
75 | 2713845.0885 | 1229183.9381 | 2713846.826 | 1229160.4865 | 2713848.1901 | 1229154.5345
76 | 2713799.6713 | 1229213.692 | 2713821.617 | 1229214.1122 | 2713833.8756 | 1229210.6997 | 2713840.7194 | 1229203.5363 | 2713844.9127 | 1229186.3922 | 2713845.0885 | 1229183.9381
77 | 2713691.1185 | 1229190.2801 | 2713698.0531 | 1229173.6743
78 | 2713688.3159 | 1229207.9762 | 2713689.6461 | 1229193.8059 | 2713691.1185 | 1229190.2801
79 | 2713687.8294 | 1229213.1584 | 2713688.3159 | 1229207.9762
80 | 2713629.2089 | 1229139.3985 | 2713623.5442 | 1229162.7004
81 | 2713622.2133 | 1229168.1753 | 2713623.5442 | 1229162.7004
82 | 2713622.2133 | 1229168.1753 | 2713604.8909 | 1229167.6868
83 | 2713622.2133 | 1229168.1753 | 2713617.7095 | 1229184.759
84 | 2713585.5093 | 1229167.1401 | 2713604.8909 | 1229167.6868
85 | 2713617.7095 | 1229184.759 | 2713608.5111 | 1229218.6289
86 | 2713585.5093 | 1229167.1401 | 2713578.6948 | 1229184.7127
87 | 2713608.5111 | 1229218.6289 | 2713605.917 | 1229228.1809
88 | 2713578.6948 | 1229184.7127 | 2713573.3725 | 1229198.4376
89 | 2713597.8065 | 1229258.0453 | 2713605.917 | 1229228.1809
90 | 2713542.5117 | 1229026.2658 | 2713551.2525 | 1229029.3424
91 | 2713542.5117 | 1229026.2658 | 2713529.0003 | 1229023.0499 | 2713518.5067 | 1229024.9734
92 | 2713542.5117 | 1229026.2658 | 2713575.822 | 1228990.7855 | 2713579.1889 | 1228983.2747
93 | 2713500.8163 | 1229028.216 | 2713518.5067 | 1229024.9734
94 | 2713592.591 | 1229103.0135 | 2713565.4149 | 1229101.5126
95 | 2713592.5977 | 1229103.0139 | 2713592.591 | 1229103.0135
96 | 2713565.4149 | 1229101.5126 | 2713532.5285 | 1229099.6962
97 | 2713593.5466 | 1229103.0663 | 2713592.5977 | 1229103.0139
98 | 2713532.5285 | 1229099.6962 | 2713526.1335 | 1229099.343 | 2713515.4231 | 1229095.8915 | 2713509.8582 | 1229078.5608
99 | 2713490.4811 | 1229067.8161 | 2713503.4784 | 1229072.1563 | 2713509.8582 | 1229078.5608 | 2713509.8582 | 1229078.5608
100 | 2713490.4811 | 1229067.8161 | 2713494.9871 | 1229054.1352
101 | 2713487.3315 | 1229078.3753 | 2713490.4811 | 1229067.8161
102 | 2713500.8163 | 1229028.216 | 2713500.8427 | 1229036.3562 | 2713494.9871 | 1229054.1352
103 | 2713487.3315 | 1229078.3753 | 2713487.5269 | 1229105.6453
104 | 2713500.8163 | 1229028.216 | 2713499.3724 | 1229014.5885
105 | 2713540.3678 | 1229130.6264 | 2713558.2822 | 1229131.8581
106 | 2713561.6842 | 1229132.092 | 2713558.2822 | 1229131.8581
107 | 2713540.3678 | 1229130.6264 | 2713529.224 | 1229129.8601
108 | 2713529.224 | 1229129.8601 | 2713528.9314 | 1229129.84
109 | 2713487.6788 | 1229126.8638 | 2713524.0493 | 1229129.5044 | 2713528.9314 | 1229129.84
110 | 2713487.6788 | 1229126.8638 | 2713487.6123 | 1229117.5818
111 | 2713487.6788 | 1229126.8638 | 2713485.8252 | 1229149.8432
112 | 2713568.4435 | 1229211.1483 | 2713573.3725 | 1229198.4376
113 | 2713487.5269 | 1229105.6453 | 2713487.6123 | 1229117.5818
114 | 2713485.8252 | 1229149.8432 | 2713483.1133 | 1229183.4634
115 | 2713483.1133 | 1229183.4634 | 2713480.5205 | 1229215.607
116 | 2713483.1133 | 1229183.4634 | 2713439.2537 | 1229175.3806
117 | 2713469.8297 | 1229244.8812 | 2713480.5205 | 1229215.607
118 | 2713499.3724 | 1229014.5885 | 2713498.677 | 1229008.0253
119 | 2713496.7196 | 1228989.5524 | 2713498.677 | 1229008.0253
120 | 2713496.7196 | 1228989.5524 | 2713457.7936 | 1228994.8917
121 | 2713445.8521 | 1229022.1745 | 2713445.8349 | 1229017.3532
122 | 2713445.7625 | 1228997.0973 | 2713445.8349 | 1229017.3532
123 | 2713445.7625 | 1228997.0973 | 2713457.7936 | 1228994.8917
124 | 2713445.7625 | 1228997.0973 | 2713432.5418 | 1228992.7607
125 | 2713432.5418 | 1228992.7607 | 2713427.8076 | 1228991.2078
126 | 2713409.3029 | 1228985.138 | 2713427.8076 | 1228991.2078
127 | 2713409.3029 | 1228985.138 | 2713387.3803 | 1228977.9471 | 2713385.1182 | 1228977.4773
128 | 2713361.319 | 1228993.7959 | 2713372.8751 | 1228981.9292 | 2713379.8922 | 1228976.392 | 2713385.1182 | 1228977.4773
129 | 2713361.319 | 1228993.7959 | 2713351.0725 | 1228983.6522
130 | 2713361.319 | 1228993.7959 | 2713371.569 | 1229003.9393
131 | 2713344.3456 | 1228976.9928 | 2713351.0725 | 1228983.6522
132 | 2713371.569 | 1229003.9393 | 2713387.694 | 1229019.8965 | 2713394.0714 | 1229024.1141
133 | 2713344.3456 | 1228976.9928 | 2713347.4667 | 1228952.6026
134 | 2713469.8297 | 1229244.8812 | 2713466.3816 | 1229254.7123
135 | 2713469.8297 | 1229244.8812 | 2713480.5705 | 1229249.3335
136 | 2713454.1642 | 1229289.546 | 2713466.3816 | 1229254.7123
137 | 2713480.5705 | 1229249.3335 | 2713492.0803 | 1229254.1046
138 | 2713454.1642 | 1229289.546 | 2713458.3678 | 1229367.3134
139 | 2713492.0803 | 1229254.1046 | 2713508.9028 | 1229261.0779
140 | 2713468.4687 | 1229380.8604 | 2713458.3678 | 1229367.3134
141 | 2713508.9028 | 1229261.0779 | 2713520.1911 | 1229265.7571
142 | 2713468.4687 | 1229380.8604 | 2713564.0494 | 1229394.3061
143 | 2713585.8699 | 1229464.288 | 2713564.0494 | 1229394.3061
144 | 2713520.1911 | 1229265.7571 | 2713536.2015 | 1229272.3938
145 | 2713536.2015 | 1229272.3938 | 2713547.8395 | 1229277.218
146 | 2713657.5466 | 1229448.5229 | 2713642.1404 | 1229423.1867 | 2713640.597 | 1229418.6981 | 2713641.67 | 1229416.0833 | 2713644.9856 | 1229412.6996 | 2713650.3273 | 1229409.5659 | 2713655.4295 | 1229408.6516 | 2713661.7906 | 1229410.2025
147 | 2713657.5466 | 1229448.5229 | 2713649.632 | 1229451.4739 | 2713639.2594 | 1229449.4186 | 2713624.1107 | 1229452.391
148 | 2713585.8699 | 1229464.288 | 2713614.7822 | 1229454.2214 | 2713624.1107 | 1229452.391

## bus_geodata
| x | y | coords
0 | 2713202.8845 | 1229220.1476
1 | 2713199.3452 | 1229212.7024
2 | 2713220.8737 | 1229257.9889
3 | 2713200.1768 | 1229169.04
4 | 2713224.3584 | 1229265.3191
5 | 2713339.7604 | 1229120.4718
6 | 2713376.4382 | 1229110.9746
7 | 2713330.2233 | 1229100.1126
8 | 2713197.833 | 1229166.015
9 | 2713214.4596 | 1229157.2807
10 | 2713226.3387 | 1229272.6751
11 | 2713328.7692 | 1229077.7595
12 | 2713229.9104 | 1229285.9424
13 | 2713373.2056 | 1229145.7621
14 | 2713418.851 | 1229099.139
15 | 2713462.3328 | 1229087.005
16 | 2713327.5382 | 1229054.9088
17 | 2713953.8279 | 1228964.9132
18 | 2713945.8398 | 1228932.9508
19 | 2713903.4055 | 1228936.3007
20 | 2713861.5588 | 1228936.9399
21 | 2713890.8061 | 1229009.1876
22 | 2713883.783 | 1228999.2404
23 | 2713869.8294 | 1228967.6283
24 | 2713840.4903 | 1228946.9396
25 | 2713875.4027 | 1228980.7539
26 | 2713789.2932 | 1228971.2392
27 | 2713883.7434 | 1228999.153
28 | 2713759.3059 | 1228974.8581
29 | 2713723.7628 | 1228979.1476
30 | 2713788.7843 | 1229017.1668
31 | 2713779.1715 | 1229026.8545
32 | 2713735.3815 | 1229003.1103
33 | 2713720.9743 | 1228963.2754
34 | 2713770.5949 | 1229035.4979
35 | 2713719.2422 | 1228953.4165
36 | 2713719.6503 | 1228955.7392
37 | 2713740.57 | 1229009.3367
38 | 2713733.3924 | 1229018.0952
39 | 2713730.1044 | 1229029.0103
40 | 2713723.2325 | 1229023.5486
41 | 2713780.8273 | 1229045.1331
42 | 2713762.662 | 1229073.3059
43 | 2713680.4371 | 1229046.5199
44 | 2713770.4047 | 1229092.2299
45 | 2713820.1431 | 1229080.3234
46 | 2713824.1564 | 1229083.8934
47 | 2713770.9272 | 1229124.2395
48 | 2713660.2873 | 1229070.227
49 | 2713654.6974 | 1229077.6036
50 | 2713628.3392 | 1229057.8562
51 | 2713644.9681 | 1229090.4559
52 | 2713677.6811 | 1229120.8689
53 | 2713721.0966 | 1229118.4933
54 | 2713714.3825 | 1229134.5711
55 | 2713735.1539 | 1229121.6756
56 | 2713612.2866 | 1229051.6404
57 | 2713730.7202 | 1229086.3042
58 | 2713772.1719 | 1229124.0994
59 | 2713827.616 | 1229080.1233
60 | 2713842.4501 | 1229099.3332
61 | 2713848.0112 | 1229101.2122
62 | 2713814.1703 | 1229110.8153
63 | 2713798.8419 | 1229115.5368
64 | 2713860.1646 | 1229102.2857
65 | 2713638.3028 | 1229101.9904
66 | 2713677.3533 | 1229124.1281
67 | 2713710.9037 | 1229142.9016
68 | 2713576.3769 | 1229038.1856
69 | 2713868.2276 | 1229099.9271
70 | 2713848.1901 | 1229154.5345
71 | 2713876.2553 | 1229095.6706
72 | 2713845.0885 | 1229183.9381
73 | 2713799.6713 | 1229213.692
74 | 2713698.0531 | 1229173.6743
75 | 2713691.1185 | 1229190.2801
76 | 2713688.3159 | 1229207.9762
77 | 2713687.8294 | 1229213.1584
78 | 2713629.2089 | 1229139.3985
79 | 2713623.5442 | 1229162.7004
80 | 2713622.2133 | 1229168.1753
81 | 2713604.8909 | 1229167.6868
82 | 2713617.7095 | 1229184.759
83 | 2713585.5093 | 1229167.1401
84 | 2713608.5111 | 1229218.6289
85 | 2713578.6948 | 1229184.7127
86 | 2713605.917 | 1229228.1809
87 | 2713551.2525 | 1229029.3424
88 | 2713542.5117 | 1229026.2658
89 | 2713518.5067 | 1229024.9734
90 | 2713579.1889 | 1228983.2747
91 | 2713592.591 | 1229103.0135
92 | 2713565.4149 | 1229101.5126
93 | 2713592.5977 | 1229103.0139
94 | 2713532.5285 | 1229099.6962
95 | 2713593.5466 | 1229103.0663
96 | 2713509.8582 | 1229078.5608
97 | 2713490.4811 | 1229067.8161
98 | 2713494.9871 | 1229054.1352
99 | 2713487.3315 | 1229078.3753
100 | 2713500.8163 | 1229028.216
101 | 2713558.2822 | 1229131.8581
102 | 2713540.3678 | 1229130.6264
103 | 2713561.6842 | 1229132.092
104 | 2713529.224 | 1229129.8601
105 | 2713528.9314 | 1229129.84
106 | 2713487.6788 | 1229126.8638
107 | 2713573.3725 | 1229198.4376
108 | 2713487.6123 | 1229117.5818
109 | 2713485.8252 | 1229149.8432
110 | 2713487.5269 | 1229105.6453
111 | 2713483.1133 | 1229183.4634
112 | 2713480.5205 | 1229215.607
113 | 2713439.2537 | 1229175.3806
114 | 2713499.3724 | 1229014.5885
115 | 2713498.677 | 1229008.0253
116 | 2713496.7196 | 1228989.5524
117 | 2713445.8349 | 1229017.3532
118 | 2713445.8521 | 1229022.1745
119 | 2713445.7625 | 1228997.0973
120 | 2713457.7936 | 1228994.8917
121 | 2713432.5418 | 1228992.7607
122 | 2713427.8076 | 1228991.2078
123 | 2713409.3029 | 1228985.138
124 | 2713385.1182 | 1228977.4773
125 | 2713361.319 | 1228993.7959
126 | 2713351.0725 | 1228983.6522
127 | 2713371.569 | 1229003.9393
128 | 2713326.6859 | 1229039.0871
129 | 2713344.3456 | 1228976.9928
130 | 2713394.0714 | 1229024.1141
131 | 2713347.4667 | 1228952.6026
132 | 2713469.8297 | 1229244.8812
133 | 2713466.3816 | 1229254.7123
134 | 2713480.5705 | 1229249.3335
135 | 2713454.1642 | 1229289.546
136 | 2713492.0803 | 1229254.1046
137 | 2713458.3678 | 1229367.3134
138 | 2713508.9028 | 1229261.0779
139 | 2713468.4687 | 1229380.8604
140 | 2713564.0494 | 1229394.3061
141 | 2713520.1911 | 1229265.7571
142 | 2713536.2015 | 1229272.3938
143 | 2713547.8395 | 1229277.218
144 | 2713568.4435 | 1229211.1483
145 | 2713597.8065 | 1229258.0453
146 | 2713661.7906 | 1229410.2025
147 | 2713657.5466 | 1229448.5229
148 | 2713624.1107 | 1229452.391
149 | 2713585.8699 | 1229464.288
150 | 2713654.6974 | 1229077.6036

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97438 | -0.49419 | 0.0018717 | 0.00046909
1 | 0.97443 | -0.49326 | 0.0004496 | 0.00011268
2 | 0.97421 | -0.49751 | 0.0006811 | 0.0001707
3 | 0.97471 | -0.48766 | 0 | 0
4 | 0.97418 | -0.49805 | 0.0021643 | 0.00054243
5 | 0.97687 | -0.44503 | 0 | 0
6 | 0.97788 | -0.42535 | 0 | 0
7 | 0.97627 | -0.4569 | 0.0045411 | 0.0011381
8 | 0.97471 | -0.48769 | 0.00042185 | 0.00010573
9 | 0.97483 | -0.48526 | 0.0049329 | 0.0012363
10 | 0.97417 | -0.49826 | 0.00083928 | 0.00021034
11 | 0.97602 | -0.46182 | 0.0041719 | 0.0010456
12 | 0.97416 | -0.49842 | 0.00062703 | 0.00015715
13 | 0.97741 | -0.43452 | 0.01429 | 0.0035814
14 | 0.97963 | -0.39104 | 0.016054 | 0.0040235
15 | 0.98209 | -0.34287 | 0 | 0
16 | 0.97585 | -0.4651 | 0.004277 | 0.0010719
17 | 0.9795 | -0.39375 | 0.0030112 | 0.00075468
18 | 0.97959 | -0.39195 | 0 | 0
19 | 0.97971 | -0.3896 | 0.00064993 | 0.00016289
20 | 0.97985 | -0.38678 | 0 | 0
21 | 0.97736 | -0.43563 | 0.014023 | 0.0035146
22 | 0.97752 | -0.43249 | 0.022038 | 0.0055233
23 | 0.9787 | -0.40927 | 0.0017472 | 0.0004379
24 | 0.98077 | -0.36877 | 0.0028266 | 0.00070842
25 | 0.97821 | -0.41893 | 0.00052247 | 0.00013094
26 | 0.98316 | -0.32225 | 0 | 0
27 | 0.97753 | -0.43243 | 0.00058736 | 0.00014721
28 | 0.98443 | -0.29755 | 0.016617 | 0.0041645
29 | 0.98649 | -0.25769 | 0 | 0
30 | 0.98607 | -0.2655 | 0.0082713 | 0.002073
31 | 0.98618 | -0.26347 | 0.0049954 | 0.001252
32 | 0.98837 | -0.22129 | 0.010553 | 0.0026449
33 | 0.98628 | -0.26164 | 0.0030637 | 0.00076783
34 | 0.98633 | -0.26058 | 0 | 0
35 | 0.98619 | -0.26341 | 0.0073326 | 0.0018377
36 | 0.98621 | -0.2631 | 0.0033052 | 0.00082836
37 | 0.98902 | -0.20882 | 0 | 0
38 | 0.99023 | -0.18547 | 0 | 0
39 | 0.99017 | -0.18667 | 0.0058719 | 0.0014716
40 | 0.99087 | -0.17329 | 0.0071715 | 0.0017973
41 | 0.98629 | -0.26136 | 0.0030926 | 0.00077508
42 | 0.98368 | -0.31169 | 0.011738 | 0.0029419
43 | 0.99363 | -0.12061 | 0.0014217 | 0.00035632
44 | 0.98144 | -0.3551 | 0.0034588 | 0.00086685
45 | 0.97326 | -0.51547 | 0.017024 | 0.0042666
46 | 0.97334 | -0.51379 | 0 | 0
47 | 0.97798 | -0.42267 | 0.0020295 | 0.00050865
48 | 0.99543 | -0.086338 | 0 | 0
49 | 0.9965 | -0.066156 | 0 | 0
50 | 0.99344 | -0.12413 | 0.0032369 | 0.00081124
51 | 0.99839 | -0.030371 | 0.0062322 | 0.0015619
52 | 0.99599 | -0.075872 | 0.0035033 | 0.00087801
53 | 0.97621 | -0.45745 | 0 | 0
54 | 0.97569 | -0.46753 | 0.0040124 | 0.0010056
55 | 0.97663 | -0.44913 | 0 | 0
56 | 0.99246 | -0.14293 | 0.0029755 | 0.00074574
57 | 0.97633 | -0.45494 | 0.0089071 | 0.0022323
58 | 0.97789 | -0.42431 | 0.011835 | 0.0029662
59 | 0.9733 | -0.51456 | 0.008162 | 0.0020456
60 | 0.9739 | -0.50272 | 0 | 0
61 | 0.97375 | -0.50574 | 0.0054786 | 0.0013731
62 | 0.97547 | -0.47181 | 0.0026834 | 0.00067253
63 | 0.97632 | -0.45523 | 0.0038668 | 0.00096911
64 | 0.97349 | -0.51088 | 0 | 0
65 | 1 | 0 | -0.58384 | -0.14964
66 | 0.99597 | -0.076248 | 0.0065299 | 0.0016365
67 | 0.97546 | -0.4721 | 0.0085917 | 0.0021533
68 | 0.99029 | -0.18444 | 0.0053294 | 0.0013357
69 | 0.97344 | -0.51176 | 0 | 0
70 | 0.97265 | -0.52748 | 0.0039908 | 0.0010002
71 | 0.97339 | -0.51271 | 0.0056935 | 0.0014269
72 | 0.97229 | -0.53449 | 0 | 0
73 | 0.97152 | -0.54978 | 0.01283 | 0.0032155
74 | 0.97487 | -0.48374 | 0.005672 | 0.0014215
75 | 0.97465 | -0.48815 | 0.0058959 | 0.0014776
76 | 0.97452 | -0.49062 | 0.0030942 | 0.00077549
77 | 0.9745 | -0.49104 | 0.0043687 | 0.0010949
78 | 0.99791 | -0.040001 | 0.0032152 | 0.0008058
79 | 0.99668 | -0.063649 | 0.0035724 | 0.00089533
80 | 0.99641 | -0.06886 | 0 | 0
81 | 0.99586 | -0.079594 | 0.0082303 | 0.0020627
82 | 0.99614 | -0.074122 | 0.004454 | 0.0011163
83 | 0.99538 | -0.088811 | 0 | 0
84 | 0.99573 | -0.082128 | 0.0032168 | 0.0008062
85 | 0.99491 | -0.097778 | 0.0069569 | 0.0017436
86 | 0.99564 | -0.083827 | 0.0057557 | 0.0014425
87 | 0.98882 | -0.21274 | 0.0043444 | 0.0010888
88 | 0.98832 | -0.22243 | 0 | 0
89 | 0.98704 | -0.24711 | 0.0029327 | 0.000735
90 | 0.98782 | -0.23204 | 0.0094615 | 0.0023713
91 | 0.98193 | -0.34627 | 0.0032871 | 0.00082384
92 | 0.98228 | -0.33941 | 0.0059395 | 0.0014886
93 | 0.98193 | -0.34627 | 0.0038345 | 0.00096101
94 | 0.98289 | -0.32759 | 0.0057042 | 0.0014296
95 | 0.98193 | -0.34638 | 0.0068159 | 0.0017082
96 | 0.98374 | -0.31105 | 0.0027687 | 0.00069389
97 | 0.98433 | -0.29945 | 0 | 0
98 | 0.98494 | -0.28756 | 0.0037558 | 0.0009413
99 | 0.98354 | -0.31484 | 0 | 0
100 | 0.98611 | -0.26499 | 0 | 0
101 | 0.97929 | -0.39775 | 0.0048675 | 0.0012199
102 | 0.97947 | -0.39407 | 0.0053424 | 0.0013389
103 | 0.97927 | -0.39815 | 0.006406 | 0.0016055
104 | 0.97965 | -0.3907 | 0.0027339 | 0.00068518
105 | 0.97965 | -0.3906 | 0.0038837 | 0.00097335
106 | 0.98054 | -0.37316 | 0 | 0
107 | 0.99465 | -0.10298 | 0.0063909 | 0.0016017
108 | 0.9813 | -0.35837 | 0.0038518 | 0.00096534
109 | 0.97915 | -0.40026 | 0.0040403 | 0.0010126
110 | 0.98232 | -0.33854 | 0.0044906 | 0.0011255
111 | 0.97725 | -0.43757 | 0.011685 | 0.0029286
112 | 0.97626 | -0.45701 | 0.0018245 | 0.00045727
113 | 0.97658 | -0.45063 | 0.016036 | 0.004019
114 | 0.98567 | -0.27352 | 0.0014264 | 0.0003575
115 | 0.98547 | -0.27746 | 0.003972 | 0.00099547
116 | 0.98497 | -0.28723 | 0.0026944 | 0.00067527
117 | 0.98358 | -0.31439 | 0.0040613 | 0.0010179
118 | 0.98356 | -0.31475 | 0.004186 | 0.0010491
119 | 0.98373 | -0.31138 | 0 | 0
120 | 0.984 | -0.30603 | 0.0022789 | 0.00057113
121 | 0.98353 | -0.31541 | 0.0031923 | 0.00080007
122 | 0.98347 | -0.31656 | 0.0037094 | 0.00092967
123 | 0.9833 | -0.31979 | 0.0041331 | 0.0010359
124 | 0.98318 | -0.32209 | 0.00024406 | 6.1166e-05
125 | 0.98305 | -0.32476 | 0 | 0
126 | 0.98304 | -0.32484 | 9.6768e-05 | 2.4252e-05
127 | 0.98299 | -0.32593 | 0.00024158 | 6.0546e-05
128 | 0.9758 | -0.46613 | 0.0035525 | 0.00089034
129 | 0.98304 | -0.32488 | 0 | 0
130 | 0.98287 | -0.32826 | 0.0042548 | 0.0010664
131 | 0.98304 | -0.32497 | 0.00020294 | 5.0862e-05
132 | 0.97535 | -0.47479 | 0 | 0
133 | 0.97518 | -0.47827 | 0.0014824 | 0.00037152
134 | 0.97521 | -0.47754 | 0.0013626 | 0.00034149
135 | 0.9746 | -0.4896 | 0.00072489 | 0.00018167
136 | 0.97508 | -0.48019 | 0.0012453 | 0.00031209
137 | 0.97344 | -0.51251 | 0.0006044 | 0.00015148
138 | 0.9749 | -0.48364 | 0.0025157 | 0.00063051
139 | 0.97319 | -0.5173 | 0 | 0
140 | 0.97181 | -0.54471 | 0.0087247 | 0.0021866
141 | 0.97481 | -0.48539 | 0.0025275 | 0.00063345
142 | 0.97473 | -0.48707 | 0.0027543 | 0.00069028
143 | 0.9747 | -0.48766 | 0.0025363 | 0.00063565
144 | 0.99448 | -0.10627 | 0.013683 | 0.0034294
145 | 0.99553 | -0.086008 | 0.004007 | 0.0010043
146 | 0.97076 | -0.56534 | 0.0038042 | 0.00095343
147 | 0.97098 | -0.56112 | 0 | 0
148 | 0.9711 | -0.5587 | 0.0028693 | 0.00071912
149 | 0.97135 | -0.55375 | 0 | 0
150 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0061842 | -0.0015493 | 0.0061845 | 0.0015494 | 2.7572e-07 | 7.3773e-08 | 0.009444 | 0.0094439 | 0.009444 | 0.97438 | -0.49419 | 0.97443 | -0.49326 | 2.5945
1 | 0.0043125 | 0.0010802 | -0.0043118 | -0.0010803 | 6.8147e-07 | -8.5651e-08 | 0.0065856 | 0.0065858 | 0.0065858 | 0.97438 | -0.49419 | 0.97421 | -0.49751 | 1.8093
2 | -0.0066341 | -0.0016621 | 0.0066359 | 0.0016626 | 1.768e-06 | 5.5907e-07 | 0.010131 | 0.01013 | 0.010131 | 0.97443 | -0.49326 | 0.97471 | -0.48766 | 2.7831
3 | 0.0036307 | 0.00090963 | -0.0036307 | -0.00090967 | 9.3601e-08 | -4.1152e-08 | 0.0055455 | 0.0055456 | 0.0055456 | 0.97421 | -0.49751 | 0.97418 | -0.49805 | 1.5235
4 | 0.00042185 | 0.00010568 | -0.00042185 | -0.00010573 | 5.9514e-10 | -4.7317e-08 | 0.00064399 | 0.00064401 | 0.00064401 | 0.97471 | -0.48766 | 0.97471 | -0.48769 | 0.17692
5 | -0.0070577 | -0.0017683 | 0.0070585 | 0.0017686 | 8.0739e-07 | 2.8553e-07 | 0.010774 | 0.010774 | 0.010774 | 0.97471 | -0.48766 | 0.97483 | -0.48526 | 2.96
6 | 0.0014663 | 0.00036724 | -0.0014663 | -0.00036732 | 1.4329e-08 | -8.5675e-08 | 0.0022396 | 0.0022397 | 0.0022397 | 0.97418 | -0.49805 | 0.97417 | -0.49826 | 0.6153
7 | -0.02857 | -0.0071716 | 0.028597 | 0.0071883 | 2.6841e-05 | 1.6705e-05 | 0.043524 | 0.043524 | 0.043524 | 0.97687 | -0.44503 | 0.97788 | -0.42535 | 11.9571
8 | 0.02857 | 0.0071716 | -0.028554 | -0.0071615 | 1.6166e-05 | 1.0061e-05 | 0.043524 | 0.043524 | 0.043524 | 0.97687 | -0.44503 | 0.97627 | -0.4569 | 11.9571
9 | 0.014296 | 0.0035849 | -0.01429 | -0.0035814 | 6.2466e-06 | 3.5565e-06 | 0.021755 | 0.021755 | 0.021755 | 0.97788 | -0.42535 | 0.97741 | -0.43452 | 5.9767
10 | -0.042893 | -0.010773 | 0.042964 | 0.010818 | 7.0364e-05 | 4.4479e-05 | 0.065278 | 0.065278 | 0.065278 | 0.97788 | -0.42535 | 0.97963 | -0.39104 | 17.9336
11 | 0.012006 | 0.0030097 | -0.012003 | -0.0030082 | 2.815e-06 | 1.5214e-06 | 0.018299 | 0.018299 | 0.018299 | 0.97627 | -0.4569 | 0.97602 | -0.46182 | 5.0272
12 | 0.012008 | 0.0030137 | -0.011991 | -0.0030049 | 1.6221e-05 | 8.7693e-06 | 0.018303 | 0.018304 | 0.018304 | 0.97627 | -0.4569 | 0.97483 | -0.48526 | 5.0286
13 | 0.00062703 | 0.00015698 | -0.00062703 | -0.00015715 | 4.7261e-09 | -1.6804e-07 | 0.00095771 | 0.00095777 | 0.00095777 | 0.97417 | -0.49826 | 0.97416 | -0.49842 | 0.26312
14 | 0.0078308 | 0.0019627 | -0.0078296 | -0.0019622 | 1.2231e-06 | 4.9687e-07 | 0.011939 | 0.011939 | 0.011939 | 0.97602 | -0.46182 | 0.97585 | -0.4651 | 3.2799
15 | -0.059018 | -0.014841 | 0.059154 | 0.014928 | 0.0001361 | 8.6533e-05 | 0.089663 | 0.089663 | 0.089663 | 0.97963 | -0.39104 | 0.98209 | -0.34287 | 24.6328
16 | -0.059154 | -0.014928 | 0.059233 | 0.014978 | 7.9524e-05 | 5.0561e-05 | 0.089663 | 0.089663 | 0.089663 | 0.98209 | -0.34287 | 0.98354 | -0.31484 | 24.6327
17 | 0.0035527 | 0.00089025 | -0.0035525 | -0.00089034 | 1.7437e-07 | -8.6348e-08 | 0.0054172 | 0.0054172 | 0.0054172 | 0.97585 | -0.4651 | 0.9758 | -0.46613 | 1.4883
18 | -0.0030112 | -0.00075468 | 0.0030115 | 0.00075443 | 2.5853e-07 | -2.4926e-07 | 0.0045745 | 0.0045744 | 0.0045745 | 0.9795 | -0.39375 | 0.97959 | -0.39195 | 1.2567
19 | -0.0030115 | -0.00075443 | 0.0030118 | 0.00075411 | 3.3681e-07 | -3.249e-07 | 0.0045744 | 0.0045742 | 0.0045744 | 0.97959 | -0.39195 | 0.97971 | -0.3896 | 1.2567
20 | -0.0036618 | -0.000917 | 0.0036622 | 0.00091678 | 4.9062e-07 | -2.1877e-07 | 0.0055613 | 0.0055611 | 0.0055613 | 0.97971 | -0.3896 | 0.97985 | -0.38678 | 1.5278
21 | 0.039004 | 0.0098072 | -0.038962 | -0.0097809 | 4.1831e-05 | 2.6372e-05 | 0.059243 | 0.059243 | 0.059243 | 0.97985 | -0.38678 | 0.9787 | -0.40927 | 16.2755
22 | -0.042666 | -0.010724 | 0.042703 | 0.010747 | 3.6727e-05 | 2.3211e-05 | 0.064804 | 0.064804 | 0.064804 | 0.97985 | -0.38678 | 0.98077 | -0.36877 | 17.8033
23 | -0.014023 | -0.0035146 | 0.014025 | 0.0035158 | 2.0948e-06 | 1.1871e-06 | 0.02135 | 0.02135 | 0.02135 | 0.97736 | -0.43563 | 0.97752 | -0.43249 | 5.8655
24 | -0.036064 | -0.0090391 | 0.036064 | 0.0090392 | 1.0849e-07 | 6.8232e-08 | 0.054898 | 0.054898 | 0.054898 | 0.97752 | -0.43249 | 0.97753 | -0.43243 | 15.0818
25 | 0.037214 | 0.009343 | -0.037197 | -0.0093322 | 1.7151e-05 | 1.0797e-05 | 0.056586 | 0.056587 | 0.056587 | 0.9787 | -0.40927 | 0.97821 | -0.41893 | 15.5457
26 | -0.045529 | -0.011456 | 0.045631 | 0.01152 | 0.00010145 | 6.4211e-05 | 0.069092 | 0.069092 | 0.069092 | 0.98077 | -0.36877 | 0.98316 | -0.32225 | 18.9814
27 | 0.036675 | 0.0092012 | -0.036651 | -0.0091864 | 2.358e-05 | 1.4838e-05 | 0.055792 | 0.055792 | 0.055792 | 0.97821 | -0.41893 | 0.97753 | -0.43243 | 15.3274
28 | -0.045631 | -0.01152 | 0.045685 | 0.011554 | 5.4071e-05 | 3.4222e-05 | 0.069092 | 0.069092 | 0.069092 | 0.98316 | -0.32225 | 0.98443 | -0.29755 | 18.9814
29 | -0.062301 | -0.015719 | 0.06242 | 0.015794 | 0.00011915 | 7.5802e-05 | 0.094209 | 0.094209 | 0.094209 | 0.98443 | -0.29755 | 0.98649 | -0.25769 | 25.8815
30 | -0.076125 | -0.01923 | 0.076258 | 0.019315 | 0.00013303 | 8.4797e-05 | 0.11488 | 0.11488 | 0.11488 | 0.98649 | -0.25769 | 0.98837 | -0.22129 | 31.5608
31 | 0.013705 | 0.0034358 | -0.013702 | -0.0034343 | 2.5827e-06 | 1.4472e-06 | 0.020673 | 0.020673 | 0.020673 | 0.98649 | -0.25769 | 0.98628 | -0.26164 | 5.6794
32 | -0.0082713 | -0.002073 | 0.0082721 | 0.0020733 | 7.9732e-07 | 3.3617e-07 | 0.012482 | 0.012482 | 0.012482 | 0.98607 | -0.2655 | 0.98618 | -0.26347 | 3.429
33 | -0.013267 | -0.0033253 | 0.013269 | 0.0033263 | 1.8299e-06 | 1.0158e-06 | 0.020019 | 0.020019 | 0.020019 | 0.98618 | -0.26347 | 0.98633 | -0.26058 | 5.4997
34 | -0.086812 | -0.02196 | 0.086864 | 0.021993 | 5.1975e-05 | 3.316e-05 | 0.13077 | 0.13077 | 0.13077 | 0.98837 | -0.22129 | 0.98902 | -0.20882 | 35.9257
35 | 0.010639 | 0.0026665 | -0.010638 | -0.0026661 | 7.3922e-07 | 3.7546e-07 | 0.016051 | 0.016051 | 0.016051 | 0.98628 | -0.26164 | 0.98621 | -0.2631 | 4.4095
36 | 0.0030927 | 0.00077497 | -0.0030926 | -0.00077508 | 1.1474e-07 | -1.0594e-07 | 0.0046658 | 0.0046658 | 0.0046658 | 0.98633 | -0.26058 | 0.98629 | -0.26136 | 1.2818
37 | 0.13064 | 0.033245 | -0.13032 | -0.03304 | 0.000321 | 0.00020432 | 0.19727 | 0.19728 | 0.19728 | 0.98633 | -0.26058 | 0.98368 | -0.31169 | 27.0982
38 | -0.14701 | -0.037346 | 0.14737 | 0.03758 | 0.00036725 | 0.00023402 | 0.22196 | 0.22196 | 0.22196 | 0.98633 | -0.26058 | 0.98902 | -0.20882 | 30.4889
39 | -0.0073326 | -0.0018377 | 0.0073327 | 0.0018378 | 1.0825e-07 | 3.9189e-08 | 0.011064 | 0.011064 | 0.011064 | 0.98619 | -0.26341 | 0.98621 | -0.2631 | 3.0395
40 | -0.23424 | -0.059573 | 0.2345 | 0.059742 | 0.00026389 | 0.0001686 | 0.35273 | 0.35273 | 0.35273 | 0.98902 | -0.20882 | 0.99023 | -0.18547 | 48.4517
41 | 0.0058723 | 0.0014717 | -0.0058719 | -0.0014716 | 3.3407e-07 | 6.6638e-08 | 0.0088242 | 0.0088243 | 0.0088243 | 0.99023 | -0.18547 | 0.99017 | -0.18667 | 2.4243
42 | -0.24037 | -0.061213 | 0.24051 | 0.061303 | 0.00014131 | 8.9846e-05 | 0.36155 | 0.36155 | 0.36155 | 0.99023 | -0.18547 | 0.99087 | -0.17329 | 24.8319
43 | -0.24769 | -0.063101 | 0.24832 | 0.063502 | 0.00063122 | 0.00040147 | 0.37232 | 0.37232 | 0.37232 | 0.99087 | -0.17329 | 0.99363 | -0.12061 | 25.5716
44 | 0.11858 | 0.030099 | -0.11834 | -0.029941 | 0.0002471 | 0.00015789 | 0.17952 | 0.17952 | 0.17952 | 0.98368 | -0.31169 | 0.98144 | -0.3551 | 49.3184
45 | -0.24974 | -0.063858 | 0.25015 | 0.064122 | 0.00041491 | 0.00026391 | 0.37445 | 0.37445 | 0.37445 | 0.99363 | -0.12061 | 0.99543 | -0.086338 | 25.7177
46 | 0.11488 | 0.029074 | -0.11451 | -0.028837 | 0.00037127 | 0.0002372 | 0.17427 | 0.17428 | 0.17428 | 0.98144 | -0.3551 | 0.97798 | -0.42267 | 47.8778
47 | -0.017024 | -0.0042666 | 0.017025 | 0.0042674 | 1.3646e-06 | 8.0656e-07 | 0.026028 | 0.026028 | 0.026028 | 0.97326 | -0.51547 | 0.97334 | -0.51379 | 7.1506
48 | 0.0081623 | 0.0020457 | -0.008162 | -0.0020456 | 2.9843e-07 | 1.2747e-07 | 0.012478 | 0.012478 | 0.012478 | 0.97334 | -0.51379 | 0.9733 | -0.51456 | 3.4281
49 | -0.025188 | -0.0063131 | 0.025201 | 0.0063213 | 1.3298e-05 | 8.2132e-06 | 0.038506 | 0.038506 | 0.038506 | 0.97334 | -0.51379 | 0.9739 | -0.50272 | 10.5787
50 | 0.071834 | 0.018104 | -0.071828 | -0.018101 | 5.6152e-06 | 3.578e-06 | 0.10933 | 0.10933 | 0.10933 | 0.97798 | -0.42267 | 0.97789 | -0.42431 | 30.0365
51 | 0.040644 | 0.010224 | -0.040593 | -0.010191 | 5.1306e-05 | 3.2388e-05 | 0.061854 | 0.061854 | 0.061854 | 0.97798 | -0.42267 | 0.97663 | -0.44913 | 16.9929
52 | -0.50403 | -0.12912 | 0.50452 | 0.12943 | 0.00049343 | 0.00031531 | 0.75444 | 0.75444 | 0.75444 | 0.99543 | -0.086338 | 0.9965 | -0.066156 | 51.816
53 | 0.25388 | 0.064997 | -0.25341 | -0.064702 | 0.00046377 | 0.00029504 | 0.37999 | 0.37999 | 0.37999 | 0.99543 | -0.086338 | 0.99344 | -0.12413 | 26.0984
54 | -0.51456 | -0.13195 | 0.51545 | 0.13252 | 0.00089467 | 0.00057175 | 0.76943 | 0.76943 | 0.76943 | 0.9965 | -0.066156 | 0.99839 | -0.030371 | 52.8455
55 | 0.010038 | 0.0025168 | -0.010033 | -0.0025146 | 4.646e-06 | 2.2555e-06 | 0.01499 | 0.01499 | 0.01499 | 0.9965 | -0.066156 | 0.99599 | -0.075872 | 4.1181
56 | 0.25017 | 0.063891 | -0.24995 | -0.063746 | 0.00022712 | 0.00014446 | 0.37514 | 0.37514 | 0.37514 | 0.99344 | -0.12413 | 0.99246 | -0.14293 | 25.7654
57 | -0.52169 | -0.13409 | 0.52246 | 0.13458 | 0.00077099 | 0.00049272 | 0.77872 | 0.77872 | 0.77872 | 0.99839 | -0.030371 | 1 | 0 | 53.4834
58 | 0.00653 | 0.0016366 | -0.0065299 | -0.0016365 | 1.1691e-07 | 3.2194e-08 | 0.0097558 | 0.0097558 | 0.0097558 | 0.99599 | -0.075872 | 0.99597 | -0.076248 | 2.6802
59 | 0.03167 | 0.00795 | -0.031655 | -0.0079404 | 1.523e-05 | 9.5292e-06 | 0.048279 | 0.048279 | 0.048279 | 0.97621 | -0.45745 | 0.97569 | -0.46753 | 13.2636
60 | -0.03167 | -0.00795 | 0.031683 | 0.0079578 | 1.2563e-05 | 7.8607e-06 | 0.048279 | 0.048279 | 0.048279 | 0.97621 | -0.45745 | 0.97663 | -0.44913 | 13.2635
61 | 0.027643 | 0.0069348 | -0.027637 | -0.0069311 | 6.0174e-06 | 3.7384e-06 | 0.04216 | 0.04216 | 0.04216 | 0.97569 | -0.46753 | 0.97546 | -0.4721 | 11.5825
62 | 0.0089096 | 0.0022335 | -0.0089071 | -0.0022323 | 2.4635e-06 | 1.1307e-06 | 0.013575 | 0.013575 | 0.013575 | 0.97663 | -0.44913 | 0.97633 | -0.45494 | 3.7295
63 | 0.24697 | 0.063001 | -0.24648 | -0.062686 | 0.00049404 | 0.00031421 | 0.37068 | 0.37068 | 0.37068 | 0.99246 | -0.14293 | 0.99029 | -0.18444 | 25.4591
64 | 0.059993 | 0.015135 | -0.059904 | -0.015078 | 8.8664e-05 | 5.639e-05 | 0.091324 | 0.091324 | 0.091324 | 0.97789 | -0.42431 | 0.97632 | -0.45523 | 25.089
65 | 0.02803 | 0.0070371 | -0.028026 | -0.0070346 | 4.0381e-06 | 2.5114e-06 | 0.042831 | 0.042831 | 0.042831 | 0.9739 | -0.50272 | 0.97375 | -0.50574 | 11.7668
66 | -0.053231 | -0.013358 | 0.053309 | 0.013408 | 7.8566e-05 | 4.9888e-05 | 0.081337 | 0.081337 | 0.081337 | 0.9739 | -0.50272 | 0.97547 | -0.47181 | 22.3454
67 | 0.022547 | 0.0056615 | -0.022542 | -0.0056581 | 5.5332e-06 | 3.3867e-06 | 0.034459 | 0.034459 | 0.034459 | 0.97375 | -0.50574 | 0.97349 | -0.51088 | 9.4668
68 | -0.055993 | -0.014081 | 0.056037 | 0.014109 | 4.4403e-05 | 2.8215e-05 | 0.08543 | 0.08543 | 0.08543 | 0.97547 | -0.47181 | 0.97632 | -0.45523 | 23.4699
69 | 0.005694 | 0.001427 | -0.0056938 | -0.001427 | 2.3802e-07 | 4.8163e-08 | 0.0087035 | 0.0087036 | 0.0087036 | 0.97349 | -0.51088 | 0.97344 | -0.51176 | 2.3911
70 | 0.016848 | 0.0042311 | -0.016834 | -0.0042232 | 1.3334e-05 | 7.868e-06 | 0.025756 | 0.025756 | 0.025756 | 0.97349 | -0.51088 | 0.97265 | -0.52748 | 7.0758
71 | 0.059733 | 0.015065 | -0.059619 | -0.014992 | 0.00011414 | 7.2544e-05 | 0.088917 | 0.088917 | 0.088917 | 1 | 0 | 0.99791 | -0.040001 | 24.4277
72 | 0.019045 | 0.0047778 | -0.019035 | -0.0047715 | 1.0556e-05 | 6.34e-06 | 0.029054 | 0.029054 | 0.029054 | 0.97546 | -0.4721 | 0.97487 | -0.48374 | 7.9819
73 | 0.24115 | 0.061351 | -0.24082 | -0.061142 | 0.00032845 | 0.00020884 | 0.36268 | 0.36268 | 0.36268 | 0.99029 | -0.18444 | 0.98882 | -0.21274 | 24.9091
74 | 0.0056938 | 0.001427 | -0.0056935 | -0.0014269 | 2.5812e-07 | 5.2241e-08 | 0.0087036 | 0.0087036 | 0.0087036 | 0.97344 | -0.51176 | 0.97339 | -0.51271 | 2.3911
75 | 0.012844 | 0.003223 | -0.012839 | -0.0032207 | 4.2893e-06 | 2.3777e-06 | 0.01965 | 0.01965 | 0.01965 | 0.97265 | -0.52748 | 0.97229 | -0.53449 | 5.3985
76 | 0.012839 | 0.0032207 | -0.01283 | -0.0032155 | 9.3518e-06 | 5.1848e-06 | 0.01965 | 0.019651 | 0.019651 | 0.97229 | -0.53449 | 0.97152 | -0.54978 | 5.3986
77 | 0.013363 | 0.0033499 | -0.01336 | -0.0033484 | 2.8075e-06 | 1.5725e-06 | 0.020397 | 0.020397 | 0.020397 | 0.97487 | -0.48374 | 0.97465 | -0.48815 | 5.6035
78 | 0.0074639 | 0.0018707 | -0.007463 | -0.0018704 | 8.7912e-07 | 3.3767e-07 | 0.011395 | 0.011395 | 0.011395 | 0.97465 | -0.48815 | 0.97452 | -0.49062 | 3.1306
79 | 0.0043688 | 0.0010949 | -0.0043687 | -0.0010949 | 8.6856e-08 | -9.2613e-09 | 0.0066707 | 0.0066708 | 0.0066708 | 0.97452 | -0.49062 | 0.9745 | -0.49104 | 1.8326
80 | 0.056403 | 0.014186 | -0.05634 | -0.014146 | 6.3638e-05 | 4.0415e-05 | 0.084122 | 0.084123 | 0.084123 | 0.99791 | -0.040001 | 0.99668 | -0.063649 | 23.1106
81 | 0.052767 | 0.013251 | -0.052754 | -0.013242 | 1.3116e-05 | 8.3209e-06 | 0.078789 | 0.078789 | 0.078789 | 0.99668 | -0.063649 | 0.99641 | -0.06886 | 21.6454
82 | 0.03531 | 0.0088674 | -0.035292 | -0.0088561 | 1.8074e-05 | 1.1342e-05 | 0.052738 | 0.052738 | 0.052738 | 0.99641 | -0.06886 | 0.99586 | -0.079594 | 14.4884
83 | 0.017444 | 0.0043748 | -0.01744 | -0.0043722 | 4.3735e-06 | 2.5753e-06 | 0.026052 | 0.026052 | 0.026052 | 0.99641 | -0.06886 | 0.99614 | -0.074122 | 7.157
84 | 0.027062 | 0.0067934 | -0.02705 | -0.006786 | 1.1891e-05 | 7.3581e-06 | 0.04044 | 0.04044 | 0.04044 | 0.99586 | -0.079594 | 0.99538 | -0.088811 | 11.1099
85 | 0.012986 | 0.0032559 | -0.012981 | -0.0032532 | 4.9525e-06 | 2.7129e-06 | 0.019398 | 0.019398 | 0.019398 | 0.99614 | -0.074122 | 0.99573 | -0.082128 | 5.3292
86 | 0.02705 | 0.006786 | -0.027038 | -0.0067789 | 1.1559e-05 | 7.1527e-06 | 0.04044 | 0.04044 | 0.04044 | 0.99538 | -0.088811 | 0.99491 | -0.097778 | 11.1099
87 | 0.009764 | 0.002447 | -0.0097632 | -0.0024466 | 7.9025e-07 | 3.7702e-07 | 0.014591 | 0.014591 | 0.014591 | 0.99573 | -0.082128 | 0.99564 | -0.083827 | 4.0086
88 | 0.020082 | 0.0050353 | -0.020077 | -0.0050323 | 4.9799e-06 | 2.996e-06 | 0.030035 | 0.030035 | 0.030035 | 0.99491 | -0.097778 | 0.99465 | -0.10298 | 8.2515
89 | 0.0040074 | 0.0010041 | -0.004007 | -0.0010043 | 4.1627e-07 | -1.36e-07 | 0.0059892 | 0.0059893 | 0.0059893 | 0.99564 | -0.083827 | 0.99553 | -0.086008 | 1.6454
90 | 0.23648 | 0.060053 | -0.23637 | -0.059983 | 0.00011019 | 7.0043e-05 | 0.35614 | 0.35614 | 0.35614 | 0.98882 | -0.21274 | 0.98832 | -0.22243 | 24.4601
91 | 0.2269 | 0.05761 | -0.22663 | -0.057439 | 0.0002691 | 0.00017097 | 0.34189 | 0.34189 | 0.34189 | 0.98832 | -0.22243 | 0.98704 | -0.24711 | 23.4813
92 | 0.0094659 | 0.0023733 | -0.0094615 | -0.0023713 | 4.3341e-06 | 2.0451e-06 | 0.014252 | 0.014252 | 0.014252 | 0.98832 | -0.22243 | 0.98782 | -0.23204 | 3.9155
93 | 0.2237 | 0.056704 | -0.22351 | -0.056582 | 0.00019202 | 0.00012197 | 0.33747 | 0.33747 | 0.33747 | 0.98704 | -0.24711 | 0.98611 | -0.26499 | 23.1777
94 | -0.013938 | -0.0034931 | 0.013942 | 0.0034957 | 4.553e-06 | 2.5695e-06 | 0.021121 | 0.021121 | 0.021121 | 0.98193 | -0.34627 | 0.98228 | -0.33941 | 5.8024
95 | 0.01065 | 0.0026693 | -0.01065 | -0.0026693 | 6.7986e-10 | 3.3125e-10 | 0.01614 | 0.01614 | 0.01614 | 0.98193 | -0.34627 | 0.98193 | -0.34627 | 4.434
96 | -0.019882 | -0.0049842 | 0.019893 | 0.004991 | 1.1204e-05 | 6.7533e-06 | 0.030118 | 0.030118 | 0.030118 | 0.98228 | -0.33941 | 0.98289 | -0.32759 | 8.2743
97 | 0.006816 | 0.0017082 | -0.0068159 | -0.0017082 | 3.8022e-08 | 1.2312e-08 | 0.010329 | 0.010329 | 0.010329 | 0.98193 | -0.34627 | 0.98193 | -0.34638 | 2.8376
98 | -0.025597 | -0.0064206 | 0.025617 | 0.0064331 | 2.0196e-05 | 1.2471e-05 | 0.038754 | 0.038754 | 0.038754 | 0.98289 | -0.32759 | 0.98374 | -0.31105 | 10.6467
99 | -0.028386 | -0.007127 | 0.028402 | 0.0071367 | 1.5726e-05 | 9.7759e-06 | 0.042942 | 0.042941 | 0.042942 | 0.98374 | -0.31105 | 0.98433 | -0.29945 | 11.7971
100 | -0.18467 | -0.046707 | 0.18478 | 0.046773 | 0.00010536 | 6.6696e-05 | 0.27932 | 0.27932 | 0.27932 | 0.98433 | -0.29945 | 0.98494 | -0.28756 | 19.1843
101 | 0.15627 | 0.03957 | -0.15616 | -0.039496 | 0.00011543 | 7.3597e-05 | 0.23638 | 0.23638 | 0.23638 | 0.98433 | -0.29945 | 0.98354 | -0.31484 | 32.47
102 | -0.18853 | -0.047715 | 0.18874 | 0.047844 | 0.00020452 | 0.00012952 | 0.285 | 0.285 | 0.285 | 0.98494 | -0.28756 | 0.98611 | -0.26499 | 19.574
103 | 0.096923 | 0.024518 | -0.096813 | -0.024448 | 0.00011007 | 6.9754e-05 | 0.14672 | 0.14672 | 0.14672 | 0.98354 | -0.31484 | 0.98232 | -0.33854 | 20.1537
104 | 0.034766 | 0.0087377 | -0.034752 | -0.0087288 | 1.4148e-05 | 8.8801e-06 | 0.05247 | 0.05247 | 0.05247 | 0.98611 | -0.26499 | 0.98567 | -0.27352 | 14.415
105 | -0.011274 | -0.0028254 | 0.011276 | 0.0028265 | 1.976e-06 | 1.0387e-06 | 0.01713 | 0.01713 | 0.01713 | 0.97929 | -0.39775 | 0.97947 | -0.39407 | 4.7061
106 | 0.0064061 | 0.0016055 | -0.006406 | -0.0016055 | 1.2116e-07 | 3.4643e-08 | 0.009734 | 0.0097341 | 0.0097341 | 0.97929 | -0.39775 | 0.97927 | -0.39815 | 2.6742
107 | -0.016618 | -0.0041654 | 0.016621 | 0.004167 | 2.6698e-06 | 1.5681e-06 | 0.025246 | 0.025246 | 0.025246 | 0.97947 | -0.39407 | 0.97965 | -0.3907 | 6.9358
108 | -0.019355 | -0.0048522 | 0.019355 | 0.0048522 | 9.5052e-08 | 5.7141e-08 | 0.029399 | 0.029399 | 0.029399 | 0.97965 | -0.3907 | 0.97965 | -0.3906 | 8.0766
109 | -0.023238 | -0.0058256 | 0.023258 | 0.0058374 | 1.9324e-05 | 1.1846e-05 | 0.035298 | 0.035298 | 0.035298 | 0.97965 | -0.3906 | 0.98054 | -0.37316 | 9.6973
110 | -0.08832 | -0.022262 | 0.088383 | 0.022302 | 6.2573e-05 | 3.9929e-05 | 0.13408 | 0.13408 | 0.13408 | 0.98054 | -0.37316 | 0.9813 | -0.35837 | 36.834
111 | 0.065063 | 0.016424 | -0.064978 | -0.01637 | 8.4353e-05 | 5.3695e-05 | 0.098778 | 0.098778 | 0.098778 | 0.98054 | -0.37316 | 0.97915 | -0.40026 | 27.1369
112 | 0.013686 | 0.0034306 | -0.013683 | -0.0034294 | 2.1431e-06 | 1.1947e-06 | 0.020474 | 0.020474 | 0.020474 | 0.99465 | -0.10298 | 0.99448 | -0.10627 | 5.6248
113 | -0.092235 | -0.023267 | 0.092322 | 0.023323 | 8.7631e-05 | 5.5933e-05 | 0.13992 | 0.13992 | 0.13992 | 0.9813 | -0.35837 | 0.98232 | -0.33854 | 38.4386
114 | 0.060938 | 0.015358 | -0.06083 | -0.015289 | 0.00010855 | 6.9047e-05 | 0.092638 | 0.092638 | 0.092638 | 0.97915 | -0.40026 | 0.97725 | -0.43757 | 25.4501
115 | 0.033098 | 0.0083354 | -0.033068 | -0.0083162 | 3.0733e-05 | 1.9265e-05 | 0.050412 | 0.050412 | 0.050412 | 0.97725 | -0.43757 | 0.97626 | -0.45701 | 13.8495
116 | 0.016046 | 0.0040249 | -0.016036 | -0.004019 | 9.9848e-06 | 5.8319e-06 | 0.024434 | 0.024434 | 0.024434 | 0.97725 | -0.43757 | 0.97658 | -0.45063 | 6.7127
117 | 0.031243 | 0.0078589 | -0.031217 | -0.0078423 | 2.6515e-05 | 1.658e-05 | 0.047631 | 0.047631 | 0.047631 | 0.97626 | -0.45701 | 0.97535 | -0.47479 | 13.0855
118 | 0.033326 | 0.0083713 | -0.03332 | -0.0083674 | 6.2662e-06 | 3.9263e-06 | 0.050317 | 0.050317 | 0.050317 | 0.98567 | -0.27352 | 0.98547 | -0.27746 | 13.8234
119 | 0.029348 | 0.0073719 | -0.029334 | -0.0073634 | 1.3683e-05 | 8.5206e-06 | 0.04432 | 0.04432 | 0.04432 | 0.98547 | -0.27746 | 0.98497 | -0.28723 | 12.1757
120 | 0.02664 | 0.0066881 | -0.026616 | -0.0066733 | 2.3869e-05 | 1.4777e-05 | 0.040249 | 0.040249 | 0.040249 | 0.98497 | -0.28723 | 0.984 | -0.30603 | 11.0575
121 | 0.0041861 | 0.0010491 | -0.004186 | -0.0010491 | 7.2512e-08 | -1.4782e-08 | 0.006333 | 0.006333 | 0.006333 | 0.98358 | -0.31439 | 0.98356 | -0.31475 | 1.7398
122 | -0.0082474 | -0.002067 | 0.0082486 | 0.0020675 | 1.1825e-06 | 4.997e-07 | 0.012477 | 0.012477 | 0.012477 | 0.98358 | -0.31439 | 0.98373 | -0.31138 | 3.4278
123 | -0.024331 | -0.0060984 | 0.024337 | 0.0061022 | 6.1952e-06 | 3.8101e-06 | 0.036803 | 0.036803 | 0.036803 | 0.98373 | -0.31138 | 0.984 | -0.30603 | 10.1108
124 | 0.016082 | 0.0040309 | -0.016079 | -0.0040291 | 3.0877e-06 | 1.7995e-06 | 0.024326 | 0.024326 | 0.024326 | 0.98373 | -0.31138 | 0.98353 | -0.31541 | 6.6831
125 | 0.012887 | 0.0032291 | -0.012886 | -0.0032287 | 7.1022e-07 | 3.9131e-07 | 0.019497 | 0.019497 | 0.019497 | 0.98353 | -0.31541 | 0.98347 | -0.31656 | 5.3562
126 | 0.0091766 | 0.002299 | -0.0091751 | -0.0022983 | 1.4078e-06 | 6.5392e-07 | 0.013884 | 0.013884 | 0.013884 | 0.98347 | -0.31656 | 0.9833 | -0.31979 | 3.8143
127 | 0.005042 | 0.0012625 | -0.0050415 | -0.0012625 | 5.5408e-07 | 3.2682e-08 | 0.0076296 | 0.0076297 | 0.0076297 | 0.9833 | -0.31979 | 0.98318 | -0.32209 | 2.0961
128 | 0.0047974 | 0.0012013 | -0.0047968 | -0.0012013 | 6.0964e-07 | -8.8383e-10 | 0.0072604 | 0.0072605 | 0.0072605 | 0.98318 | -0.32209 | 0.98305 | -0.32476 | 1.9946
129 | 0.00029971 | 7.4501e-05 | -0.00029971 | -7.4683e-05 | 1.1119e-09 | -1.8209e-07 | 0.00045345 | 0.00045351 | 0.00045351 | 0.98305 | -0.32476 | 0.98304 | -0.32484 | 0.12459
130 | 0.0044971 | 0.0011268 | -0.0044968 | -0.0011268 | 2.5057e-07 | -2.2449e-08 | 0.0068071 | 0.0068071 | 0.0068071 | 0.98305 | -0.32476 | 0.98299 | -0.32593 | 1.8701
131 | 0.00020294 | 5.0431e-05 | -0.00020294 | -5.0551e-05 | 3.3466e-10 | -1.1979e-07 | 0.00030704 | 0.00030708 | 0.00030708 | 0.98304 | -0.32484 | 0.98304 | -0.32488 | 0.084362
132 | 0.0042553 | 0.0010663 | -0.0042548 | -0.0010664 | 4.7196e-07 | -8.2407e-08 | 0.0064414 | 0.0064416 | 0.0064416 | 0.98299 | -0.32593 | 0.98287 | -0.32826 | 1.7697
133 | 0.00020294 | 5.0551e-05 | -0.00020294 | -5.0862e-05 | 8.6983e-10 | -3.1118e-07 | 0.00030708 | 0.00030719 | 0.00030719 | 0.98304 | -0.32488 | 0.98304 | -0.32497 | 0.084393
134 | 0.018269 | 0.004596 | -0.018266 | -0.0045942 | 3.0363e-06 | 1.8132e-06 | 0.027878 | 0.027878 | 0.027878 | 0.97535 | -0.47479 | 0.97518 | -0.47827 | 7.6587
135 | 0.012948 | 0.0032463 | -0.012946 | -0.0032453 | 1.7014e-06 | 9.4378e-07 | 0.019754 | 0.019754 | 0.019754 | 0.97535 | -0.47479 | 0.97521 | -0.47754 | 5.4268
136 | 0.016783 | 0.0042227 | -0.016774 | -0.0042174 | 9.0832e-06 | 5.353e-06 | 0.025616 | 0.025616 | 0.025616 | 0.97518 | -0.47827 | 0.9746 | -0.4896 | 7.0373
137 | 0.011583 | 0.0029038 | -0.011582 | -0.002903 | 1.4596e-06 | 7.787e-07 | 0.017675 | 0.017675 | 0.017675 | 0.97521 | -0.47754 | 0.97508 | -0.48019 | 4.8557
138 | 0.016049 | 0.0040357 | -0.016032 | -0.0040254 | 1.7544e-05 | 1.0259e-05 | 0.024509 | 0.024509 | 0.024509 | 0.9746 | -0.4896 | 0.97344 | -0.51251 | 6.7334
139 | 0.010337 | 0.002591 | -0.010335 | -0.0025901 | 1.6993e-06 | 8.6041e-07 | 0.015774 | 0.015774 | 0.015774 | 0.97508 | -0.48019 | 0.9749 | -0.48364 | 4.3336
140 | 0.015428 | 0.0038739 | -0.015424 | -0.0038719 | 3.5251e-06 | 2.046e-06 | 0.023586 | 0.023586 | 0.023586 | 0.97344 | -0.51251 | 0.97319 | -0.5173 | 6.4796
141 | 0.0078192 | 0.0019596 | -0.0078185 | -0.0019593 | 6.5269e-07 | 2.6537e-07 | 0.011935 | 0.011935 | 0.011935 | 0.9749 | -0.48364 | 0.97481 | -0.48539 | 3.2787
142 | 0.015424 | 0.0038719 | -0.015404 | -0.0038602 | 2.0135e-05 | 1.1689e-05 | 0.023586 | 0.023586 | 0.023586 | 0.97319 | -0.5173 | 0.97181 | -0.54471 | 6.4797
143 | 0.0066792 | 0.0016736 | -0.0066763 | -0.0016727 | 2.8752e-06 | 9.3233e-07 | 0.010227 | 0.010227 | 0.010227 | 0.97181 | -0.54471 | 0.97135 | -0.55375 | 2.8097
144 | 0.005291 | 0.0013259 | -0.0052906 | -0.0013258 | 4.2395e-07 | 5.5278e-08 | 0.0080765 | 0.0080765 | 0.0080765 | 0.97481 | -0.48539 | 0.97473 | -0.48707 | 2.2188
145 | 0.0025363 | 0.00063553 | -0.0025363 | -0.00063565 | 7.0826e-08 | -1.117e-07 | 0.0038719 | 0.003872 | 0.003872 | 0.97473 | -0.48707 | 0.9747 | -0.48766 | 1.0637
146 | -0.0038042 | -0.00095343 | 0.003805 | 0.00095318 | 7.636e-07 | -2.5186e-07 | 0.0058312 | 0.005831 | 0.0058312 | 0.97076 | -0.56534 | 0.97098 | -0.56112 | 1.602
147 | -0.003805 | -0.00095318 | 0.0038054 | 0.00095303 | 4.3934e-07 | -1.4509e-07 | 0.005831 | 0.0058308 | 0.005831 | 0.97098 | -0.56112 | 0.9711 | -0.5587 | 1.6019
148 | -0.0066748 | -0.0016722 | 0.0066763 | 0.0016727 | 1.5737e-06 | 5.1069e-07 | 0.010227 | 0.010227 | 0.010227 | 0.9711 | -0.5587 | 0.97135 | -0.55375 | 2.8098

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58756 | 0.15058

## res_load
| p_mw | q_mvar
0 | 0.0018717 | 0.00046909
1 | 0.0004496 | 0.00011268
2 | 0.0006811 | 0.0001707
3 | 0.0021643 | 0.00054243
4 | 0.0045411 | 0.0011381
5 | 0.00042185 | 0.00010573
6 | 0.0049329 | 0.0012363
7 | 0.00083928 | 0.00021034
8 | 0.0041719 | 0.0010456
9 | 0.00062703 | 0.00015715
10 | 0.01429 | 0.0035814
11 | 0.016054 | 0.0040235
12 | 0.004277 | 0.0010719
13 | 0.0030112 | 0.00075468
14 | 0.00064993 | 0.00016289
15 | 0.014023 | 0.0035146
16 | 0.022038 | 0.0055233
17 | 0.0017472 | 0.0004379
18 | 0.0028266 | 0.00070842
19 | 0.00052247 | 0.00013094
20 | 0.00058736 | 0.00014721
21 | 0.016617 | 0.0041645
22 | 0.0082713 | 0.002073
23 | 0.0049954 | 0.001252
24 | 0.010553 | 0.0026449
25 | 0.0030637 | 0.00076783
26 | 0.0073326 | 0.0018377
27 | 0.0033052 | 0.00082836
28 | 0.0058719 | 0.0014716
29 | 0.0071715 | 0.0017973
30 | 0.0030926 | 0.00077508
31 | 0.011738 | 0.0029419
32 | 0.0014217 | 0.00035632
33 | 0.0034588 | 0.00086685
34 | 0.017024 | 0.0042666
35 | 0.0020295 | 0.00050865
36 | 0.0032369 | 0.00081124
37 | 0.0062322 | 0.0015619
38 | 0.0035033 | 0.00087801
39 | 0.0040124 | 0.0010056
40 | 0.0029755 | 0.00074574
41 | 0.0089071 | 0.0022323
42 | 0.011835 | 0.0029662
43 | 0.008162 | 0.0020456
44 | 0.0054786 | 0.0013731
45 | 0.0026834 | 0.00067253
46 | 0.0038668 | 0.00096911
47 | 0.0037195 | 0.00093221
48 | 0.0065299 | 0.0016365
49 | 0.0085917 | 0.0021533
50 | 0.0053294 | 0.0013357
51 | 0.0039908 | 0.0010002
52 | 0.0056935 | 0.0014269
53 | 0.01283 | 0.0032155
54 | 0.005672 | 0.0014215
55 | 0.0058959 | 0.0014776
56 | 0.0030942 | 0.00077549
57 | 0.0043687 | 0.0010949
58 | 0.0032152 | 0.0008058
59 | 0.0035724 | 0.00089533
60 | 0.0082303 | 0.0020627
61 | 0.004454 | 0.0011163
62 | 0.0032168 | 0.0008062
63 | 0.0069569 | 0.0017436
64 | 0.0057557 | 0.0014425
65 | 0.0043444 | 0.0010888
66 | 0.0029327 | 0.000735
67 | 0.0094615 | 0.0023713
68 | 0.0032871 | 0.00082384
69 | 0.0059395 | 0.0014886
70 | 0.0038345 | 0.00096101
71 | 0.0057042 | 0.0014296
72 | 0.0068159 | 0.0017082
73 | 0.0027687 | 0.00069389
74 | 0.0037558 | 0.0009413
75 | 0.0048675 | 0.0012199
76 | 0.0053424 | 0.0013389
77 | 0.006406 | 0.0016055
78 | 0.0027339 | 0.00068518
79 | 0.0038837 | 0.00097335
80 | 0.0063909 | 0.0016017
81 | 0.0038518 | 0.00096534
82 | 0.0040403 | 0.0010126
83 | 0.0044906 | 0.0011255
84 | 0.011685 | 0.0029286
85 | 0.0018245 | 0.00045727
86 | 0.016036 | 0.004019
87 | 0.0014264 | 0.0003575
88 | 0.003972 | 0.00099547
89 | 0.0026944 | 0.00067527
90 | 0.0040613 | 0.0010179
91 | 0.004186 | 0.0010491
92 | 0.0022789 | 0.00057113
93 | 0.0031923 | 0.00080007
94 | 0.0037094 | 0.00092967
95 | 0.0041331 | 0.0010359
96 | 0.00024406 | 6.1166e-05
97 | 9.6768e-05 | 2.4252e-05
98 | 0.00024158 | 6.0546e-05
99 | 0.0035525 | 0.00089034
100 | 0.0042548 | 0.0010664
101 | 0.00020294 | 5.0862e-05
102 | 0.0014824 | 0.00037152
103 | 0.0013626 | 0.00034149
104 | 0.00072489 | 0.00018167
105 | 0.0012453 | 0.00031209
106 | 0.0006044 | 0.00015148
107 | 0.0025157 | 0.00063051
108 | 0.0087247 | 0.0021866
109 | 0.0025275 | 0.00063345
110 | 0.0027543 | 0.00069028
111 | 0.0025363 | 0.00063565
112 | 0.013683 | 0.0034294
113 | 0.004007 | 0.0010043
114 | 0.0038042 | 0.00095343
115 | 0.0028693 | 0.00071912

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1