## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1348-1_0_1_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1348-1_0_1_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1348-1_0_1_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1348-1_0_1_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1348-1_0_1_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1348-1_0_1_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1348-1_0_1_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1348-1_0_1_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1348-1_0_1_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1348-1_0_1_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1348-1_0_1_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1348-1_0_1_node_83 | 0.4 | n |  | TRUE
12 | bus_LV_1348-1_0_1_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1348-1_0_1_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1348-1_0_1_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1348-1_0_1_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1348-1_0_1_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1348-1_0_1_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1348-1_0_1_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1348-1_0_1_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_1348-1_0_1_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1348-1_0_1_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1348-1_0_1_node_167 | 0.4 | n |  | TRUE
23 | bus_LV_1348-1_0_1_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1348-1_0_1_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_1348-1_0_1_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1348-1_0_1_node_181 | 0.4 | n |  | TRUE
27 | bus_LV_1348-1_0_1_node_38 | 0.4 | n |  | TRUE
28 | bus_LV_1348-1_0_1_node_182 | 0.4 | n |  | TRUE
29 | bus_LV_1348-1_0_1_node_64 | 0.4 | n |  | TRUE
30 | bus_LV_1348-1_0_1_node_65 | 0.4 | n |  | TRUE
31 | bus_LV_1348-1_0_1_node_66 | 0.4 | n |  | TRUE
32 | bus_LV_1348-1_0_1_node_67 | 0.4 | n |  | TRUE
33 | bus_LV_1348-1_0_1_node_68 | 0.4 | n |  | TRUE
34 | bus_LV_1348-1_0_1_node_69 | 0.4 | n |  | TRUE
35 | bus_LV_1348-1_0_1_node_75 | 0.4 | n |  | TRUE
36 | bus_LV_1348-1_0_1_node_70 | 0.4 | n |  | TRUE
37 | bus_LV_1348-1_0_1_node_76 | 0.4 | n |  | TRUE
38 | bus_LV_1348-1_0_1_node_79 | 0.4 | n |  | TRUE
39 | bus_LV_1348-1_0_1_node_71 | 0.4 | n |  | TRUE
40 | bus_LV_1348-1_0_1_node_72 | 0.4 | n |  | TRUE
41 | bus_LV_1348-1_0_1_node_74 | 0.4 | n |  | TRUE
42 | bus_LV_1348-1_0_1_node_73 | 0.4 | n |  | TRUE
43 | bus_LV_1348-1_0_1_node_85 | 0.4 | n |  | TRUE
44 | bus_LV_1348-1_0_1_node_77 | 0.4 | n |  | TRUE
45 | bus_LV_1348-1_0_1_node_78 | 0.4 | n |  | TRUE
46 | bus_LV_1348-1_0_1_node_80 | 0.4 | n |  | TRUE
47 | bus_LV_1348-1_0_1_node_81 | 0.4 | n |  | TRUE
48 | bus_LV_1348-1_0_1_node_82 | 0.4 | n |  | TRUE
49 | bus_LV_1348-1_0_1_node_84 | 0.4 | n |  | TRUE
50 | bus_LV_1348-1_0_1_node_87 | 0.4 | n |  | TRUE
51 | bus_LV_1348-1_0_1_node_86 | 0.4 | n |  | TRUE
52 | bus_LV_1348-1_0_1_node_88 | 0.4 | n |  | TRUE
53 | bus_LV_1348-1_0_1_node_89 | 0.4 | n |  | TRUE
54 | bus_LV_1348-1_0_1_node_90 | 0.4 | n |  | TRUE
55 | bus_MV_0_node_84 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1348-1_0_1_load_0 | 0 | 0.0027413 | 0.00068704 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1348-1_0_1_load_1 | 1 | 0.00055195 | 0.00013833 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1348-1_0_1_load_3 | 3 | 0.0006164 | 0.00015449 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1348-1_0_1_load_6 | 6 | 0.00023511 | 5.8925e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1348-1_0_1_load_7 | 7 | 0.00084174 | 0.00021096 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1348-1_0_1_load_8 | 8 | 0.0002573 | 6.4486e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1348-1_0_1_load_9 | 9 | 0.0013674 | 0.00034269 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1348-1_0_1_load_10 | 10 | 0.00043887 | 0.00010999 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1348-1_0_1_load_83 | 11 | 0.0057145 | 0.0014322 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1348-1_0_1_load_17 | 12 | 0.00095538 | 0.00023944 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1348-1_0_1_load_11 | 13 | 0.0026251 | 0.0006579 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1348-1_0_1_load_13 | 16 | 0.0018434 | 0.000462 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1348-1_0_1_load_15 | 17 | 0.0018766 | 0.00047033 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1348-1_0_1_load_14 | 18 | 0.0013677 | 0.00034277 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1348-1_0_1_load_22 | 19 | 0.00080582 | 0.00020196 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1348-1_0_1_load_16 | 20 | 0.00042533 | 0.0001066 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1348-1_0_1_load_167 | 22 | 0.0001747 | 4.3783e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1348-1_0_1_load_19 | 23 | 0.00032993 | 8.2688e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1348-1_0_1_load_40 | 24 | 0.00059819 | 0.00014992 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1348-1_0_1_load_21 | 25 | 0.00044137 | 0.00011062 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1348-1_0_1_load_181 | 26 | 0.0006397 | 0.00016032 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1348-1_0_1_load_38 | 27 | 0.00017274 | 4.3292e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1348-1_0_1_load_182 | 28 | 0.00050796 | 0.00012731 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1348-1_0_1_load_64 | 29 | 0.00021641 | 5.4236e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1348-1_0_1_load_65 | 30 | 0.00039992 | 0.00010023 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1348-1_0_1_load_66 | 31 | 0.00096068 | 0.00024077 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1348-1_0_1_load_67 | 32 | 0.0016363 | 0.0004101 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1348-1_0_1_load_69 | 34 | 0.00083947 | 0.00021039 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1348-1_0_1_load_75 | 35 | 0.0033901 | 0.00084963 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1348-1_0_1_load_70 | 36 | 0.00053783 | 0.00013479 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1348-1_0_1_load_76 | 37 | 0.0015434 | 0.0003868 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1348-1_0_1_load_79 | 38 | 0.0040285 | 0.0010096 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1348-1_0_1_load_71 | 39 | 0.0086509 | 0.0021681 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1348-1_0_1_load_72 | 40 | 0.0013518 | 0.00033879 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1348-1_0_1_load_73 | 42 | 0.0021573 | 0.00054068 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1348-1_0_1_load_80 | 46 | 0.0032583 | 0.00081661 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1348-1_0_1_load_81 | 47 | 0.00064176 | 0.00016084 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1348-1_0_1_load_82 | 48 | 0.0014632 | 0.00036672 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1348-1_0_1_load_84 | 49 | 0.00083885 | 0.00021024 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1348-1_0_1_load_89 | 53 | 0.0013808 | 0.00034607 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1348-1_0_1_load_90 | 54 | 0.0015748 | 0.00039469 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 49 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1348-1_0_1_line_0 |  | 0 | 1 | 0.056161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1348-1_0_1_line_1 |  | 0 | 2 | 0.020408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1348-1_0_1_line_2 |  | 1 | 3 | 0.0619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1348-1_0_1_line_3 |  | 2 | 4 | 0.081372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1348-1_0_1_line_4 |  | 2 | 5 | 0.12694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1348-1_0_1_line_5 |  | 3 | 6 | 0.0094384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1348-1_0_1_line_6 |  | 4 | 7 | 0.014357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1348-1_0_1_line_7 |  | 4 | 8 | 0.14191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1348-1_0_1_line_8 |  | 5 | 9 | 0.1612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1348-1_0_1_line_9 |  | 6 | 10 | 0.11647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1348-1_0_1_line_10 |  | 8 | 11 | 0.21349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1348-1_0_1_line_11 |  | 10 | 12 | 0.045094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1348-1_0_1_line_12 |  | 11 | 45 | 0.11293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1348-1_0_1_line_13 |  | 11 | 48 | 0.0015857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1348-1_0_1_line_14 |  | 12 | 22 | 0.25112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1348-1_0_1_line_15 |  | 12 | 20 | 0.16277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1348-1_0_1_line_16 |  | 13 | 14 | 0.064886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1348-1_0_1_line_17 |  | 13 | 15 | 0.155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1348-1_0_1_line_18 |  | 14 | 16 | 0.042291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1348-1_0_1_line_19 |  | 15 | 25 | 0.033638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1348-1_0_1_line_20 |  | 16 | 17 | 0.085425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1348-1_0_1_line_21 |  | 17 | 21 | 0.035854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1348-1_0_1_line_22 |  | 18 | 19 | 0.052872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1348-1_0_1_line_23 |  | 18 | 20 | 0.12028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1348-1_0_1_line_24 |  | 19 | 26 | 0.030713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1348-1_0_1_line_25 |  | 19 | 25 | 0.040975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1348-1_0_1_line_26 |  | 21 | 23 | 0.16052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1348-1_0_1_line_27 |  | 21 | 24 | 0.16899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1348-1_0_1_line_28 |  | 24 | 27 | 0.0085505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1348-1_0_1_line_29 |  | 26 | 28 | 0.022543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1348-1_0_1_line_30 |  | 29 | 30 | 0.016184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1348-1_0_1_line_31 |  | 29 | 31 | 6.4645e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1348-1_0_1_line_32 |  | 30 | 32 | 0.02248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1348-1_0_1_line_33 |  | 31 | 33 | 0.01281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1348-1_0_1_line_34 |  | 32 | 34 | 0.013076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1348-1_0_1_line_35 |  | 32 | 35 | 0.32091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1348-1_0_1_line_36 |  | 33 | 36 | 0.02058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1348-1_0_1_line_37 |  | 34 | 37 | 0.023897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1348-1_0_1_line_38 |  | 35 | 41 | 0.17511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1348-1_0_1_line_39 |  | 36 | 38 | 0.026514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1348-1_0_1_line_40 |  | 37 | 44 | 0.096331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1348-1_0_1_line_41 |  | 38 | 46 | 0.0081706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1348-1_0_1_line_42 |  | 39 | 40 | 0.023398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1348-1_0_1_line_43 |  | 39 | 41 | 0.18471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1348-1_0_1_line_44 |  | 40 | 42 | 0.012869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1348-1_0_1_line_45 |  | 42 | 43 | 0.22621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1348-1_0_1_line_46 |  | 43 | 50 | 0.068927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1348-1_0_1_line_47 |  | 44 | 45 | 0.14701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1348-1_0_1_line_48 |  | 46 | 47 | 0.00069874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1348-1_0_1_line_49 |  | 48 | 49 | 0.086819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1348-1_0_1_line_50 |  | 50 | 54 | 0.037613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1348-1_0_1_line_51 |  | 51 | 52 | 0.022162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1348-1_0_1_line_52 |  | 51 | 53 | 0.029044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1348-1_0_1_line_53 |  | 52 | 54 | 0.03939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1348-1_0_1_trafo_84 | 0.63 MVA 20/0.4 kV | 55 | 49 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2710695.6282 | 1221522.9631 | 2710655.4976 | 1221497.471 | 2710648.357 | 1221492.6447
1 | 2710714.5832 | 1221529.7265 | 2710701.8051 | 1221526.8869 | 2710695.6282 | 1221522.9631
2 | 2710648.357 | 1221492.6447 | 2710614.17 | 1221469.538 | 2710596.0363 | 1221459.6865
3 | 2710714.5832 | 1221529.7265 | 2710727.7957 | 1221549.587 | 2710737.9498 | 1221560.9176 | 2710736.2914 | 1221584.7935 | 2710742.4714 | 1221602.1325
4 | 2710714.5832 | 1221529.7265 | 2710718.1423 | 1221530.5155 | 2710731.3377 | 1221531.317 | 2710746.8097 | 1221536.5864 | 2710766.5261 | 1221548.2284 | 2710776.7086 | 1221549.4632 | 2710797.4391 | 1221542.0878 | 2710810.3256 | 1221538.6916 | 2710820.2879 | 1221537.8986 | 2710834.2417 | 1221544.8301
5 | 2710587.7428 | 1221455.1809 | 2710596.0363 | 1221459.6865
6 | 2710742.4714 | 1221602.1325 | 2710756.3591 | 1221598.3435
7 | 2710742.4714 | 1221602.1325 | 2710758.9108 | 1221625.1332 | 2710780.0174 | 1221637.4794 | 2710800.1928 | 1221667.2325 | 2710806.6212 | 1221704.2242 | 2710819.2435 | 1221713.7774
8 | 2710751.2031 | 1221416.7119 | 2710756.1407 | 1221446.1813 | 2710771.8443 | 1221465.1097 | 2710794.4891 | 1221493.4966 | 2710825.6585 | 1221511.5011 | 2710833.725 | 1221537.5373 | 2710834.2417 | 1221544.8301
9 | 2710473.9167 | 1221452.3349 | 2710496.0351 | 1221444.6042 | 2710517.9066 | 1221442.3861 | 2710551.0479 | 1221447.0158 | 2710587.7428 | 1221455.1809 | 2710587.7428 | 1221455.1809
10 | 2710819.2435 | 1221713.7774 | 2710650.6082 | 1221844.6917
11 | 2710430.0521 | 1221461.9199 | 2710442.6168 | 1221460.9478 | 2710465.5237 | 1221455.2684 | 2710473.9167 | 1221452.3349
12 | 2710692.7146 | 1221896.8834 | 2710687.5881 | 1221890.6278 | 2710688.3837 | 1221880.4906 | 2710696.9633 | 1221856.9213 | 2710696.246 | 1221851.8375 | 2710682.2499 | 1221827.2257 | 2710650.6082 | 1221844.6917
13 | 2710649.22 | 1221845.458 | 2710650.6082 | 1221844.6917
14 | 2710430.0521 | 1221461.9199 | 2710321.8659 | 1221235.2971
15 | 2710430.0521 | 1221461.9199 | 2710416.6519 | 1221462.9567 | 2710377.6135 | 1221461.2652 | 2710359.9462 | 1221467.5536 | 2710324.3809 | 1221495.8602 | 2710286.3966 | 1221521.8927
16 | 2710114.6676 | 1221486.1274 | 2710108.7241 | 1221514.9612 | 2710116.0044 | 1221535.6779 | 2710124.5611 | 1221541.1291 | 2710127.6525 | 1221542.3985
17 | 2710127.6525 | 1221542.3985 | 2710198.4687 | 1221680.2777
18 | 2710114.6676 | 1221486.1274 | 2710102.5348 | 1221482.0222 | 2710074.5339 | 1221472.7924
19 | 2710198.4687 | 1221680.2777 | 2710210.3743 | 1221679.0082 | 2710228.3739 | 1221678.085 | 2710231.7639 | 1221676.7537
20 | 2710074.5339 | 1221472.7924 | 2709993.4029 | 1221446.0496
21 | 2709959.4422 | 1221443.9391 | 2709972.7697 | 1221439.2483 | 2709993.4029 | 1221446.0496
22 | 2710269.378 | 1221686.9961 | 2710296.7058 | 1221641.7342
23 | 2710286.3966 | 1221521.8927 | 2710296.7058 | 1221641.7342
24 | 2710269.378 | 1221686.9961 | 2710279.161 | 1221691.4019 | 2710289.5359 | 1221703.125 | 2710289.2464 | 1221707.4444
25 | 2710231.7639 | 1221676.7537 | 2710239.1889 | 1221673.8376 | 2710245.2943 | 1221675.6186 | 2710260.4921 | 1221682.9944 | 2710269.378 | 1221686.9961
26 | 2709959.4422 | 1221443.9391 | 2709960.1435 | 1221445.4087 | 2709985.9284 | 1221468.3241 | 2710027.1734 | 1221498.8198 | 2710056.0381 | 1221531.1883 | 2710063.1469 | 1221560.0552
27 | 2709959.4422 | 1221443.9391 | 2709967.137 | 1221275.1222
28 | 2709967.137 | 1221275.1222 | 2709964.816 | 1221266.8927
29 | 2710289.2464 | 1221707.4444 | 2710288.9591 | 1221711.7318 | 2710284.5249 | 1221717.6319 | 2710275.6129 | 1221717.0442 | 2710273.7336 | 1221717.5001
30 | 2710711.1736 | 1222061.0825 | 2710700.6878 | 1222048.7544
31 | 2710711.2154 | 1222061.1317 | 2710711.1736 | 1222061.0825
32 | 2710693.3799 | 1222028.0206 | 2710694.6859 | 1222038.0812 | 2710698.4215 | 1222046.0899 | 2710700.6878 | 1222048.7544
33 | 2710719.515 | 1222070.8895 | 2710711.2154 | 1222061.1317
34 | 2710691.6967 | 1222015.0536 | 2710693.3799 | 1222028.0206
35 | 2710693.3799 | 1222028.0206 | 2710386.2414 | 1222121.0066
36 | 2710719.515 | 1222070.8895 | 2710732.852 | 1222086.5635
37 | 2710691.6967 | 1222015.0536 | 2710688.6204 | 1221991.3557
38 | 2710386.2414 | 1222121.0066 | 2710380.9142 | 1222121.8863 | 2710372.2984 | 1222121.7264 | 2710331.2657 | 1222107.9335 | 2710315.0023 | 1222107.7655 | 2710303.106 | 1222111.8481 | 2710286.2101 | 1222131.0718 | 2710284.0061 | 1222137.4135 | 2710279.184 | 1222149.9335 | 2710273.5245 | 1222155.6441 | 2710256.6976 | 1222163.3716 | 2710242.2958 | 1222172.4785
39 | 2710732.852 | 1222086.5635 | 2710745.5683 | 1222101.508 | 2710750.0149 | 1222106.7724
40 | 2710760.8429 | 1221939.1706 | 2710758.7763 | 1221951.5525 | 2710749.6749 | 1221957.8991 | 2710725.4841 | 1221962.942 | 2710708.3736 | 1221971.9862 | 2710693.0798 | 1221982.0761 | 2710688.6204 | 1221991.3557 | 2710688.6204 | 1221991.3557
41 | 2710758.1682 | 1222107.3044 | 2710750.0149 | 1222106.7724 | 2710750.0149 | 1222106.7724
42 | 2710351.8548 | 1222321.1856 | 2710361.8935 | 1222342.3209
43 | 2710351.8548 | 1222321.1856 | 2710242.2958 | 1222172.4785
44 | 2710367.415 | 1222353.9457 | 2710361.8935 | 1222342.3209
45 | 2710525.621 | 1222515.6316 | 2710367.415 | 1222353.9457
46 | 2710556.9561 | 1222564.8835 | 2710558.6283 | 1222545.5223 | 2710557.8486 | 1222532.3646 | 2710525.621 | 1222515.6316
47 | 2710692.7146 | 1221896.8834 | 2710701.1492 | 1221879.883 | 2710706.7795 | 1221861.0958 | 2710706.4852 | 1221856.9317 | 2710716.0567 | 1221859.5783 | 2710718.5485 | 1221863.8945 | 2710718.7689 | 1221874.0729 | 2710720.5972 | 1221885.5043 | 2710735.384 | 1221903.0813 | 2710756.1553 | 1221927.6859 | 2710760.8429 | 1221939.1706
48 | 2710758.8655 | 1222107.3499 | 2710758.1682 | 1222107.3044
49 | 2710569.3205 | 1221836.4166 | 2710578.9329 | 1221835.368 | 2710597.7853 | 1221839.1654 | 2710613.2818 | 1221848.3823 | 2710631.056 | 1221855.4844 | 2710649.22 | 1221845.458
50 | 2710556.9561 | 1222564.8835 | 2710548.6702 | 1222583.7438 | 2710548.0469 | 1222597.2868 | 2710548.197 | 1222600.739
51 | 2710534.4152 | 1222651.9525 | 2710542.5942 | 1222643.7315 | 2710552.4678 | 1222639.8563
52 | 2710534.4152 | 1222651.9525 | 2710528.3957 | 1222665.6176 | 2710531.4893 | 1222677.1392 | 2710532.7819 | 1222678.8971
53 | 2710552.4678 | 1222639.8563 | 2710548.7538 | 1222613.5454 | 2710548.197 | 1222600.739

## bus_geodata
| x | y | coords
0 | 2710695.6282 | 1221522.9631
1 | 2710648.357 | 1221492.6447
2 | 2710714.5832 | 1221529.7265
3 | 2710596.0363 | 1221459.6865
4 | 2710742.4714 | 1221602.1325
5 | 2710834.2417 | 1221544.8301
6 | 2710587.7428 | 1221455.1809
7 | 2710756.3591 | 1221598.3435
8 | 2710819.2435 | 1221713.7774
9 | 2710751.2031 | 1221416.7119
10 | 2710473.9167 | 1221452.3349
11 | 2710650.6082 | 1221844.6917
12 | 2710430.0521 | 1221461.9199
13 | 2710127.6525 | 1221542.3985
14 | 2710114.6676 | 1221486.1274
15 | 2710198.4687 | 1221680.2777
16 | 2710074.5339 | 1221472.7924
17 | 2709993.4029 | 1221446.0496
18 | 2710296.7058 | 1221641.7342
19 | 2710269.378 | 1221686.9961
20 | 2710286.3966 | 1221521.8927
21 | 2709959.4422 | 1221443.9391
22 | 2710321.8659 | 1221235.2971
23 | 2710063.1469 | 1221560.0552
24 | 2709967.137 | 1221275.1222
25 | 2710231.7639 | 1221676.7537
26 | 2710289.2464 | 1221707.4444
27 | 2709964.816 | 1221266.8927
28 | 2710273.7336 | 1221717.5001
29 | 2710711.1736 | 1222061.0825
30 | 2710700.6878 | 1222048.7544
31 | 2710711.2154 | 1222061.1317
32 | 2710693.3799 | 1222028.0206
33 | 2710719.515 | 1222070.8895
34 | 2710691.6967 | 1222015.0536
35 | 2710386.2414 | 1222121.0066
36 | 2710732.852 | 1222086.5635
37 | 2710688.6204 | 1221991.3557
38 | 2710750.0149 | 1222106.7724
39 | 2710351.8548 | 1222321.1856
40 | 2710361.8935 | 1222342.3209
41 | 2710242.2958 | 1222172.4785
42 | 2710367.415 | 1222353.9457
43 | 2710525.621 | 1222515.6316
44 | 2710760.8429 | 1221939.1706
45 | 2710692.7146 | 1221896.8834
46 | 2710758.1682 | 1222107.3044
47 | 2710758.8655 | 1222107.3499
48 | 2710649.22 | 1221845.458
49 | 2710569.3205 | 1221836.4166
50 | 2710556.9561 | 1222564.8835
51 | 2710534.4152 | 1222651.9525
52 | 2710552.4678 | 1222639.8563
53 | 2710532.7819 | 1222678.8971
54 | 2710548.197 | 1222600.739
55 | 2710569.3205 | 1221836.4166

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98692 | -0.25061 | 0.0027413 | 0.00068704
1 | 0.98617 | -0.26536 | 0.00055195 | 0.00013833
2 | 0.98725 | -0.24426 | 0 | 0
3 | 0.98536 | -0.28102 | 0.0006164 | 0.00015449
4 | 0.98866 | -0.21697 | 0 | 0
5 | 0.98709 | -0.24738 | 0 | 0
6 | 0.98524 | -0.28331 | 0.00023511 | 5.8925e-05
7 | 0.98865 | -0.21718 | 0.00084174 | 0.00021096
8 | 0.99122 | -0.16743 | 0.0002573 | 6.4486e-05
9 | 0.98689 | -0.25133 | 0.0013674 | 0.00034269
10 | 0.98382 | -0.31106 | 0.00043887 | 0.00010999
11 | 0.99513 | -0.09239 | 0.0057145 | 0.0014322
12 | 0.98329 | -0.32147 | 0.00095538 | 0.00023944
13 | 0.9782 | -0.42124 | 0.0026251 | 0.0006579
14 | 0.97791 | -0.42696 | 0 | 0
15 | 0.97927 | -0.40018 | 0 | 0
16 | 0.97772 | -0.43069 | 0.0018434 | 0.000462
17 | 0.97749 | -0.43535 | 0.0018766 | 0.00047033
18 | 0.98028 | -0.38026 | 0.0013677 | 0.00034277
19 | 0.9798 | -0.38973 | 0.00080582 | 0.00020196
20 | 0.98153 | -0.35577 | 0.00042533 | 0.0001066
21 | 0.97745 | -0.43608 | 0 | 0
22 | 0.98325 | -0.32228 | 0.0001747 | 4.3783e-05
23 | 0.9774 | -0.43705 | 0.00032993 | 8.2688e-05
24 | 0.97733 | -0.43846 | 0.00059819 | 0.00014992
25 | 0.9795 | -0.39562 | 0.00044137 | 0.00011062
26 | 0.97977 | -0.39037 | 0.0006397 | 0.00016032
27 | 0.97733 | -0.43849 | 0.00017274 | 4.3292e-05
28 | 0.97976 | -0.39058 | 0.00050796 | 0.00012731
29 | 0.98295 | -0.32652 | 0.00021641 | 5.4236e-05
30 | 0.98309 | -0.3237 | 0.00039992 | 0.00010023
31 | 0.98295 | -0.32653 | 0.00096068 | 0.00024077
32 | 0.9833 | -0.31963 | 0.0016363 | 0.0004101
33 | 0.98285 | -0.32848 | 0 | 0
34 | 0.98367 | -0.31251 | 0.00083947 | 0.00021039
35 | 0.97777 | -0.42747 | 0.0033901 | 0.00084963
36 | 0.98269 | -0.33163 | 0.00053783 | 0.00013479
37 | 0.98436 | -0.29914 | 0.0015434 | 0.0003868
38 | 0.98249 | -0.33542 | 0.0040285 | 0.0010096
39 | 0.9727 | -0.52728 | 0.0086509 | 0.0021681
40 | 0.97256 | -0.53007 | 0.0013518 | 0.00033879
41 | 0.9753 | -0.47592 | 0 | 0
42 | 0.9725 | -0.53128 | 0.0021573 | 0.00054068
43 | 0.97187 | -0.54366 | 0 | 0
44 | 0.98727 | -0.2428 | 0 | 0
45 | 0.99171 | -0.15745 | 0 | 0
46 | 0.98247 | -0.336 | 0.0032583 | 0.00081661
47 | 0.98246 | -0.33601 | 0.00064176 | 0.00016084
48 | 0.99521 | -0.090765 | 0.0014632 | 0.00036672
49 | 1 | 0 | -0.062264 | -0.015549
50 | 0.97168 | -0.54742 | 0 | 0
51 | 0.9715 | -0.55105 | 0 | 0
52 | 0.97153 | -0.55048 | 0 | 0
53 | 0.97146 | -0.55179 | 0.0013808 | 0.00034607
54 | 0.97158 | -0.54948 | 0.0015748 | 0.00039469
55 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.014703 | 0.0037011 | -0.014693 | -0.0036952 | 1.0356e-05 | 5.9106e-06 | 0.022175 | 0.022175 | 0.022175 | 0.98692 | -0.25061 | 0.98617 | -0.26536 | 6.092
1 | -0.017445 | -0.0043882 | 0.01745 | 0.0043913 | 5.2965e-06 | 3.1289e-06 | 0.026308 | 0.026308 | 0.026308 | 0.98692 | -0.25061 | 0.98725 | -0.24426 | 7.2274
2 | 0.014141 | 0.0035569 | -0.014131 | -0.0035509 | 1.0573e-05 | 5.9776e-06 | 0.021342 | 0.021342 | 0.021342 | 0.98617 | -0.26536 | 0.98536 | -0.28102 | 5.8633
3 | -0.018818 | -0.0047306 | 0.018842 | 0.0047453 | 2.4556e-05 | 1.4674e-05 | 0.028368 | 0.028368 | 0.028368 | 0.98725 | -0.24426 | 0.98866 | -0.21697 | 7.7934
4 | 0.0013678 | 0.0003393 | -0.0013676 | -0.0003408 | 2.0213e-07 | -1.4935e-06 | 0.0020604 | 0.0020609 | 0.0020609 | 0.98725 | -0.24426 | 0.98709 | -0.24738 | 0.56619
5 | 0.013514 | 0.0033964 | -0.013513 | -0.0033956 | 1.4746e-06 | 8.2354e-07 | 0.020411 | 0.020412 | 0.020412 | 0.98536 | -0.28102 | 0.98524 | -0.28331 | 5.6076
6 | 0.00084175 | 0.00021078 | -0.00084174 | -0.00021096 | 8.6409e-09 | -1.7857e-07 | 0.0012668 | 0.0012669 | 0.0012669 | 0.98866 | -0.21697 | 0.98865 | -0.21718 | 0.34805
7 | -0.019684 | -0.0049561 | 0.019731 | 0.0049841 | 4.6734e-05 | 2.8085e-05 | 0.029634 | 0.029634 | 0.029634 | 0.98866 | -0.21697 | 0.99122 | -0.16743 | 8.1413
8 | 0.0013676 | 0.0003408 | -0.0013674 | -0.00034269 | 2.5686e-07 | -1.8958e-06 | 0.0020609 | 0.0020617 | 0.0020617 | 0.98709 | -0.24738 | 0.98689 | -0.25133 | 0.56639
9 | 0.013278 | 0.0033367 | -0.01326 | -0.0033269 | 1.757e-05 | 9.7635e-06 | 0.020056 | 0.020057 | 0.020057 | 0.98524 | -0.28331 | 0.98382 | -0.31106 | 5.5101
10 | -0.019988 | -0.0050486 | 0.02006 | 0.005092 | 7.2146e-05 | 4.3411e-05 | 0.03002 | 0.030019 | 0.03002 | 0.99122 | -0.16743 | 0.99513 | -0.09239 | 8.2473
11 | 0.012821 | 0.0032169 | -0.012815 | -0.0032134 | 6.3599e-06 | 3.498e-06 | 0.019393 | 0.019393 | 0.019393 | 0.98382 | -0.31106 | 0.98329 | -0.32147 | 5.3278
12 | 0.033106 | 0.0084859 | -0.033002 | -0.0084208 | 0.00010406 | 6.5137e-05 | 0.049571 | 0.049571 | 0.049571 | 0.99513 | -0.09239 | 0.99171 | -0.15745 | 13.6185
13 | -0.058881 | -0.01501 | 0.058886 | 0.015013 | 4.6189e-06 | 2.9355e-06 | 0.088135 | 0.088135 | 0.088135 | 0.99513 | -0.09239 | 0.99521 | -0.090765 | 24.2128
14 | 0.0001747 | 4.0602e-05 | -0.0001747 | -4.3783e-05 | 6.5546e-09 | -3.181e-06 | 0.00026328 | 0.00026438 | 0.00026438 | 0.98329 | -0.32147 | 0.98325 | -0.32228 | 0.072633
15 | 0.011685 | 0.0029334 | -0.011666 | -0.0029232 | 1.909e-05 | 1.0157e-05 | 0.017684 | 0.017685 | 0.017685 | 0.98329 | -0.32147 | 0.98153 | -0.35577 | 4.8585
16 | 0.0048238 | 0.001203 | -0.0048225 | -0.001203 | 1.3095e-06 | 2.374e-08 | 0.0073358 | 0.007336 | 0.007336 | 0.9782 | -0.42124 | 0.97791 | -0.42696 | 2.0154
17 | -0.0074489 | -0.0018609 | 0.0074564 | 0.0018637 | 7.4597e-06 | 2.8262e-06 | 0.011329 | 0.011328 | 0.011329 | 0.9782 | -0.42124 | 0.97927 | -0.40018 | 3.1123
18 | 0.0048225 | 0.001203 | -0.0048217 | -0.001203 | 8.5353e-07 | 1.5769e-08 | 0.007336 | 0.0073362 | 0.0073362 | 0.97791 | -0.42696 | 0.97772 | -0.43069 | 2.0154
19 | -0.0074564 | -0.0018637 | 0.007458 | 0.0018644 | 1.6188e-06 | 6.1271e-07 | 0.011328 | 0.011328 | 0.011328 | 0.97927 | -0.40018 | 0.9795 | -0.39562 | 3.1122
20 | 0.0029783 | 0.00074098 | -0.0029776 | -0.00074163 | 6.5764e-07 | -6.5019e-07 | 0.0045307 | 0.0045311 | 0.0045311 | 0.97772 | -0.43069 | 0.97749 | -0.43535 | 1.2448
21 | 0.001101 | 0.0002713 | -0.001101 | -0.00027173 | 3.7698e-08 | -4.253e-07 | 0.0016744 | 0.0016745 | 0.0016745 | 0.97749 | -0.43535 | 0.97745 | -0.43608 | 0.46004
22 | 0.0098595 | 0.002467 | -0.0098551 | -0.0024648 | 4.4402e-06 | 2.1755e-06 | 0.014965 | 0.014965 | 0.014965 | 0.98028 | -0.38026 | 0.9798 | -0.38973 | 4.1113
23 | -0.011227 | -0.0028098 | 0.01124 | 0.0028166 | 1.3098e-05 | 6.8644e-06 | 0.017041 | 0.01704 | 0.017041 | 0.98028 | -0.38026 | 0.98153 | -0.35577 | 4.6815
24 | 0.0011477 | 0.00028699 | -0.0011477 | -0.00028735 | 3.4984e-08 | -3.6442e-07 | 0.0017428 | 0.0017429 | 0.0017429 | 0.9798 | -0.38973 | 0.97977 | -0.39037 | 0.47882
25 | 0.0079016 | 0.0019759 | -0.0078993 | -0.001975 | 2.2121e-06 | 8.9984e-07 | 0.011998 | 0.011999 | 0.011999 | 0.9798 | -0.38973 | 0.9795 | -0.39562 | 3.2963
26 | 0.00032994 | 8.0685e-05 | -0.00032993 | -8.2688e-05 | 1.5165e-08 | -2.0022e-06 | 0.00050157 | 0.00050229 | 0.00050229 | 0.97745 | -0.43608 | 0.9774 | -0.43705 | 0.13799
27 | 0.00077101 | 0.00019104 | -0.00077092 | -0.0001931 | 8.7246e-08 | -2.0621e-06 | 0.001173 | 0.0011737 | 0.0011737 | 0.97745 | -0.43608 | 0.97733 | -0.43846 | 0.32245
28 | 0.00017274 | 4.3185e-05 | -0.00017274 | -4.3292e-05 | 2.2173e-10 | -1.0701e-07 | 0.00026296 | 0.000263 | 0.000263 | 0.97733 | -0.43846 | 0.97733 | -0.43849 | 0.072251
29 | 0.00050797 | 0.00012703 | -0.00050796 | -0.00012731 | 5.0306e-09 | -2.8068e-07 | 0.00077137 | 0.00077147 | 0.00077147 | 0.97977 | -0.39037 | 0.97976 | -0.39058 | 0.21194
30 | -0.0096471 | -0.0024183 | 0.0096484 | 0.0024189 | 1.2944e-06 | 6.2326e-07 | 0.014604 | 0.014604 | 0.014604 | 0.98295 | -0.32652 | 0.98309 | -0.3237 | 4.0121
31 | 0.0094307 | 0.0023641 | -0.0094306 | -0.0023641 | 4.9399e-09 | 2.3433e-09 | 0.014277 | 0.014277 | 0.014277 | 0.98295 | -0.32652 | 0.98295 | -0.32653 | 3.9221
32 | -0.010048 | -0.0025192 | 0.01005 | 0.0025201 | 1.9501e-06 | 9.6295e-07 | 0.015209 | 0.015209 | 0.015209 | 0.98309 | -0.3237 | 0.9833 | -0.31963 | 4.1784
33 | 0.00847 | 0.0021233 | -0.0084692 | -0.002123 | 7.898e-07 | 3.4311e-07 | 0.012822 | 0.012822 | 0.012822 | 0.98295 | -0.32653 | 0.98285 | -0.32848 | 3.5226
34 | -0.030365 | -0.0076642 | 0.030375 | 0.0076707 | 1.0362e-05 | 6.4657e-06 | 0.04597 | 0.04597 | 0.04597 | 0.9833 | -0.31963 | 0.98367 | -0.31251 | 12.629
35 | 0.018678 | 0.004734 | -0.018582 | -0.0046764 | 9.6276e-05 | 5.7569e-05 | 0.028284 | 0.028286 | 0.028286 | 0.9833 | -0.31963 | 0.97777 | -0.42747 | 7.7708
36 | 0.0084692 | 0.002123 | -0.0084679 | -0.0021224 | 1.2689e-06 | 5.5131e-07 | 0.012822 | 0.012822 | 0.012822 | 0.98285 | -0.32848 | 0.98269 | -0.33163 | 3.5226
37 | -0.031214 | -0.0078811 | 0.031234 | 0.0078936 | 1.9998e-05 | 1.2495e-05 | 0.047239 | 0.047239 | 0.047239 | 0.98367 | -0.31251 | 0.98436 | -0.29914 | 12.9779
38 | 0.015192 | 0.0038268 | -0.015157 | -0.0038065 | 3.5122e-05 | 2.0287e-05 | 0.023126 | 0.023127 | 0.023127 | 0.97777 | -0.42747 | 0.9753 | -0.47592 | 6.3536
39 | 0.0079301 | 0.0019876 | -0.0079287 | -0.001987 | 1.4337e-06 | 5.8171e-07 | 0.012008 | 0.012008 | 0.012008 | 0.98269 | -0.33163 | 0.98249 | -0.33542 | 3.2989
40 | -0.032778 | -0.0082804 | 0.032867 | 0.008336 | 8.8772e-05 | 5.5586e-05 | 0.049572 | 0.049572 | 0.049572 | 0.98436 | -0.29914 | 0.98727 | -0.2428 | 13.6188
41 | 0.0039002 | 0.00097741 | -0.0039001 | -0.00097744 | 1.0691e-07 | -3.5049e-08 | 0.0059069 | 0.0059069 | 0.0059069 | 0.98249 | -0.33542 | 0.98247 | -0.336 | 1.6228
42 | 0.0064686 | 0.001617 | -0.0064677 | -0.0016167 | 8.5895e-07 | 2.5933e-07 | 0.009894 | 0.0098942 | 0.0098942 | 0.9727 | -0.52728 | 0.97256 | -0.53007 | 2.7182
43 | -0.015119 | -0.0037851 | 0.015157 | 0.0038065 | 3.7049e-05 | 2.1413e-05 | 0.023128 | 0.023127 | 0.023128 | 0.9727 | -0.52728 | 0.9753 | -0.47592 | 6.3539
44 | 0.005116 | 0.0012779 | -0.0051157 | -0.0012779 | 2.9558e-07 | 2.948e-08 | 0.0078259 | 0.007826 | 0.007826 | 0.97256 | -0.53007 | 0.9725 | -0.53128 | 2.15
45 | 0.0029584 | 0.00073724 | -0.0029566 | -0.00073893 | 1.7374e-06 | -1.693e-06 | 0.0045251 | 0.0045261 | 0.0045261 | 0.9725 | -0.53128 | 0.97187 | -0.54366 | 1.2434
46 | 0.0029566 | 0.00073893 | -0.0029561 | -0.00073945 | 5.2953e-07 | -5.1505e-07 | 0.0045261 | 0.0045264 | 0.0045264 | 0.97187 | -0.54366 | 0.97168 | -0.54742 | 1.2435
47 | -0.032867 | -0.008336 | 0.033002 | 0.0084208 | 0.00013547 | 8.4813e-05 | 0.049572 | 0.049571 | 0.049572 | 0.98727 | -0.2428 | 0.99171 | -0.15745 | 13.6187
48 | 0.00064176 | 0.00016083 | -0.00064176 | -0.00016084 | 2.4749e-10 | -8.6901e-09 | 0.00097199 | 0.000972 | 0.000972 | 0.98247 | -0.336 | 0.98246 | -0.33601 | 0.26703
49 | -0.060349 | -0.01538 | 0.060614 | 0.015549 | 0.0002656 | 0.00016885 | 0.090322 | 0.090322 | 0.090322 | 0.99521 | -0.090765 | 1 | 0 | 24.8138
50 | 0.0029561 | 0.00073945 | -0.0029558 | -0.00073973 | 2.8899e-07 | -2.809e-07 | 0.0045264 | 0.0045266 | 0.0045266 | 0.97168 | -0.54742 | 0.97158 | -0.54948 | 1.2436
51 | -0.0013809 | -0.00034574 | 0.0013809 | 0.00034549 | 3.7172e-08 | -2.5063e-07 | 0.0021149 | 0.0021148 | 0.0021149 | 0.9715 | -0.55105 | 0.97153 | -0.55048 | 0.58103
52 | 0.0013809 | 0.00034574 | -0.0013808 | -0.00034607 | 4.872e-08 | -3.2843e-07 | 0.0021149 | 0.0021151 | 0.0021151 | 0.9715 | -0.55105 | 0.97146 | -0.55179 | 0.58106
53 | -0.0013809 | -0.00034549 | 0.001381 | 0.00034504 | 6.606e-08 | -4.4551e-07 | 0.0021148 | 0.0021147 | 0.0021148 | 0.97153 | -0.55048 | 0.97158 | -0.54948 | 0.581

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.063103 | 0.015759

## res_load
| p_mw | q_mvar
0 | 0.0027413 | 0.00068704
1 | 0.00055195 | 0.00013833
2 | 0.0006164 | 0.00015449
3 | 0.00023511 | 5.8925e-05
4 | 0.00084174 | 0.00021096
5 | 0.0002573 | 6.4486e-05
6 | 0.0013674 | 0.00034269
7 | 0.00043887 | 0.00010999
8 | 0.0057145 | 0.0014322
9 | 0.00095538 | 0.00023944
10 | 0.0026251 | 0.0006579
11 | 0.0018434 | 0.000462
12 | 0.0018766 | 0.00047033
13 | 0.0013677 | 0.00034277
14 | 0.00080582 | 0.00020196
15 | 0.00042533 | 0.0001066
16 | 0.0001747 | 4.3783e-05
17 | 0.00032993 | 8.2688e-05
18 | 0.00059819 | 0.00014992
19 | 0.00044137 | 0.00011062
20 | 0.0006397 | 0.00016032
21 | 0.00017274 | 4.3292e-05
22 | 0.00050796 | 0.00012731
23 | 0.00021641 | 5.4236e-05
24 | 0.00039992 | 0.00010023
25 | 0.00096068 | 0.00024077
26 | 0.0016363 | 0.0004101
27 | 0.00083947 | 0.00021039
28 | 0.0033901 | 0.00084963
29 | 0.00053783 | 0.00013479
30 | 0.0015434 | 0.0003868
31 | 0.0040285 | 0.0010096
32 | 0.0086509 | 0.0021681
33 | 0.0013518 | 0.00033879
34 | 0.0021573 | 0.00054068
35 | 0.0032583 | 0.00081661
36 | 0.00064176 | 0.00016084
37 | 0.0014632 | 0.00036672
38 | 0.00083885 | 0.00021024
39 | 0.0013808 | 0.00034607
40 | 0.0015748 | 0.00039469

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1