## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1371-3_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1371-3_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1371-3_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1371-3_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1371-3_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1371-3_0_5_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_1371-3_0_5_node_68 | 0.4 | n |  | TRUE
7 | bus_LV_1371-3_0_5_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1371-3_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1371-3_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1371-3_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1371-3_0_5_node_51 | 0.4 | n |  | TRUE
12 | bus_LV_1371-3_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1371-3_0_5_node_38 | 0.4 | n |  | TRUE
14 | bus_LV_1371-3_0_5_node_39 | 0.4 | n |  | TRUE
15 | bus_LV_1371-3_0_5_node_52 | 0.4 | n |  | TRUE
16 | bus_LV_1371-3_0_5_node_111 | 0.4 | n |  | TRUE
17 | bus_LV_1371-3_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1371-3_0_5_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1371-3_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1371-3_0_5_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1371-3_0_5_node_66 | 0.4 | n |  | TRUE
22 | bus_LV_1371-3_0_5_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1371-3_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1371-3_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1371-3_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1371-3_0_5_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1371-3_0_5_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1371-3_0_5_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_1371-3_0_5_node_56 | 0.4 | n |  | TRUE
30 | bus_LV_1371-3_0_5_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1371-3_0_5_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1371-3_0_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_1371-3_0_5_node_43 | 0.4 | n |  | TRUE
34 | bus_LV_1371-3_0_5_node_57 | 0.4 | n |  | TRUE
35 | bus_LV_1371-3_0_5_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_1371-3_0_5_node_55 | 0.4 | n |  | TRUE
37 | bus_LV_1371-3_0_5_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1371-3_0_5_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1371-3_0_5_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_1371-3_0_5_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_1371-3_0_5_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_1371-3_0_5_node_46 | 0.4 | n |  | TRUE
43 | bus_LV_1371-3_0_5_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_1371-3_0_5_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_1371-3_0_5_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_1371-3_0_5_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_1371-3_0_5_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_1371-3_0_5_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_1371-3_0_5_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_1371-3_0_5_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_1371-3_0_5_node_76 | 0.4 | n |  | TRUE
52 | bus_LV_1371-3_0_5_node_65 | 0.4 | n |  | TRUE
53 | bus_LV_1371-3_0_5_node_91 | 0.4 | n |  | TRUE
54 | bus_LV_1371-3_0_5_node_75 | 0.4 | n |  | TRUE
55 | bus_LV_1371-3_0_5_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_1371-3_0_5_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_1371-3_0_5_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_1371-3_0_5_node_112 | 0.4 | n |  | TRUE
59 | bus_LV_1371-3_0_5_node_113 | 0.4 | n |  | TRUE
60 | bus_LV_1371-3_0_5_node_63 | 0.4 | n |  | TRUE
61 | bus_LV_1371-3_0_5_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_1371-3_0_5_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_1371-3_0_5_node_44 | 0.4 | n |  | TRUE
64 | bus_LV_1371-3_0_5_node_67 | 0.4 | n |  | TRUE
65 | bus_LV_1371-3_0_5_node_82 | 0.4 | n |  | TRUE
66 | bus_LV_1371-3_0_5_node_89 | 0.4 | n |  | TRUE
67 | bus_LV_1371-3_0_5_node_81 | 0.4 | n |  | TRUE
68 | bus_LV_1371-3_0_5_node_77 | 0.4 | n |  | TRUE
69 | bus_LV_1371-3_0_5_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_1371-3_0_5_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_1371-3_0_5_node_47 | 0.4 | n |  | TRUE
72 | bus_LV_1371-3_0_5_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_1371-3_0_5_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_1371-3_0_5_node_58 | 0.4 | n |  | TRUE
75 | bus_LV_1371-3_0_5_node_87 | 0.4 | n |  | TRUE
76 | bus_LV_1371-3_0_5_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_1371-3_0_5_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_1371-3_0_5_node_60 | 0.4 | n |  | TRUE
79 | bus_LV_1371-3_0_5_node_61 | 0.4 | n |  | TRUE
80 | bus_LV_1371-3_0_5_node_80 | 0.4 | n |  | TRUE
81 | bus_LV_1371-3_0_5_node_95 | 0.4 | n |  | TRUE
82 | bus_LV_1371-3_0_5_node_93 | 0.4 | n |  | TRUE
83 | bus_LV_1371-3_0_5_node_85 | 0.4 | n |  | TRUE
84 | bus_LV_1371-3_0_5_node_90 | 0.4 | n |  | TRUE
85 | bus_LV_1371-3_0_5_node_69 | 0.4 | n |  | TRUE
86 | bus_LV_1371-3_0_5_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_1371-3_0_5_node_71 | 0.4 | n |  | TRUE
88 | bus_LV_1371-3_0_5_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_1371-3_0_5_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_1371-3_0_5_node_73 | 0.4 | n |  | TRUE
91 | bus_LV_1371-3_0_5_node_88 | 0.4 | n |  | TRUE
92 | bus_LV_1371-3_0_5_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_1371-3_0_5_node_79 | 0.4 | n |  | TRUE
94 | bus_LV_1371-3_0_5_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_1371-3_0_5_node_94 | 0.4 | n |  | TRUE
96 | bus_LV_1371-3_0_5_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_1371-3_0_5_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_1371-3_0_5_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_1371-3_0_5_node_110 | 0.4 | n |  | TRUE
100 | bus_LV_1371-3_0_5_node_107 | 0.4 | n |  | TRUE
101 | bus_LV_1371-3_0_5_node_96 | 0.4 | n |  | TRUE
102 | bus_LV_1371-3_0_5_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_1371-3_0_5_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_1371-3_0_5_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_1371-3_0_5_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_1371-3_0_5_node_101 | 0.4 | n |  | TRUE
107 | bus_LV_1371-3_0_5_node_102 | 0.4 | n |  | TRUE
108 | bus_LV_1371-3_0_5_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_1371-3_0_5_node_114 | 0.4 | n |  | TRUE
110 | bus_LV_1371-3_0_5_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_1371-3_0_5_node_104 | 0.4 | n |  | TRUE
112 | bus_LV_1371-3_0_5_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_1371-3_0_5_node_108 | 0.4 | n |  | TRUE
114 | bus_LV_1371-3_0_5_node_109 | 0.4 | n |  | TRUE
115 | bus_MV_22_0_node_218 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1371-3_0_5_load_0 | 0 | 0.0014489 | 0.00036313 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1371-3_0_5_load_1 | 1 | 0.00075421 | 0.00018902 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1371-3_0_5_load_2 | 2 | 0.0019532 | 0.00048953 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1371-3_0_5_load_3 | 3 | 0.0047355 | 0.0011868 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1371-3_0_5_load_4 | 4 | 0.0036897 | 0.00092472 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1371-3_0_5_load_68 | 6 | 0.0031217 | 0.00078238 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1371-3_0_5_load_10 | 7 | 0.0062355 | 0.0015628 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1371-3_0_5_load_5 | 8 | 0.00067437 | 0.00016901 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1371-3_0_5_load_6 | 9 | 0.0025076 | 0.00062847 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1371-3_0_5_load_7 | 10 | 0.0016155 | 0.00040489 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1371-3_0_5_load_8 | 12 | 0.0005597 | 0.00014027 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1371-3_0_5_load_38 | 13 | 0.0026854 | 0.00067303 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1371-3_0_5_load_39 | 14 | 0.0017052 | 0.00042735 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1371-3_0_5_load_52 | 15 | 0.00086219 | 0.00021608 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1371-3_0_5_load_9 | 17 | 0.0036469 | 0.00091401 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1371-3_0_5_load_11 | 18 | 0.0060874 | 0.0015256 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1371-3_0_5_load_13 | 19 | 0.0050339 | 0.0012616 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1371-3_0_5_load_20 | 20 | 0.005804 | 0.0014546 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1371-3_0_5_load_19 | 22 | 0.0077889 | 0.0019521 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1371-3_0_5_load_14 | 23 | 0.0021572 | 0.00054065 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1371-3_0_5_load_15 | 24 | 0.0059457 | 0.0014901 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1371-3_0_5_load_16 | 25 | 0.0039527 | 0.00099064 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1371-3_0_5_load_17 | 26 | 0.0035359 | 0.00088618 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1371-3_0_5_load_18 | 27 | 0.0032412 | 0.00081232 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1371-3_0_5_load_45 | 28 | 0.013105 | 0.0032845 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1371-3_0_5_load_56 | 29 | 0.0065925 | 0.0016522 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1371-3_0_5_load_22 | 31 | 0.0010326 | 0.0002588 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1371-3_0_5_load_23 | 32 | 0.0038896 | 0.00097483 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1371-3_0_5_load_43 | 33 | 0.009371 | 0.0023486 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1371-3_0_5_load_57 | 34 | 0.0036902 | 0.00092485 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1371-3_0_5_load_41 | 35 | 0.00080284 | 0.00020121 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1371-3_0_5_load_55 | 36 | 0.0043898 | 0.0011002 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1371-3_0_5_load_24 | 37 | 0.0024726 | 0.0006197 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1371-3_0_5_load_25 | 38 | 0.0018398 | 0.00046109 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1371-3_0_5_load_26 | 39 | 0.0042813 | 0.001073 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1371-3_0_5_load_27 | 40 | 0.0023978 | 0.00060095 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1371-3_0_5_load_28 | 41 | 0.0022771 | 0.0005707 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1371-3_0_5_load_46 | 42 | 0.0046195 | 0.0011577 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1371-3_0_5_load_34 | 43 | 0.0029656 | 0.00074325 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1371-3_0_5_load_29 | 46 | 0.0014882 | 0.00037299 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1371-3_0_5_load_30 | 47 | 0.0016857 | 0.00042248 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1371-3_0_5_load_33 | 50 | 0.004004 | 0.0010035 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1371-3_0_5_load_65 | 52 | 0.0075137 | 0.0018831 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1371-3_0_5_load_91 | 53 | 0.0024403 | 0.0006116 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1371-3_0_5_load_75 | 54 | 0.0030662 | 0.00076845 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1371-3_0_5_load_36 | 55 | 0.0050511 | 0.0012659 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1371-3_0_5_load_37 | 56 | 0.0022302 | 0.00055894 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1371-3_0_5_load_53 | 57 | 0.0016085 | 0.00040314 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1371-3_0_5_load_112 | 58 | 0.0013962 | 0.00034993 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1371-3_0_5_load_63 | 60 | 0.0021123 | 0.00052939 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1371-3_0_5_load_40 | 61 | 0.0076545 | 0.0019184 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1371-3_0_5_load_42 | 62 | 0.0075867 | 0.0019014 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1371-3_0_5_load_44 | 63 | 0.0022189 | 0.0005561 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1371-3_0_5_load_67 | 64 | 0.0028629 | 0.0007175 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1371-3_0_5_load_82 | 65 | 0.0038656 | 0.00096882 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1371-3_0_5_load_89 | 66 | 0.004303 | 0.0010784 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1371-3_0_5_load_81 | 67 | 0.0020385 | 0.00051089 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1371-3_0_5_load_77 | 68 | 0.0042876 | 0.0010746 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1371-3_0_5_load_54 | 69 | 0.0040374 | 0.0010119 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1371-3_0_5_load_47 | 71 | 0.0023465 | 0.00058808 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1371-3_0_5_load_48 | 72 | 0.0053068 | 0.00133 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1371-3_0_5_load_62 | 73 | 0.001975 | 0.00049498 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1371-3_0_5_load_58 | 74 | 0.0036944 | 0.00092589 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1371-3_0_5_load_64 | 77 | 0.0022505 | 0.00056403 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1371-3_0_5_load_61 | 79 | 0.0016382 | 0.00041057 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1371-3_0_5_load_80 | 80 | 0.0095812 | 0.0024013 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1371-3_0_5_load_95 | 81 | 0.0019438 | 0.00048717 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1371-3_0_5_load_85 | 83 | 0.00079034 | 0.00019808 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1371-3_0_5_load_90 | 84 | 0.0033091 | 0.00082935 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1371-3_0_5_load_69 | 85 | 0.002606 | 0.00065313 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1371-3_0_5_load_70 | 86 | 0.0037788 | 0.00094705 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1371-3_0_5_load_71 | 87 | 0.003508 | 0.0008792 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1371-3_0_5_load_83 | 88 | 0.0027946 | 0.0007004 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1371-3_0_5_load_72 | 89 | 0.0034477 | 0.00086408 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1371-3_0_5_load_73 | 90 | 0.0032798 | 0.00082199 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1371-3_0_5_load_92 | 92 | 0.0041838 | 0.0010486 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1371-3_0_5_load_74 | 94 | 0.0039735 | 0.00099584 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1371-3_0_5_load_94 | 95 | 0.014136 | 0.0035429 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1371-3_0_5_load_78 | 96 | 0.0028034 | 0.0007026 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1371-3_0_5_load_84 | 97 | 0.0019453 | 0.00048755 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1371-3_0_5_load_86 | 98 | 0.0017466 | 0.00043773 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1371-3_0_5_load_110 | 99 | 0.00090207 | 0.00022608 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1371-3_0_5_load_107 | 100 | 0.00041672 | 0.00010444 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1371-3_0_5_load_96 | 101 | 0.00090652 | 0.00022719 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1371-3_0_5_load_97 | 102 | 0.00027283 | 6.8377e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1371-3_0_5_load_98 | 103 | 0.001115 | 0.00027944 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1371-3_0_5_load_99 | 104 | 0.00099051 | 0.00024824 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1371-3_0_5_load_100 | 105 | 0.00079057 | 0.00019814 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1371-3_0_5_load_101 | 106 | 0.0012135 | 0.00030412 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1371-3_0_5_load_106 | 108 | 0.0010376 | 0.00026005 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1371-3_0_5_load_114 | 109 | 0.00099898 | 0.00025037 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1371-3_0_5_load_103 | 110 | 0.00095722 | 0.0002399 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1371-3_0_5_load_104 | 111 | 0.0012026 | 0.00030139 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1371-3_0_5_load_105 | 112 | 0.0023452 | 0.00058777 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1371-3_0_5_line_0 |  | 0 | 1 | 0.028792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1371-3_0_5_line_1 |  | 0 | 2 | 0.074034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1371-3_0_5_line_2 |  | 1 | 3 | 0.042856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1371-3_0_5_line_3 |  | 2 | 4 | 0.012293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1371-3_0_5_line_4 |  | 4 | 5 | 0.050712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1371-3_0_5_line_5 |  | 5 | 6 | 0.017469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1371-3_0_5_line_6 |  | 5 | 7 | 0.020069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1371-3_0_5_line_7 |  | 6 | 21 | 0.018755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1371-3_0_5_line_8 |  | 7 | 17 | 0.017186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1371-3_0_5_line_9 |  | 8 | 9 | 0.0096531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1371-3_0_5_line_10 |  | 8 | 10 | 0.042074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1371-3_0_5_line_11 |  | 9 | 11 | 0.17396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1371-3_0_5_line_12 |  | 10 | 12 | 0.0027971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1371-3_0_5_line_13 |  | 11 | 15 | 0.1286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1371-3_0_5_line_14 |  | 12 | 13 | 0.12519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1371-3_0_5_line_15 |  | 13 | 14 | 0.085381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1371-3_0_5_line_16 |  | 14 | 57 | 0.029979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1371-3_0_5_line_17 |  | 15 | 16 | 0.13621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1371-3_0_5_line_18 |  | 16 | 58 | 0.067209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1371-3_0_5_line_19 |  | 17 | 18 | 0.027416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1371-3_0_5_line_20 |  | 18 | 19 | 0.0023028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1371-3_0_5_line_21 |  | 19 | 20 | 0.033544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1371-3_0_5_line_22 |  | 20 | 22 | 0.00051888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1371-3_0_5_line_23 |  | 21 | 52 | 0.023362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1371-3_0_5_line_24 |  | 21 | 49 | 0.017432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1371-3_0_5_line_25 |  | 22 | 30 | 0.024658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_1371-3_0_5_line_26 |  | 23 | 24 | 0.0029755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1371-3_0_5_line_27 |  | 23 | 25 | 0.013083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1371-3_0_5_line_28 |  | 24 | 26 | 0.0069241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1371-3_0_5_line_29 |  | 25 | 27 | 0.0089243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1371-3_0_5_line_30 |  | 27 | 28 | 0.014924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1371-3_0_5_line_31 |  | 28 | 29 | 0.0046288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1371-3_0_5_line_32 |  | 29 | 69 | 0.0022309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1371-3_0_5_line_33 |  | 30 | 31 | 0.0045075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_1371-3_0_5_line_34 |  | 30 | 32 | 0.027509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1371-3_0_5_line_35 |  | 31 | 33 | 0.01452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1371-3_0_5_line_36 |  | 32 | 34 | 0.025603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1371-3_0_5_line_37 |  | 33 | 35 | 0.016317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1371-3_0_5_line_38 |  | 34 | 36 | 0.005956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1371-3_0_5_line_39 |  | 35 | 61 | 0.013964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_1371-3_0_5_line_40 |  | 36 | 69 | 0.025091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1371-3_0_5_line_41 |  | 37 | 38 | 0.027899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1371-3_0_5_line_42 |  | 37 | 39 | 0.017614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1371-3_0_5_line_43 |  | 38 | 40 | 0.0098134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1371-3_0_5_line_44 |  | 39 | 41 | 0.020186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1371-3_0_5_line_45 |  | 40 | 42 | 0.02195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1371-3_0_5_line_46 |  | 41 | 43 | 0.021084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1371-3_0_5_line_47 |  | 42 | 44 | 0.014927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1371-3_0_5_line_48 |  | 43 | 45 | 0.010173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1371-3_0_5_line_49 |  | 44 | 70 | 0.018127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1371-3_0_5_line_50 |  | 44 | 71 | 0.036315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1371-3_0_5_line_51 |  | 45 | 55 | 0.00346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1371-3_0_5_line_52 |  | 45 | 56 | 0.011425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1371-3_0_5_line_53 |  | 46 | 47 | 0.032606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1371-3_0_5_line_54 |  | 46 | 48 | 0.010939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1371-3_0_5_line_55 |  | 47 | 49 | 0.056385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1371-3_0_5_line_56 |  | 48 | 50 | 0.025754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1371-3_0_5_line_57 |  | 49 | 51 | 0.017245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1371-3_0_5_line_58 |  | 51 | 53 | 0.01288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1371-3_0_5_line_59 |  | 51 | 54 | 0.044662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1371-3_0_5_line_60 |  | 52 | 56 | 0.020177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_1371-3_0_5_line_61 |  | 53 | 95 | 0.075281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1371-3_0_5_line_62 |  | 54 | 94 | 0.0035656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1371-3_0_5_line_63 |  | 57 | 60 | 0.040749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1371-3_0_5_line_64 |  | 58 | 59 | 0.12949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1371-3_0_5_line_65 |  | 59 | 93 | 0.31298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1371-3_0_5_line_66 |  | 60 | 77 | 0.023329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1371-3_0_5_line_67 |  | 61 | 62 | 0.035408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_1371-3_0_5_line_68 |  | 62 | 63 | 0.08142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_1371-3_0_5_line_69 |  | 63 | 64 | 0.022007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_1371-3_0_5_line_70 |  | 63 | 65 | 0.11976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1371-3_0_5_line_71 |  | 64 | 66 | 0.0074375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_1371-3_0_5_line_72 |  | 65 | 67 | 0.017055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1371-3_0_5_line_73 |  | 66 | 84 | 0.01469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_1371-3_0_5_line_74 |  | 67 | 68 | 0.15038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1371-3_0_5_line_75 |  | 70 | 73 | 0.11791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1371-3_0_5_line_76 |  | 70 | 74 | 0.064274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1371-3_0_5_line_77 |  | 71 | 72 | 0.0046553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1371-3_0_5_line_78 |  | 73 | 75 | 0.03785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1371-3_0_5_line_79 |  | 74 | 76 | 0.13471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1371-3_0_5_line_80 |  | 75 | 82 | 0.006397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1371-3_0_5_line_81 |  | 75 | 83 | 0.019277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1371-3_0_5_line_82 |  | 76 | 78 | 0.003971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1371-3_0_5_line_83 |  | 76 | 79 | 0.14358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1371-3_0_5_line_84 |  | 78 | 80 | 0.048897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1371-3_0_5_line_85 |  | 79 | 81 | 0.04665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1371-3_0_5_line_86 |  | 82 | 99 | 0.07952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1371-3_0_5_line_87 |  | 83 | 97 | 0.079004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1371-3_0_5_line_88 |  | 84 | 90 | 0.018704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_1371-3_0_5_line_89 |  | 85 | 86 | 0.012008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1371-3_0_5_line_90 |  | 85 | 87 | 0.032201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1371-3_0_5_line_91 |  | 85 | 88 | 0.051058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1371-3_0_5_line_92 |  | 86 | 89 | 0.015949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1371-3_0_5_line_93 |  | 87 | 90 | 0.0071339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_1371-3_0_5_line_94 |  | 89 | 91 | 0.032942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1371-3_0_5_line_95 |  | 91 | 92 | 0.041524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1371-3_0_5_line_96 |  | 91 | 93 | 0.11055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1371-3_0_5_line_97 |  | 93 | 96 | 0.048826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1371-3_0_5_line_98 |  | 97 | 98 | 0.013238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1371-3_0_5_line_99 |  | 99 | 100 | 0.13016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1371-3_0_5_line_100 |  | 100 | 113 | 0.038309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1371-3_0_5_line_101 |  | 101 | 102 | 0.072874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1371-3_0_5_line_102 |  | 102 | 103 | 0.023706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1371-3_0_5_line_103 |  | 103 | 104 | 0.13027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1371-3_0_5_line_104 |  | 104 | 105 | 0.021785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1371-3_0_5_line_105 |  | 105 | 106 | 0.022221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1371-3_0_5_line_106 |  | 106 | 107 | 0.11042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1371-3_0_5_line_107 |  | 106 | 108 | 0.12557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1371-3_0_5_line_108 |  | 107 | 109 | 0.11086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1371-3_0_5_line_109 |  | 108 | 111 | 0.051304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1371-3_0_5_line_110 |  | 109 | 114 | 0.055792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1371-3_0_5_line_111 |  | 110 | 111 | 0.0051925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1371-3_0_5_line_112 |  | 110 | 112 | 0.038772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1371-3_0_5_line_113 |  | 113 | 114 | 0.0077679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1371-3_0_5_trafo_21 | 0.63 MVA 20/0.4 kV | 115 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2690190.6588 | 1215275.2186 | 2690164.1159 | 1215269.5391 | 2690162.809 | 1215270.5442
1 | 2690190.6588 | 1215275.2186 | 2690239.3271 | 1215285.6323 | 2690254.3442 | 1215289.5066 | 2690256.3933 | 1215291.1054 | 2690257.4434 | 1215297.1714
2 | 2690162.809 | 1215270.5442 | 2690143.9139 | 1215285.0775 | 2690133.7272 | 1215285.7128 | 2690125.0023 | 1215284.4807
3 | 2690260.0765 | 1215309.1734 | 2690258.0974 | 1215300.949 | 2690257.4434 | 1215297.1714
4 | 2690305.5325 | 1215331.6547 | 2690300.5724 | 1215329.2002 | 2690288.82 | 1215323.396 | 2690260.0765 | 1215309.1734 | 2690260.0765 | 1215309.1734
5 | 2690305.5325 | 1215331.6547 | 2690309.023 | 1215326.8488 | 2690318.912 | 1215320.9221
6 | 2690305.5325 | 1215331.6547 | 2690302.4222 | 1215335.9327 | 2690293.457 | 1215347.6827
7 | 2690336.4889 | 1215314.6233 | 2690328.3326 | 1215317.0902 | 2690321.9606 | 1215319.0951 | 2690318.912 | 1215320.9221
8 | 2690279.7108 | 1215357.9984 | 2690293.457 | 1215347.6827
9 | 2689778.8614 | 1214783.7053 | 2689769.4327 | 1214781.6356
10 | 2689778.8614 | 1214783.7053 | 2689778.9866 | 1214783.7328 | 2689797.7298 | 1214790.4417 | 2689815.9208 | 1214802.8818
11 | 2689769.4327 | 1214781.6356 | 2689604.6608 | 1214837.4245
12 | 2689818.2297 | 1214804.4607 | 2689815.9208 | 1214802.8818
13 | 2689604.6608 | 1214837.4245 | 2689594.6771 | 1214846.236 | 2689592.6978 | 1214852.5994 | 2689594.3493 | 1214860.9632 | 2689605.8739 | 1214888.0769 | 2689616.1229 | 1214910.6128 | 2689624.6735 | 1214928.3978 | 2689631.524 | 1214936.5062 | 2689639.5124 | 1214942.686 | 2689641.5947 | 1214946.6422 | 2689641.6725 | 1214947.6006
14 | 2689872.1869 | 1214917.427 | 2689818.2297 | 1214804.4607
15 | 2689872.1869 | 1214917.427 | 2689895.6425 | 1214918.8482 | 2689918.4393 | 1214918.1248 | 2689936.9685 | 1214912.8118 | 2689952.3107 | 1214900.2992
16 | 2689975.5428 | 1214881.3518 | 2689952.3107 | 1214900.2992
17 | 2689589.957 | 1215064.1787 | 2689617.5686 | 1215040.222 | 2689624.6569 | 1215031.5004 | 2689629.588 | 1215021.2787 | 2689630.8967 | 1215009.5127 | 2689629.5655 | 1214989.9573 | 2689629.8529 | 1214980.4441 | 2689632.4721 | 1214972.945 | 2689641.9351 | 1214958.3441 | 2689642.101 | 1214952.8763 | 2689641.6725 | 1214947.6006
18 | 2689589.957 | 1215064.1787 | 2689588.0577 | 1215070.2765 | 2689588.7802 | 1215079.3046 | 2689589.2092 | 1215084.6146 | 2689592.0111 | 1215094.2632 | 2689600.6628 | 1215102.7879 | 2689613.3914 | 1215112.4301 | 2689616.4198 | 1215118.6243 | 2689616.487 | 1215120.0042
19 | 2690255.1317 | 1215370.1209 | 2690279.2681 | 1215358.3306 | 2690279.7108 | 1215357.9984
20 | 2690255.1317 | 1215370.1209 | 2690253.0626 | 1215371.1316
21 | 2690253.0626 | 1215371.1316 | 2690228.8227 | 1215382.9725 | 2690222.9023 | 1215385.8132
22 | 2690222.9023 | 1215385.8132 | 2690222.4345 | 1215386.0376
23 | 2690336.4889 | 1215314.6233 | 2690340.7909 | 1215329.4318 | 2690343.4436 | 1215336.9163
24 | 2690337.1225 | 1215297.3767 | 2690335.713 | 1215303.6819 | 2690336.4889 | 1215314.6233
25 | 2690200.203 | 1215396.7043 | 2690222.4345 | 1215386.0376
26 | 2690313.3522 | 1215447.7979 | 2690316.1624 | 1215448.7757
27 | 2690300.9958 | 1215443.4983 | 2690313.3522 | 1215447.7979
28 | 2690322.7019 | 1215451.0512 | 2690316.1624 | 1215448.7757
29 | 2690300.9958 | 1215443.4983 | 2690292.5671 | 1215440.5654
30 | 2690292.5671 | 1215440.5654 | 2690278.4724 | 1215435.661
31 | 2690274.1007 | 1215434.1398 | 2690278.4724 | 1215435.661
32 | 2690271.9936 | 1215433.4066 | 2690274.1007 | 1215434.1398
33 | 2690200.203 | 1215396.7043 | 2690195.7586 | 1215397.4562
34 | 2690200.203 | 1215396.7043 | 2690208.012 | 1215411.1433 | 2690218.4894 | 1215414.7891
35 | 2690181.4416 | 1215399.8782 | 2690181.4416 | 1215399.8782 | 2690195.7586 | 1215397.4562
36 | 2690218.4894 | 1215414.7891 | 2690242.6708 | 1215423.2033
37 | 2690165.1939 | 1215398.3792 | 2690181.4416 | 1215399.8782
38 | 2690248.296 | 1215425.1607 | 2690242.6708 | 1215423.2033
39 | 2690151.2887 | 1215397.0964 | 2690165.1939 | 1215398.3792
40 | 2690271.9936 | 1215433.4066 | 2690248.296 | 1215425.1607
41 | 2690394.1369 | 1215455.0239 | 2690391.2241 | 1215446.8202 | 2690383.5095 | 1215429.2459
42 | 2690376.4297 | 1215413.1178 | 2690383.5095 | 1215429.2459
43 | 2690394.1369 | 1215455.0239 | 2690397.4203 | 1215464.2717
44 | 2690376.4297 | 1215413.1178 | 2690368.3159 | 1215394.6341
45 | 2690397.4203 | 1215464.2717 | 2690401.8215 | 1215476.6677 | 2690404.7169 | 1215484.9732
46 | 2690368.3159 | 1215394.6341 | 2690361.6105 | 1215379.3589 | 2690359.832 | 1215375.3327
47 | 2690409.6305 | 1215499.068 | 2690404.7169 | 1215484.9732
48 | 2690355.7217 | 1215366.0273 | 2690359.832 | 1215375.3327
49 | 2690409.5112 | 1215513.9429 | 2690413.1948 | 1215512.9203 | 2690409.6305 | 1215499.068
50 | 2690409.6305 | 1215499.068 | 2690442.1366 | 1215486.4747 | 2690443.535 | 1215486.0729
51 | 2690352.4827 | 1215367.2679 | 2690355.7217 | 1215366.0273
52 | 2690355.7217 | 1215366.0273 | 2690351.1082 | 1215355.5752
53 | 2690266.4449 | 1215245.92 | 2690291.3313 | 1215262.4261 | 2690293.9435 | 1215263.2653
54 | 2690257.3289 | 1215239.8738 | 2690266.4449 | 1215245.92
55 | 2690337.1225 | 1215297.3767 | 2690322.4715 | 1215282.8894 | 2690317.4088 | 1215276.6752 | 2690312.9724 | 1215271.2265 | 2690305.7143 | 1215267.0471 | 2690293.9435 | 1215263.2653
56 | 2690257.3289 | 1215239.8738 | 2690260.358 | 1215230.9358 | 2690246.3361 | 1215222.5925
57 | 2690343.8418 | 1215281.49 | 2690337.1225 | 1215297.3767
58 | 2690343.8418 | 1215281.49 | 2690355.8643 | 1215286.1107
59 | 2690343.8418 | 1215281.49 | 2690347.3438 | 1215274.4272 | 2690363.4855 | 1215241.3798
60 | 2690351.1082 | 1215355.5752 | 2690349.9064 | 1215352.8525 | 2690344.5272 | 1215339.9733 | 2690343.4436 | 1215336.9163
61 | 2690414.0438 | 1215275.8059 | 2690409.3471 | 1215271.4984 | 2690395.6501 | 1215266.7208 | 2690388.7541 | 1215273.2207 | 2690379.461 | 1215291.5478 | 2690365.0446 | 1215289.6391 | 2690355.8643 | 1215286.1107
62 | 2690365.0504 | 1215238.1759 | 2690363.4855 | 1215241.3798
63 | 2689975.5428 | 1214881.3518 | 2689989.2376 | 1214870.1827 | 2690004.2619 | 1214860.0805 | 2690009.1477 | 1214859.1547
64 | 2689582.3716 | 1215236.3031 | 2689584.7445 | 1215227.9999 | 2689585.0745 | 1215223.2238 | 2689581.7802 | 1215197.8461 | 2689583.1453 | 1215185.347 | 2689586.1638 | 1215179.0659 | 2689600.9755 | 1215167.3473 | 2689608.6089 | 1215159.2343 | 2689616.3317 | 1215141.6496 | 2689617.1278 | 1215133.1558 | 2689616.487 | 1215120.0042
65 | 2689815.1298 | 1215445.5351 | 2689582.3716 | 1215236.3031
66 | 2690032.2443 | 1214858.933 | 2690018.0109 | 1214857.4752 | 2690009.1477 | 1214859.1547
67 | 2690151.2887 | 1215397.0964 | 2690129.3994 | 1215395.0769 | 2690116.6221 | 1215399.1996
68 | 2690116.6221 | 1215399.1996 | 2690105.107 | 1215402.915 | 2690085.9486 | 1215410.753 | 2690060.9209 | 1215412.9764 | 2690038.6332 | 1215405.5441
69 | 2690017.7568 | 1215398.5824 | 2690038.6332 | 1215405.5441
70 | 2690038.6332 | 1215405.5441 | 2690012 | 1215522.3005
71 | 2690010.7013 | 1215396.2295 | 2690017.7568 | 1215398.5824
72 | 2690012 | 1215522.3005 | 2690019.9972 | 1215537.3648
73 | 2690010.7013 | 1215396.2295 | 2689996.7653 | 1215391.5822
74 | 2690019.9972 | 1215537.3648 | 2690060.7638 | 1215682.1118
75 | 2690409.5112 | 1215513.9429 | 2690440.3286 | 1215627.7507
76 | 2690409.5112 | 1215513.9429 | 2690362.7442 | 1215529.4444 | 2690347.8436 | 1215531.2071
77 | 2690443.535 | 1215486.0729 | 2690448.0093 | 1215484.7873
78 | 2690450.2215 | 1215664.2845 | 2690440.3286 | 1215627.7507
79 | 2690228.8533 | 1215590.0688 | 2690263.0951 | 1215565.615 | 2690316.5717 | 1215536.8053 | 2690326.1717 | 1215533.7709 | 2690347.8436 | 1215531.2071
80 | 2690455.84 | 1215667.3719 | 2690450.2215 | 1215664.2845
81 | 2690450.2215 | 1215664.2845 | 2690436.1645 | 1215663.2706 | 2690431.0101 | 1215662.7244
82 | 2690224.8721 | 1215590.1864 | 2690228.8533 | 1215590.0688
83 | 2690228.8533 | 1215590.0688 | 2690229.5816 | 1215600.1533 | 2690228.5774 | 1215613.3026 | 2690215.0565 | 1215645.5865 | 2690210.102 | 1215676.3768 | 2690213.423 | 1215726.3832 | 2690213.2301 | 1215730.3584
84 | 2690224.8721 | 1215590.1864 | 2690223.7332 | 1215587.6563 | 2690220.349 | 1215584.9588 | 2690198.3314 | 1215570.4937 | 2690184.8177 | 1215563.0041
85 | 2690202.0937 | 1215774.9446 | 2690212.2418 | 1215750.7262 | 2690213.2301 | 1215730.3584
86 | 2690455.84 | 1215667.3719 | 2690470.4184 | 1215678.0559 | 2690484.6458 | 1215694.8499 | 2690493.4449 | 1215703.0334 | 2690518.4279 | 1215714.6761
87 | 2690352.4936 | 1215653.9712 | 2690357.0804 | 1215654.5211 | 2690392.2031 | 1215658.6119 | 2690431.0101 | 1215662.7244
88 | 2689996.7653 | 1215391.5822 | 2689989.7451 | 1215389.2412 | 2689978.9804 | 1215385.7919
89 | 2689941.2226 | 1215374.9078 | 2689929.4817 | 1215372.387
90 | 2689941.2226 | 1215374.9078 | 2689952.7103 | 1215377.3743 | 2689972.1867 | 1215383.615
91 | 2689941.2226 | 1215374.9078 | 2689955.1977 | 1215325.7992
92 | 2689929.4817 | 1215372.387 | 2689923.3001 | 1215371.0597 | 2689920.5417 | 1215380.283
93 | 2689972.1867 | 1215383.615 | 2689978.9804 | 1215385.7919
94 | 2689908.2727 | 1215410.6488 | 2689909.5375 | 1215406.8541 | 2689915.9976 | 1215395.4772 | 2689920.5417 | 1215380.283
95 | 2689873.7576 | 1215394.3618 | 2689875.5287 | 1215396.779 | 2689878.5306 | 1215396.6464 | 2689882.3158 | 1215396.9481 | 2689883.9526 | 1215400.2083 | 2689888.4363 | 1215401.5324 | 2689889.7214 | 1215403.9423 | 2689893.3264 | 1215408.1328 | 2689903.0878 | 1215410.5038 | 2689908.2727 | 1215410.6488
96 | 2689908.2727 | 1215410.6488 | 2689906.1819 | 1215415.3315 | 2689890.6101 | 1215416.5197 | 2689891.5991 | 1215420.9376 | 2689884.9275 | 1215426.7076 | 2689875.671 | 1215431.6492 | 2689863.4711 | 1215440.9049 | 2689859.5044 | 1215443.0688 | 2689855.2966 | 1215443.0943 | 2689836.5152 | 1215439.5644 | 2689821.8958 | 1215440.5559 | 2689815.1298 | 1215445.5351
97 | 2689815.1298 | 1215445.5351 | 2689828.1034 | 1215470.592 | 2689840.1451 | 1215483.9046 | 2689841.6738 | 1215486.0806
98 | 2690339.3493 | 1215652.3954 | 2690352.4936 | 1215653.9712
99 | 2690518.4279 | 1215714.6761 | 2690511.1193 | 1215844.6264
100 | 2690523.9931 | 1215880.7066 | 2690518.7394 | 1215865.6166 | 2690511.1193 | 1215844.6264
101 | 2690329.6843 | 1216136.5227 | 2690373.3677 | 1216139.786 | 2690387.8952 | 1216121.7274 | 2690387.1975 | 1216115.8769
102 | 2690387.1975 | 1216115.8769 | 2690384.3902 | 1216092.3373
103 | 2690384.3902 | 1216092.3373 | 2690384.0216 | 1216089.2466 | 2690380.3554 | 1216082.631 | 2690370.7655 | 1216074.0464 | 2690358.8008 | 1216066.8268 | 2690343.9766 | 1216062.388 | 2690318.6426 | 1216057.9345 | 2690305.5111 | 1216055.545 | 2690299.4492 | 1216052.1731 | 2690296.0824 | 1216046.3404 | 2690295.5617 | 1216039.6057 | 2690297.572 | 1216030.7301 | 2690298.2897 | 1216024.9593 | 2690298.0319 | 1216022.1059
104 | 2690298.0319 | 1216022.1059 | 2690296.6769 | 1216007.1117 | 2690295.9856 | 1216000.4174
105 | 2690290.3095 | 1215979.0899 | 2690295.1737 | 1215992.5568 | 2690295.9856 | 1216000.4174
106 | 2690366.5183 | 1215924.0025 | 2690313.9577 | 1215947.1995 | 2690287.3603 | 1215954.9241 | 2690285.24 | 1215965.0544 | 2690290.3095 | 1215979.0899
107 | 2690290.3095 | 1215979.0899 | 2690177.2071 | 1215924.5476
108 | 2690366.5183 | 1215924.0025 | 2690462.114 | 1215867.8586
109 | 2690177.2071 | 1215924.5476 | 2690158.5332 | 1215925.9992 | 2690132.1085 | 1215931.8592 | 2690128.4581 | 1215935.982
110 | 2690462.114 | 1215867.8586 | 2690485.9479 | 1215875.6256 | 2690507.1949 | 1215880.7071 | 2690516.2258 | 1215880.6108
111 | 2690125.016 | 1215939.8697 | 2690128.4581 | 1215935.982
112 | 2690125.016 | 1215939.8697 | 2690122.5205 | 1215942.6882 | 2690117.667 | 1215953.789 | 2690110.4392 | 1215975.5099
113 | 2690516.2258 | 1215880.6108 | 2690519.8399 | 1215880.6546 | 2690523.9931 | 1215880.7066

## bus_geodata
| x | y | coords
0 | 2690190.6588 | 1215275.2186
1 | 2690162.809 | 1215270.5442
2 | 2690257.4434 | 1215297.1714
3 | 2690125.0023 | 1215284.4807
4 | 2690260.0765 | 1215309.1734
5 | 2690305.5325 | 1215331.6547
6 | 2690318.912 | 1215320.9221
7 | 2690293.457 | 1215347.6827
8 | 2689778.8614 | 1214783.7053
9 | 2689769.4327 | 1214781.6356
10 | 2689815.9208 | 1214802.8818
11 | 2689604.6608 | 1214837.4245
12 | 2689818.2297 | 1214804.4607
13 | 2689872.1869 | 1214917.427
14 | 2689952.3107 | 1214900.2992
15 | 2689641.6725 | 1214947.6006
16 | 2689589.957 | 1215064.1787
17 | 2690279.7108 | 1215357.9984
18 | 2690255.1317 | 1215370.1209
19 | 2690253.0626 | 1215371.1316
20 | 2690222.9023 | 1215385.8132
21 | 2690336.4889 | 1215314.6233
22 | 2690222.4344 | 1215386.0376
23 | 2690313.3522 | 1215447.7979
24 | 2690316.1624 | 1215448.7757
25 | 2690300.9958 | 1215443.4983
26 | 2690322.7019 | 1215451.0512
27 | 2690292.5671 | 1215440.5654
28 | 2690278.4724 | 1215435.661
29 | 2690274.1007 | 1215434.1398
30 | 2690200.203 | 1215396.7043
31 | 2690195.7586 | 1215397.4562
32 | 2690218.4894 | 1215414.7891
33 | 2690181.4416 | 1215399.8782
34 | 2690242.6708 | 1215423.2033
35 | 2690165.1939 | 1215398.3792
36 | 2690248.296 | 1215425.1607
37 | 2690383.5095 | 1215429.2459
38 | 2690394.1369 | 1215455.0239
39 | 2690376.4297 | 1215413.1178
40 | 2690397.4203 | 1215464.2717
41 | 2690368.3159 | 1215394.6341
42 | 2690404.7169 | 1215484.9732
43 | 2690359.832 | 1215375.3327
44 | 2690409.6305 | 1215499.068
45 | 2690355.7217 | 1215366.0273
46 | 2690266.4449 | 1215245.92
47 | 2690293.9435 | 1215263.2653
48 | 2690257.3289 | 1215239.8738
49 | 2690337.1225 | 1215297.3767
50 | 2690246.3361 | 1215222.5925
51 | 2690343.8418 | 1215281.49
52 | 2690343.4436 | 1215336.9163
53 | 2690355.8643 | 1215286.1107
54 | 2690363.4855 | 1215241.3798
55 | 2690352.4827 | 1215367.2679
56 | 2690351.1082 | 1215355.5752
57 | 2689975.5428 | 1214881.3518
58 | 2689616.487 | 1215120.0042
59 | 2689582.3716 | 1215236.3031
60 | 2690009.1477 | 1214859.1547
61 | 2690151.2887 | 1215397.0964
62 | 2690116.6221 | 1215399.1996
63 | 2690038.6332 | 1215405.5441
64 | 2690017.7568 | 1215398.5824
65 | 2690012 | 1215522.3005
66 | 2690010.7013 | 1215396.2295
67 | 2690019.9972 | 1215537.3648
68 | 2690060.7638 | 1215682.1118
69 | 2690271.9936 | 1215433.4066
70 | 2690409.5112 | 1215513.9429
71 | 2690443.535 | 1215486.0729
72 | 2690448.0093 | 1215484.7873
73 | 2690440.3286 | 1215627.7507
74 | 2690347.8436 | 1215531.2071
75 | 2690450.2215 | 1215664.2845
76 | 2690228.8533 | 1215590.0688
77 | 2690032.2443 | 1214858.933
78 | 2690224.8721 | 1215590.1864
79 | 2690213.2301 | 1215730.3584
80 | 2690184.8177 | 1215563.0041
81 | 2690202.0937 | 1215774.9446
82 | 2690455.84 | 1215667.3719
83 | 2690431.0101 | 1215662.7244
84 | 2689996.7653 | 1215391.5822
85 | 2689941.2226 | 1215374.9078
86 | 2689929.4817 | 1215372.387
87 | 2689972.1867 | 1215383.615
88 | 2689955.1977 | 1215325.7992
89 | 2689920.5417 | 1215380.283
90 | 2689978.9804 | 1215385.7919
91 | 2689908.2727 | 1215410.6488
92 | 2689873.7576 | 1215394.3618
93 | 2689815.1298 | 1215445.5351
94 | 2690365.0504 | 1215238.1759
95 | 2690414.0438 | 1215275.8059
96 | 2689841.6738 | 1215486.0806
97 | 2690352.4936 | 1215653.9712
98 | 2690339.3493 | 1215652.3954
99 | 2690518.4279 | 1215714.6761
100 | 2690511.1193 | 1215844.6264
101 | 2690329.6843 | 1216136.5227
102 | 2690387.1975 | 1216115.8769
103 | 2690384.3902 | 1216092.3373
104 | 2690298.0319 | 1216022.1059
105 | 2690295.9856 | 1216000.4174
106 | 2690290.3096 | 1215979.0899
107 | 2690366.5183 | 1215924.0025
108 | 2690177.2071 | 1215924.5475
109 | 2690462.114 | 1215867.8586
110 | 2690125.016 | 1215939.8697
111 | 2690128.4581 | 1215935.982
112 | 2690110.4392 | 1215975.5099
113 | 2690523.9931 | 1215880.7066
114 | 2690516.2258 | 1215880.6108
115 | 2690305.5325 | 1215331.6547

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99062 | -0.17939 | 0.0014489 | 0.00036313
1 | 0.99047 | -0.1822 | 0.00075421 | 0.00018902
2 | 0.99109 | -0.17027 | 0.0019532 | 0.00048953
3 | 0.99029 | -0.18581 | 0.0047355 | 0.0011868
4 | 0.99119 | -0.16833 | 0.0036897 | 0.00092472
5 | 0.99177 | -0.15701 | 0 | 0
6 | 0.99085 | -0.17463 | 0.0031217 | 0.00078238
7 | 0.99294 | -0.13457 | 0.0062355 | 0.0015628
8 | 0.97279 | -0.52557 | 0.00067437 | 0.00016901
9 | 0.97291 | -0.52321 | 0.0025076 | 0.00062847
10 | 0.9723 | -0.53529 | 0.0016155 | 0.00040489
11 | 0.97546 | -0.47295 | 0 | 0
12 | 0.97227 | -0.53586 | 0.0005597 | 0.00014027
13 | 0.97106 | -0.55982 | 0.0026854 | 0.00067303
14 | 0.97045 | -0.57195 | 0.0017052 | 0.00042735
15 | 0.97735 | -0.43595 | 0.00086219 | 0.00021608
16 | 0.97946 | -0.39477 | 0 | 0
17 | 0.99399 | -0.11445 | 0.0036469 | 0.00091401
18 | 0.99571 | -0.081561 | 0.0060874 | 0.0015256
19 | 0.99586 | -0.078681 | 0.0050339 | 0.0012616
20 | 0.99814 | -0.035345 | 0.005804 | 0.0014546
21 | 0.9899 | -0.19307 | 0 | 0
22 | 0.99817 | -0.03465 | 0.0077889 | 0.0019521
23 | 0.99549 | -0.08669 | 0.0021572 | 0.00054065
24 | 0.99547 | -0.087187 | 0.0059457 | 0.0014901
25 | 0.99563 | -0.084012 | 0.0039527 | 0.00099064
26 | 0.99544 | -0.087617 | 0.0035359 | 0.00088618
27 | 0.99576 | -0.081566 | 0.0032412 | 0.00081232
28 | 0.99601 | -0.076627 | 0.013105 | 0.0032845
29 | 0.99615 | -0.07403 | 0.0065925 | 0.0016522
30 | 1 | 0 | -0.31389 | -0.079405
31 | 0.99981 | -0.003685 | 0.0010326 | 0.0002588
32 | 0.99863 | -0.026187 | 0.0038896 | 0.00097483
33 | 0.99919 | -0.015435 | 0.009371 | 0.0023486
34 | 0.99745 | -0.048879 | 0.0036902 | 0.00092485
35 | 0.99857 | -0.027318 | 0.00080284 | 0.00020121
36 | 0.9972 | -0.05378 | 0.0043898 | 0.0011002
37 | 0.98377 | -0.31151 | 0.0024726 | 0.0006197
38 | 0.98239 | -0.33819 | 0.0018398 | 0.00046109
39 | 0.98467 | -0.29391 | 0.0042813 | 0.001073
40 | 0.98193 | -0.34727 | 0.0023978 | 0.00060095
41 | 0.98579 | -0.27224 | 0.0022771 | 0.0005707
42 | 0.98093 | -0.36665 | 0.0046195 | 0.0011577
43 | 0.987 | -0.2488 | 0.0029656 | 0.00074325
44 | 0.98032 | -0.3786 | 0 | 0
45 | 0.98762 | -0.23697 | 0 | 0
46 | 0.98887 | -0.21303 | 0.0014882 | 0.00037299
47 | 0.98903 | -0.20983 | 0.0016857 | 0.00042248
48 | 0.98883 | -0.21381 | 0 | 0
49 | 0.9894 | -0.20262 | 0 | 0
50 | 0.98873 | -0.21565 | 0.004004 | 0.0010035
51 | 0.98903 | -0.20988 | 0 | 0
52 | 0.98903 | -0.20967 | 0.0075137 | 0.0018831
53 | 0.98883 | -0.21368 | 0.0024403 | 0.0006116
54 | 0.98874 | -0.21548 | 0.0030662 | 0.00076845
55 | 0.9876 | -0.23729 | 0.0050511 | 0.0012659
56 | 0.98836 | -0.22268 | 0.0022302 | 0.00055894
57 | 0.97028 | -0.57527 | 0.0016085 | 0.00040314
58 | 0.9805 | -0.37451 | 0.0013962 | 0.00034993
59 | 0.98267 | -0.33233 | 0 | 0
60 | 0.97011 | -0.57856 | 0.0021123 | 0.00052939
61 | 0.99804 | -0.037402 | 0.0076545 | 0.0019184
62 | 0.99682 | -0.060642 | 0.0075867 | 0.0019014
63 | 0.9943 | -0.10885 | 0.0022189 | 0.0005561
64 | 0.99375 | -0.11951 | 0.0028629 | 0.0007175
65 | 0.99319 | -0.1304 | 0.0038656 | 0.00096882
66 | 0.99357 | -0.12292 | 0.004303 | 0.0010784
67 | 0.99309 | -0.13231 | 0.0020385 | 0.00051089
68 | 0.9925 | -0.14372 | 0.0042876 | 0.0010746
69 | 0.99623 | -0.07252 | 0.0040374 | 0.0010119
70 | 0.97971 | -0.39061 | 0 | 0
71 | 0.98006 | -0.38364 | 0.0023465 | 0.00058808
72 | 0.98004 | -0.38409 | 0.0053068 | 0.00133
73 | 0.97755 | -0.43277 | 0.001975 | 0.00049498
74 | 0.9787 | -0.41032 | 0.0036944 | 0.00092589
75 | 0.97693 | -0.44497 | 0 | 0
76 | 0.97706 | -0.44267 | 0 | 0
77 | 0.97006 | -0.57953 | 0.0022505 | 0.00056403
78 | 0.97702 | -0.44336 | 0 | 0
79 | 0.97658 | -0.45207 | 0.0016382 | 0.00041057
80 | 0.97659 | -0.45192 | 0.0095812 | 0.0024013
81 | 0.97649 | -0.45373 | 0.0019438 | 0.00048717
82 | 0.97685 | -0.44651 | 0 | 0
83 | 0.97685 | -0.44655 | 0.00079034 | 0.00019808
84 | 0.99324 | -0.12912 | 0.0033091 | 0.00082935
85 | 0.99161 | -0.16052 | 0.002606 | 0.00065313
86 | 0.99125 | -0.16738 | 0.0037788 | 0.00094705
87 | 0.99273 | -0.13906 | 0.003508 | 0.0008792
88 | 0.99148 | -0.16305 | 0.0027946 | 0.0007004
89 | 0.99083 | -0.17544 | 0.0034477 | 0.00086408
90 | 0.99286 | -0.13646 | 0.0032798 | 0.00082199
91 | 0.99007 | -0.19008 | 0 | 0
92 | 0.98991 | -0.19317 | 0.0041838 | 0.0010486
93 | 0.98793 | -0.23111 | 0 | 0
94 | 0.98873 | -0.21574 | 0.0039735 | 0.00099584
95 | 0.98786 | -0.23267 | 0.014136 | 0.0035429
96 | 0.9878 | -0.23355 | 0.0028034 | 0.0007026
97 | 0.97658 | -0.45188 | 0.0019453 | 0.00048755
98 | 0.97656 | -0.45231 | 0.0017466 | 0.00043773
99 | 0.97588 | -0.46568 | 0.00090207 | 0.00022608
100 | 0.97439 | -0.49496 | 0.00041672 | 0.00010444
101 | 0.97051 | -0.57172 | 0.00090652 | 0.00022719
102 | 0.97057 | -0.5705 | 0.00027283 | 6.8377e-05
103 | 0.97059 | -0.56998 | 0.001115 | 0.00027944
104 | 0.97087 | -0.56444 | 0.00099051 | 0.00024824
105 | 0.97094 | -0.56312 | 0.00079057 | 0.00019814
106 | 0.97102 | -0.56144 | 0.0012135 | 0.00030412
107 | 0.97214 | -0.53932 | 0 | 0
108 | 0.97037 | -0.57432 | 0.0010376 | 0.00026005
109 | 0.97326 | -0.51716 | 0.00099898 | 0.00025037
110 | 0.97014 | -0.57892 | 0.00095722 | 0.0002399
111 | 0.97016 | -0.5786 | 0.0012026 | 0.00030139
112 | 0.97006 | -0.58061 | 0.0023452 | 0.00058777
113 | 0.97396 | -0.5033 | 0 | 0
114 | 0.97388 | -0.50499 | 0 | 0
115 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0054912 | 0.0013759 | -0.0054905 | -0.0013758 | 7.3459e-07 | 9.9511e-08 | 0.0082483 | 0.0082484 | 0.0082484 | 0.99062 | -0.17939 | 0.99047 | -0.1822 | 2.2661
1 | -0.0069401 | -0.001739 | 0.0069432 | 0.00174 | 3.017e-06 | 9.7731e-07 | 0.010425 | 0.010424 | 0.010425 | 0.99062 | -0.17939 | 0.99109 | -0.17027 | 2.8639
2 | 0.0047363 | 0.0011868 | -0.0047355 | -0.0011868 | 8.1366e-07 | -3.0725e-08 | 0.0071154 | 0.0071156 | 0.0071156 | 0.99047 | -0.1822 | 0.99029 | -0.18581 | 1.9548
3 | -0.0088964 | -0.0022296 | 0.0088972 | 0.0022299 | 8.2244e-07 | 3.6793e-07 | 0.013357 | 0.013357 | 0.013357 | 0.99109 | -0.17027 | 0.99119 | -0.16833 | 3.6695
4 | -0.012587 | -0.0031546 | 0.012594 | 0.0031583 | 6.7901e-06 | 3.6917e-06 | 0.018896 | 0.018896 | 0.018896 | 0.99119 | -0.16833 | 0.99177 | -0.15701 | 5.1912
5 | 0.11465 | 0.029078 | -0.11455 | -0.029017 | 9.705e-05 | 6.1662e-05 | 0.17213 | 0.17213 | 0.17213 | 0.99177 | -0.15701 | 0.99085 | -0.17463 | 23.6448
6 | -0.12724 | -0.032237 | 0.12738 | 0.032324 | 0.00013732 | 8.7364e-05 | 0.19103 | 0.19103 | 0.19103 | 0.99177 | -0.15701 | 0.99294 | -0.13457 | 26.2403
7 | 0.11143 | 0.028234 | -0.11133 | -0.028172 | 9.86e-05 | 6.2621e-05 | 0.16745 | 0.16745 | 0.16745 | 0.99085 | -0.17463 | 0.9899 | -0.19307 | 23.0009
8 | -0.13361 | -0.033887 | 0.13374 | 0.033969 | 0.00012938 | 8.2358e-05 | 0.20037 | 0.20037 | 0.20037 | 0.99294 | -0.13457 | 0.99399 | -0.11445 | 27.5239
9 | -0.013236 | -0.0033222 | 0.013237 | 0.0033231 | 1.484e-06 | 8.2992e-07 | 0.020248 | 0.020248 | 0.020248 | 0.97279 | -0.52557 | 0.97291 | -0.52321 | 5.5625
10 | 0.012561 | 0.0031532 | -0.012555 | -0.00315 | 5.826e-06 | 3.2066e-06 | 0.019216 | 0.019216 | 0.019216 | 0.97279 | -0.52557 | 0.9723 | -0.53529 | 5.2792
11 | -0.015745 | -0.0039515 | 0.015783 | 0.0039736 | 3.7834e-05 | 2.2048e-05 | 0.024083 | 0.024082 | 0.024083 | 0.97291 | -0.52321 | 0.97546 | -0.47295 | 6.6161
12 | 0.01094 | 0.0027451 | -0.01094 | -0.002745 | 2.9406e-07 | 1.5351e-07 | 0.016744 | 0.016744 | 0.016744 | 0.9723 | -0.53529 | 0.97227 | -0.53586 | 4.5999
13 | -0.015783 | -0.0039736 | 0.015811 | 0.0039899 | 2.7968e-05 | 1.6291e-05 | 0.024082 | 0.024081 | 0.024082 | 0.97546 | -0.47295 | 0.97735 | -0.43595 | 6.6159
14 | 0.01038 | 0.0026047 | -0.010368 | -0.0025987 | 1.185e-05 | 6.0333e-06 | 0.015887 | 0.015888 | 0.015888 | 0.97227 | -0.53586 | 0.97106 | -0.55982 | 4.3648
15 | 0.0076827 | 0.0019256 | -0.0076783 | -0.0019239 | 4.4377e-06 | 1.7846e-06 | 0.011773 | 0.011773 | 0.011773 | 0.97106 | -0.55982 | 0.97045 | -0.57195 | 3.2344
16 | 0.0059731 | 0.0014965 | -0.0059721 | -0.0014963 | 9.4299e-07 | 2.3318e-07 | 0.0091585 | 0.0091587 | 0.0091587 | 0.97045 | -0.57195 | 0.97028 | -0.57527 | 2.5161
17 | -0.016673 | -0.004206 | 0.016706 | 0.0042253 | 3.2937e-05 | 1.9369e-05 | 0.025394 | 0.025393 | 0.025394 | 0.97735 | -0.43595 | 0.97946 | -0.39477 | 6.9764
18 | -0.016706 | -0.0042253 | 0.016722 | 0.0042349 | 1.6252e-05 | 9.5543e-06 | 0.025393 | 0.025393 | 0.025393 | 0.97946 | -0.39477 | 0.9805 | -0.37451 | 6.9762
19 | -0.13739 | -0.034883 | 0.13761 | 0.035022 | 0.00021779 | 0.00013867 | 0.20583 | 0.20583 | 0.20583 | 0.99399 | -0.11445 | 0.99571 | -0.081561 | 28.2738
20 | -0.14369 | -0.036547 | 0.14371 | 0.03656 | 1.9945e-05 | 1.2705e-05 | 0.21493 | 0.21493 | 0.21493 | 0.99571 | -0.081561 | 0.99586 | -0.078681 | 29.5234
21 | -0.14875 | -0.037822 | 0.14906 | 0.03802 | 0.00031123 | 0.00019832 | 0.22245 | 0.22245 | 0.22245 | 0.99586 | -0.078681 | 0.99814 | -0.035345 | 30.5566
22 | -0.15486 | -0.039475 | 0.15487 | 0.039478 | 5.1962e-06 | 3.312e-06 | 0.2311 | 0.2311 | 0.2311 | 0.99814 | -0.035345 | 0.99817 | -0.03465 | 31.745
23 | 0.080491 | 0.02043 | -0.080427 | -0.020389 | 6.4223e-05 | 4.0503e-05 | 0.12109 | 0.12109 | 0.12109 | 0.9899 | -0.19307 | 0.98903 | -0.20967 | 16.6327
24 | 0.030838 | 0.0077419 | -0.030824 | -0.0077332 | 1.405e-05 | 8.7679e-06 | 0.04636 | 0.04636 | 0.04636 | 0.9899 | -0.19307 | 0.9894 | -0.20262 | 12.7364
25 | -0.16266 | -0.04143 | 0.16293 | 0.041604 | 0.00027237 | 0.00017367 | 0.24272 | 0.24271 | 0.24272 | 0.99817 | -0.03465 | 1 | 0 | 33.34
26 | 0.0094819 | 0.0023764 | -0.0094817 | -0.0023763 | 2.2414e-07 | 1.0476e-07 | 0.014173 | 0.014173 | 0.014173 | 0.99549 | -0.08669 | 0.99547 | -0.087187 | 3.8937
27 | -0.011639 | -0.002917 | 0.011641 | 0.0029178 | 1.485e-06 | 7.8027e-07 | 0.017398 | 0.017398 | 0.017398 | 0.99549 | -0.08669 | 0.99563 | -0.084012 | 4.7796
28 | 0.003536 | 0.00088614 | -0.0035359 | -0.00088618 | 7.254e-08 | -4.359e-08 | 0.0052855 | 0.0052856 | 0.0052856 | 0.99547 | -0.087187 | 0.99544 | -0.087617 | 1.4521
29 | -0.015593 | -0.0039084 | 0.015595 | 0.0039095 | 1.8176e-06 | 1.0472e-06 | 0.023305 | 0.023305 | 0.023305 | 0.99563 | -0.084012 | 0.99576 | -0.081566 | 6.4025
30 | -0.018836 | -0.0047218 | 0.018841 | 0.0047245 | 4.4342e-06 | 2.6437e-06 | 0.028149 | 0.028148 | 0.028149 | 0.99576 | -0.081566 | 0.99601 | -0.076627 | 7.7331
31 | -0.031946 | -0.008009 | 0.03195 | 0.0080114 | 3.954e-06 | 2.4703e-06 | 0.047727 | 0.047727 | 0.047727 | 0.99601 | -0.076627 | 0.99615 | -0.07403 | 13.1119
32 | -0.038543 | -0.0096637 | 0.038545 | 0.0096654 | 2.7733e-06 | 1.7458e-06 | 0.057575 | 0.057575 | 0.057575 | 0.99615 | -0.07403 | 0.99623 | -0.07252 | 15.8173
33 | 0.094586 | 0.024015 | -0.09457 | -0.024004 | 1.6768e-05 | 1.0613e-05 | 0.14086 | 0.14086 | 0.14086 | 1 | 0 | 0.99981 | -0.003685 | 19.3483
34 | 0.054725 | 0.013786 | -0.054656 | -0.013743 | 6.8447e-05 | 4.3446e-05 | 0.081456 | 0.081456 | 0.081456 | 1 | 0 | 0.99863 | -0.026187 | 22.3781
35 | 0.093537 | 0.023746 | -0.093484 | -0.023712 | 5.2844e-05 | 3.344e-05 | 0.13932 | 0.13932 | 0.13932 | 0.99981 | -0.003685 | 0.99919 | -0.015435 | 19.1372
36 | 0.050767 | 0.012768 | -0.050712 | -0.012733 | 5.4963e-05 | 3.4842e-05 | 0.075661 | 0.075661 | 0.075661 | 0.99863 | -0.026187 | 0.99745 | -0.048879 | 20.7859
37 | 0.084113 | 0.021363 | -0.084065 | -0.021333 | 4.8081e-05 | 3.0345e-05 | 0.12536 | 0.12536 | 0.12536 | 0.99919 | -0.015435 | 0.99857 | -0.027318 | 17.2202
38 | 0.047022 | 0.011808 | -0.047011 | -0.011801 | 1.0993e-05 | 6.9577e-06 | 0.070156 | 0.070156 | 0.070156 | 0.99745 | -0.048879 | 0.9972 | -0.05378 | 19.2736
39 | 0.083262 | 0.021132 | -0.083222 | -0.021106 | 4.0368e-05 | 2.547e-05 | 0.12417 | 0.12417 | 0.12417 | 0.99857 | -0.027318 | 0.99804 | -0.037402 | 17.0559
40 | 0.042621 | 0.010701 | -0.042583 | -0.010677 | 3.8067e-05 | 2.4036e-05 | 0.063605 | 0.063606 | 0.063606 | 0.9972 | -0.05378 | 0.99623 | -0.07252 | 17.474
41 | 0.053324 | 0.013477 | -0.053255 | -0.013434 | 6.8127e-05 | 4.3247e-05 | 0.080696 | 0.080696 | 0.080696 | 0.98377 | -0.31151 | 0.98239 | -0.33819 | 22.1693
42 | -0.055796 | -0.014096 | 0.055843 | 0.014126 | 4.7091e-05 | 2.9914e-05 | 0.084436 | 0.084436 | 0.084436 | 0.98377 | -0.31151 | 0.98467 | -0.29391 | 23.1967
43 | 0.051416 | 0.012972 | -0.051393 | -0.012958 | 2.2337e-05 | 1.4172e-05 | 0.077909 | 0.07791 | 0.07791 | 0.98239 | -0.33819 | 0.98193 | -0.34727 | 21.4037
44 | -0.060125 | -0.015199 | 0.060187 | 0.015239 | 6.2556e-05 | 3.9779e-05 | 0.090906 | 0.090906 | 0.090906 | 0.98467 | -0.29391 | 0.98579 | -0.27224 | 24.9741
45 | 0.048996 | 0.012357 | -0.04895 | -0.012329 | 4.5411e-05 | 2.8786e-05 | 0.074276 | 0.074276 | 0.074276 | 0.98193 | -0.34727 | 0.98093 | -0.36665 | 20.4055
46 | -0.062464 | -0.01581 | 0.062535 | 0.015855 | 7.0371e-05 | 4.4769e-05 | 0.094343 | 0.094343 | 0.094343 | 0.98579 | -0.27224 | 0.987 | -0.2488 | 25.9184
47 | 0.044331 | 0.011171 | -0.044305 | -0.011155 | 2.5329e-05 | 1.6022e-05 | 0.067269 | 0.067269 | 0.067269 | 0.98093 | -0.36665 | 0.98032 | -0.3786 | 18.4804
48 | -0.0655 | -0.016598 | 0.065538 | 0.016622 | 3.7248e-05 | 2.3709e-05 | 0.098814 | 0.098814 | 0.098814 | 0.987 | -0.2488 | 0.98762 | -0.23697 | 27.1467
49 | 0.03665 | 0.0092359 | -0.036629 | -0.0092227 | 2.105e-05 | 1.3244e-05 | 0.055649 | 0.055649 | 0.055649 | 0.98032 | -0.3786 | 0.97971 | -0.39061 | 15.2882
50 | 0.0076552 | 0.0019188 | -0.0076533 | -0.0019181 | 1.8387e-06 | 7.1905e-07 | 0.01162 | 0.01162 | 0.01162 | 0.98032 | -0.3786 | 0.98006 | -0.38364 | 3.1923
51 | 0.0050512 | 0.0012659 | -0.0050511 | -0.0012659 | 7.5151e-08 | 3.822e-09 | 0.0076105 | 0.0076105 | 0.0076105 | 0.98762 | -0.23697 | 0.9876 | -0.23729 | 2.0908
52 | -0.070589 | -0.017888 | 0.070637 | 0.017918 | 4.8525e-05 | 3.091e-05 | 0.10642 | 0.10642 | 0.10642 | 0.98762 | -0.23697 | 0.98836 | -0.22268 | 29.2374
53 | -0.0054928 | -0.0013763 | 0.0054936 | 0.0013765 | 8.3529e-07 | 1.1621e-07 | 0.0082652 | 0.0082651 | 0.0082652 | 0.98887 | -0.21303 | 0.98903 | -0.20983 | 2.2707
54 | 0.0040045 | 0.0010033 | -0.0040044 | -0.0010034 | 1.4895e-07 | -4.5002e-08 | 0.0060258 | 0.0060258 | 0.0060258 | 0.98887 | -0.21303 | 0.98883 | -0.21381 | 1.6554
55 | -0.0071793 | -0.0017989 | 0.0071818 | 0.0017998 | 2.4668e-06 | 8.5488e-07 | 0.010801 | 0.010801 | 0.010801 | 0.98903 | -0.20983 | 0.9894 | -0.20262 | 2.9674
56 | 0.0040044 | 0.0010034 | -0.004004 | -0.0010035 | 3.5068e-07 | -1.059e-07 | 0.0060258 | 0.0060259 | 0.0060259 | 0.98883 | -0.21381 | 0.98873 | -0.21565 | 1.6555
57 | 0.023642 | 0.0059334 | -0.023634 | -0.0059284 | 8.1772e-06 | 5.012e-06 | 0.035559 | 0.035559 | 0.035559 | 0.9894 | -0.20262 | 0.98903 | -0.20988 | 9.7691
58 | 0.016592 | 0.0041635 | -0.016589 | -0.0041617 | 3.0104e-06 | 1.7614e-06 | 0.024965 | 0.024965 | 0.024965 | 0.98903 | -0.20988 | 0.98883 | -0.21368 | 6.8586
59 | 0.0070415 | 0.0017649 | -0.0070397 | -0.0017643 | 1.8798e-06 | 6.301e-07 | 0.010594 | 0.010594 | 0.010594 | 0.98903 | -0.20988 | 0.98874 | -0.21548 | 2.9105
60 | 0.072913 | 0.018506 | -0.072868 | -0.018477 | 4.5595e-05 | 2.8663e-05 | 0.10978 | 0.10978 | 0.10978 | 0.98903 | -0.20967 | 0.98836 | -0.22268 | 15.0799
61 | 0.014149 | 0.0035501 | -0.014136 | -0.0035429 | 1.28e-05 | 7.2271e-06 | 0.021293 | 0.021293 | 0.021293 | 0.98883 | -0.21368 | 0.98786 | -0.23267 | 5.8498
62 | 0.0039735 | 0.00099583 | -0.0039735 | -0.00099584 | 4.7815e-08 | -1.5129e-08 | 0.00598 | 0.00598 | 0.00598 | 0.98874 | -0.21548 | 0.98873 | -0.21574 | 1.6429
63 | 0.0043636 | 0.0010931 | -0.0043629 | -0.0010932 | 6.8431e-07 | -6.5252e-08 | 0.0066918 | 0.006692 | 0.006692 | 0.97028 | -0.57527 | 0.97011 | -0.57856 | 1.8385
64 | -0.018118 | -0.0045848 | 0.018155 | 0.0046067 | 3.6753e-05 | 2.1885e-05 | 0.027512 | 0.027512 | 0.027512 | 0.9805 | -0.37451 | 0.98267 | -0.33233 | 7.5583
65 | -0.018155 | -0.0046067 | 0.018244 | 0.0046596 | 8.8828e-05 | 5.2864e-05 | 0.027512 | 0.02751 | 0.027512 | 0.98267 | -0.33233 | 0.98793 | -0.23111 | 7.5581
66 | 0.0022506 | 0.00056381 | -0.0022505 | -0.00056403 | 1.0425e-07 | -2.213e-07 | 0.003452 | 0.0034521 | 0.0034521 | 0.97011 | -0.57856 | 0.97006 | -0.57953 | 0.94839
67 | 0.075567 | 0.019188 | -0.075483 | -0.019135 | 8.4406e-05 | 5.3096e-05 | 0.11275 | 0.11275 | 0.11275 | 0.99804 | -0.037402 | 0.99682 | -0.060642 | 15.4883
68 | 0.067896 | 0.017234 | -0.067739 | -0.017135 | 0.00015706 | 9.8401e-05 | 0.10143 | 0.10143 | 0.10143 | 0.99682 | -0.060642 | 0.9943 | -0.10885 | 13.9328
69 | 0.055315 | 0.01402 | -0.055287 | -0.014002 | 2.8314e-05 | 1.7551e-05 | 0.082837 | 0.082837 | 0.082837 | 0.9943 | -0.10885 | 0.99375 | -0.11951 | 11.3788
70 | 0.010205 | 0.0025591 | -0.010195 | -0.002554 | 1.0476e-05 | 5.1529e-06 | 0.015273 | 0.015273 | 0.015273 | 0.9943 | -0.10885 | 0.99319 | -0.1304 | 4.196
71 | 0.052424 | 0.013285 | -0.052415 | -0.01328 | 8.6046e-06 | 5.3143e-06 | 0.078551 | 0.078551 | 0.078551 | 0.99375 | -0.11951 | 0.99357 | -0.12292 | 10.7899
72 | 0.006329 | 0.0015852 | -0.0063284 | -0.001585 | 5.7502e-07 | 1.4732e-07 | 0.0094818 | 0.0094819 | 0.0094819 | 0.99319 | -0.1304 | 0.99309 | -0.13231 | 2.6049
73 | 0.048112 | 0.012201 | -0.048098 | -0.012192 | 1.4321e-05 | 8.7853e-06 | 0.072106 | 0.072106 | 0.072106 | 0.99357 | -0.12292 | 0.99324 | -0.12912 | 9.9047
74 | 0.0042899 | 0.0010741 | -0.0042876 | -0.0010746 | 2.33e-06 | -4.5334e-07 | 0.0064275 | 0.0064282 | 0.0064282 | 0.99309 | -0.13231 | 0.9925 | -0.14372 | 1.766
75 | 0.019729 | 0.0049763 | -0.01969 | -0.0049524 | 3.9733e-05 | 2.3948e-05 | 0.029977 | 0.029978 | 0.029978 | 0.97971 | -0.39061 | 0.97755 | -0.43277 | 8.2356
76 | 0.0169 | 0.0042464 | -0.016884 | -0.004237 | 1.5885e-05 | 9.3578e-06 | 0.025672 | 0.025672 | 0.025672 | 0.97971 | -0.39061 | 0.9787 | -0.41032 | 7.0528
77 | 0.0053069 | 0.00133 | -0.0053068 | -0.00133 | 1.1333e-07 | 1.3872e-08 | 0.0080573 | 0.0080574 | 0.0080574 | 0.98006 | -0.38364 | 0.98004 | -0.38409 | 2.2136
78 | 0.017715 | 0.0044574 | -0.017704 | -0.0044513 | 1.0325e-05 | 6.1339e-06 | 0.026971 | 0.026971 | 0.026971 | 0.97755 | -0.43277 | 0.97693 | -0.44497 | 7.4097
79 | 0.013189 | 0.0033111 | -0.013169 | -0.0032998 | 2.0319e-05 | 1.1314e-05 | 0.020055 | 0.020056 | 0.020056 | 0.9787 | -0.41032 | 0.97706 | -0.44267 | 5.5099
80 | 0.013221 | 0.0033285 | -0.01322 | -0.0033279 | 9.7328e-07 | 5.4281e-07 | 0.020143 | 0.020143 | 0.020143 | 0.97693 | -0.44497 | 0.97685 | -0.44651 | 5.5337
81 | 0.0044836 | 0.0011228 | -0.0044832 | -0.0011228 | 3.3711e-07 | -2.5596e-08 | 0.0068289 | 0.0068289 | 0.0068289 | 0.97693 | -0.44497 | 0.97685 | -0.44655 | 1.8761
82 | 0.0095854 | 0.0024033 | -0.0095851 | -0.0024032 | 3.1736e-07 | 1.5338e-07 | 0.014599 | 0.014599 | 0.014599 | 0.97706 | -0.44267 | 0.97702 | -0.44336 | 4.0106
83 | 0.0035838 | 0.00089648 | -0.0035822 | -0.00089725 | 1.6038e-06 | -7.7096e-07 | 0.0054573 | 0.005458 | 0.005458 | 0.97706 | -0.44267 | 0.97658 | -0.45207 | 1.4994
84 | 0.0095851 | 0.0024032 | -0.0095812 | -0.0024013 | 3.9079e-06 | 1.889e-06 | 0.014599 | 0.014599 | 0.014599 | 0.97702 | -0.44336 | 0.97659 | -0.45192 | 4.0107
85 | 0.001944 | 0.00048668 | -0.0019438 | -0.00048717 | 1.5348e-07 | -4.8541e-07 | 0.0029619 | 0.0029621 | 0.0029621 | 0.97658 | -0.45207 | 0.97649 | -0.45373 | 0.81376
86 | 0.01322 | 0.0033279 | -0.013208 | -0.0033212 | 1.2099e-05 | 6.7488e-06 | 0.020143 | 0.020143 | 0.020143 | 0.97685 | -0.44651 | 0.97588 | -0.46568 | 5.5338
87 | 0.0036929 | 0.00092475 | -0.003692 | -0.00092514 | 9.3747e-07 | -3.8879e-07 | 0.005625 | 0.0056254 | 0.0056254 | 0.97685 | -0.44655 | 0.97658 | -0.45188 | 1.5454
88 | 0.044789 | 0.011363 | -0.044773 | -0.011353 | 1.5813e-05 | 9.6364e-06 | 0.067149 | 0.067149 | 0.067149 | 0.99324 | -0.12912 | 0.99286 | -0.13646 | 9.2238
89 | 0.03254 | 0.0082713 | -0.032529 | -0.0082646 | 1.0755e-05 | 6.7285e-06 | 0.048871 | 0.048871 | 0.048871 | 0.99161 | -0.16052 | 0.99125 | -0.16738 | 13.4261
90 | -0.037941 | -0.0096244 | 0.03798 | 0.009649 | 3.92e-05 | 2.4672e-05 | 0.056976 | 0.056976 | 0.056976 | 0.99161 | -0.16052 | 0.99273 | -0.13906 | 15.6527
91 | 0.002795 | 0.00069996 | -0.0027946 | -0.0007004 | 3.368e-07 | -4.4301e-07 | 0.004194 | 0.0041942 | 0.0041942 | 0.99161 | -0.16052 | 0.99148 | -0.16305 | 1.1523
92 | 0.02875 | 0.0073175 | -0.028739 | -0.0073106 | 1.1161e-05 | 6.9377e-06 | 0.043199 | 0.043199 | 0.043199 | 0.99125 | -0.16738 | 0.99083 | -0.17544 | 11.8678
93 | -0.041488 | -0.010528 | 0.041493 | 0.010531 | 5.1806e-06 | 3.1311e-06 | 0.062234 | 0.062234 | 0.062234 | 0.99273 | -0.13906 | 0.99286 | -0.13646 | 8.5486
94 | 0.025292 | 0.0064465 | -0.025274 | -0.0064355 | 1.7858e-05 | 1.1005e-05 | 0.038021 | 0.038021 | 0.038021 | 0.99083 | -0.17544 | 0.99007 | -0.19008 | 10.4454
95 | 0.0041844 | 0.0010484 | -0.0041838 | -0.0010486 | 6.1587e-07 | -1.3975e-07 | 0.0062889 | 0.0062891 | 0.0062891 | 0.99007 | -0.19008 | 0.98991 | -0.19317 | 1.7278
96 | 0.021089 | 0.005387 | -0.021047 | -0.0053618 | 4.1744e-05 | 2.5297e-05 | 0.031732 | 0.031733 | 0.031733 | 0.99007 | -0.19008 | 0.98793 | -0.23111 | 8.7178
97 | 0.0028037 | 0.00070218 | -0.0028034 | -0.0007026 | 3.2652e-07 | -4.1614e-07 | 0.0042228 | 0.004223 | 0.004223 | 0.98793 | -0.23111 | 0.9878 | -0.23355 | 1.1602
98 | 0.0017466 | 0.00043759 | -0.0017466 | -0.00043773 | 3.516e-08 | -1.4313e-07 | 0.0026613 | 0.0026613 | 0.0026613 | 0.97658 | -0.45188 | 0.97656 | -0.45231 | 0.73113
99 | 0.012306 | 0.0030951 | -0.012288 | -0.0030857 | 1.7192e-05 | 9.3791e-06 | 0.018768 | 0.018768 | 0.018768 | 0.97588 | -0.46568 | 0.97439 | -0.49496 | 5.1561
100 | 0.011872 | 0.0029813 | -0.011867 | -0.0029787 | 4.723e-06 | 2.5457e-06 | 0.018132 | 0.018132 | 0.018132 | 0.97439 | -0.49496 | 0.97396 | -0.5033 | 4.9813
101 | -0.00090652 | -0.00022719 | 0.00090657 | 0.00022633 | 5.278e-08 | -8.6677e-07 | 0.0013899 | 0.0013896 | 0.0013899 | 0.97051 | -0.57172 | 0.97057 | -0.5705 | 0.38184
102 | -0.0011794 | -0.0002947 | 0.0011794 | 0.00029443 | 2.9054e-08 | -2.7439e-07 | 0.0018079 | 0.0018078 | 0.0018079 | 0.97057 | -0.5705 | 0.97059 | -0.56998 | 0.49667
103 | -0.0022944 | -0.00057387 | 0.002295 | 0.00057265 | 6.0421e-07 | -1.2238e-06 | 0.0035171 | 0.0035165 | 0.0035171 | 0.97059 | -0.56998 | 0.97087 | -0.56444 | 0.96624
104 | -0.0032855 | -0.00082089 | 0.0032857 | 0.00082075 | 2.0707e-07 | -1.3689e-07 | 0.0050347 | 0.0050346 | 0.0050347 | 0.97087 | -0.56444 | 0.97094 | -0.56312 | 1.3831
105 | -0.0040763 | -0.0010189 | 0.0040766 | 0.0010188 | 3.251e-07 | -6.6787e-08 | 0.0062462 | 0.0062461 | 0.0062462 | 0.97094 | -0.56312 | 0.97102 | -0.56144 | 1.716
106 | -0.010837 | -0.0027122 | 0.010849 | 0.0027182 | 1.1418e-05 | 5.9401e-06 | 0.016606 | 0.016605 | 0.016606 | 0.97102 | -0.56144 | 0.97214 | -0.53932 | 4.562
107 | 0.0055472 | 0.0013893 | -0.0055438 | -0.0013887 | 3.4025e-06 | 6.2538e-07 | 0.0085002 | 0.0085008 | 0.0085008 | 0.97102 | -0.56144 | 0.97037 | -0.57432 | 2.3354
108 | -0.010849 | -0.0027182 | 0.01086 | 0.0027241 | 1.1463e-05 | 5.9602e-06 | 0.016605 | 0.016605 | 0.016605 | 0.97214 | -0.53932 | 0.97326 | -0.51716 | 4.5619
109 | 0.0045061 | 0.0011286 | -0.0045052 | -0.0011287 | 9.1856e-07 | -4.5755e-08 | 0.0069097 | 0.0069099 | 0.0069099 | 0.97037 | -0.57432 | 0.97016 | -0.5786 | 1.8983
110 | -0.011859 | -0.0029745 | 0.011866 | 0.0029782 | 6.8785e-06 | 3.7085e-06 | 0.018132 | 0.018132 | 0.018132 | 0.97326 | -0.51716 | 0.97388 | -0.50499 | 4.9814
111 | -0.0033026 | -0.00082731 | 0.0033027 | 0.00082728 | 4.9962e-08 | -3.214e-08 | 0.0050655 | 0.0050654 | 0.0050655 | 0.97014 | -0.57892 | 0.97016 | -0.5786 | 1.3916
112 | 0.0023454 | 0.00058741 | -0.0023452 | -0.00058777 | 1.8815e-07 | -3.5828e-07 | 0.0035973 | 0.0035974 | 0.0035974 | 0.97014 | -0.57892 | 0.97006 | -0.58061 | 0.98831
113 | 0.011867 | 0.0029787 | -0.011866 | -0.0029782 | 9.5768e-07 | 5.1625e-07 | 0.018132 | 0.018132 | 0.018132 | 0.97396 | -0.5033 | 0.97388 | -0.50499 | 4.9813

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31389 | 0.079405

## res_load
| p_mw | q_mvar
0 | 0.0014489 | 0.00036313
1 | 0.00075421 | 0.00018902
2 | 0.0019532 | 0.00048953
3 | 0.0047355 | 0.0011868
4 | 0.0036897 | 0.00092472
5 | 0.0031217 | 0.00078238
6 | 0.0062355 | 0.0015628
7 | 0.00067437 | 0.00016901
8 | 0.0025076 | 0.00062847
9 | 0.0016155 | 0.00040489
10 | 0.0005597 | 0.00014027
11 | 0.0026854 | 0.00067303
12 | 0.0017052 | 0.00042735
13 | 0.00086219 | 0.00021608
14 | 0.0036469 | 0.00091401
15 | 0.0060874 | 0.0015256
16 | 0.0050339 | 0.0012616
17 | 0.005804 | 0.0014546
18 | 0.0077889 | 0.0019521
19 | 0.0021572 | 0.00054065
20 | 0.0059457 | 0.0014901
21 | 0.0039527 | 0.00099064
22 | 0.0035359 | 0.00088618
23 | 0.0032412 | 0.00081232
24 | 0.013105 | 0.0032845
25 | 0.0065925 | 0.0016522
26 | 0.0010326 | 0.0002588
27 | 0.0038896 | 0.00097483
28 | 0.009371 | 0.0023486
29 | 0.0036902 | 0.00092485
30 | 0.00080284 | 0.00020121
31 | 0.0043898 | 0.0011002
32 | 0.0024726 | 0.0006197
33 | 0.0018398 | 0.00046109
34 | 0.0042813 | 0.001073
35 | 0.0023978 | 0.00060095
36 | 0.0022771 | 0.0005707
37 | 0.0046195 | 0.0011577
38 | 0.0029656 | 0.00074325
39 | 0.0014882 | 0.00037299
40 | 0.0016857 | 0.00042248
41 | 0.004004 | 0.0010035
42 | 0.0075137 | 0.0018831
43 | 0.0024403 | 0.0006116
44 | 0.0030662 | 0.00076845
45 | 0.0050511 | 0.0012659
46 | 0.0022302 | 0.00055894
47 | 0.0016085 | 0.00040314
48 | 0.0013962 | 0.00034993
49 | 0.0021123 | 0.00052939
50 | 0.0076545 | 0.0019184
51 | 0.0075867 | 0.0019014
52 | 0.0022189 | 0.0005561
53 | 0.0028629 | 0.0007175
54 | 0.0038656 | 0.00096882
55 | 0.004303 | 0.0010784
56 | 0.0020385 | 0.00051089
57 | 0.0042876 | 0.0010746
58 | 0.0040374 | 0.0010119
59 | 0.0023465 | 0.00058808
60 | 0.0053068 | 0.00133
61 | 0.001975 | 0.00049498
62 | 0.0036944 | 0.00092589
63 | 0.0022505 | 0.00056403
64 | 0.0016382 | 0.00041057
65 | 0.0095812 | 0.0024013
66 | 0.0019438 | 0.00048717
67 | 0.00079034 | 0.00019808
68 | 0.0033091 | 0.00082935
69 | 0.002606 | 0.00065313
70 | 0.0037788 | 0.00094705
71 | 0.003508 | 0.0008792
72 | 0.0027946 | 0.0007004
73 | 0.0034477 | 0.00086408
74 | 0.0032798 | 0.00082199
75 | 0.0041838 | 0.0010486
76 | 0.0039735 | 0.00099584
77 | 0.014136 | 0.0035429
78 | 0.0028034 | 0.0007026
79 | 0.0019453 | 0.00048755
80 | 0.0017466 | 0.00043773
81 | 0.00090207 | 0.00022608
82 | 0.00041672 | 0.00010444
83 | 0.00090652 | 0.00022719
84 | 0.00027283 | 6.8377e-05
85 | 0.001115 | 0.00027944
86 | 0.00099051 | 0.00024824
87 | 0.00079057 | 0.00019814
88 | 0.0012135 | 0.00030412
89 | 0.0010376 | 0.00026005
90 | 0.00099898 | 0.00025037
91 | 0.00095722 | 0.0002399
92 | 0.0012026 | 0.00030139
93 | 0.0023452 | 0.00058777

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1