## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1507-19_1_3_node_14 | 0.4 | n |  | TRUE
1 | bus_LV_1507-19_1_3_node_15 | 0.4 | n |  | TRUE
2 | bus_LV_1507-19_1_3_node_16 | 0.4 | n |  | TRUE
3 | bus_LV_1507-19_1_3_node_60 | 0.4 | n |  | TRUE
4 | bus_LV_1507-19_1_3_node_24 | 0.4 | n |  | TRUE
5 | bus_LV_1507-19_1_3_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_1507-19_1_3_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_1507-19_1_3_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_1507-19_1_3_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_1507-19_1_3_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_1507-19_1_3_node_59 | 0.4 | n |  | TRUE
11 | bus_LV_1507-19_1_3_node_87 | 0.4 | n |  | TRUE
12 | bus_LV_1507-19_1_3_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_1507-19_1_3_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_1507-19_1_3_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_1507-19_1_3_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_1507-19_1_3_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_1507-19_1_3_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_1507-19_1_3_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_1507-19_1_3_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_1507-19_1_3_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_1507-19_1_3_node_44 | 0.4 | n |  | TRUE
22 | bus_LV_1507-19_1_3_node_45 | 0.4 | n |  | TRUE
23 | bus_LV_1507-19_1_3_node_47 | 0.4 | n |  | TRUE
24 | bus_LV_1507-19_1_3_node_56 | 0.4 | n |  | TRUE
25 | bus_LV_1507-19_1_3_node_48 | 0.4 | n |  | TRUE
26 | bus_LV_1507-19_1_3_node_49 | 0.4 | n |  | TRUE
27 | bus_LV_1507-19_1_3_node_50 | 0.4 | n |  | TRUE
28 | bus_LV_1507-19_1_3_node_51 | 0.4 | n |  | TRUE
29 | bus_LV_1507-19_1_3_node_52 | 0.4 | n |  | TRUE
30 | bus_LV_1507-19_1_3_node_53 | 0.4 | n |  | TRUE
31 | bus_LV_1507-19_1_3_node_54 | 0.4 | n |  | TRUE
32 | bus_LV_1507-19_1_3_node_78 | 0.4 | n |  | TRUE
33 | bus_LV_1507-19_1_3_node_55 | 0.4 | n |  | TRUE
34 | bus_LV_1507-19_1_3_node_66 | 0.4 | n |  | TRUE
35 | bus_LV_1507-19_1_3_node_57 | 0.4 | n |  | TRUE
36 | bus_LV_1507-19_1_3_node_58 | 0.4 | n |  | TRUE
37 | bus_LV_1507-19_1_3_node_61 | 0.4 | n |  | TRUE
38 | bus_LV_1507-19_1_3_node_62 | 0.4 | n |  | TRUE
39 | bus_LV_1507-19_1_3_node_64 | 0.4 | n |  | TRUE
40 | bus_LV_1507-19_1_3_node_76 | 0.4 | n |  | TRUE
41 | bus_LV_1507-19_1_3_node_84 | 0.4 | n |  | TRUE
42 | bus_LV_1507-19_1_3_node_77 | 0.4 | n |  | TRUE
43 | bus_MV_23_0_node_22 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1507-19_1_3_load_14 | 0 | 0.0044324 | 0.0011109 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1507-19_1_3_load_16 | 2 | 0.0048298 | 0.0012105 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1507-19_1_3_load_60 | 3 | 0.0046131 | 0.0011562 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1507-19_1_3_load_24 | 4 | 0.0078789 | 0.0019746 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1507-19_1_3_load_25 | 5 | 0.0090426 | 0.0022663 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1507-19_1_3_load_27 | 7 | 0.0087922 | 0.0022035 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1507-19_1_3_load_30 | 9 | 0.010216 | 0.0025604 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1507-19_1_3_load_87 | 11 | 0.0022623 | 0.00056699 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1507-19_1_3_load_29 | 12 | 0.0089736 | 0.002249 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1507-19_1_3_load_31 | 13 | 0.014295 | 0.0035827 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1507-19_1_3_load_32 | 14 | 0.011172 | 0.0027999 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1507-19_1_3_load_33 | 15 | 0.0067257 | 0.0016856 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1507-19_1_3_load_34 | 16 | 0.050415 | 0.012635 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1507-19_1_3_load_35 | 17 | 0.0035568 | 0.00089141 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1507-19_1_3_load_36 | 18 | 0.0027362 | 0.00068575 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1507-19_1_3_load_38 | 19 | 0.002736 | 0.00068571 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1507-19_1_3_load_46 | 20 | 0.0042576 | 0.0010671 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1507-19_1_3_load_44 | 21 | 0.0083815 | 0.0021006 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1507-19_1_3_load_45 | 22 | 0.006375 | 0.0015977 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1507-19_1_3_load_47 | 23 | 0.0080268 | 0.0020117 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1507-19_1_3_load_56 | 24 | 0.0068984 | 0.0017289 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1507-19_1_3_load_48 | 25 | 0.0044015 | 0.0011031 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1507-19_1_3_load_49 | 26 | 0.0075672 | 0.0018965 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1507-19_1_3_load_51 | 28 | 0.0055842 | 0.0013995 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1507-19_1_3_load_52 | 29 | 0.0030528 | 0.00076511 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1507-19_1_3_load_53 | 30 | 0.0084 | 0.0021052 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1507-19_1_3_load_54 | 31 | 0.012831 | 0.0032158 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1507-19_1_3_load_78 | 32 | 0.0057029 | 0.0014293 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1507-19_1_3_load_55 | 33 | 0.0048144 | 0.0012066 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1507-19_1_3_load_66 | 34 | 0.007786 | 0.0019514 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1507-19_1_3_load_57 | 35 | 0.0016663 | 0.00041761 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1507-19_1_3_load_58 | 36 | 0.0026295 | 0.00065902 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1507-19_1_3_load_61 | 37 | 0.0087787 | 0.0022001 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1507-19_1_3_load_62 | 38 | 0.003328 | 0.00083408 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1507-19_1_3_load_64 | 39 | 0.0033268 | 0.00083379 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1507-19_1_3_load_76 | 40 | 0.0030679 | 0.00076889 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1507-19_1_3_load_84 | 41 | 0.0030689 | 0.00076913 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1507-19_1_3_load_77 | 42 | 0.0030679 | 0.00076888 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1507-19_1_3_line_0 |  | 0 | 1 | 0.082387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1507-19_1_3_line_1 |  | 1 | 2 | 0.056455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1507-19_1_3_line_2 |  | 2 | 3 | 0.0049477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1507-19_1_3_line_3 |  | 3 | 36 | 0.01026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1507-19_1_3_line_4 |  | 4 | 5 | 0.0091193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1507-19_1_3_line_5 |  | 4 | 6 | 0.044672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1507-19_1_3_line_6 |  | 5 | 7 | 0.019722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1507-19_1_3_line_7 |  | 6 | 8 | 0.075534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1507-19_1_3_line_8 |  | 7 | 9 | 0.018079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1507-19_1_3_line_9 |  | 8 | 10 | 0.085103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1507-19_1_3_line_10 |  | 8 | 11 | 0.065409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1507-19_1_3_line_11 |  | 9 | 12 | 0.0325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1507-19_1_3_line_12 |  | 10 | 35 | 0.019186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1507-19_1_3_line_13 |  | 11 | 41 | 0.00089537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1507-19_1_3_line_14 |  | 12 | 13 | 0.018384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1507-19_1_3_line_15 |  | 13 | 14 | 0.015117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1507-19_1_3_line_16 |  | 14 | 15 | 0.011202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1507-19_1_3_line_17 |  | 15 | 16 | 0.0088464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1507-19_1_3_line_18 |  | 17 | 18 | 0.011628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1507-19_1_3_line_19 |  | 18 | 19 | 0.00010139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1507-19_1_3_line_20 |  | 19 | 20 | 0.020216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1507-19_1_3_line_21 |  | 20 | 21 | 0.0046296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1507-19_1_3_line_22 |  | 21 | 22 | 0.021662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1507-19_1_3_line_23 |  | 22 | 23 | 0.0057148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1507-19_1_3_line_24 |  | 23 | 24 | 0.011097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1507-19_1_3_line_25 |  | 24 | 28 | 0.0060082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1507-19_1_3_line_26 |  | 25 | 26 | 0.020259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1507-19_1_3_line_27 |  | 25 | 27 | 0.0029103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1507-19_1_3_line_28 |  | 26 | 28 | 0.035337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1507-19_1_3_line_29 |  | 27 | 29 | 0.014657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_1507-19_1_3_line_30 |  | 27 | 30 | 0.023097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1507-19_1_3_line_31 |  | 29 | 31 | 0.011242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_1507-19_1_3_line_32 |  | 30 | 32 | 0.029163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1507-19_1_3_line_33 |  | 31 | 33 | 0.016377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_1507-19_1_3_line_34 |  | 32 | 42 | 0.021785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1507-19_1_3_line_35 |  | 33 | 34 | 0.010228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1507-19_1_3_line_36 |  | 34 | 41 | 0.018473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1507-19_1_3_line_37 |  | 35 | 36 | 0.023624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1507-19_1_3_line_38 |  | 37 | 38 | 0.021069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1507-19_1_3_line_39 |  | 38 | 39 | 0.0065091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1507-19_1_3_line_40 |  | 39 | 40 | 0.012636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1507-19_1_3_line_41 |  | 40 | 42 | 0.0061333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1507-19_1_3_trafo_53 | 0.63 MVA 20/0.4 kV | 43 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2665959.8876 | 1204548.9545 | 2665956.5053 | 1204470.8477 | 2665955.2287 | 1204466.8391
1 | 2665959.8876 | 1204548.9545 | 2665975.7063 | 1204562.5263 | 2665982.7305 | 1204573.3326 | 2665994.3032 | 1204592.8891
2 | 2665994.3032 | 1204592.8891 | 2665996.823 | 1204597.1471
3 | 2666000.07 | 1204606.8008 | 2665999.7944 | 1204604.3176 | 2665996.823 | 1204597.1471 | 2665996.823 | 1204597.1471
4 | 2666121.6386 | 1204705.4306 | 2666124.2921 | 1204699.941 | 2666125.4188 | 1204697.1368
5 | 2666102.332 | 1204745.7145 | 2666108.9461 | 1204731.6903 | 2666121.6386 | 1204705.4306
6 | 2666132.772 | 1204678.8368 | 2666125.4188 | 1204697.1368
7 | 2666033.8288 | 1204726.2674 | 2666033.6103 | 1204730.89 | 2666051.0736 | 1204737.3981 | 2666067.1428 | 1204742.0119 | 2666069.0172 | 1204742.4329 | 2666078.8213 | 1204744.6649 | 2666081.0751 | 1204745.179 | 2666102.332 | 1204745.7145
8 | 2666132.772 | 1204678.8368 | 2666135.135 | 1204672.9558 | 2666138.0454 | 1204661.5811 | 2666138.0454 | 1204661.5811
9 | 2666001.9569 | 1204649.5577 | 2666004.0658 | 1204670.7494 | 2666006.5574 | 1204681.4056 | 2666012.393 | 1204694.4224 | 2666029.4054 | 1204722.4495 | 2666033.8288 | 1204726.2674
10 | 2666033.8288 | 1204726.2674 | 2666040.026 | 1204718.2755 | 2666065.6894 | 1204669.2953
11 | 2666138.6931 | 1204629.1272 | 2666139.1078 | 1204648.0847 | 2666138.0454 | 1204661.5811
12 | 2666001.9569 | 1204649.5577 | 2666001.2685 | 1204630.3837
13 | 2666066.105 | 1204668.5022 | 2666065.6894 | 1204669.2953
14 | 2666138.6931 | 1204629.1272 | 2666138.2911 | 1204610.7474
15 | 2666137.9605 | 1204595.6339 | 2666138.2911 | 1204610.7474
16 | 2666137.9605 | 1204595.6339 | 2666137.7155 | 1204584.4343
17 | 2666137.5221 | 1204575.59 | 2666137.7155 | 1204584.4343
18 | 2666045.6948 | 1204465.1872 | 2666047.5284 | 1204472.6322 | 2666048.7478 | 1204476.4003
19 | 2666048.7478 | 1204476.4003 | 2666048.779 | 1204476.4968
20 | 2666055.0031 | 1204495.7304 | 2666048.779 | 1204476.4968
21 | 2666056.4284 | 1204500.1351 | 2666055.0031 | 1204495.7304
22 | 2666056.4284 | 1204500.1351 | 2666063.0979 | 1204520.7449
23 | 2666063.0979 | 1204520.7449 | 2666064.8573 | 1204526.1821
24 | 2666068.274 | 1204536.7404 | 2666064.8573 | 1204526.1821
25 | 2666068.274 | 1204536.7404 | 2666068.5968 | 1204537.7378 | 2666070.0016 | 1204542.4946
26 | 2666080.2134 | 1204596.8507 | 2666078.5271 | 1204576.6625
27 | 2666080.4556 | 1204599.7509 | 2666080.2134 | 1204596.8507
28 | 2666078.5271 | 1204576.6625 | 2666077.9096 | 1204569.271 | 2666070.0016 | 1204542.4946
29 | 2666080.4556 | 1204599.7509 | 2666079.8135 | 1204614.3942
30 | 2666080.4556 | 1204599.7509 | 2666084.8241 | 1204598.2205 | 2666086.9409 | 1204594.6196 | 2666090.0678 | 1204580.6747
31 | 2666079.8135 | 1204614.3942 | 2666079.3973 | 1204623.8871 | 2666079.0333 | 1204625.5889
32 | 2666095.6524 | 1204552.0984 | 2666095.1997 | 1204557.7887 | 2666090.0678 | 1204580.6747
33 | 2666079.0333 | 1204625.5889 | 2666075.6078 | 1204641.6036
34 | 2666095.6524 | 1204552.0984 | 2666096.2602 | 1204544.459 | 2666093.9295 | 1204533.0263 | 2666093.1753 | 1204530.692
35 | 2666075.6078 | 1204641.6036 | 2666073.4685 | 1204651.605 | 2666073.4685 | 1204651.605
36 | 2666066.105 | 1204668.5022 | 2666070.079 | 1204660.9176 | 2666073.4685 | 1204651.605
37 | 2666001.2685 | 1204630.3837 | 2666000.59 | 1204611.4863 | 2666000.07 | 1204606.8008
38 | 2666078.9263 | 1204486.59 | 2666085.4038 | 1204506.6383
39 | 2666085.4038 | 1204506.6383 | 2666087.4049 | 1204512.8322
40 | 2666091.2896 | 1204524.8557 | 2666087.4049 | 1204512.8322
41 | 2666091.2896 | 1204524.8557 | 2666093.1753 | 1204530.692

## bus_geodata
| x | y | coords
0 | 2665955.2287 | 1204466.8391
1 | 2665959.8876 | 1204548.9545
2 | 2665994.3032 | 1204592.8891
3 | 2665996.823 | 1204597.1471
4 | 2666121.6386 | 1204705.4306
5 | 2666125.4188 | 1204697.1368
6 | 2666102.332 | 1204745.7145
7 | 2666132.772 | 1204678.8368
8 | 2666033.8288 | 1204726.2674
9 | 2666138.0454 | 1204661.5811
10 | 2666001.9569 | 1204649.5577
11 | 2666065.6894 | 1204669.2953
12 | 2666138.6931 | 1204629.1272
13 | 2666138.2911 | 1204610.7474
14 | 2666137.9605 | 1204595.6339
15 | 2666137.7155 | 1204584.4343
16 | 2666137.5221 | 1204575.59
17 | 2666045.6948 | 1204465.1872
18 | 2666048.7478 | 1204476.4003
19 | 2666048.779 | 1204476.4968
20 | 2666055.0031 | 1204495.7304
21 | 2666056.4284 | 1204500.1351
22 | 2666063.0979 | 1204520.7449
23 | 2666064.8573 | 1204526.1821
24 | 2666068.274 | 1204536.7404
25 | 2666080.2134 | 1204596.8507
26 | 2666078.5271 | 1204576.6625
27 | 2666080.4556 | 1204599.7509
28 | 2666070.0016 | 1204542.4946
29 | 2666079.8135 | 1204614.3942
30 | 2666090.0678 | 1204580.6747
31 | 2666079.0333 | 1204625.5889
32 | 2666095.6524 | 1204552.0984
33 | 2666075.6078 | 1204641.6036
34 | 2666073.4685 | 1204651.605
35 | 2666001.2685 | 1204630.3837
36 | 2666000.07 | 1204606.8008
37 | 2666078.9263 | 1204486.59
38 | 2666085.4038 | 1204506.6383
39 | 2666087.4049 | 1204512.8322
40 | 2666091.2896 | 1204524.8557
41 | 2666066.105 | 1204668.5022
42 | 2666093.1753 | 1204530.692
43 | 2666080.4556 | 1204599.7509

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98466 | -0.29293 | 0.0044324 | 0.0011109
1 | 0.98499 | -0.28637 | 0 | 0
2 | 0.98522 | -0.28187 | 0.0048298 | 0.0012105
3 | 0.98527 | -0.28104 | 0.0046131 | 0.0011562
4 | 0.98036 | -0.37553 | 0.0078789 | 0.0019746
5 | 0.97985 | -0.38543 | 0.0090426 | 0.0022663
6 | 0.98301 | -0.32402 | 0 | 0
7 | 0.97883 | -0.40525 | 0.0087922 | 0.0022035
8 | 0.9875 | -0.23754 | 0 | 0
9 | 0.97711 | -0.43879 | 0.010216 | 0.0025604
10 | 0.98608 | -0.26524 | 0 | 0
11 | 0.99194 | -0.15275 | 0.0022623 | 0.00056699
12 | 0.97434 | -0.49328 | 0.0089736 | 0.002249
13 | 0.97292 | -0.5212 | 0.014295 | 0.0035827
14 | 0.97195 | -0.54024 | 0.011172 | 0.0027999
15 | 0.97136 | -0.55205 | 0.0067257 | 0.0016856
16 | 0.97094 | -0.5603 | 0.050415 | 0.012635
17 | 0.99324 | -0.12943 | 0.0035568 | 0.00089141
18 | 0.99328 | -0.1287 | 0.0027362 | 0.00068575
19 | 0.99328 | -0.12869 | 0.002736 | 0.00068571
20 | 0.99344 | -0.12546 | 0.0042576 | 0.0010671
21 | 0.9935 | -0.12437 | 0.0083815 | 0.0021006
22 | 0.99393 | -0.11609 | 0.006375 | 0.0015977
23 | 0.99407 | -0.11326 | 0.0080268 | 0.0020117
24 | 0.99444 | -0.1062 | 0.0068984 | 0.0017289
25 | 0.99728 | -0.05153 | 0.0044015 | 0.0011031
26 | 0.99624 | -0.071476 | 0.0075672 | 0.0018965
27 | 0.99744 | -0.048443 | 0 | 0
28 | 0.99468 | -0.10165 | 0.0055842 | 0.0013995
29 | 0.99622 | -0.071522 | 0.0030528 | 0.00076511
30 | 1 | 0 | -0.27286 | -0.069481
31 | 0.9953 | -0.088959 | 0.012831 | 0.0032158
32 | 0.99928 | -0.013874 | 0.0057029 | 0.0014293
33 | 0.99405 | -0.11257 | 0.0048144 | 0.0012066
34 | 0.9933 | -0.1269 | 0.007786 | 0.0019514
35 | 0.98576 | -0.27149 | 0.0016663 | 0.00041761
36 | 0.9854 | -0.27849 | 0.0026295 | 0.00065902
37 | 0.99833 | -0.032082 | 0.0087787 | 0.0022001
38 | 0.9985 | -0.028848 | 0.003328 | 0.00083408
39 | 0.99857 | -0.02747 | 0.0033268 | 0.00083379
40 | 0.99875 | -0.024062 | 0.0030679 | 0.00076889
41 | 0.992 | -0.15158 | 0.0030689 | 0.00076913
42 | 0.99885 | -0.022079 | 0.0030679 | 0.00076888
43 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0044324 | -0.0011109 | 0.0044338 | 0.0011107 | 1.3861e-06 | -1.612e-07 | 0.0066983 | 0.0066979 | 0.0066983 | 0.98466 | -0.29293 | 0.98499 | -0.28637 | 1.8402
1 | -0.0044338 | -0.0011107 | 0.0044348 | 0.0011106 | 9.4973e-07 | -1.1094e-07 | 0.0066979 | 0.0066977 | 0.0066979 | 0.98499 | -0.28637 | 0.98522 | -0.28187 | 1.8401
2 | -0.0092645 | -0.0023211 | 0.0092649 | 0.0023212 | 3.6325e-07 | 1.6947e-07 | 0.013992 | 0.013992 | 0.013992 | 0.98522 | -0.28187 | 0.98527 | -0.28104 | 3.844
3 | -0.013878 | -0.0034774 | 0.01388 | 0.0034783 | 1.6902e-06 | 9.5104e-07 | 0.020959 | 0.020959 | 0.020959 | 0.98527 | -0.28104 | 0.9854 | -0.27849 | 5.758
4 | 0.12042 | 0.030487 | -0.12037 | -0.030451 | 5.7196e-05 | 3.6375e-05 | 0.18289 | 0.18289 | 0.18289 | 0.98036 | -0.37553 | 0.97985 | -0.38543 | 25.1228
5 | -0.1283 | -0.032462 | 0.12862 | 0.032664 | 0.00031802 | 0.0002024 | 0.19485 | 0.19485 | 0.19485 | 0.98036 | -0.37553 | 0.98301 | -0.32402 | 26.7655
6 | 0.11132 | 0.028185 | -0.11122 | -0.028118 | 0.00010582 | 6.7227e-05 | 0.16916 | 0.16916 | 0.16916 | 0.97985 | -0.38543 | 0.97883 | -0.40525 | 23.2365
7 | -0.12862 | -0.032664 | 0.12916 | 0.033007 | 0.00053772 | 0.00034222 | 0.19485 | 0.19485 | 0.19485 | 0.98301 | -0.32402 | 0.9875 | -0.23754 | 26.7654
8 | 0.10243 | 0.025914 | -0.10226 | -0.025809 | 0.00016456 | 0.00010509 | 0.1558 | 0.1558 | 0.1558 | 0.97883 | -0.40525 | 0.97711 | -0.43879 | 42.8012
9 | 0.01821 | 0.0045757 | -0.018186 | -0.0045614 | 2.4038e-05 | 1.4297e-05 | 0.027445 | 0.027445 | 0.027445 | 0.9875 | -0.23754 | 0.98608 | -0.26524 | 7.5399
10 | -0.14737 | -0.037582 | 0.14798 | 0.037969 | 0.00060604 | 0.00038619 | 0.2223 | 0.2223 | 0.2223 | 0.9875 | -0.23754 | 0.99194 | -0.15275 | 30.5352
11 | 0.092046 | 0.023249 | -0.091806 | -0.023096 | 0.00023969 | 0.000153 | 0.14024 | 0.14024 | 0.14024 | 0.97711 | -0.43879 | 0.97434 | -0.49328 | 38.5272
12 | 0.018186 | 0.0045614 | -0.018181 | -0.0045582 | 5.4194e-06 | 3.2238e-06 | 0.027445 | 0.027445 | 0.027445 | 0.98608 | -0.26524 | 0.98576 | -0.27149 | 7.5399
13 | -0.15024 | -0.038536 | 0.15025 | 0.038541 | 8.5512e-06 | 5.4496e-06 | 0.22569 | 0.22569 | 0.22569 | 0.99194 | -0.15275 | 0.992 | -0.15158 | 31.0013
14 | 0.082833 | 0.020847 | -0.082722 | -0.020776 | 0.00011038 | 7.0415e-05 | 0.12653 | 0.12653 | 0.12653 | 0.97434 | -0.49328 | 0.97292 | -0.5212 | 34.7622
15 | 0.068427 | 0.017193 | -0.068365 | -0.017154 | 6.2108e-05 | 3.9562e-05 | 0.10467 | 0.10467 | 0.10467 | 0.97292 | -0.5212 | 0.97195 | -0.54024 | 28.7556
16 | 0.057193 | 0.014354 | -0.057161 | -0.014333 | 3.2212e-05 | 2.0477e-05 | 0.087567 | 0.087567 | 0.087567 | 0.97195 | -0.54024 | 0.97136 | -0.55205 | 24.0569
17 | 0.050435 | 0.012648 | -0.050415 | -0.012635 | 1.9804e-05 | 1.2565e-05 | 0.077264 | 0.077264 | 0.077264 | 0.97136 | -0.55205 | 0.97094 | -0.5603 | 21.2264
18 | -0.0035568 | -0.00089141 | 0.0035569 | 0.00089134 | 1.2381e-07 | -7.1264e-08 | 0.0053285 | 0.0053285 | 0.0053285 | 0.99324 | -0.12943 | 0.99328 | -0.1287 | 1.4639
19 | -0.006293 | -0.0015771 | 0.006293 | 0.0015771 | 3.378e-09 | 8.5092e-10 | 0.0094275 | 0.0094275 | 0.0094275 | 0.99328 | -0.1287 | 0.99328 | -0.12869 | 2.59
20 | -0.0090291 | -0.0022628 | 0.0090305 | 0.0022634 | 1.387e-06 | 6.2597e-07 | 0.013526 | 0.013526 | 0.013526 | 0.99328 | -0.12869 | 0.99344 | -0.12546 | 3.716
21 | -0.013288 | -0.0033305 | 0.013289 | 0.0033309 | 6.8774e-07 | 3.8021e-07 | 0.019903 | 0.019903 | 0.019903 | 0.99344 | -0.12546 | 0.9935 | -0.12437 | 5.468
22 | -0.02167 | -0.0054314 | 0.021679 | 0.0054366 | 8.5574e-06 | 5.1961e-06 | 0.032457 | 0.032457 | 0.032457 | 0.9935 | -0.12437 | 0.99393 | -0.11609 | 8.9167
23 | -0.028054 | -0.0070344 | 0.028057 | 0.0070367 | 3.7804e-06 | 2.3454e-06 | 0.042001 | 0.042001 | 0.042001 | 0.99393 | -0.11609 | 0.99407 | -0.11326 | 11.5386
24 | -0.036084 | -0.0090484 | 0.036096 | 0.009056 | 1.2142e-05 | 7.627e-06 | 0.054016 | 0.054016 | 0.054016 | 0.99407 | -0.11326 | 0.99444 | -0.1062 | 14.8395
25 | -0.042995 | -0.010785 | 0.043004 | 0.010791 | 9.3264e-06 | 5.8909e-06 | 0.064338 | 0.064338 | 0.064338 | 0.99444 | -0.1062 | 0.99468 | -0.10165 | 17.6753
26 | 0.056279 | 0.014165 | -0.056225 | -0.014131 | 5.3597e-05 | 3.4038e-05 | 0.083994 | 0.083994 | 0.083994 | 0.99728 | -0.05153 | 0.99624 | -0.071476 | 23.0753
27 | -0.060681 | -0.015268 | 0.06069 | 0.015274 | 8.9506e-06 | 5.6904e-06 | 0.090561 | 0.090561 | 0.090561 | 0.99728 | -0.05153 | 0.99744 | -0.048443 | 24.8795
28 | 0.048658 | 0.012235 | -0.048588 | -0.01219 | 7.0021e-05 | 4.4354e-05 | 0.072692 | 0.072692 | 0.072692 | 0.99624 | -0.071476 | 0.99468 | -0.10165 | 19.9703
29 | 0.18264 | 0.046987 | -0.18244 | -0.046856 | 0.00020468 | 0.00013061 | 0.2729 | 0.27291 | 0.27291 | 0.99744 | -0.048443 | 0.99622 | -0.071522 | 37.487
30 | -0.24333 | -0.062261 | 0.2439 | 0.062626 | 0.00057211 | 0.00036555 | 0.36347 | 0.36347 | 0.36347 | 0.99744 | -0.048443 | 1 | 0 | 49.9266
31 | 0.17939 | 0.046091 | -0.17923 | -0.045994 | 0.00015179 | 9.6854e-05 | 0.26835 | 0.26835 | 0.26835 | 0.99622 | -0.071522 | 0.9953 | -0.088959 | 36.8606
32 | 0.027305 | 0.0068549 | -0.027287 | -0.0068437 | 1.8057e-05 | 1.1174e-05 | 0.040635 | 0.040635 | 0.040635 | 1 | 0 | 0.99928 | -0.013874 | 11.1634
33 | 0.1664 | 0.042778 | -0.16621 | -0.042657 | 0.00019063 | 0.00012158 | 0.24916 | 0.24916 | 0.24916 | 0.9953 | -0.088959 | 0.99405 | -0.11257 | 34.2256
34 | 0.021584 | 0.0054144 | -0.021576 | -0.0054093 | 8.44e-06 | 5.1163e-06 | 0.032143 | 0.032143 | 0.032143 | 0.99928 | -0.013874 | 0.99885 | -0.022079 | 8.8304
35 | 0.1614 | 0.04145 | -0.16128 | -0.041379 | 0.00011227 | 7.1585e-05 | 0.24196 | 0.24196 | 0.24196 | 0.99405 | -0.11257 | 0.9933 | -0.1269 | 33.2357
36 | 0.1535 | 0.039427 | -0.15332 | -0.03931 | 0.00018369 | 0.00011709 | 0.23029 | 0.23029 | 0.23029 | 0.9933 | -0.1269 | 0.992 | -0.15158 | 31.6336
37 | 0.016515 | 0.0041406 | -0.016509 | -0.0041374 | 5.5059e-06 | 3.2227e-06 | 0.02493 | 0.02493 | 0.02493 | 0.98576 | -0.27149 | 0.9854 | -0.27849 | 6.8489
38 | -0.0087787 | -0.0022001 | 0.00878 | 0.0022007 | 1.3527e-06 | 5.9017e-07 | 0.013085 | 0.013085 | 0.013085 | 0.99833 | -0.032082 | 0.9985 | -0.028848 | 3.5947
39 | -0.012108 | -0.0030348 | 0.012109 | 0.0030352 | 7.9474e-07 | 4.2349e-07 | 0.018044 | 0.018044 | 0.018044 | 0.9985 | -0.028848 | 0.99857 | -0.02747 | 4.9572
40 | -0.015436 | -0.003869 | 0.015438 | 0.0038705 | 2.5069e-06 | 1.4391e-06 | 0.023002 | 0.023002 | 0.023002 | 0.99857 | -0.02747 | 0.99875 | -0.024062 | 6.3191
41 | -0.018506 | -0.0046394 | 0.018508 | 0.0046404 | 1.7485e-06 | 1.0388e-06 | 0.027572 | 0.027572 | 0.027572 | 0.99875 | -0.024062 | 0.99885 | -0.022079 | 7.5748

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28126 | 0.071587

## res_load
| p_mw | q_mvar
0 | 0.0044324 | 0.0011109
1 | 0.0048298 | 0.0012105
2 | 0.0046131 | 0.0011562
3 | 0.0078789 | 0.0019746
4 | 0.0090426 | 0.0022663
5 | 0.0087922 | 0.0022035
6 | 0.010216 | 0.0025604
7 | 0.0022623 | 0.00056699
8 | 0.0089736 | 0.002249
9 | 0.014295 | 0.0035827
10 | 0.011172 | 0.0027999
11 | 0.0067257 | 0.0016856
12 | 0.050415 | 0.012635
13 | 0.0035568 | 0.00089141
14 | 0.0027362 | 0.00068575
15 | 0.002736 | 0.00068571
16 | 0.0042576 | 0.0010671
17 | 0.0083815 | 0.0021006
18 | 0.006375 | 0.0015977
19 | 0.0080268 | 0.0020117
20 | 0.0068984 | 0.0017289
21 | 0.0044015 | 0.0011031
22 | 0.0075672 | 0.0018965
23 | 0.0055842 | 0.0013995
24 | 0.0030528 | 0.00076511
25 | 0.0084 | 0.0021052
26 | 0.012831 | 0.0032158
27 | 0.0057029 | 0.0014293
28 | 0.0048144 | 0.0012066
29 | 0.007786 | 0.0019514
30 | 0.0016663 | 0.00041761
31 | 0.0026295 | 0.00065902
32 | 0.0087787 | 0.0022001
33 | 0.003328 | 0.00083408
34 | 0.0033268 | 0.00083379
35 | 0.0030679 | 0.00076889
36 | 0.0030689 | 0.00076913
37 | 0.0030679 | 0.00076888

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1