## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1507-20_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1507-20_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1507-20_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1507-20_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1507-20_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1507-20_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1507-20_0_4_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1507-20_0_4_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_1507-20_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_1507-20_0_4_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_1507-20_0_4_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_1507-20_0_4_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_1507-20_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1507-20_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1507-20_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1507-20_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1507-20_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1507-20_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1507-20_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1507-20_0_4_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_1507-20_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1507-20_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1507-20_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1507-20_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1507-20_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1507-20_0_4_node_27 | 0.4 | n |  | TRUE
26 | bus_MV_23_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1507-20_0_4_load_0 | 0 | 0.0081814 | 0.0020505 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1507-20_0_4_load_1 | 1 | 0.09942 | 0.024917 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1507-20_0_4_load_2 | 2 | 0.050252 | 0.012594 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1507-20_0_4_load_3 | 3 | 0.0033489 | 0.00083931 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1507-20_0_4_load_4 | 4 | 0.016945 | 0.0042469 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1507-20_0_4_load_5 | 5 | 0.008471 | 0.002123 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1507-20_0_4_load_17 | 6 | 0.0053234 | 0.0013342 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1507-20_0_4_load_18 | 7 | 0.0052327 | 0.0013114 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1507-20_0_4_load_19 | 8 | 0.0066116 | 0.001657 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1507-20_0_4_load_26 | 9 | 0.0065032 | 0.0016299 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1507-20_0_4_load_23 | 10 | 0.043029 | 0.010784 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1507-20_0_4_load_10 | 13 | 0.044242 | 0.011088 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1507-20_0_4_load_6 | 14 | 0.007313 | 0.0018328 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1507-20_0_4_load_7 | 15 | 0.024106 | 0.0060416 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1507-20_0_4_load_9 | 16 | 0.0087264 | 0.002187 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1507-20_0_4_load_12 | 17 | 0.028401 | 0.0071181 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1507-20_0_4_load_13 | 18 | 0.015457 | 0.0038739 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1507-20_0_4_load_22 | 19 | 0.010514 | 0.0026351 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1507-20_0_4_load_14 | 20 | 0.02828 | 0.0070877 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1507-20_0_4_load_15 | 21 | 0.012098 | 0.003032 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1507-20_0_4_load_16 | 22 | 0.012207 | 0.0030595 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1507-20_0_4_load_21 | 23 | 0.011575 | 0.0029011 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1507-20_0_4_load_24 | 24 | 0.0042555 | 0.0010665 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1507-20_0_4_load_27 | 25 | 0.01434 | 0.0035939 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1507-20_0_4_line_0 |  | 0 | 1 | 0.011754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1507-20_0_4_line_1 |  | 0 | 2 | 0.023791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1507-20_0_4_line_2 |  | 1 | 3 | 0.026578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1507-20_0_4_line_3 |  | 2 | 4 | 0.010435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1507-20_0_4_line_4 |  | 3 | 5 | 0.0072562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1507-20_0_4_line_5 |  | 4 | 12 | 0.012873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1507-20_0_4_line_6 |  | 6 | 7 | 0.013888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1507-20_0_4_line_7 |  | 6 | 8 | 0.019023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1507-20_0_4_line_8 |  | 6 | 9 | 0.095361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1507-20_0_4_line_9 |  | 7 | 11 | 0.021041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1507-20_0_4_line_10 |  | 9 | 25 | 0.026847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1507-20_0_4_line_11 |  | 10 | 11 | 0.025851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1507-20_0_4_line_12 |  | 11 | 19 | 0.023597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1507-20_0_4_line_13 |  | 12 | 13 | 0.027864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1507-20_0_4_line_14 |  | 12 | 14 | 0.024832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1507-20_0_4_line_15 |  | 13 | 17 | 0.044039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1507-20_0_4_line_16 |  | 14 | 15 | 0.014022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1507-20_0_4_line_17 |  | 15 | 16 | 0.0086526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1507-20_0_4_line_18 |  | 17 | 18 | 0.011922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1507-20_0_4_line_19 |  | 18 | 19 | 0.094846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1507-20_0_4_line_20 |  | 19 | 23 | 0.027696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1507-20_0_4_line_21 |  | 20 | 21 | 0.0123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1507-20_0_4_line_22 |  | 21 | 22 | 0.033503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1507-20_0_4_line_23 |  | 22 | 23 | 0.01168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1507-20_0_4_line_24 |  | 24 | 25 | 0.035994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1507-20_0_4_trafo_10 | 0.63 MVA 20/0.4 kV | 26 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2666309.9193 | 1205281.5696 | 2666309.5346 | 1205286.9942 | 2666309.6408 | 1205293.188 | 2666309.6631 | 1205293.3067
1 | 2666309.9193 | 1205281.5696 | 2666311.602 | 1205257.8377
2 | 2666309.6631 | 1205293.3067 | 2666310.6751 | 1205298.6806 | 2666313.9136 | 1205303.6529 | 2666324.1487 | 1205314.8572
3 | 2666311.9188 | 1205247.4248 | 2666312.0962 | 1205250.8674 | 2666311.602 | 1205257.8377
4 | 2666329.0426 | 1205320.2146 | 2666324.1487 | 1205314.8572
5 | 2666309.5657 | 1205234.8852 | 2666311.5893 | 1205241.0336 | 2666311.9188 | 1205247.4248
6 | 2666180.3007 | 1205302.492 | 2666182.5655 | 1205288.7901
7 | 2666180.3007 | 1205302.492 | 2666179.6623 | 1205306.3545 | 2666179.8381 | 1205312.4491 | 2666183.5701 | 1205320.6514
8 | 2666180.3007 | 1205302.492 | 2666086.2847 | 1205318.4503
9 | 2666193.3018 | 1205271.3067 | 2666190.4555 | 1205274.1769 | 2666186.4248 | 1205278.2124 | 2666182.8503 | 1205287.0671 | 2666182.5655 | 1205288.7901
10 | 2666086.2847 | 1205318.4503 | 2666079.9389 | 1205302.1146 | 2666076.3065 | 1205293.5295
11 | 2666193.3018 | 1205271.3067 | 2666209.1032 | 1205291.7663
12 | 2666193.3018 | 1205271.3067 | 2666177.8005 | 1205253.515
13 | 2666309.5657 | 1205234.8852 | 2666306.8821 | 1205231.3199 | 2666306.1024 | 1205230.2884 | 2666299.5148 | 1205224.812 | 2666288.4314 | 1205217.0305
14 | 2666309.5657 | 1205234.8852 | 2666312.7655 | 1205227.5941 | 2666313.9011 | 1205210.7628
15 | 2666288.4314 | 1205217.0305 | 2666286.5624 | 1205215.7183 | 2666283.2478 | 1205213.4801 | 2666274.4895 | 1205207.5682 | 2666267.3229 | 1205202.1632 | 2666259.8374 | 1205196.7102 | 2666252.4357 | 1205191.6762
16 | 2666313.9011 | 1205210.7628 | 2666314.2316 | 1205205.8638 | 2666314.7789 | 1205196.7683
17 | 2666314.7789 | 1205196.7683 | 2666315.2986 | 1205188.1313
18 | 2666252.4357 | 1205191.6762 | 2666247.6896 | 1205188.4483 | 2666242.9001 | 1205184.5387
19 | 2666242.9001 | 1205184.5387 | 2666177.8005 | 1205253.515
20 | 2666158.7829 | 1205233.3939 | 2666172.3605 | 1205247.2712 | 2666177.8005 | 1205253.515
21 | 2666117.1957 | 1205193.7235 | 2666126.1681 | 1205202.1365
22 | 2666126.1681 | 1205202.1365 | 2666150.6079 | 1205225.0525
23 | 2666158.7829 | 1205233.3939 | 2666150.7733 | 1205225.2076 | 2666150.6079 | 1205225.0525
24 | 2666076.3065 | 1205293.5295 | 2666045.9695 | 1205312.9011

## bus_geodata
| x | y | coords
0 | 2666309.9193 | 1205281.5696
1 | 2666309.6631 | 1205293.3067
2 | 2666311.602 | 1205257.8377
3 | 2666324.1487 | 1205314.8572
4 | 2666311.9188 | 1205247.4248
5 | 2666329.0426 | 1205320.2146
6 | 2666180.3007 | 1205302.492
7 | 2666182.5655 | 1205288.7901
8 | 2666183.5701 | 1205320.6514
9 | 2666086.2847 | 1205318.4503
10 | 2666209.1032 | 1205291.7662
11 | 2666193.3018 | 1205271.3067
12 | 2666309.5657 | 1205234.8852
13 | 2666288.4314 | 1205217.0305
14 | 2666313.9011 | 1205210.7628
15 | 2666314.7789 | 1205196.7683
16 | 2666315.2986 | 1205188.1313
17 | 2666252.4357 | 1205191.6762
18 | 2666242.9001 | 1205184.5387
19 | 2666177.8005 | 1205253.515
20 | 2666117.1957 | 1205193.7235
21 | 2666126.1681 | 1205202.1365
22 | 2666150.6079 | 1205225.0525
23 | 2666158.7829 | 1205233.3939
24 | 2666045.9695 | 1205312.9011
25 | 2666076.3065 | 1205293.5295
26 | 2666275.4659 | 1205208.2273

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99261 | -0.142 | 0.0081814 | 0.0020505
1 | 0.99141 | -0.16516 | 0.09942 | 0.024917
2 | 0.99521 | -0.091872 | 0.050252 | 0.012594
3 | 0.99113 | -0.17073 | 0.0033489 | 0.00083931
4 | 0.99602 | -0.076306 | 0.016945 | 0.0042469
5 | 0.99107 | -0.17182 | 0.008471 | 0.002123
6 | 0.98477 | -0.29271 | 0.0053234 | 0.0013342
7 | 0.98525 | -0.28347 | 0.0052327 | 0.0013114
8 | 0.98466 | -0.29497 | 0.0066116 | 0.001657
9 | 0.98256 | -0.33582 | 0.0065032 | 0.0016299
10 | 0.98504 | -0.28747 | 0.043029 | 0.010784
11 | 0.98607 | -0.26751 | 0 | 0
12 | 0.99712 | -0.055226 | 0 | 0
13 | 1 | 0 | -0.43607 | -0.11036
14 | 0.99621 | -0.072718 | 0.007313 | 0.0018328
15 | 0.99579 | -0.080807 | 0.024106 | 0.0060416
16 | 0.99572 | -0.082135 | 0.0087264 | 0.002187
17 | 0.99587 | -0.078558 | 0.028401 | 0.0071181
18 | 0.99491 | -0.096956 | 0.015457 | 0.0038739
19 | 0.98792 | -0.23149 | 0.010514 | 0.0026351
20 | 0.98415 | -0.30485 | 0.02828 | 0.0070877
21 | 0.98447 | -0.29859 | 0.012098 | 0.003032
22 | 0.98572 | -0.27429 | 0.012207 | 0.0030595
23 | 0.98628 | -0.26328 | 0.011575 | 0.0029011
24 | 0.98196 | -0.34761 | 0.0042555 | 0.0010665
25 | 0.9821 | -0.34484 | 0.01434 | 0.0035939
26 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.11137 | 0.02796 | -0.11124 | -0.027881 | 0.00012287 | 7.8488e-05 | 0.16697 | 0.16697 | 0.16697 | 0.99261 | -0.142 | 0.99141 | -0.16516 | 45.8697
1 | -0.11955 | -0.03001 | 0.11983 | 0.030193 | 0.0002866 | 0.00018312 | 0.17923 | 0.17923 | 0.17923 | 0.99261 | -0.142 | 0.99521 | -0.091872 | 49.2391
2 | 0.011823 | 0.0029642 | -0.01182 | -0.0029625 | 3.1388e-06 | 1.6662e-06 | 0.017746 | 0.017746 | 0.017746 | 0.99141 | -0.16516 | 0.99113 | -0.17073 | 4.8753
3 | -0.17009 | -0.042788 | 0.17021 | 0.042868 | 0.00012659 | 8.0748e-05 | 0.25437 | 0.25437 | 0.25437 | 0.99521 | -0.091872 | 0.99602 | -0.076306 | 34.9404
4 | 0.0084714 | 0.0021232 | -0.008471 | -0.002123 | 4.4016e-07 | 1.8819e-07 | 0.012718 | 0.012718 | 0.012718 | 0.99113 | -0.17073 | 0.99107 | -0.17182 | 3.4941
5 | -0.18716 | -0.047115 | 0.18735 | 0.047236 | 0.0001888 | 0.00012049 | 0.27968 | 0.27968 | 0.27968 | 0.99602 | -0.076306 | 0.99712 | -0.055226 | 38.4178
6 | -0.037094 | -0.0093182 | 0.037111 | 0.0093285 | 1.6366e-05 | 1.0298e-05 | 0.056058 | 0.056058 | 0.056058 | 0.98477 | -0.29271 | 0.98525 | -0.28347 | 15.4006
7 | 0.0066123 | 0.0016572 | -0.0066116 | -0.001657 | 7.1215e-07 | 2.1377e-07 | 0.0099913 | 0.0099914 | 0.0099914 | 0.98477 | -0.29271 | 0.98466 | -0.29497 | 2.7449
8 | 0.025159 | 0.0063268 | -0.025107 | -0.0062949 | 5.1701e-05 | 3.1878e-05 | 0.038023 | 0.038024 | 0.038024 | 0.98477 | -0.29271 | 0.98256 | -0.33582 | 10.446
9 | -0.042343 | -0.01064 | 0.042376 | 0.01066 | 3.228e-05 | 2.0391e-05 | 0.063961 | 0.063961 | 0.063961 | 0.98525 | -0.28347 | 0.98607 | -0.26751 | 17.5718
10 | 0.018604 | 0.0046651 | -0.018596 | -0.0046603 | 7.992e-06 | 4.775e-06 | 0.028175 | 0.028175 | 0.028175 | 0.98256 | -0.33582 | 0.9821 | -0.34484 | 7.7404
11 | -0.043029 | -0.010784 | 0.04307 | 0.01081 | 4.0958e-05 | 2.5884e-05 | 0.065 | 0.065 | 0.065 | 0.98504 | -0.28747 | 0.98607 | -0.26751 | 17.8572
12 | -0.085446 | -0.02147 | 0.085593 | 0.021564 | 0.00014717 | 9.3885e-05 | 0.12896 | 0.12896 | 0.12896 | 0.98607 | -0.26751 | 0.98792 | -0.23149 | 35.4289
13 | -0.22754 | -0.057326 | 0.22814 | 0.057712 | 0.00060278 | 0.00038505 | 0.33967 | 0.33967 | 0.33967 | 0.99712 | -0.055226 | 1 | 0 | 46.6577
14 | 0.040193 | 0.010091 | -0.040159 | -0.01007 | 3.3508e-05 | 2.1121e-05 | 0.059986 | 0.059987 | 0.059987 | 0.99712 | -0.055226 | 0.99621 | -0.072718 | 16.4798
15 | 0.20628 | 0.052646 | -0.2055 | -0.052149 | 0.0007797 | 0.00049785 | 0.30729 | 0.30729 | 0.30729 | 1 | 0 | 0.99587 | -0.078558 | 42.2098
16 | 0.032846 | 0.0082368 | -0.032833 | -0.0082289 | 1.2658e-05 | 7.9185e-06 | 0.049063 | 0.049063 | 0.049063 | 0.99621 | -0.072718 | 0.99579 | -0.080807 | 13.4789
17 | 0.008727 | 0.0021873 | -0.0087264 | -0.002187 | 5.5181e-07 | 2.406e-07 | 0.013041 | 0.013041 | 0.013041 | 0.99579 | -0.080807 | 0.99572 | -0.082135 | 3.5827
18 | 0.1771 | 0.045031 | -0.17694 | -0.044931 | 0.00015681 | 0.00010005 | 0.26485 | 0.26485 | 0.26485 | 0.99587 | -0.078558 | 0.99491 | -0.096956 | 36.3806
19 | 0.16149 | 0.041057 | -0.16045 | -0.040394 | 0.0010392 | 0.00066263 | 0.24173 | 0.24173 | 0.24173 | 0.99491 | -0.096956 | 0.98792 | -0.23149 | 33.2052
20 | 0.064341 | 0.016195 | -0.064244 | -0.016133 | 9.7593e-05 | 6.2105e-05 | 0.096936 | 0.096936 | 0.096936 | 0.98792 | -0.23149 | 0.98628 | -0.26328 | 26.6308
21 | -0.02828 | -0.0070877 | 0.028289 | 0.0070929 | 8.4329e-06 | 5.2407e-06 | 0.042759 | 0.042759 | 0.042759 | 0.98415 | -0.30485 | 0.98447 | -0.29859 | 11.747
22 | -0.040386 | -0.010125 | 0.040433 | 0.010154 | 4.6817e-05 | 2.9536e-05 | 0.061044 | 0.061044 | 0.061044 | 0.98447 | -0.29859 | 0.98572 | -0.27429 | 16.7704
23 | -0.05264 | -0.013214 | 0.052668 | 0.013231 | 2.7663e-05 | 1.7555e-05 | 0.079472 | 0.079472 | 0.079472 | 0.98572 | -0.27429 | 0.98628 | -0.26328 | 21.833
24 | -0.0042555 | -0.0010665 | 0.0042561 | 0.0010664 | 5.6129e-07 | -9.6177e-08 | 0.0064486 | 0.0064484 | 0.0064486 | 0.98196 | -0.34761 | 0.9821 | -0.34484 | 1.7716

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48032 | 0.12145

## res_load
| p_mw | q_mvar
0 | 0.0081814 | 0.0020505
1 | 0.09942 | 0.024917
2 | 0.050252 | 0.012594
3 | 0.0033489 | 0.00083931
4 | 0.016945 | 0.0042469
5 | 0.008471 | 0.002123
6 | 0.0053234 | 0.0013342
7 | 0.0052327 | 0.0013114
8 | 0.0066116 | 0.001657
9 | 0.0065032 | 0.0016299
10 | 0.043029 | 0.010784
11 | 0.044242 | 0.011088
12 | 0.007313 | 0.0018328
13 | 0.024106 | 0.0060416
14 | 0.0087264 | 0.002187
15 | 0.028401 | 0.0071181
16 | 0.015457 | 0.0038739
17 | 0.010514 | 0.0026351
18 | 0.02828 | 0.0070877
19 | 0.012098 | 0.003032
20 | 0.012207 | 0.0030595
21 | 0.011575 | 0.0029011
22 | 0.0042555 | 0.0010665
23 | 0.01434 | 0.0035939

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1