## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1507-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1507-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1507-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1507-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1507-4_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1507-4_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1507-4_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_1507-4_0_4_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1507-4_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1507-4_0_4_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_1507-4_0_4_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_1507-4_0_4_node_34 | 0.4 | n |  | TRUE
12 | bus_LV_1507-4_0_4_node_55 | 0.4 | n |  | TRUE
13 | bus_LV_1507-4_0_4_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_1507-4_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1507-4_0_4_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_1507-4_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1507-4_0_4_node_61 | 0.4 | n |  | TRUE
18 | bus_LV_1507-4_0_4_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1507-4_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1507-4_0_4_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_1507-4_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1507-4_0_4_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1507-4_0_4_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1507-4_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1507-4_0_4_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_1507-4_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1507-4_0_4_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_1507-4_0_4_node_77 | 0.4 | n |  | TRUE
29 | bus_LV_1507-4_0_4_node_69 | 0.4 | n |  | TRUE
30 | bus_LV_1507-4_0_4_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_1507-4_0_4_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_1507-4_0_4_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_1507-4_0_4_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_1507-4_0_4_node_60 | 0.4 | n |  | TRUE
35 | bus_LV_1507-4_0_4_node_59 | 0.4 | n |  | TRUE
36 | bus_LV_1507-4_0_4_node_56 | 0.4 | n |  | TRUE
37 | bus_LV_1507-4_0_4_node_57 | 0.4 | n |  | TRUE
38 | bus_LV_1507-4_0_4_node_49 | 0.4 | n |  | TRUE
39 | bus_LV_1507-4_0_4_node_46 | 0.4 | n |  | TRUE
40 | bus_LV_1507-4_0_4_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1507-4_0_4_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_1507-4_0_4_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_1507-4_0_4_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_1507-4_0_4_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_1507-4_0_4_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_1507-4_0_4_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_1507-4_0_4_node_52 | 0.4 | n |  | TRUE
48 | bus_LV_1507-4_0_4_node_76 | 0.4 | n |  | TRUE
49 | bus_LV_1507-4_0_4_node_53 | 0.4 | n |  | TRUE
50 | bus_LV_1507-4_0_4_node_75 | 0.4 | n |  | TRUE
51 | bus_LV_1507-4_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_1507-4_0_4_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_1507-4_0_4_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_1507-4_0_4_node_64 | 0.4 | n |  | TRUE
55 | bus_LV_1507-4_0_4_node_62 | 0.4 | n |  | TRUE
56 | bus_LV_1507-4_0_4_node_89 | 0.4 | n |  | TRUE
57 | bus_LV_1507-4_0_4_node_38 | 0.4 | n |  | TRUE
58 | bus_LV_1507-4_0_4_node_39 | 0.4 | n |  | TRUE
59 | bus_LV_1507-4_0_4_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_1507-4_0_4_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_1507-4_0_4_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_1507-4_0_4_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_1507-4_0_4_node_73 | 0.4 | n |  | TRUE
64 | bus_LV_1507-4_0_4_node_67 | 0.4 | n |  | TRUE
65 | bus_LV_1507-4_0_4_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_1507-4_0_4_node_71 | 0.4 | n |  | TRUE
67 | bus_LV_1507-4_0_4_node_65 | 0.4 | n |  | TRUE
68 | bus_LV_1507-4_0_4_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_1507-4_0_4_node_50 | 0.4 | n |  | TRUE
70 | bus_LV_1507-4_0_4_node_79 | 0.4 | n |  | TRUE
71 | bus_LV_1507-4_0_4_node_74 | 0.4 | n |  | TRUE
72 | bus_LV_1507-4_0_4_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_1507-4_0_4_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_1507-4_0_4_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_1507-4_0_4_node_86 | 0.4 | n |  | TRUE
76 | bus_LV_1507-4_0_4_node_83 | 0.4 | n |  | TRUE
77 | bus_LV_1507-4_0_4_node_80 | 0.4 | n |  | TRUE
78 | bus_LV_1507-4_0_4_node_81 | 0.4 | n |  | TRUE
79 | bus_LV_1507-4_0_4_node_82 | 0.4 | n |  | TRUE
80 | bus_LV_1507-4_0_4_node_84 | 0.4 | n |  | TRUE
81 | bus_LV_1507-4_0_4_node_85 | 0.4 | n |  | TRUE
82 | bus_MV_24_0_node_7 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1507-4_0_4_load_0 | 0 | 0.0063572 | 0.0015933 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1507-4_0_4_load_5 | 4 | 0.0082805 | 0.0020753 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1507-4_0_4_load_6 | 5 | 0.009143 | 0.0022914 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1507-4_0_4_load_19 | 7 | 0.0061672 | 0.0015457 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1507-4_0_4_load_7 | 8 | 0.0060883 | 0.0015259 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1507-4_0_4_load_17 | 9 | 0.0059029 | 0.0014794 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1507-4_0_4_load_34 | 11 | 0.011794 | 0.0029559 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1507-4_0_4_load_55 | 12 | 0.025302 | 0.0063414 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1507-4_0_4_load_28 | 15 | 0.0033063 | 0.00082863 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1507-4_0_4_load_8 | 16 | 0.018443 | 0.0046223 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1507-4_0_4_load_61 | 17 | 0.0054335 | 0.0013618 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1507-4_0_4_load_27 | 20 | 0.0033062 | 0.00082861 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1507-4_0_4_load_10 | 21 | 0.031448 | 0.0078817 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1507-4_0_4_load_22 | 22 | 0.0092973 | 0.0023301 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1507-4_0_4_load_24 | 23 | 0.010865 | 0.0027229 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1507-4_0_4_load_21 | 24 | 0.059989 | 0.015035 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1507-4_0_4_load_12 | 25 | 0.010875 | 0.0027255 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1507-4_0_4_load_23 | 26 | 0.014997 | 0.0037587 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1507-4_0_4_load_13 | 27 | 0.0086951 | 0.0021792 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1507-4_0_4_load_77 | 28 | 0.00011501 | 2.8824e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1507-4_0_4_load_69 | 29 | 0.00032717 | 8.1997e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1507-4_0_4_load_54 | 30 | 0.0025413 | 0.00063691 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1507-4_0_4_load_14 | 31 | 0.014522 | 0.0036396 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1507-4_0_4_load_20 | 32 | 0.025254 | 0.0063293 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1507-4_0_4_load_51 | 33 | 0.010279 | 0.0025763 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1507-4_0_4_load_56 | 36 | 0.015531 | 0.0038925 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1507-4_0_4_load_57 | 37 | 0.005389 | 0.0013506 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1507-4_0_4_load_32 | 40 | 0.011454 | 0.0028706 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1507-4_0_4_load_29 | 43 | 0.0053327 | 0.0013365 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1507-4_0_4_load_30 | 44 | 0.009187 | 0.0023025 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1507-4_0_4_load_33 | 46 | 0.0034911 | 0.00087494 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1507-4_0_4_load_52 | 47 | 0.028521 | 0.0071481 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1507-4_0_4_load_53 | 49 | 0.0079543 | 0.0019935 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1507-4_0_4_load_75 | 50 | 0.0097833 | 0.0024519 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1507-4_0_4_load_44 | 53 | 0.0059242 | 0.0014847 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1507-4_0_4_load_64 | 54 | 0.017806 | 0.0044626 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1507-4_0_4_load_62 | 55 | 0.010716 | 0.0026857 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1507-4_0_4_load_89 | 56 | 0.01589 | 0.0039824 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1507-4_0_4_load_38 | 57 | 0.00011652 | 2.9202e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1507-4_0_4_load_39 | 58 | 0.0057821 | 0.0014491 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1507-4_0_4_load_43 | 62 | 0.00016739 | 4.1951e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1507-4_0_4_load_73 | 63 | 0.0012827 | 0.00032148 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1507-4_0_4_load_47 | 65 | 0.006008 | 0.0015058 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1507-4_0_4_load_71 | 66 | 0.0048258 | 0.0012095 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1507-4_0_4_load_65 | 67 | 0.00012848 | 3.2199e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1507-4_0_4_load_48 | 68 | 0.004785 | 0.0011992 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1507-4_0_4_load_50 | 69 | 0.00095497 | 0.00023934 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1507-4_0_4_load_79 | 70 | 0.014046 | 0.0035202 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1507-4_0_4_load_66 | 72 | 0.0010269 | 0.00025738 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1507-4_0_4_load_68 | 73 | 0.0020388 | 0.00051097 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1507-4_0_4_load_72 | 74 | 0.0021812 | 0.00054665 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1507-4_0_4_load_86 | 75 | 0.0011174 | 0.00028006 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1507-4_0_4_load_80 | 77 | 0.0034871 | 0.00087395 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1507-4_0_4_load_81 | 78 | 0.010906 | 0.0027333 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1507-4_0_4_load_84 | 80 | 0.0034209 | 0.00085736 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1507-4_0_4_load_85 | 81 | 0.0034874 | 0.00087403 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1507-4_0_4_line_0 |  | 0 | 1 | 0.012948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1507-4_0_4_line_1 |  | 0 | 2 | 0.016403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1507-4_0_4_line_2 |  | 1 | 3 | 0.008807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1507-4_0_4_line_3 |  | 2 | 4 | 0.011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1507-4_0_4_line_4 |  | 2 | 5 | 0.010289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1507-4_0_4_line_5 |  | 3 | 6 | 0.043163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1507-4_0_4_line_6 |  | 3 | 7 | 0.020088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1507-4_0_4_line_7 |  | 4 | 8 | 0.028131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1507-4_0_4_line_8 |  | 5 | 9 | 0.020712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1507-4_0_4_line_9 |  | 6 | 10 | 0.012105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1507-4_0_4_line_10 |  | 6 | 11 | 0.029139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1507-4_0_4_line_11 |  | 7 | 13 | 0.014977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1507-4_0_4_line_12 |  | 8 | 16 | 0.00069037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1507-4_0_4_line_13 |  | 9 | 19 | 0.010471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1507-4_0_4_line_14 |  | 10 | 12 | 0.0094245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1507-4_0_4_line_15 |  | 11 | 42 | 0.025114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1507-4_0_4_line_16 |  | 13 | 32 | 0.015453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1507-4_0_4_line_17 |  | 14 | 15 | 0.010287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1507-4_0_4_line_18 |  | 14 | 16 | 0.024509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1507-4_0_4_line_19 |  | 15 | 20 | 0.0074436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1507-4_0_4_line_20 |  | 17 | 18 | 0.01126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1507-4_0_4_line_21 |  | 18 | 19 | 0.021698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1507-4_0_4_line_22 |  | 19 | 31 | 0.014684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1507-4_0_4_line_23 |  | 21 | 22 | 0.045324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1507-4_0_4_line_24 |  | 22 | 23 | 0.018799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1507-4_0_4_line_25 |  | 22 | 24 | 0.014329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1507-4_0_4_line_26 |  | 23 | 39 | 0.032491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1507-4_0_4_line_27 |  | 24 | 26 | 0.024287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1507-4_0_4_line_28 |  | 25 | 26 | 0.029213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1507-4_0_4_line_29 |  | 27 | 28 | 0.036124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1507-4_0_4_line_30 |  | 27 | 29 | 0.049149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1507-4_0_4_line_31 |  | 28 | 30 | 0.01384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1507-4_0_4_line_32 |  | 30 | 60 | 0.07174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1507-4_0_4_line_33 |  | 32 | 33 | 0.009543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1507-4_0_4_line_34 |  | 33 | 38 | 0.022524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1507-4_0_4_line_35 |  | 34 | 35 | 0.030961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1507-4_0_4_line_36 |  | 34 | 36 | 0.021266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1507-4_0_4_line_37 |  | 35 | 37 | 0.0024977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1507-4_0_4_line_38 |  | 36 | 69 | 0.023735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1507-4_0_4_line_39 |  | 38 | 65 | 0.0057211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1507-4_0_4_line_40 |  | 38 | 60 | 0.038454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1507-4_0_4_line_41 |  | 39 | 40 | 0.0079279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1507-4_0_4_line_42 |  | 39 | 41 | 0.031277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_1507-4_0_4_line_43 |  | 40 | 44 | 0.020633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1507-4_0_4_line_44 |  | 41 | 56 | 0.009039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1507-4_0_4_line_45 |  | 41 | 51 | 0.020957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1507-4_0_4_line_46 |  | 42 | 51 | 0.014352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_1507-4_0_4_line_47 |  | 42 | 52 | 0.012735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1507-4_0_4_line_48 |  | 43 | 44 | 0.022293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1507-4_0_4_line_49 |  | 43 | 45 | 0.023924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1507-4_0_4_line_50 |  | 45 | 46 | 0.059042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1507-4_0_4_line_51 |  | 46 | 47 | 0.0094371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1507-4_0_4_line_52 |  | 46 | 48 | 0.055852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1507-4_0_4_line_53 |  | 47 | 49 | 0.0059515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1507-4_0_4_line_54 |  | 48 | 50 | 0.0045669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1507-4_0_4_line_55 |  | 51 | 53 | 0.0036709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1507-4_0_4_line_56 |  | 52 | 54 | 0.044766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1507-4_0_4_line_57 |  | 52 | 55 | 0.003403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1507-4_0_4_line_58 |  | 57 | 58 | 0.004925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1507-4_0_4_line_59 |  | 57 | 59 | 0.016722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1507-4_0_4_line_60 |  | 58 | 60 | 0.022413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1507-4_0_4_line_61 |  | 59 | 61 | 0.032073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1507-4_0_4_line_62 |  | 59 | 62 | 0.0079084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1507-4_0_4_line_63 |  | 61 | 63 | 0.012492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1507-4_0_4_line_64 |  | 62 | 64 | 0.027952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1507-4_0_4_line_65 |  | 63 | 66 | 0.0049421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1507-4_0_4_line_66 |  | 64 | 67 | 0.0027858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1507-4_0_4_line_67 |  | 65 | 68 | 0.016667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1507-4_0_4_line_68 |  | 66 | 74 | 0.025797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1507-4_0_4_line_69 |  | 67 | 72 | 0.0044464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1507-4_0_4_line_70 |  | 68 | 69 | 0.00034432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1507-4_0_4_line_71 |  | 70 | 71 | 0.033942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1507-4_0_4_line_72 |  | 71 | 75 | 0.01499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1507-4_0_4_line_73 |  | 71 | 74 | 0.043851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1507-4_0_4_line_74 |  | 72 | 73 | 0.036248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1507-4_0_4_line_75 |  | 75 | 76 | 0.0071795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1507-4_0_4_line_76 |  | 76 | 79 | 0.004516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1507-4_0_4_line_77 |  | 77 | 78 | 0.018302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1507-4_0_4_line_78 |  | 77 | 79 | 0.024146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1507-4_0_4_line_79 |  | 79 | 80 | 0.0095408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1507-4_0_4_line_80 |  | 79 | 81 | 0.007893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1507-4_0_4_trafo_55 | 0.63 MVA 20/0.4 kV | 82 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2666351.8467 | 1203810.0929 | 2666364.4997 | 1203807.3444
1 | 2666379.1705 | 1203801.102 | 2666374.2933 | 1203805.217 | 2666364.4997 | 1203807.3444
2 | 2666351.8467 | 1203810.0929 | 2666350.3453 | 1203801.4154
3 | 2666379.1705 | 1203801.102 | 2666379.3306 | 1203812.1005
4 | 2666379.1705 | 1203801.102 | 2666379.5442 | 1203790.8194
5 | 2666310.3552 | 1203810.2212 | 2666310.0308 | 1203807.9162 | 2666327.3178 | 1203805.1731 | 2666331.2434 | 1203804.5274 | 2666350.3453 | 1203801.4154
6 | 2666350.3453 | 1203801.4154 | 2666347.2561 | 1203785.6716 | 2666346.2465 | 1203781.7552
7 | 2666379.2502 | 1203840.2045 | 2666379.6839 | 1203836.3735 | 2666379.3306 | 1203812.1005
8 | 2666379.5442 | 1203790.8194 | 2666380.1132 | 1203775.1635 | 2666379.6396 | 1203770.1402
9 | 2666310.3552 | 1203810.2212 | 2666310.0308 | 1203807.9162 | 2666308.5632 | 1203798.2496
10 | 2666310.3552 | 1203810.2212 | 2666314.5087 | 1203839.0628
11 | 2666342.5075 | 1203767.2522 | 2666346.2465 | 1203781.7552
12 | 2666379.1726 | 1203840.8905 | 2666379.2502 | 1203840.2045
13 | 2666378.6567 | 1203759.7158 | 2666379.6396 | 1203770.1402
14 | 2666308.5632 | 1203798.2496 | 2666307.152 | 1203788.9313
15 | 2666316.5137 | 1203864.0665 | 2666315.8509 | 1203848.383 | 2666314.5087 | 1203839.0628
16 | 2666342.5075 | 1203767.2522 | 2666339.5911 | 1203753.0779 | 2666339.4487 | 1203752.1061
17 | 2666374.2317 | 1203864.8301 | 2666372.0888 | 1203874.8909
18 | 2666374.2317 | 1203864.8301 | 2666378.0977 | 1203850.3865 | 2666379.1726 | 1203840.8905
19 | 2666372.0888 | 1203874.8909 | 2666370.5382 | 1203882.1712
20 | 2666400.4092 | 1203759.1127 | 2666400.2051 | 1203770.3711
21 | 2666400.4092 | 1203759.1127 | 2666378.6567 | 1203759.7158
22 | 2666378.6567 | 1203759.7158 | 2666364.2813 | 1203762.7128
23 | 2666243.8235 | 1203815.3438 | 2666198.8202 | 1203820.7226
24 | 2666243.8235 | 1203815.3438 | 2666246.4775 | 1203833.9541
25 | 2666243.8235 | 1203815.3438 | 2666241.8005 | 1203801.158
26 | 2666251.0645 | 1203866.1194 | 2666246.4775 | 1203833.9541
27 | 2666238.3716 | 1203777.1139 | 2666241.8005 | 1203801.158
28 | 2666221.1505 | 1203755.3877 | 2666226.8012 | 1203757.685 | 2666230.9984 | 1203761.3671 | 2666236.0661 | 1203769.5727 | 2666238.3716 | 1203777.1139 | 2666238.3716 | 1203777.1139
29 | 2666189.92 | 1203674.7708 | 2666197.2216 | 1203675.7189 | 2666201.6282 | 1203676.9907 | 2666205.6444 | 1203678.4806 | 2666211.0237 | 1203681.2418 | 2666214.5757 | 1203683.4158 | 2666217.9564 | 1203685.9437 | 2666222.0171 | 1203689.5909
30 | 2666189.92 | 1203674.7708 | 2666216.9428 | 1203633.7177
31 | 2666222.0171 | 1203689.5909 | 2666225.2496 | 1203693.14 | 2666228.0188 | 1203696.6061 | 2666230.6974 | 1203700.3496
32 | 2666294.7912 | 1203720.1386 | 2666282.1404 | 1203719.9092 | 2666255.5716 | 1203719.1252 | 2666251.3349 | 1203718.311 | 2666248.2401 | 1203717.4428 | 2666245.5138 | 1203716.2897 | 2666242.6867 | 1203714.6129 | 2666240.2054 | 1203712.6286 | 2666236.9276 | 1203709.0568 | 2666230.6974 | 1203700.3496
33 | 2666339.4487 | 1203752.1061 | 2666338.0655 | 1203742.6638
34 | 2666333.3539 | 1203720.7002 | 2666336.26 | 1203730.3383 | 2666338.0655 | 1203742.6638
35 | 2666401.0458 | 1203723.0758 | 2666400.8361 | 1203733.035 | 2666400.7562 | 1203739.5381 | 2666408.2373 | 1203740.066 | 2666415.2168 | 1203740.5549
36 | 2666401.0458 | 1203723.0758 | 2666379.7928 | 1203722.3299
37 | 2666415.2168 | 1203740.5549 | 2666417.7082 | 1203740.7327
38 | 2666356.0721 | 1203721.4975 | 2666379.7928 | 1203722.3299
39 | 2666333.3539 | 1203720.7002 | 2666339.0715 | 1203720.9009
40 | 2666294.7912 | 1203720.1386 | 2666333.3539 | 1203720.7002
41 | 2666251.0645 | 1203866.1194 | 2666252.0212 | 1203873.9894
42 | 2666251.0645 | 1203866.1194 | 2666264.9118 | 1203866.8401 | 2666282.3949 | 1203867.6567
43 | 2666252.0212 | 1203873.9894 | 2666254.5109 | 1203894.4713
44 | 2666282.3949 | 1203867.6567 | 2666282.0428 | 1203865.1068 | 2666281.1552 | 1203858.7042
45 | 2666282.3949 | 1203867.6567 | 2666297.0409 | 1203865.6514 | 2666303.2206 | 1203864.8305
46 | 2666316.5137 | 1203864.0665 | 2666309.8914 | 1203865.0047 | 2666303.3832 | 1203865.9441 | 2666303.2206 | 1203864.8305
47 | 2666316.5137 | 1203864.0665 | 2666316.1043 | 1203870.7882 | 2666315.551 | 1203876.7635
48 | 2666254.5109 | 1203894.4713 | 2666255.3733 | 1203901.5664 | 2666253.2428 | 1203905.0115 | 2666251.4167 | 1203906.381 | 2666242.7387 | 1203907.9149
49 | 2666236.9974 | 1203925.6883 | 2666234.4966 | 1203912.4415 | 2666235.0858 | 1203910.0799 | 2666238.1595 | 1203908.7243 | 2666242.7387 | 1203907.9149
50 | 2666236.9974 | 1203925.6883 | 2666222.9002 | 1203915.2702 | 2666188.3081 | 1203892.32
51 | 2666180.4443 | 1203887.1027 | 2666188.3081 | 1203892.32
52 | 2666188.3081 | 1203892.32 | 2666156.8068 | 1203938.4409
53 | 2666180.4443 | 1203887.1027 | 2666175.485 | 1203883.8125
54 | 2666156.8068 | 1203938.4409 | 2666152.4492 | 1203937.0743
55 | 2666303.2206 | 1203864.8305 | 2666302.7513 | 1203861.1898
56 | 2666315.551 | 1203876.7635 | 2666322.4511 | 1203877.5294 | 2666330.3289 | 1203871.1019 | 2666328.1677 | 1203849.2091 | 2666333.8289 | 1203848.4938
57 | 2666315.551 | 1203876.7635 | 2666315.2256 | 1203880.1509
58 | 2666296.5011 | 1203692.8536 | 2666296.193 | 1203697.769
59 | 2666297.5469 | 1203676.1648 | 2666296.5011 | 1203692.8536
60 | 2666294.7912 | 1203720.1386 | 2666296.193 | 1203697.769
61 | 2666297.5469 | 1203676.1648 | 2666305.8457 | 1203676.3793 | 2666317.5293 | 1203676.7091 | 2666322.8039 | 1203675.8672 | 2666324.9818 | 1203672.9674 | 2666325.1086 | 1203669.778
62 | 2666297.5469 | 1203676.1648 | 2666298.3468 | 1203668.297
63 | 2666325.1086 | 1203669.778 | 2666333.5903 | 1203666.548 | 2666335.7409 | 1203663.8943
64 | 2666301.9138 | 1203640.5807 | 2666299.5712 | 1203656.2531 | 2666298.3468 | 1203668.297
65 | 2666338.8526 | 1203660.0547 | 2666335.7409 | 1203663.8943
66 | 2666301.9138 | 1203640.5807 | 2666302.4993 | 1203637.8571
67 | 2666339.0715 | 1203720.9009 | 2666355.728 | 1203721.4854
68 | 2666338.8526 | 1203660.0547 | 2666342.5469 | 1203655.4963 | 2666360.6295 | 1203647.1179
69 | 2666302.4993 | 1203637.8571 | 2666303.4338 | 1203633.51
70 | 2666355.728 | 1203721.4854 | 2666356.0721 | 1203721.4975
71 | 2666401.4114 | 1203632.7142 | 2666401.3339 | 1203666.6558
72 | 2666401.4114 | 1203632.7142 | 2666401.3878 | 1203617.7243
73 | 2666401.4114 | 1203632.7142 | 2666394.0681 | 1203632.7771 | 2666391.409 | 1203633.1033 | 2666388.8266 | 1203634.0529 | 2666360.6295 | 1203647.1179
74 | 2666303.4338 | 1203633.51 | 2666305.1231 | 1203625.6518 | 2666307.7805 | 1203614.519 | 2666311.5319 | 1203602.8536 | 2666313.3873 | 1203598.7423
75 | 2666401.3764 | 1203610.5449 | 2666401.3878 | 1203617.7243
76 | 2666401.3764 | 1203610.5449 | 2666405.8989 | 1203610.295
77 | 2666430.0086 | 1203608.9781 | 2666448.2833 | 1203607.98
78 | 2666405.8989 | 1203610.295 | 2666430.0086 | 1203608.9781
79 | 2666405.8989 | 1203610.295 | 2666405.9196 | 1203607.7492 | 2666405.8374 | 1203600.7547
80 | 2666405.8989 | 1203610.295 | 2666405.8431 | 1203618.1878

## bus_geodata
| x | y | coords
0 | 2666364.4997 | 1203807.3444
1 | 2666351.8467 | 1203810.0929
2 | 2666379.1705 | 1203801.102
3 | 2666350.3453 | 1203801.4154
4 | 2666379.3306 | 1203812.1005
5 | 2666379.5442 | 1203790.8194
6 | 2666310.3552 | 1203810.2212
7 | 2666346.2465 | 1203781.7552
8 | 2666379.2502 | 1203840.2045
9 | 2666379.6396 | 1203770.1402
10 | 2666308.5632 | 1203798.2496
11 | 2666314.5087 | 1203839.0628
12 | 2666307.152 | 1203788.9313
13 | 2666342.5075 | 1203767.2522
14 | 2666374.2317 | 1203864.8301
15 | 2666372.0888 | 1203874.8909
16 | 2666379.1726 | 1203840.8905
17 | 2666400.2051 | 1203770.3711
18 | 2666400.4092 | 1203759.1127
19 | 2666378.6567 | 1203759.7158
20 | 2666370.5382 | 1203882.1712
21 | 2666198.8202 | 1203820.7226
22 | 2666243.8235 | 1203815.3438
23 | 2666246.4775 | 1203833.9541
24 | 2666241.8005 | 1203801.158
25 | 2666221.1505 | 1203755.3877
26 | 2666238.3716 | 1203777.1139
27 | 2666189.92 | 1203674.7708
28 | 2666222.0171 | 1203689.5909
29 | 2666216.9428 | 1203633.7177
30 | 2666230.6974 | 1203700.3496
31 | 2666364.2813 | 1203762.7128
32 | 2666339.4487 | 1203752.1061
33 | 2666338.0655 | 1203742.6638
34 | 2666401.0458 | 1203723.0758
35 | 2666415.2168 | 1203740.5549
36 | 2666379.7928 | 1203722.3299
37 | 2666417.7082 | 1203740.7327
38 | 2666333.3539 | 1203720.7002
39 | 2666251.0645 | 1203866.1194
40 | 2666252.0212 | 1203873.9894
41 | 2666282.3949 | 1203867.6567
42 | 2666316.5137 | 1203864.0665
43 | 2666242.7387 | 1203907.9149
44 | 2666254.5109 | 1203894.4713
45 | 2666236.9974 | 1203925.6883
46 | 2666188.3081 | 1203892.32
47 | 2666180.4443 | 1203887.1027
48 | 2666156.8068 | 1203938.4409
49 | 2666175.485 | 1203883.8125
50 | 2666152.4492 | 1203937.0743
51 | 2666303.2206 | 1203864.8305
52 | 2666315.551 | 1203876.7635
53 | 2666302.7512 | 1203861.1898
54 | 2666333.8289 | 1203848.4938
55 | 2666315.2256 | 1203880.1509
56 | 2666281.1552 | 1203858.7042
57 | 2666296.5011 | 1203692.8536
58 | 2666296.193 | 1203697.769
59 | 2666297.5469 | 1203676.1648
60 | 2666294.7912 | 1203720.1386
61 | 2666325.1086 | 1203669.778
62 | 2666298.3468 | 1203668.297
63 | 2666335.7409 | 1203663.8943
64 | 2666301.9138 | 1203640.5807
65 | 2666339.0715 | 1203720.9009
66 | 2666338.8526 | 1203660.0547
67 | 2666302.4993 | 1203637.8571
68 | 2666355.728 | 1203721.4854
69 | 2666356.0721 | 1203721.4975
70 | 2666401.3339 | 1203666.6558
71 | 2666401.4114 | 1203632.7142
72 | 2666303.4338 | 1203633.51
73 | 2666313.3873 | 1203598.7423
74 | 2666360.6295 | 1203647.1179
75 | 2666401.3878 | 1203617.7243
76 | 2666401.3764 | 1203610.5449
77 | 2666430.0086 | 1203608.9781
78 | 2666448.2833 | 1203607.98
79 | 2666405.8989 | 1203610.295
80 | 2666405.8374 | 1203600.7547
81 | 2666405.8431 | 1203618.1878
82 | 2666308.5632 | 1203798.2496

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99154 | -0.16164 | 0.0063572 | 0.0015933
1 | 0.9925 | -0.14311 | 0 | 0
2 | 0.99042 | -0.18331 | 0 | 0
3 | 0.99315 | -0.13053 | 0 | 0
4 | 0.99002 | -0.19102 | 0.0082805 | 0.0020753
5 | 0.99009 | -0.18971 | 0.009143 | 0.0022914
6 | 0.99754 | -0.046668 | 0 | 0
7 | 0.99185 | -0.15543 | 0.0061672 | 0.0015457
8 | 0.98922 | -0.20661 | 0.0060883 | 0.0015259
9 | 0.9896 | -0.19924 | 0.0059029 | 0.0014794
10 | 0.99892 | -0.0204 | 0 | 0
11 | 0.99569 | -0.081867 | 0.011794 | 0.0029559
12 | 1 | 0 | -0.50471 | -0.12873
13 | 0.98999 | -0.19103 | 0 | 0
14 | 0.98905 | -0.20981 | 0 | 0
15 | 0.98899 | -0.21102 | 0.0033063 | 0.00082863
16 | 0.9892 | -0.20692 | 0.018443 | 0.0046223
17 | 0.98924 | -0.20615 | 0.0054335 | 0.0013618
18 | 0.9893 | -0.20506 | 0 | 0
19 | 0.98941 | -0.20296 | 0 | 0
20 | 0.98897 | -0.21146 | 0.0033062 | 0.00082861
21 | 0.98156 | -0.35481 | 0.031448 | 0.0078817
22 | 0.98288 | -0.32906 | 0.0092973 | 0.0023301
23 | 0.98507 | -0.28621 | 0.010865 | 0.0027229
24 | 0.98174 | -0.35128 | 0.059989 | 0.015035
25 | 0.98087 | -0.3684 | 0.010875 | 0.0027255
26 | 0.98116 | -0.36265 | 0.014997 | 0.0037587
27 | 0.98154 | -0.35497 | 0.0086951 | 0.0021792
28 | 0.98184 | -0.34908 | 0.00011501 | 2.8824e-05
29 | 0.98152 | -0.35526 | 0.00032717 | 8.1997e-05
30 | 0.98195 | -0.34679 | 0.0025413 | 0.00063691
31 | 0.98921 | -0.20676 | 0.014522 | 0.0036396
32 | 0.98808 | -0.2279 | 0.025254 | 0.0063293
33 | 0.98712 | -0.24644 | 0.010279 | 0.0025763
34 | 0.98392 | -0.30863 | 0 | 0
35 | 0.98377 | -0.31164 | 0 | 0
36 | 0.98403 | -0.30657 | 0.015531 | 0.0038925
37 | 0.98375 | -0.31188 | 0.005389 | 0.0013506
38 | 0.98507 | -0.28616 | 0 | 0
39 | 0.9892 | -0.20631 | 0 | 0
40 | 0.98865 | -0.21701 | 0.011454 | 0.0028706
41 | 0.99228 | -0.14711 | 0 | 0
42 | 0.99417 | -0.111 | 0 | 0
43 | 0.98629 | -0.26267 | 0.0053327 | 0.0013365
44 | 0.98742 | -0.24069 | 0.009187 | 0.0023025
45 | 0.98519 | -0.28402 | 0 | 0
46 | 0.98248 | -0.33692 | 0.0034911 | 0.00087494
47 | 0.98216 | -0.34314 | 0.028521 | 0.0071481
48 | 0.98198 | -0.34679 | 0 | 0
49 | 0.98212 | -0.34399 | 0.0079543 | 0.0019935
50 | 0.98193 | -0.3476 | 0.0097833 | 0.0024519
51 | 0.99339 | -0.12589 | 0 | 0
52 | 0.99383 | -0.11741 | 0 | 0
53 | 0.99337 | -0.12627 | 0.0059242 | 0.0014847
54 | 0.99311 | -0.13149 | 0.017806 | 0.0044626
55 | 0.9938 | -0.11805 | 0.010716 | 0.0026857
56 | 0.99215 | -0.14965 | 0.01589 | 0.0039824
57 | 0.98138 | -0.35783 | 0.00011652 | 2.9202e-05
58 | 0.9816 | -0.35353 | 0.0057821 | 0.0014491
59 | 0.98064 | -0.3724 | 0 | 0
60 | 0.98273 | -0.33165 | 0 | 0
61 | 0.9793 | -0.39846 | 0 | 0
62 | 0.98061 | -0.37288 | 0.00016739 | 4.1951e-05
63 | 0.97878 | -0.40863 | 0.0012827 | 0.00032148
64 | 0.98053 | -0.3745 | 0 | 0
65 | 0.9849 | -0.28951 | 0.006008 | 0.0015058
66 | 0.97858 | -0.41254 | 0.0048258 | 0.0012095
67 | 0.98052 | -0.37467 | 0.00012848 | 3.2199e-05
68 | 0.98449 | -0.2975 | 0.004785 | 0.0011992
69 | 0.98448 | -0.29764 | 0.00095497 | 0.00023934
70 | 0.97573 | -0.46863 | 0.014046 | 0.0035202
71 | 0.97617 | -0.45991 | 0 | 0
72 | 0.98051 | -0.37491 | 0.0010269 | 0.00025738
73 | 0.98044 | -0.37625 | 0.0020388 | 0.00051097
74 | 0.97766 | -0.4307 | 0.0021812 | 0.00054665
75 | 0.97586 | -0.46606 | 0.0011174 | 0.00028006
76 | 0.97572 | -0.46886 | 0 | 0
77 | 0.9753 | -0.47698 | 0.0034871 | 0.00087395
78 | 0.97512 | -0.48064 | 0.010906 | 0.0027333
79 | 0.97563 | -0.47062 | 0 | 0
80 | 0.9756 | -0.47121 | 0.0034209 | 0.00085736
81 | 0.9756 | -0.47112 | 0.0034874 | 0.00087403
82 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.080929 | -0.020337 | 0.081001 | 0.020383 | 7.1644e-05 | 4.5685e-05 | 0.12147 | 0.12147 | 0.12147 | 0.99154 | -0.16164 | 0.9925 | -0.14311 | 33.3711
1 | 0.074572 | 0.018744 | -0.074495 | -0.018695 | 7.7065e-05 | 4.9111e-05 | 0.11193 | 0.11193 | 0.11193 | 0.99154 | -0.16164 | 0.99042 | -0.18331 | 30.7502
2 | -0.081001 | -0.020383 | 0.081049 | 0.020414 | 4.8731e-05 | 3.1074e-05 | 0.12147 | 0.12147 | 0.12147 | 0.9925 | -0.14311 | 0.99315 | -0.13053 | 33.3711
3 | 0.039464 | 0.0099049 | -0.039449 | -0.0098957 | 1.4503e-05 | 9.1405e-06 | 0.059296 | 0.059296 | 0.059296 | 0.99042 | -0.18331 | 0.99002 | -0.19102 | 16.2901
4 | 0.035031 | 0.0087899 | -0.03502 | -0.0087832 | 1.069e-05 | 6.709e-06 | 0.052635 | 0.052635 | 0.052635 | 0.99042 | -0.18331 | 0.99009 | -0.18971 | 14.4601
5 | -0.22251 | -0.056404 | 0.22341 | 0.05698 | 0.00090075 | 0.00057536 | 0.33362 | 0.33361 | 0.33362 | 0.99315 | -0.13053 | 0.99754 | -0.046668 | 45.8263
6 | 0.14146 | 0.03599 | -0.14129 | -0.035882 | 0.00016952 | 0.00010797 | 0.21214 | 0.21214 | 0.21214 | 0.99315 | -0.13053 | 0.99185 | -0.15543 | 29.1408
7 | 0.031169 | 0.0078204 | -0.031146 | -0.007806 | 2.3155e-05 | 1.4458e-05 | 0.04685 | 0.04685 | 0.04685 | 0.99002 | -0.19102 | 0.98922 | -0.20661 | 12.871
8 | 0.025877 | 0.0064917 | -0.025866 | -0.0064845 | 1.1749e-05 | 7.2532e-06 | 0.038894 | 0.038894 | 0.038894 | 0.99009 | -0.18971 | 0.9896 | -0.19924 | 10.6851
9 | -0.50192 | -0.12801 | 0.50256 | 0.12842 | 0.0006375 | 0.00040737 | 0.7495 | 0.7495 | 0.7495 | 0.99754 | -0.046668 | 0.99892 | -0.0204 | 51.4767
10 | 0.27851 | 0.07103 | -0.27804 | -0.070729 | 0.00047249 | 0.00030088 | 0.41589 | 0.41589 | 0.41589 | 0.99754 | -0.046668 | 0.99569 | -0.081867 | 28.5637
11 | 0.13513 | 0.034337 | -0.1349 | -0.034189 | 0.0002312 | 0.00014778 | 0.20289 | 0.20289 | 0.20289 | 0.99185 | -0.15543 | 0.98999 | -0.19103 | 55.7397
12 | 0.025057 | 0.0062801 | -0.025057 | -0.0062799 | 3.678e-07 | 2.2653e-07 | 0.037692 | 0.037692 | 0.037692 | 0.98922 | -0.20661 | 0.9892 | -0.20692 | 10.355
13 | 0.019963 | 0.0050051 | -0.019959 | -0.005003 | 3.538e-06 | 2.1298e-06 | 0.030018 | 0.030018 | 0.030018 | 0.9896 | -0.19924 | 0.98941 | -0.20296 | 8.2466
14 | -0.50256 | -0.12842 | 0.50306 | 0.12873 | 0.00049634 | 0.00031716 | 0.7495 | 0.7495 | 0.7495 | 0.99892 | -0.0204 | 1 | 0 | 51.4767
15 | 0.26624 | 0.067773 | -0.26587 | -0.067536 | 0.00037344 | 0.0002377 | 0.39826 | 0.39826 | 0.39826 | 0.99569 | -0.081867 | 0.99417 | -0.111 | 27.3531
16 | 0.1349 | 0.034189 | -0.13466 | -0.034037 | 0.00023855 | 0.00015248 | 0.20289 | 0.20289 | 0.20289 | 0.98999 | -0.19103 | 0.98808 | -0.2279 | 55.7397
17 | 0.0066129 | 0.0016573 | -0.0066125 | -0.0016572 | 3.8182e-07 | 1.1236e-07 | 0.009949 | 0.009949 | 0.009949 | 0.98905 | -0.20981 | 0.98899 | -0.21102 | 2.7333
18 | -0.0066129 | -0.0016573 | 0.0066138 | 0.0016576 | 9.0971e-07 | 2.6763e-07 | 0.009949 | 0.0099489 | 0.009949 | 0.98905 | -0.20981 | 0.9892 | -0.20692 | 2.7332
19 | 0.0033063 | 0.00082856 | -0.0033062 | -0.00082861 | 6.9074e-08 | -5.1306e-08 | 0.0049745 | 0.0049745 | 0.0049745 | 0.98899 | -0.21102 | 0.98897 | -0.21146 | 1.3666
20 | -0.0054335 | -0.0013618 | 0.0054338 | 0.0013618 | 2.8207e-07 | 3.5948e-08 | 0.0081731 | 0.008173 | 0.0081731 | 0.98924 | -0.20615 | 0.9893 | -0.20506 | 2.2454
21 | -0.0054338 | -0.0013618 | 0.0054343 | 0.0013619 | 5.4352e-07 | 6.9217e-08 | 0.008173 | 0.0081729 | 0.008173 | 0.9893 | -0.20506 | 0.98941 | -0.20296 | 2.2453
22 | 0.014525 | 0.0036411 | -0.014522 | -0.0036396 | 2.6278e-06 | 1.4932e-06 | 0.021845 | 0.021845 | 0.021845 | 0.98941 | -0.20296 | 0.98921 | -0.20676 | 6.0013
23 | -0.031448 | -0.0078817 | 0.031487 | 0.0079058 | 3.863e-05 | 2.415e-05 | 0.047675 | 0.047674 | 0.047675 | 0.98156 | -0.35481 | 0.98288 | -0.32906 | 13.0974
24 | -0.12675 | -0.031823 | 0.12701 | 0.031989 | 0.00025965 | 0.00016594 | 0.19192 | 0.19192 | 0.19192 | 0.98288 | -0.32906 | 0.98507 | -0.28621 | 52.7247
25 | 0.08597 | 0.021587 | -0.085879 | -0.021529 | 9.1046e-05 | 5.8088e-05 | 0.13017 | 0.13017 | 0.13017 | 0.98288 | -0.32906 | 0.98174 | -0.35128 | 35.7604
26 | -0.13788 | -0.034712 | 0.13841 | 0.03505 | 0.0005288 | 0.00033802 | 0.20833 | 0.20833 | 0.20833 | 0.98507 | -0.28621 | 0.9892 | -0.20631 | 57.2334
27 | 0.025889 | 0.0064944 | -0.025875 | -0.0064857 | 1.4026e-05 | 8.6695e-06 | 0.039242 | 0.039242 | 0.039242 | 0.98174 | -0.35128 | 0.98116 | -0.36265 | 10.7809
28 | -0.010875 | -0.0027255 | 0.010878 | 0.002727 | 2.9816e-06 | 1.5394e-06 | 0.016498 | 0.016497 | 0.016498 | 0.98087 | -0.3684 | 0.98116 | -0.36265 | 4.5323
29 | -0.0090223 | -0.0022606 | 0.0090248 | 0.0022617 | 2.5342e-06 | 1.1652e-06 | 0.013678 | 0.013677 | 0.013678 | 0.98154 | -0.35497 | 0.98184 | -0.34908 | 3.7576
30 | 0.00032718 | 8.1379e-05 | -0.00032717 | -8.1997e-05 | 4.5323e-09 | -6.183e-07 | 0.00049578 | 0.000496 | 0.000496 | 0.98154 | -0.35497 | 0.98152 | -0.35526 | 0.13626
31 | -0.0091398 | -0.0022906 | 0.0091408 | 0.002291 | 9.9581e-07 | 4.6226e-07 | 0.013852 | 0.013852 | 0.013852 | 0.98184 | -0.34908 | 0.98195 | -0.34679 | 3.8054
32 | -0.011682 | -0.0029279 | 0.011691 | 0.0029324 | 8.4308e-06 | 4.4874e-06 | 0.017703 | 0.017702 | 0.017703 | 0.98195 | -0.34679 | 0.98273 | -0.33165 | 4.8634
33 | 0.1094 | 0.027707 | -0.10931 | -0.027645 | 9.7264e-05 | 6.2127e-05 | 0.16486 | 0.16486 | 0.16486 | 0.98808 | -0.2279 | 0.98712 | -0.24644 | 45.2914
34 | 0.099027 | 0.025069 | -0.098838 | -0.024948 | 0.00018844 | 0.00012031 | 0.14937 | 0.14937 | 0.14937 | 0.98712 | -0.24644 | 0.98507 | -0.28616 | 41.0344
35 | 0.0053898 | 0.0013507 | -0.005389 | -0.0013506 | 7.7142e-07 | 1.0054e-07 | 0.0081511 | 0.0081513 | 0.0081513 | 0.98392 | -0.30863 | 0.98377 | -0.31164 | 2.2394
36 | -0.0053898 | -0.0013507 | 0.0053903 | 0.0013508 | 5.2984e-07 | 6.8976e-08 | 0.0081511 | 0.008151 | 0.0081511 | 0.98392 | -0.30863 | 0.98403 | -0.30657 | 2.2393
37 | 0.005389 | 0.0013506 | -0.005389 | -0.0013506 | 6.2234e-08 | 8.1171e-09 | 0.0081513 | 0.0081513 | 0.0081513 | 0.98377 | -0.31164 | 0.98375 | -0.31188 | 2.2394
38 | -0.020922 | -0.0052433 | 0.020931 | 0.0052487 | 8.9087e-06 | 5.3999e-06 | 0.031637 | 0.031637 | 0.031637 | 0.98403 | -0.30657 | 0.98448 | -0.29764 | 8.6915
39 | 0.032694 | 0.0082027 | -0.032689 | -0.0081994 | 5.2333e-06 | 3.2765e-06 | 0.04939 | 0.04939 | 0.04939 | 0.98507 | -0.28616 | 0.9849 | -0.28951 | 13.5686
40 | 0.066144 | 0.016746 | -0.066 | -0.016654 | 0.00014413 | 9.1757e-05 | 0.099976 | 0.099976 | 0.099976 | 0.98507 | -0.28616 | 0.98273 | -0.33165 | 27.4659
41 | 0.076087 | 0.019208 | -0.076048 | -0.019183 | 3.8979e-05 | 2.4845e-05 | 0.1145 | 0.1145 | 0.1145 | 0.9892 | -0.20631 | 0.98865 | -0.21701 | 31.457
42 | -0.21449 | -0.054258 | 0.2151 | 0.054648 | 0.0006112 | 0.00039036 | 0.32283 | 0.32283 | 0.32283 | 0.9892 | -0.20631 | 0.99228 | -0.14711 | 44.3452
43 | 0.064594 | 0.016312 | -0.064521 | -0.016266 | 7.3197e-05 | 4.6582e-05 | 0.097264 | 0.097265 | 0.097265 | 0.98865 | -0.21701 | 0.98742 | -0.24069 | 26.721
44 | 0.015892 | 0.0039836 | -0.01589 | -0.0039824 | 1.9252e-06 | 1.1154e-06 | 0.023832 | 0.023832 | 0.023832 | 0.99228 | -0.14711 | 0.99215 | -0.14965 | 6.5472
45 | -0.231 | -0.058632 | 0.23123 | 0.058782 | 0.00023611 | 0.00015003 | 0.34666 | 0.34666 | 0.34666 | 0.99228 | -0.14711 | 0.99339 | -0.12589 | 23.8094
46 | 0.23733 | 0.060375 | -0.23716 | -0.060267 | 0.00017008 | 0.00010811 | 0.35554 | 0.35554 | 0.35554 | 0.99417 | -0.111 | 0.99339 | -0.12589 | 24.4188
47 | 0.028543 | 0.0071609 | -0.028534 | -0.0071555 | 8.7172e-06 | 5.4139e-06 | 0.042724 | 0.042724 | 0.042724 | 0.99417 | -0.111 | 0.99383 | -0.11741 | 11.7374
48 | -0.055275 | -0.013926 | 0.055334 | 0.013963 | 5.8176e-05 | 3.6948e-05 | 0.08342 | 0.08342 | 0.08342 | 0.98629 | -0.26267 | 0.98742 | -0.24069 | 22.9176
49 | 0.049943 | 0.01259 | -0.049892 | -0.012558 | 5.0971e-05 | 3.2316e-05 | 0.075375 | 0.075375 | 0.075375 | 0.98629 | -0.26267 | 0.98519 | -0.28402 | 20.7073
50 | 0.049892 | 0.012558 | -0.049766 | -0.012478 | 0.00012579 | 7.9756e-05 | 0.075375 | 0.075375 | 0.075375 | 0.98519 | -0.28402 | 0.98248 | -0.33692 | 20.7074
51 | 0.036487 | 0.0091485 | -0.036476 | -0.0091417 | 1.0808e-05 | 6.7974e-06 | 0.055262 | 0.055262 | 0.055262 | 0.98248 | -0.33692 | 0.98216 | -0.34314 | 15.182
52 | 0.0097883 | 0.0024543 | -0.0097837 | -0.0024521 | 4.6034e-06 | 2.2393e-06 | 0.014825 | 0.014826 | 0.014826 | 0.98248 | -0.33692 | 0.98198 | -0.34679 | 4.0729
53 | 0.0079547 | 0.0019937 | -0.0079543 | -0.0019935 | 3.2416e-07 | 1.3214e-07 | 0.012052 | 0.012052 | 0.012052 | 0.98216 | -0.34314 | 0.98212 | -0.34399 | 3.3109
54 | 0.0097837 | 0.0024521 | -0.0097833 | -0.0024519 | 3.7642e-07 | 1.8314e-07 | 0.014826 | 0.014826 | 0.014826 | 0.98198 | -0.34679 | 0.98193 | -0.3476 | 4.0729
55 | 0.0059243 | 0.0014848 | -0.0059242 | -0.0014847 | 1.0841e-07 | 2.1857e-08 | 0.0088741 | 0.0088742 | 0.0088742 | 0.99339 | -0.12589 | 0.99337 | -0.12627 | 2.438
56 | 0.017818 | 0.0044697 | -0.017806 | -0.0044626 | 1.1949e-05 | 7.0678e-06 | 0.026679 | 0.02668 | 0.02668 | 0.99383 | -0.11741 | 0.99311 | -0.13149 | 7.3296
57 | 0.010716 | 0.0026858 | -0.010716 | -0.0026857 | 3.2853e-07 | 1.6616e-07 | 0.016045 | 0.016045 | 0.016045 | 0.99383 | -0.11741 | 0.9938 | -0.11805 | 4.4079
58 | -0.048461 | -0.01223 | 0.048471 | 0.012236 | 9.9796e-06 | 6.3247e-06 | 0.073509 | 0.073509 | 0.073509 | 0.98138 | -0.35783 | 0.9816 | -0.35353 | 20.1947
59 | 0.048344 | 0.012201 | -0.04831 | -0.012179 | 3.3721e-05 | 2.137e-05 | 0.073332 | 0.073332 | 0.073332 | 0.98138 | -0.35783 | 0.98064 | -0.3724 | 20.1462
60 | -0.054253 | -0.013685 | 0.05431 | 0.013722 | 5.6893e-05 | 3.6128e-05 | 0.082274 | 0.082274 | 0.082274 | 0.9816 | -0.35353 | 0.98273 | -0.33165 | 22.6026
61 | 0.044948 | 0.011338 | -0.044892 | -0.011302 | 5.5993e-05 | 3.5431e-05 | 0.068231 | 0.068231 | 0.068231 | 0.98064 | -0.3724 | 0.9793 | -0.39846 | 18.7447
62 | 0.0033621 | 0.00084183 | -0.003362 | -0.00084188 | 7.7179e-08 | -5.0376e-08 | 0.0051014 | 0.0051014 | 0.0051014 | 0.98064 | -0.3724 | 0.98061 | -0.37288 | 1.4015
63 | 0.044892 | 0.011302 | -0.044871 | -0.011288 | 2.1808e-05 | 1.38e-05 | 0.068231 | 0.068231 | 0.068231 | 0.9793 | -0.39846 | 0.97878 | -0.40863 | 18.7447
64 | 0.0031947 | 0.00079993 | -0.0031944 | -0.00080012 | 2.4631e-07 | -1.9497e-07 | 0.0048474 | 0.0048476 | 0.0048476 | 0.98061 | -0.37288 | 0.98053 | -0.3745 | 1.3317
65 | 0.043588 | 0.010967 | -0.04358 | -0.010962 | 8.1418e-06 | 5.1487e-06 | 0.066281 | 0.066281 | 0.066281 | 0.97878 | -0.40863 | 0.97858 | -0.41254 | 18.209
66 | 0.0031944 | 0.00080012 | -0.0031944 | -0.00080014 | 2.4549e-08 | -1.9427e-08 | 0.0048476 | 0.0048476 | 0.0048476 | 0.98053 | -0.3745 | 0.98052 | -0.37467 | 1.3317
67 | 0.026681 | 0.0066936 | -0.026671 | -0.0066873 | 1.0157e-05 | 6.2884e-06 | 0.040313 | 0.040313 | 0.040313 | 0.9849 | -0.28951 | 0.98449 | -0.2975 | 11.0749
68 | 0.038754 | 0.0097523 | -0.03872 | -0.0097311 | 3.3609e-05 | 2.1186e-05 | 0.058943 | 0.058943 | 0.058943 | 0.97858 | -0.41254 | 0.97766 | -0.4307 | 16.1931
69 | 0.0030659 | 0.00076794 | -0.0030659 | -0.00076797 | 3.6094e-08 | -3.2983e-08 | 0.0046526 | 0.0046526 | 0.0046526 | 0.98052 | -0.37467 | 0.98051 | -0.37491 | 1.2782
70 | 0.021886 | 0.0054881 | -0.021885 | -0.005488 | 1.413e-07 | 8.6052e-08 | 0.03308 | 0.03308 | 0.03308 | 0.98449 | -0.2975 | 0.98448 | -0.29764 | 9.088
71 | -0.014046 | -0.0035202 | 0.014052 | 0.0035235 | 5.8399e-06 | 3.3134e-06 | 0.02142 | 0.02142 | 0.02142 | 0.97573 | -0.46863 | 0.97617 | -0.45991 | 5.8847
72 | 0.022437 | 0.005629 | -0.02243 | -0.0056249 | 6.5761e-06 | 4.0213e-06 | 0.034203 | 0.034203 | 0.034203 | 0.97617 | -0.45991 | 0.97586 | -0.46606 | 9.3965
73 | -0.036488 | -0.0091525 | 0.036539 | 0.0091845 | 5.0877e-05 | 3.2012e-05 | 0.055623 | 0.055623 | 0.055623 | 0.97617 | -0.45991 | 0.97766 | -0.4307 | 15.2811
74 | 0.0020389 | 0.0005106 | -0.0020388 | -0.00051097 | 1.3014e-07 | -3.7386e-07 | 0.0030941 | 0.0030943 | 0.0030943 | 0.98051 | -0.37491 | 0.98044 | -0.37625 | 0.85008
75 | 0.021313 | 0.0053449 | -0.02131 | -0.0053432 | 2.8437e-06 | 1.7303e-06 | 0.032499 | 0.032499 | 0.032499 | 0.97586 | -0.46606 | 0.97572 | -0.46886 | 8.9284
76 | 0.02131 | 0.0053432 | -0.021308 | -0.0053421 | 1.7887e-06 | 1.0884e-06 | 0.032499 | 0.032499 | 0.032499 | 0.97572 | -0.46886 | 0.97563 | -0.47062 | 8.9284
77 | 0.010908 | 0.0027343 | -0.010906 | -0.0027333 | 1.901e-06 | 9.8827e-07 | 0.016643 | 0.016643 | 0.016643 | 0.9753 | -0.47698 | 0.97512 | -0.48064 | 4.5722
78 | -0.014395 | -0.0036083 | 0.0144 | 0.0036108 | 4.3676e-06 | 2.4939e-06 | 0.021963 | 0.021963 | 0.021963 | 0.9753 | -0.47698 | 0.97563 | -0.47062 | 6.0338
79 | 0.003421 | 0.0008573 | -0.0034209 | -0.00085736 | 9.7402e-08 | -5.6801e-08 | 0.0052176 | 0.0052177 | 0.0052177 | 0.97563 | -0.47062 | 0.9756 | -0.47121 | 1.4334
80 | 0.0034875 | 0.00087399 | -0.0034874 | -0.00087403 | 8.3744e-08 | -4.4966e-08 | 0.0053191 | 0.0053191 | 0.0053191 | 0.97563 | -0.47062 | 0.9756 | -0.47112 | 1.4613

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53001 | 0.13508

## res_load
| p_mw | q_mvar
0 | 0.0063572 | 0.0015933
1 | 0.0082805 | 0.0020753
2 | 0.009143 | 0.0022914
3 | 0.0061672 | 0.0015457
4 | 0.0060883 | 0.0015259
5 | 0.0059029 | 0.0014794
6 | 0.011794 | 0.0029559
7 | 0.025302 | 0.0063414
8 | 0.0033063 | 0.00082863
9 | 0.018443 | 0.0046223
10 | 0.0054335 | 0.0013618
11 | 0.0033062 | 0.00082861
12 | 0.031448 | 0.0078817
13 | 0.0092973 | 0.0023301
14 | 0.010865 | 0.0027229
15 | 0.059989 | 0.015035
16 | 0.010875 | 0.0027255
17 | 0.014997 | 0.0037587
18 | 0.0086951 | 0.0021792
19 | 0.00011501 | 2.8824e-05
20 | 0.00032717 | 8.1997e-05
21 | 0.0025413 | 0.00063691
22 | 0.014522 | 0.0036396
23 | 0.025254 | 0.0063293
24 | 0.010279 | 0.0025763
25 | 0.015531 | 0.0038925
26 | 0.005389 | 0.0013506
27 | 0.011454 | 0.0028706
28 | 0.0053327 | 0.0013365
29 | 0.009187 | 0.0023025
30 | 0.0034911 | 0.00087494
31 | 0.028521 | 0.0071481
32 | 0.0079543 | 0.0019935
33 | 0.0097833 | 0.0024519
34 | 0.0059242 | 0.0014847
35 | 0.017806 | 0.0044626
36 | 0.010716 | 0.0026857
37 | 0.01589 | 0.0039824
38 | 0.00011652 | 2.9202e-05
39 | 0.0057821 | 0.0014491
40 | 0.00016739 | 4.1951e-05
41 | 0.0012827 | 0.00032148
42 | 0.006008 | 0.0015058
43 | 0.0048258 | 0.0012095
44 | 0.00012848 | 3.2199e-05
45 | 0.004785 | 0.0011992
46 | 0.00095497 | 0.00023934
47 | 0.014046 | 0.0035202
48 | 0.0010269 | 0.00025738
49 | 0.0020388 | 0.00051097
50 | 0.0021812 | 0.00054665
51 | 0.0011174 | 0.00028006
52 | 0.0034871 | 0.00087395
53 | 0.010906 | 0.0027333
54 | 0.0034209 | 0.00085736
55 | 0.0034874 | 0.00087403

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1