## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1507-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1507-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1507-6_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1507-6_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1507-6_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1507-6_0_4_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_1507-6_0_4_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_1507-6_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1507-6_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1507-6_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1507-6_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1507-6_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1507-6_0_4_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_1507-6_0_4_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_1507-6_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_1507-6_0_4_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_1507-6_0_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1507-6_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1507-6_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1507-6_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1507-6_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1507-6_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1507-6_0_4_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_1507-6_0_4_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1507-6_0_4_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_1507-6_0_4_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_1507-6_0_4_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_1507-6_0_4_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_1507-6_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1507-6_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_MV_24_0_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1507-6_0_4_load_0 | 0 | 0.02184 | 0.0054737 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1507-6_0_4_load_4 | 4 | 0.0050916 | 0.0012761 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1507-6_0_4_load_33 | 5 | 0.024211 | 0.0060677 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1507-6_0_4_load_15 | 6 | 0.0095839 | 0.002402 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1507-6_0_4_load_5 | 7 | 0.0023652 | 0.00059278 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1507-6_0_4_load_6 | 8 | 0.018183 | 0.004557 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1507-6_0_4_load_7 | 9 | 0.0085183 | 0.0021349 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1507-6_0_4_load_20 | 12 | 0.0039891 | 0.00099977 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1507-6_0_4_load_18 | 13 | 0.042095 | 0.01055 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1507-6_0_4_load_16 | 14 | 0.035321 | 0.0088522 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1507-6_0_4_load_23 | 16 | 0.033544 | 0.0084068 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1507-6_0_4_load_10 | 17 | 0.016916 | 0.0042396 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1507-6_0_4_load_11 | 18 | 0.012078 | 0.0030271 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1507-6_0_4_load_13 | 20 | 0.018225 | 0.0045677 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1507-6_0_4_load_14 | 21 | 0.014529 | 0.0036414 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1507-6_0_4_load_24 | 23 | 0.017579 | 0.0044058 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1507-6_0_4_load_31 | 24 | 0.0047472 | 0.0011898 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1507-6_0_4_load_30 | 25 | 0.0049728 | 0.0012463 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1507-6_0_4_load_28 | 26 | 0.0060639 | 0.0015198 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1507-6_0_4_load_25 | 28 | 0.0053807 | 0.0013485 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1507-6_0_4_load_22 | 29 | 0.0036989 | 0.00092702 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1507-6_0_4_line_0 |  | 0 | 1 | 0.014433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1507-6_0_4_line_1 |  | 0 | 2 | 0.033998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1507-6_0_4_line_2 |  | 1 | 3 | 0.004611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1507-6_0_4_line_3 |  | 2 | 4 | 0.00981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1507-6_0_4_line_4 |  | 3 | 5 | 0.029367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1507-6_0_4_line_5 |  | 5 | 6 | 0.032898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1507-6_0_4_line_6 |  | 6 | 19 | 0.032028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1507-6_0_4_line_7 |  | 7 | 8 | 0.0072751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1507-6_0_4_line_8 |  | 7 | 9 | 0.000938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1507-6_0_4_line_9 |  | 8 | 10 | 0.025226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1507-6_0_4_line_10 |  | 9 | 11 | 0.035635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1507-6_0_4_line_11 |  | 10 | 12 | 0.013212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1507-6_0_4_line_12 |  | 11 | 13 | 0.020218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1507-6_0_4_line_13 |  | 11 | 14 | 0.034295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1507-6_0_4_line_14 |  | 12 | 15 | 0.0078829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1507-6_0_4_line_15 |  | 13 | 16 | 0.018326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1507-6_0_4_line_16 |  | 15 | 28 | 0.014383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1507-6_0_4_line_17 |  | 16 | 23 | 0.0091733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1507-6_0_4_line_18 |  | 17 | 18 | 0.010392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1507-6_0_4_line_19 |  | 17 | 19 | 0.006253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1507-6_0_4_line_20 |  | 18 | 20 | 0.029225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1507-6_0_4_line_21 |  | 19 | 21 | 0.022187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1507-6_0_4_line_22 |  | 20 | 22 | 0.0033591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1507-6_0_4_line_23 |  | 21 | 23 | 0.0037978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1507-6_0_4_line_24 |  | 22 | 24 | 0.015449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1507-6_0_4_line_25 |  | 22 | 25 | 0.010168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1507-6_0_4_line_26 |  | 24 | 29 | 0.010468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1507-6_0_4_line_27 |  | 25 | 27 | 0.023659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1507-6_0_4_line_28 |  | 26 | 27 | 0.018724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1507-6_0_4_trafo_24 | 0.63 MVA 20/0.4 kV | 30 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2666359.4468 | 1204146.3359 | 2666358.1434 | 1204150.6574 | 2666356.9976 | 1204152.4346 | 2666353.5039 | 1204154.6305 | 2666350.0213 | 1204155.8147
1 | 2666328.8794 | 1204174.8693 | 2666333.3493 | 1204169.7269 | 2666333.1669 | 1204164.2327 | 2666335.2536 | 1204157.8853 | 2666339.5902 | 1204156.5215 | 2666344.8609 | 1204156.002 | 2666350.0213 | 1204155.8147
2 | 2666363.608 | 1204144.3253 | 2666359.4468 | 1204146.3359
3 | 2666328.8794 | 1204174.8693 | 2666319.0943 | 1204174.171
4 | 2666363.608 | 1204144.3253 | 2666368.2907 | 1204152.2155 | 2666367.835 | 1204172.4024
5 | 2666367.835 | 1204172.4024 | 2666367.0925 | 1204205.2922
6 | 2666366.371 | 1204237.3122 | 2666366.717 | 1204221.929 | 2666367.0925 | 1204205.2922
7 | 2666436.0767 | 1204195.5961 | 2666435.3202 | 1204188.3604
8 | 2666436.1742 | 1204196.529 | 2666436.0767 | 1204195.5961
9 | 2666432.6932 | 1204163.2712 | 2666434.117 | 1204176.8508 | 2666435.3202 | 1204188.3604
10 | 2666439.8793 | 1204231.9704 | 2666436.1742 | 1204196.529
11 | 2666432.6932 | 1204163.2712 | 2666439.9993 | 1204162.3853 | 2666444.7348 | 1204158.9468
12 | 2666439.8793 | 1204231.9704 | 2666419.715 | 1204233.4358
13 | 2666439.8793 | 1204231.9704 | 2666443.3155 | 1204266.0927
14 | 2666451.1135 | 1204154.3151 | 2666444.7348 | 1204158.9468
15 | 2666401.4369 | 1204234.764 | 2666419.715 | 1204233.4358
16 | 2666451.1135 | 1204154.3151 | 2666462.2393 | 1204145.2
17 | 2666401.4369 | 1204234.764 | 2666392.2878 | 1204235.4289
18 | 2666365.0033 | 1204253.9005 | 2666365.8572 | 1204243.544
19 | 2666366.371 | 1204237.3122 | 2666365.8572 | 1204243.544
20 | 2666365.0033 | 1204253.9005 | 2666362.6019 | 1204283.027
21 | 2666366.371 | 1204237.3122 | 2666388.5 | 1204235.7041
22 | 2666362.3259 | 1204286.3747 | 2666362.6019 | 1204283.027
23 | 2666388.5 | 1204235.7041 | 2666392.2878 | 1204235.4289
24 | 2666362.3259 | 1204286.3747 | 2666347.8499 | 1204280.9794
25 | 2666362.3259 | 1204286.3747 | 2666361.4907 | 1204296.5079
26 | 2666347.8499 | 1204280.9794 | 2666338.0412 | 1204277.3237
27 | 2666359.5471 | 1204320.0865 | 2666361.4907 | 1204296.5079
28 | 2666359.5471 | 1204320.0865 | 2666377.8713 | 1204316.2385

## bus_geodata
| x | y | coords
0 | 2666350.0213 | 1204155.8147
1 | 2666359.4468 | 1204146.3359
2 | 2666328.8794 | 1204174.8693
3 | 2666363.608 | 1204144.3253
4 | 2666319.0943 | 1204174.171
5 | 2666367.835 | 1204172.4024
6 | 2666367.0925 | 1204205.2922
7 | 2666436.0767 | 1204195.5961
8 | 2666435.3202 | 1204188.3604
9 | 2666436.1742 | 1204196.529
10 | 2666432.6932 | 1204163.2712
11 | 2666439.8793 | 1204231.9704
12 | 2666444.7348 | 1204158.9468
13 | 2666419.715 | 1204233.4358
14 | 2666443.3155 | 1204266.0927
15 | 2666451.1135 | 1204154.3151
16 | 2666401.4369 | 1204234.764
17 | 2666365.8572 | 1204243.544
18 | 2666365.0033 | 1204253.9005
19 | 2666366.371 | 1204237.3122
20 | 2666362.6019 | 1204283.027
21 | 2666388.5 | 1204235.7041
22 | 2666362.3259 | 1204286.3747
23 | 2666392.2878 | 1204235.4289
24 | 2666347.8499 | 1204280.9794
25 | 2666361.4907 | 1204296.5079
26 | 2666377.8713 | 1204316.2385
27 | 2666359.5471 | 1204320.0865
28 | 2666462.2393 | 1204145.2
29 | 2666338.0412 | 1204277.3237
30 | 2666366.371 | 1204237.3122

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99267 | -0.14097 | 0.02184 | 0.0054737
1 | 0.99303 | -0.13409 | 0 | 0
2 | 0.99252 | -0.14403 | 0 | 0
3 | 0.99314 | -0.1319 | 0 | 0
4 | 0.99247 | -0.14491 | 0.0050916 | 0.0012761
5 | 0.99387 | -0.11793 | 0.024211 | 0.0060677
6 | 0.9954 | -0.088288 | 0.0095839 | 0.002402
7 | 0.99481 | -0.099823 | 0.0023652 | 0.00059278
8 | 0.99463 | -0.10335 | 0.018183 | 0.004557
9 | 0.99484 | -0.099329 | 0.0085183 | 0.0021349
10 | 0.99441 | -0.10752 | 0 | 0
11 | 0.99608 | -0.075237 | 0 | 0
12 | 0.9943 | -0.1097 | 0.0039891 | 0.00099977
13 | 0.99744 | -0.049076 | 0.042095 | 0.01055
14 | 0.99498 | -0.09654 | 0.035321 | 0.0088522
15 | 0.99426 | -0.11045 | 0 | 0
16 | 0.99938 | -0.011951 | 0.033544 | 0.0084068
17 | 0.9968 | -0.061447 | 0.016916 | 0.0042396
18 | 0.99633 | -0.070528 | 0.012078 | 0.0030271
19 | 0.99718 | -0.054133 | 0 | 0
20 | 0.99532 | -0.089898 | 0.018225 | 0.0045677
21 | 0.99975 | -0.0046998 | 0.014529 | 0.0036414
22 | 0.99526 | -0.09105 | 0 | 0
23 | 1 | 0 | -0.2941 | -0.073713
24 | 0.99514 | -0.093346 | 0.0047472 | 0.0011898
25 | 0.99516 | -0.093025 | 0.0049728 | 0.0012463
26 | 0.99493 | -0.09755 | 0.0060639 | 0.0015198
27 | 0.99503 | -0.095551 | 0 | 0
28 | 0.99419 | -0.11182 | 0.0053807 | 0.0013485
29 | 0.99511 | -0.094028 | 0.0036989 | 0.00092702
30 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.026933 | -0.0067498 | 0.026942 | 0.0067552 | 8.8217e-06 | 5.4592e-06 | 0.040372 | 0.040372 | 0.040372 | 0.99267 | -0.14097 | 0.99303 | -0.13409 | 11.0912
1 | 0.0050925 | 0.0012761 | -0.0050918 | -0.0012761 | 7.4295e-07 | 3.6031e-08 | 0.0076336 | 0.0076338 | 0.0076338 | 0.99267 | -0.14097 | 0.99252 | -0.14403 | 2.0972
2 | -0.026942 | -0.0067552 | 0.026944 | 0.006757 | 2.8183e-06 | 1.744e-06 | 0.040372 | 0.040372 | 0.040372 | 0.99303 | -0.13409 | 0.99314 | -0.1319 | 11.0912
3 | 0.0050918 | 0.0012761 | -0.0050916 | -0.0012761 | 2.1438e-07 | 1.0426e-08 | 0.0076338 | 0.0076338 | 0.0076338 | 0.99252 | -0.14403 | 0.99247 | -0.14491 | 2.0972
4 | -0.026944 | -0.006757 | 0.026962 | 0.0067681 | 1.7949e-05 | 1.1107e-05 | 0.040372 | 0.040372 | 0.040372 | 0.99314 | -0.1319 | 0.99387 | -0.11793 | 11.0912
5 | -0.051173 | -0.012836 | 0.051245 | 0.012882 | 7.2424e-05 | 4.5925e-05 | 0.07662 | 0.07662 | 0.07662 | 0.99387 | -0.11793 | 0.9954 | -0.088288 | 21.0494
6 | -0.060829 | -0.015284 | 0.060928 | 0.015347 | 9.9342e-05 | 6.3162e-05 | 0.090946 | 0.090946 | 0.090946 | 0.9954 | -0.088288 | 0.99718 | -0.054133 | 24.9853
7 | 0.027561 | 0.0069096 | -0.027556 | -0.0069067 | 4.6366e-06 | 2.873e-06 | 0.041225 | 0.041225 | 0.041225 | 0.99481 | -0.099823 | 0.99463 | -0.10335 | 11.3257
8 | -0.029926 | -0.0075024 | 0.029927 | 0.0075028 | 7.0481e-07 | 4.389e-07 | 0.044763 | 0.044763 | 0.044763 | 0.99481 | -0.099823 | 0.99484 | -0.099329 | 12.2976
9 | 0.0093732 | 0.0023497 | -0.0093713 | -0.0023488 | 1.8602e-06 | 8.6322e-07 | 0.014023 | 0.014023 | 0.014023 | 0.99463 | -0.10335 | 0.99441 | -0.10752 | 3.8525
10 | -0.038445 | -0.0096377 | 0.038489 | 0.0096655 | 4.4188e-05 | 2.7817e-05 | 0.057504 | 0.057504 | 0.057504 | 0.99484 | -0.099329 | 0.99608 | -0.075237 | 15.7979
11 | 0.0093713 | 0.0023488 | -0.0093703 | -0.0023483 | 9.7428e-07 | 4.5216e-07 | 0.014023 | 0.014023 | 0.014023 | 0.99441 | -0.10752 | 0.9943 | -0.1097 | 3.8525
12 | -0.073846 | -0.01854 | 0.073938 | 0.018599 | 9.2283e-05 | 5.8798e-05 | 0.11033 | 0.11033 | 0.11033 | 0.99608 | -0.075237 | 0.99744 | -0.049076 | 30.3096
13 | 0.035357 | 0.0088747 | -0.035321 | -0.0088522 | 3.5884e-05 | 2.252e-05 | 0.052823 | 0.052823 | 0.052823 | 0.99608 | -0.075237 | 0.99498 | -0.09654 | 14.5118
14 | 0.0053812 | 0.0013486 | -0.005381 | -0.0013486 | 1.9172e-07 | 2.046e-08 | 0.0080532 | 0.0080533 | 0.0080533 | 0.9943 | -0.1097 | 0.99426 | -0.11045 | 2.2124
15 | -0.11603 | -0.029149 | 0.11624 | 0.029281 | 0.00020598 | 0.00013159 | 0.17313 | 0.17313 | 0.17313 | 0.99744 | -0.049076 | 0.99938 | -0.011951 | 47.5618
16 | 0.005381 | 0.0013486 | -0.0053807 | -0.0013485 | 3.498e-07 | 3.7354e-08 | 0.0080533 | 0.0080533 | 0.0080533 | 0.99426 | -0.11045 | 0.99419 | -0.11182 | 2.2124
17 | -0.14978 | -0.037687 | 0.14987 | 0.037742 | 8.5587e-05 | 5.4535e-05 | 0.22307 | 0.22307 | 0.22307 | 0.99938 | -0.011951 | 1 | 0 | 30.6414
18 | 0.049847 | 0.012515 | -0.049825 | -0.012501 | 2.1582e-05 | 1.3677e-05 | 0.074419 | 0.074419 | 0.074419 | 0.9968 | -0.061447 | 0.99633 | -0.070528 | 20.4449
19 | -0.066763 | -0.016755 | 0.066786 | 0.016769 | 2.3295e-05 | 1.4827e-05 | 0.099672 | 0.099672 | 0.099672 | 0.9968 | -0.061447 | 0.99718 | -0.054133 | 27.3823
20 | 0.037747 | 0.0094742 | -0.037713 | -0.0094523 | 3.4838e-05 | 2.1916e-05 | 0.056381 | 0.056381 | 0.056381 | 0.99633 | -0.070528 | 0.99532 | -0.089898 | 15.4892
21 | -0.12771 | -0.032116 | 0.12802 | 0.032309 | 0.00030232 | 0.00019319 | 0.19062 | 0.19062 | 0.19062 | 0.99718 | -0.054133 | 0.99975 | -0.0046998 | 52.3675
22 | 0.019487 | 0.0048846 | -0.019486 | -0.004884 | 1.0692e-06 | 6.4062e-07 | 0.029134 | 0.029134 | 0.029134 | 0.99532 | -0.089898 | 0.99526 | -0.09105 | 8.0038
23 | -0.14255 | -0.035951 | 0.14258 | 0.035971 | 3.2077e-05 | 2.043e-05 | 0.21224 | 0.21224 | 0.21224 | 0.99975 | -0.0046998 | 1 | 0 | 29.1542
24 | 0.0084471 | 0.0021171 | -0.0084462 | -0.0021167 | 9.2404e-07 | 3.9065e-07 | 0.012629 | 0.012629 | 0.012629 | 0.99526 | -0.09105 | 0.99514 | -0.093346 | 3.4696
25 | 0.011039 | 0.0027669 | -0.011038 | -0.0027663 | 1.0386e-06 | 5.326e-07 | 0.016505 | 0.016505 | 0.016505 | 0.99526 | -0.09105 | 0.99516 | -0.093025 | 4.5342
26 | 0.003699 | 0.00092696 | -0.0036989 | -0.00092702 | 1.2009e-07 | -5.9139e-08 | 0.005531 | 0.005531 | 0.005531 | 0.99514 | -0.093346 | 0.99511 | -0.094028 | 1.5195
27 | 0.0060652 | 0.00152 | -0.0060645 | -0.0015199 | 7.297e-07 | 1.5966e-07 | 0.009069 | 0.0090691 | 0.0090691 | 0.99516 | -0.093025 | 0.99503 | -0.095551 | 2.4915
28 | -0.0060639 | -0.0015198 | 0.0060645 | 0.0015199 | 5.7751e-07 | 1.2643e-07 | 0.0090692 | 0.0090691 | 0.0090692 | 0.99493 | -0.09755 | 0.99503 | -0.095551 | 2.4915

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.31168 | 0.078119

## res_load
| p_mw | q_mvar
0 | 0.02184 | 0.0054737
1 | 0.0050916 | 0.0012761
2 | 0.024211 | 0.0060677
3 | 0.0095839 | 0.002402
4 | 0.0023652 | 0.00059278
5 | 0.018183 | 0.004557
6 | 0.0085183 | 0.0021349
7 | 0.0039891 | 0.00099977
8 | 0.042095 | 0.01055
9 | 0.035321 | 0.0088522
10 | 0.033544 | 0.0084068
11 | 0.016916 | 0.0042396
12 | 0.012078 | 0.0030271
13 | 0.018225 | 0.0045677
14 | 0.014529 | 0.0036414
15 | 0.017579 | 0.0044058
16 | 0.0047472 | 0.0011898
17 | 0.0049728 | 0.0012463
18 | 0.0060639 | 0.0015198
19 | 0.0053807 | 0.0013485
20 | 0.0036989 | 0.00092702

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1