## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1710-4_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1710-4_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1710-4_0_2_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1710-4_0_2_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1710-4_0_2_node_183 | 0.4 | n |  | TRUE
5 | bus_LV_1710-4_0_2_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1710-4_0_2_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_1710-4_0_2_node_185 | 0.4 | n |  | TRUE
8 | bus_LV_1710-4_0_2_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1710-4_0_2_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1710-4_0_2_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1710-4_0_2_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1710-4_0_2_node_171 | 0.4 | n |  | TRUE
13 | bus_LV_1710-4_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1710-4_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1710-4_0_2_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1710-4_0_2_node_166 | 0.4 | n |  | TRUE
17 | bus_LV_1710-4_0_2_node_165 | 0.4 | n |  | TRUE
18 | bus_LV_1710-4_0_2_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1710-4_0_2_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1710-4_0_2_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1710-4_0_2_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1710-4_0_2_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1710-4_0_2_node_186 | 0.4 | n |  | TRUE
24 | bus_LV_1710-4_0_2_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1710-4_0_2_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_1710-4_0_2_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1710-4_0_2_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1710-4_0_2_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1710-4_0_2_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1710-4_0_2_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1710-4_0_2_node_173 | 0.4 | n |  | TRUE
32 | bus_LV_1710-4_0_2_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_1710-4_0_2_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1710-4_0_2_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1710-4_0_2_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_1710-4_0_2_node_175 | 0.4 | n |  | TRUE
37 | bus_LV_1710-4_0_2_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_1710-4_0_2_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_1710-4_0_2_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_1710-4_0_2_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_1710-4_0_2_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_1710-4_0_2_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_1710-4_0_2_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_1710-4_0_2_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_1710-4_0_2_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1710-4_0_2_node_174 | 0.4 | n |  | TRUE
47 | bus_LV_1710-4_0_2_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_1710-4_0_2_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_1710-4_0_2_node_181 | 0.4 | n |  | TRUE
50 | bus_LV_1710-4_0_2_node_143 | 0.4 | n |  | TRUE
51 | bus_LV_1710-4_0_2_node_144 | 0.4 | n |  | TRUE
52 | bus_LV_1710-4_0_2_node_145 | 0.4 | n |  | TRUE
53 | bus_LV_1710-4_0_2_node_189 | 0.4 | n |  | TRUE
54 | bus_LV_1710-4_0_2_node_147 | 0.4 | n |  | TRUE
55 | bus_LV_1710-4_0_2_node_148 | 0.4 | n |  | TRUE
56 | bus_LV_1710-4_0_2_node_149 | 0.4 | n |  | TRUE
57 | bus_LV_1710-4_0_2_node_150 | 0.4 | n |  | TRUE
58 | bus_LV_1710-4_0_2_node_151 | 0.4 | n |  | TRUE
59 | bus_LV_1710-4_0_2_node_152 | 0.4 | n |  | TRUE
60 | bus_LV_1710-4_0_2_node_177 | 0.4 | n |  | TRUE
61 | bus_LV_1710-4_0_2_node_157 | 0.4 | n |  | TRUE
62 | bus_LV_1710-4_0_2_node_158 | 0.4 | n |  | TRUE
63 | bus_LV_1710-4_0_2_node_159 | 0.4 | n |  | TRUE
64 | bus_LV_1710-4_0_2_node_160 | 0.4 | n |  | TRUE
65 | bus_LV_1710-4_0_2_node_167 | 0.4 | n |  | TRUE
66 | bus_LV_1710-4_0_2_node_162 | 0.4 | n |  | TRUE
67 | bus_LV_1710-4_0_2_node_161 | 0.4 | n |  | TRUE
68 | bus_LV_1710-4_0_2_node_163 | 0.4 | n |  | TRUE
69 | bus_LV_1710-4_0_2_node_164 | 0.4 | n |  | TRUE
70 | bus_LV_1710-4_0_2_node_172 | 0.4 | n |  | TRUE
71 | bus_LV_1710-4_0_2_node_168 | 0.4 | n |  | TRUE
72 | bus_LV_1710-4_0_2_node_169 | 0.4 | n |  | TRUE
73 | bus_LV_1710-4_0_2_node_170 | 0.4 | n |  | TRUE
74 | bus_LV_1710-4_0_2_node_176 | 0.4 | n |  | TRUE
75 | bus_LV_1710-4_0_2_node_178 | 0.4 | n |  | TRUE
76 | bus_LV_1710-4_0_2_node_180 | 0.4 | n |  | TRUE
77 | bus_LV_1710-4_0_2_node_179 | 0.4 | n |  | TRUE
78 | bus_LV_1710-4_0_2_node_191 | 0.4 | n |  | TRUE
79 | bus_LV_1710-4_0_2_node_184 | 0.4 | n |  | TRUE
80 | bus_LV_1710-4_0_2_node_182 | 0.4 | n |  | TRUE
81 | bus_LV_1710-4_0_2_node_188 | 0.4 | n |  | TRUE
82 | bus_MV_0_node_162 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1710-4_0_2_load_0 | 0 | 0.00013631 | 3.4163e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1710-4_0_2_load_1 | 1 | 0.000156 | 3.9097e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1710-4_0_2_load_2 | 3 | 0.00045845 | 0.0001149 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1710-4_0_2_load_183 | 4 | 0.00028782 | 7.2134e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1710-4_0_2_load_185 | 7 | 0.00019569 | 4.9045e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1710-4_0_2_load_5 | 8 | 0.0012544 | 0.00031438 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1710-4_0_2_load_6 | 9 | 0.00066653 | 0.00016705 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1710-4_0_2_load_9 | 13 | 0.00026272 | 6.5843e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1710-4_0_2_load_11 | 15 | 0.00059133 | 0.0001482 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1710-4_0_2_load_166 | 16 | 0.0075585 | 0.0018943 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1710-4_0_2_load_165 | 17 | 0.0015384 | 0.00038555 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1710-4_0_2_load_12 | 18 | 0.0032414 | 0.00081236 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1710-4_0_2_load_13 | 19 | 0.0030796 | 0.00077181 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1710-4_0_2_load_16 | 22 | 0.0018498 | 0.0004636 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1710-4_0_2_load_186 | 23 | 0.0003539 | 8.8695e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1710-4_0_2_load_27 | 25 | 0.00030569 | 7.6613e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1710-4_0_2_load_21 | 26 | 0.00014923 | 3.7401e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1710-4_0_2_load_22 | 27 | 0.00030259 | 7.5836e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1710-4_0_2_load_18 | 28 | 0.00015236 | 3.8186e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1710-4_0_2_load_19 | 29 | 0.00012358 | 3.0973e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1710-4_0_2_load_20 | 30 | 0.00029371 | 7.3611e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1710-4_0_2_load_173 | 31 | 0.00013352 | 3.3464e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1710-4_0_2_load_24 | 32 | 0.0027393 | 0.00068654 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1710-4_0_2_load_23 | 33 | 0.00073252 | 0.00018359 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1710-4_0_2_load_25 | 34 | 8.5281e-05 | 2.1373e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1710-4_0_2_load_26 | 35 | 8.5128e-05 | 2.1335e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1710-4_0_2_load_175 | 36 | 0.0001137 | 2.8497e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1710-4_0_2_load_34 | 37 | 0.00012369 | 3.1e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1710-4_0_2_load_36 | 38 | 0.0001609 | 4.0324e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1710-4_0_2_load_39 | 40 | 0.00010095 | 2.5301e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1710-4_0_2_load_40 | 41 | 0.00040498 | 0.0001015 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1710-4_0_2_load_38 | 42 | 0.00014703 | 3.685e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1710-4_0_2_load_41 | 44 | 0.00071406 | 0.00017896 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1710-4_0_2_load_174 | 46 | 0.00093801 | 0.00023509 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1710-4_0_2_load_44 | 47 | 0.00023983 | 6.0108e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1710-4_0_2_load_45 | 48 | 0.00031106 | 7.7959e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1710-4_0_2_load_181 | 49 | 0.00057955 | 0.00014525 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1710-4_0_2_load_145 | 52 | 0.0022316 | 0.00055928 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1710-4_0_2_load_189 | 53 | 0.0030347 | 0.00076058 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1710-4_0_2_load_147 | 54 | 0.00022789 | 5.7115e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1710-4_0_2_load_148 | 55 | 0.00024056 | 6.0289e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1710-4_0_2_load_150 | 57 | 0.00024707 | 6.1922e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1710-4_0_2_load_151 | 58 | 0.00012376 | 3.1016e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1710-4_0_2_load_152 | 59 | 0.00027552 | 6.9053e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1710-4_0_2_load_157 | 61 | 0.00059113 | 0.00014815 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1710-4_0_2_load_158 | 62 | 0.00012496 | 3.1317e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1710-4_0_2_load_167 | 65 | 0.0023663 | 0.00059306 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1710-4_0_2_load_162 | 66 | 0.005323 | 0.0013341 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1710-4_0_2_load_161 | 67 | 0.0040791 | 0.0010223 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1710-4_0_2_load_163 | 68 | 0.0020158 | 0.00050521 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1710-4_0_2_load_164 | 69 | 0.0036902 | 0.00092485 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1710-4_0_2_load_168 | 71 | 0.00061992 | 0.00015537 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1710-4_0_2_load_169 | 72 | 0.0062717 | 0.0015718 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1710-4_0_2_load_170 | 73 | 0.0047325 | 0.0011861 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1710-4_0_2_load_178 | 75 | 0.00016064 | 4.026e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1710-4_0_2_load_179 | 77 | 0.00087514 | 0.00021933 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1710-4_0_2_load_191 | 78 | 0.00019876 | 4.9814e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1710-4_0_2_load_188 | 81 | 0.0017031 | 0.00042685 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 66 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1710-4_0_2_line_0 |  | 0 | 1 | 0.026449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1710-4_0_2_line_1 |  | 0 | 2 | 0.271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1710-4_0_2_line_2 |  | 1 | 3 | 0.070236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1710-4_0_2_line_3 |  | 2 | 5 | 0.043832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1710-4_0_2_line_4 |  | 2 | 6 | 0.21932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1710-4_0_2_line_5 |  | 3 | 4 | 0.17995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1710-4_0_2_line_6 |  | 4 | 80 | 0.017494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1710-4_0_2_line_7 |  | 5 | 7 | 0.14974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1710-4_0_2_line_8 |  | 6 | 37 | 0.059327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1710-4_0_2_line_9 |  | 8 | 9 | 0.025479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1710-4_0_2_line_10 |  | 8 | 10 | 0.016339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1710-4_0_2_line_11 |  | 9 | 11 | 0.073366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1710-4_0_2_line_12 |  | 10 | 12 | 0.12535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1710-4_0_2_line_13 |  | 11 | 13 | 0.0332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1710-4_0_2_line_14 |  | 11 | 14 | 0.11966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1710-4_0_2_line_15 |  | 12 | 72 | 0.028869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1710-4_0_2_line_16 |  | 13 | 15 | 0.10049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1710-4_0_2_line_17 |  | 14 | 16 | 0.031609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1710-4_0_2_line_18 |  | 14 | 17 | 0.043736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1710-4_0_2_line_19 |  | 15 | 18 | 0.010185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1710-4_0_2_line_20 |  | 16 | 65 | 0.050752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1710-4_0_2_line_21 |  | 19 | 20 | 0.034585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1710-4_0_2_line_22 |  | 19 | 21 | 0.059403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1710-4_0_2_line_23 |  | 20 | 22 | 0.023345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1710-4_0_2_line_24 |  | 20 | 23 | 0.1181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1710-4_0_2_line_25 |  | 21 | 24 | 0.044201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1710-4_0_2_line_26 |  | 22 | 25 | 0.019118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1710-4_0_2_line_27 |  | 24 | 26 | 0.015691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1710-4_0_2_line_28 |  | 24 | 27 | 0.0071752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1710-4_0_2_line_29 |  | 24 | 28 | 0.010819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1710-4_0_2_line_30 |  | 27 | 32 | 0.043911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1710-4_0_2_line_31 |  | 28 | 29 | 0.1471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1710-4_0_2_line_32 |  | 29 | 30 | 0.0059283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1710-4_0_2_line_33 |  | 30 | 31 | 0.03084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1710-4_0_2_line_34 |  | 31 | 46 | 0.012087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1710-4_0_2_line_35 |  | 32 | 33 | 0.0076128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1710-4_0_2_line_36 |  | 34 | 35 | 0.025998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1710-4_0_2_line_37 |  | 35 | 36 | 0.093292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1710-4_0_2_line_38 |  | 36 | 74 | 0.030171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1710-4_0_2_line_39 |  | 38 | 39 | 0.015728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1710-4_0_2_line_40 |  | 38 | 40 | 0.20786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1710-4_0_2_line_41 |  | 39 | 41 | 0.015768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1710-4_0_2_line_42 |  | 40 | 43 | 0.14242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1710-4_0_2_line_43 |  | 40 | 42 | 0.010324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1710-4_0_2_line_44 |  | 41 | 44 | 0.018219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1710-4_0_2_line_45 |  | 43 | 47 | 0.11946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1710-4_0_2_line_46 |  | 43 | 48 | 0.16419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1710-4_0_2_line_47 |  | 44 | 45 | 0.13344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1710-4_0_2_line_48 |  | 45 | 46 | 0.21173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1710-4_0_2_line_49 |  | 48 | 49 | 0.016475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1710-4_0_2_line_50 |  | 49 | 80 | 0.023076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1710-4_0_2_line_51 |  | 50 | 51 | 0.11794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_1710-4_0_2_line_52 |  | 50 | 52 | 0.035691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1710-4_0_2_line_53 |  | 50 | 53 | 0.21691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_1710-4_0_2_line_54 |  | 51 | 54 | 0.13431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_1710-4_0_2_line_55 |  | 53 | 67 | 0.1363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_1710-4_0_2_line_56 |  | 54 | 55 | 0.065464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1710-4_0_2_line_57 |  | 54 | 56 | 0.11916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_1710-4_0_2_line_58 |  | 55 | 57 | 0.031145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1710-4_0_2_line_59 |  | 56 | 58 | 0.11867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_1710-4_0_2_line_60 |  | 56 | 59 | 0.14741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1710-4_0_2_line_61 |  | 58 | 60 | 0.0852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_1710-4_0_2_line_62 |  | 60 | 76 | 0.20997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_1710-4_0_2_line_63 |  | 60 | 74 | 0.074584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1710-4_0_2_line_64 |  | 61 | 62 | 0.014175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1710-4_0_2_line_65 |  | 62 | 63 | 0.13638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1710-4_0_2_line_66 |  | 63 | 64 | 0.043388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1710-4_0_2_line_67 |  | 63 | 65 | 0.25257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1710-4_0_2_line_68 |  | 64 | 66 | 0.030144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_1710-4_0_2_line_69 |  | 64 | 67 | 0.063165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_1710-4_0_2_line_70 |  | 65 | 71 | 0.022195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1710-4_0_2_line_71 |  | 68 | 69 | 0.027551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1710-4_0_2_line_72 |  | 69 | 70 | 0.29048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1710-4_0_2_line_73 |  | 70 | 73 | 0.17063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1710-4_0_2_line_74 |  | 72 | 73 | 0.014673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1710-4_0_2_line_75 |  | 74 | 75 | 0.085618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1710-4_0_2_line_76 |  | 75 | 77 | 0.053016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1710-4_0_2_line_77 |  | 76 | 78 | 0.087939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1710-4_0_2_line_78 |  | 76 | 79 | 0.11752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_1710-4_0_2_line_79 |  | 79 | 81 | 0.17672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1710-4_0_2_line_80 |  | 79 | 80 | 0.21108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1710-4_0_2_trafo_162 | 0.63 MVA 20/0.4 kV | 82 | 66 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2682567.5067 | 1218807.0694 | 2682556.3239 | 1218802.1064 | 2682546.4467 | 1218791.885
1 | 2682567.5067 | 1218807.0694 | 2682764.1822 | 1218993.506
2 | 2682552.4917 | 1218754.9664 | 2682561.2727 | 1218747.3607 | 2682564.9732 | 1218745.9666 | 2682566.6317 | 1218759.3763 | 2682563.0893 | 1218767.9774 | 2682551.644 | 1218777.792 | 2682544.9574 | 1218785.4378 | 2682546.4467 | 1218791.885
3 | 2682796.1962 | 1218963.4752 | 2682764.1822 | 1218993.506
4 | 2682764.1822 | 1218993.506 | 2682706.3239 | 1219205.0548
5 | 2682402.0167 | 1218656.2737 | 2682552.4917 | 1218754.9664
6 | 2682384.5876 | 1218654.765 | 2682402.0167 | 1218656.2737
7 | 2682796.1962 | 1218963.4752 | 2682801.2866 | 1218967.4708 | 2682815.3102 | 1218969.2892 | 2682839.7513 | 1218968.6173 | 2682853.3538 | 1218971.2415 | 2682886.6928 | 1218974.752 | 2682904.8304 | 1218987.9909 | 2682924.5339 | 1218990.7002 | 2682937.0318 | 1218999.6023
8 | 2682706.3239 | 1219205.0548 | 2682705.744 | 1219256.6367 | 2682705.6566 | 1219264.3785
9 | 2681191.3902 | 1219065.7587 | 2681197.4432 | 1219062.3079 | 2681208.1135 | 1219047.1809
10 | 2681177.1959 | 1219073.8508 | 2681191.3902 | 1219065.7587
11 | 2681276.757 | 1219046.6344 | 2681268.3205 | 1219051.9562 | 2681250.8417 | 1219050.2611 | 2681215.5301 | 1219041.6741 | 2681210.0196 | 1219044.4786 | 2681208.1135 | 1219047.1809
12 | 2681177.1959 | 1219073.8508 | 2681130.3395 | 1219190.112
13 | 2681276.757 | 1219046.6344 | 2681287.4013 | 1219056.386 | 2681300.1438 | 1219062.5417 | 2681304.6694 | 1219063.4356
14 | 2681232.449 | 1218940.8601 | 2681229.8604 | 1218948.1296 | 2681228.7497 | 1218954.9968 | 2681231.9454 | 1218962.2007 | 2681241.1233 | 1218976.5353 | 2681253.1407 | 1218995.8008 | 2681268.5583 | 1219021.1835 | 2681273.2846 | 1219030.2317 | 2681276.9227 | 1219037.2749 | 2681277.7431 | 1219042.7786 | 2681276.757 | 1219046.6344
15 | 2681130.3395 | 1219190.112 | 2681142.6387 | 1219193.1481 | 2681156.2182 | 1219198.0252 | 2681157.6558 | 1219199.0617
16 | 2681304.6694 | 1219063.4356 | 2681311.2101 | 1219064.7275 | 2681318.2127 | 1219066.035 | 2681323.3158 | 1219072.4979 | 2681324.5128 | 1219081.5535 | 2681320.1603 | 1219087.3758 | 2681315.9451 | 1219090.3647 | 2681309.0454 | 1219088.7472 | 2681295.7753 | 1219083.9964 | 2681275.9279 | 1219084.0256 | 2681267.3682 | 1219085.0318 | 2681260.3606 | 1219086.8775
17 | 2681232.449 | 1218940.8601 | 2681264.055 | 1218940.4462
18 | 2681232.449 | 1218940.8601 | 2681236.0435 | 1218929.9574 | 2681247.52 | 1218905.998 | 2681250.1398 | 1218900.9468
19 | 2681250.5117 | 1219089.4715 | 2681260.3606 | 1219086.8775
20 | 2681264.055 | 1218940.4462 | 2681269.0387 | 1218940.3809 | 2681280.5342 | 1218937.269 | 2681287.6567 | 1218937.5885 | 2681292.668 | 1218939.6694 | 2681295.8568 | 1218944.5939 | 2681296.8313 | 1218952.7126 | 2681297.1194 | 1218959.9658
21 | 2682056.0573 | 1219595.0463 | 2682023.1419 | 1219584.4311
22 | 2682024.5715 | 1219530.5031 | 2682024.8262 | 1219540.113 | 2682016.6932 | 1219582.3514 | 2682023.1419 | 1219584.4311
23 | 2682056.0573 | 1219595.0463 | 2682051.2964 | 1219617.9008
24 | 2682056.0573 | 1219595.0463 | 2682152.4165 | 1219526.762
25 | 2681994.8486 | 1219497.7166 | 2682015.3809 | 1219520.0474 | 2682024.5715 | 1219530.5031
26 | 2682051.2964 | 1219617.9008 | 2682047.3976 | 1219636.6174
27 | 2681994.8486 | 1219497.7166 | 2681984.7898 | 1219485.6744
28 | 2681994.8486 | 1219497.7166 | 2681990.9832 | 1219503.7617
29 | 2681994.8486 | 1219497.7166 | 2682000.3879 | 1219488.4235
30 | 2681971.0276 | 1219542.7551 | 2681983.2162 | 1219515.7797 | 2681986.596 | 1219510.6228 | 2681990.9832 | 1219503.7617
31 | 2682082.4936 | 1219366.6928 | 2682055.9791 | 1219399.1593 | 2682028.425 | 1219441.3857 | 2682000.3879 | 1219488.4235
32 | 2682082.4936 | 1219366.6928 | 2682086.2434 | 1219362.1012
33 | 2682086.2434 | 1219362.1012 | 2682089.6598 | 1219357.918 | 2682103.594 | 1219346.3467 | 2682106.7704 | 1219339.7438
34 | 2682112.0105 | 1219328.8513 | 2682106.7704 | 1219339.7438
35 | 2681971.0276 | 1219542.7551 | 2681967.893 | 1219549.6925
36 | 2681985.0662 | 1219177.7846 | 2681977.9725 | 1219200.9759 | 2681977.893 | 1219202.7204
37 | 2682007.0224 | 1219087.6659 | 2682004.5488 | 1219093.1255 | 2682001.9497 | 1219122.5871 | 2681985.0662 | 1219177.7846
38 | 2682023.8578 | 1219062.7599 | 2682009.535 | 1219082.1201 | 2682007.0224 | 1219087.6659
39 | 2682276.8424 | 1219189.3764 | 2682288.1353 | 1219178.4295
40 | 2682364.67 | 1218985.1761 | 2682288.1353 | 1219178.4295
41 | 2682276.8424 | 1219189.3764 | 2682287.6707 | 1219197.2089 | 2682290.0114 | 1219197.7569
42 | 2682331.8118 | 1218851.3552 | 2682341.795 | 1218860.5215 | 2682349.0592 | 1218875.2983 | 2682350.6085 | 1218909.8094 | 2682353.8448 | 1218941.4196 | 2682358.5681 | 1218976.9196 | 2682364.67 | 1218985.1761
43 | 2682364.67 | 1218985.1761 | 2682364.67 | 1218985.1761 | 2682374.9276 | 1218986.3419
44 | 2682290.0114 | 1219197.7569 | 2682306.7499 | 1219201.6754 | 2682306.7364 | 1219202.703
45 | 2682286.1181 | 1218960.7968 | 2682305.1598 | 1218924.1021 | 2682328.6446 | 1218853.713 | 2682331.8118 | 1218851.3552
46 | 2682331.8118 | 1218851.3552 | 2682332.3181 | 1218842.7342 | 2682373.9917 | 1218692.8695
47 | 2682323.7296 | 1219331.0961 | 2682320.9078 | 1219325.4978 | 2682308.5202 | 1219303.1118 | 2682301.9095 | 1219278.9711 | 2682306.1549 | 1219246.9195 | 2682306.7364 | 1219202.703
48 | 2682112.0105 | 1219328.8513 | 2682323.7296 | 1219331.0961
49 | 2682373.9917 | 1218692.8695 | 2682378.4054 | 1218676.9972
50 | 2682384.5876 | 1218654.765 | 2682378.4054 | 1218676.9972
51 | 2681934.5537 | 1218745.2649 | 2681921.3286 | 1218747.151 | 2681911.4495 | 1218741.9451 | 2681903.8557 | 1218732.2787 | 2681886.1399 | 1218689.8071 | 2681875.0697 | 1218659.1568 | 2681874.0782 | 1218656.7416
52 | 2681888.5839 | 1218624.1193 | 2681874.0782 | 1218656.7416
53 | 2681874.0782 | 1218656.7416 | 2681678.32 | 1218750.1617
54 | 2682057.7882 | 1218691.8442 | 2681934.5537 | 1218745.2649
55 | 2681543.1093 | 1218767.3325 | 2681678.32 | 1218750.1617
56 | 2682057.7882 | 1218691.8442 | 2682056.2137 | 1218678.7725 | 2682049.7301 | 1218646.9288 | 2682047.2509 | 1218633.5079 | 2682048.2359 | 1218627.4345
57 | 2682098.1175 | 1218802.7765 | 2682095.0758 | 1218794.9294 | 2682083.4431 | 1218777.1017 | 2682074.9201 | 1218758.3274 | 2682059.735 | 1218708.0071 | 2682057.7882 | 1218691.8442
58 | 2682048.2359 | 1218627.4345 | 2682048.7605 | 1218624.2003 | 2682060.4503 | 1218603.214 | 2682061.1515 | 1218599.4323
59 | 2682098.1175 | 1218802.7765 | 2682100.4845 | 1218817.719 | 2682101.3209 | 1218827.5259 | 2682100.9486 | 1218838.5615 | 2682099.0794 | 1218850.8217 | 2682096.9183 | 1218860.0313 | 2682094.0943 | 1218868.3313 | 2682090.2924 | 1218873.2377 | 2682080.9058 | 1218881.336 | 2682074.5882 | 1218888.6983 | 2682067.2854 | 1218902.0066 | 2682064.4207 | 1218910.0585
60 | 2682160.5287 | 1218675.8301 | 2682151.9602 | 1218695.0247 | 2682140.9299 | 1218708.9041 | 2682130.3533 | 1218723.468 | 2682119.6143 | 1218732.7484 | 2682109.5944 | 1218739.9707 | 2682108.3947 | 1218741.6553 | 2682107.5449 | 1218743.8339 | 2682106.5129 | 1218746.5659 | 2682104.1942 | 1218758.3974 | 2682101.9051 | 1218774.6878 | 2682100.1199 | 1218791.8635 | 2682098.1175 | 1218802.7765
61 | 2682046.7078 | 1218991.8941 | 2682044.9825 | 1218986.0109 | 2682044.4158 | 1218978.1089 | 2682045.0877 | 1218970.1129 | 2682048.5427 | 1218957.3186 | 2682053.76 | 1218940.0234 | 2682064.4207 | 1218910.0585
62 | 2682196.9875 | 1218857.6314 | 2682191.0402 | 1218868.9458 | 2682192.5624 | 1218874.1369 | 2682182.1321 | 1218887.4575 | 2682172.6733 | 1218896.9333 | 2682162.9141 | 1218905.082 | 2682139.235 | 1218922.5783 | 2682100.1348 | 1218952.0924 | 2682083.3227 | 1218965.3474 | 2682075.3256 | 1218974.5211 | 2682064.4023 | 1218987.8462 | 2682058.1191 | 1218992.7184 | 2682053.2471 | 1218993.2183 | 2682046.7078 | 1218991.8941
63 | 2682023.8578 | 1219062.7599 | 2682031.1392 | 1219044.9261 | 2682039.0656 | 1219018.2842 | 2682043.8727 | 1219004.8637 | 2682046.7078 | 1218991.8941
64 | 2681391.3305 | 1218659.6999 | 2681396.7452 | 1218672.8002
65 | 2681474.4197 | 1218780.0903 | 2681467.4723 | 1218768.621 | 2681454.9973 | 1218757.8545 | 2681437.441 | 1218747.3409 | 2681424.6761 | 1218734.4468 | 2681413.2209 | 1218715.1442 | 2681402.3799 | 1218686.4326 | 2681396.7452 | 1218672.8002
66 | 2681474.4197 | 1218780.0903 | 2681482.7205 | 1218793.6016 | 2681488.7055 | 1218799.9655 | 2681496.4106 | 1218806.5307 | 2681504.4394 | 1218809.965
67 | 2681297.1194 | 1218959.9658 | 2681474.4197 | 1218780.0903
68 | 2681504.4394 | 1218809.965 | 2681504.4716 | 1218817.5928 | 2681513.4152 | 1218826.8323 | 2681522.3522 | 1218830.4928
69 | 2681504.4394 | 1218809.965 | 2681512.443 | 1218810.2525 | 2681519.8218 | 1218806.8289 | 2681525.7162 | 1218802.062 | 2681531.7192 | 1218794.906 | 2681537.4937 | 1218782.8215 | 2681543.1124 | 1218770.479 | 2681543.1093 | 1218767.3325
70 | 2681283.229 | 1218977.2767 | 2681297.1194 | 1218959.9658
71 | 2681496.8471 | 1219510.6811 | 2681502.6427 | 1219505.1686 | 2681519.1911 | 1219494.7553
72 | 2681255.1132 | 1219349.6068 | 2681496.8471 | 1219510.6811
73 | 2681255.1132 | 1219349.6068 | 2681221.7021 | 1219321.4437 | 2681205.9054 | 1219306.096 | 2681202.5113 | 1219296.1987 | 2681197.0653 | 1219273.1426 | 2681192.9223 | 1219257.498 | 2681188.7406 | 1219245.244 | 2681175.7384 | 1219224.1973 | 2681171.6432 | 1219213.9458 | 2681168.0168 | 1219209.3605
74 | 2681157.6558 | 1219199.0617 | 2681160.5247 | 1219201.1303 | 2681166.6742 | 1219207.6629 | 2681168.0168 | 1219209.3605
75 | 2682023.8578 | 1219062.7599 | 2682032.7472 | 1219067.5855 | 2682039.7301 | 1219064.2572 | 2682056.2805 | 1219050.6872 | 2682076.072 | 1219032.7034 | 2682090.0586 | 1219022.3336 | 2682092.125 | 1219021.5425
76 | 2682092.125 | 1219021.5425 | 2682100.2905 | 1219018.4164 | 2682109.617 | 1219020.1683 | 2682117.5599 | 1219019.8775 | 2682129.0807 | 1219011.1083 | 2682134.8446 | 1219000.1794
77 | 2682196.9875 | 1218857.6314 | 2682194.6794 | 1218849.9834 | 2682194.9656 | 1218844.0946 | 2682201.004 | 1218834.4381 | 2682201.8831 | 1218829.5803 | 2682196.7688 | 1218831.133 | 2682192.2831 | 1218831.6826 | 2682194.2119 | 1218825.0159 | 2682195.7211 | 1218820.1557 | 2682198.6104 | 1218815.9372 | 2682198.9049 | 1218809.4481 | 2682198.3686 | 1218803.7591 | 2682195.7866 | 1218799.4651 | 2682189.4081 | 1218799.6662 | 2682184.2537 | 1218804.6762
78 | 2682196.9875 | 1218857.6314 | 2682191.0402 | 1218868.9458 | 2682192.5624 | 1218874.1369 | 2682215.8036 | 1218842.203 | 2682225.3405 | 1218825.9793 | 2682255.2159 | 1218797.8841
79 | 2682255.2159 | 1218797.8841 | 2682254.1475 | 1218789.5082 | 2682260.186 | 1218779.8518 | 2682266.879 | 1218762.377 | 2682278.0973 | 1218735.4474 | 2682281.5228 | 1218719.3506 | 2682281.023 | 1218700.5868 | 2682277.7248 | 1218684.3972 | 2682271.3737 | 1218677.1158 | 2682264.3008 | 1218668.7904 | 2682258.975 | 1218660.9116 | 2682256.2722 | 1218650.523 | 2682254.6008 | 1218634.1446
80 | 2682255.2159 | 1218797.8841 | 2682269.1955 | 1218780.9436 | 2682283.869 | 1218762.1337 | 2682295.173 | 1218746.5906 | 2682300.876 | 1218734.8504 | 2682317.7577 | 1218684.7948 | 2682322.4196 | 1218676.4536 | 2682328.6401 | 1218667.3668 | 2682333.807 | 1218662.5795 | 2682340.1319 | 1218658.5753 | 2682345.6507 | 1218656.3279 | 2682353.8344 | 1218654.0283 | 2682363.3564 | 1218653.2038 | 2682384.5876 | 1218654.765

## bus_geodata
| x | y | coords
0 | 2682567.5067 | 1218807.0694
1 | 2682546.4467 | 1218791.885
2 | 2682764.1822 | 1218993.506
3 | 2682552.4917 | 1218754.9664
4 | 2682402.0167 | 1218656.2737
5 | 2682796.1962 | 1218963.4752
6 | 2682706.3239 | 1219205.0548
7 | 2682937.0318 | 1218999.6023
8 | 2681191.3902 | 1219065.7587
9 | 2681208.1135 | 1219047.1809
10 | 2681177.1959 | 1219073.8508
11 | 2681276.757 | 1219046.6344
12 | 2681130.3395 | 1219190.112
13 | 2681304.6694 | 1219063.4356
14 | 2681232.449 | 1218940.8601
15 | 2681260.3606 | 1219086.8775
16 | 2681264.055 | 1218940.4462
17 | 2681250.1398 | 1218900.9468
18 | 2681250.5117 | 1219089.4715
19 | 2682023.1419 | 1219584.4311
20 | 2682056.0573 | 1219595.0463
21 | 2682024.5715 | 1219530.5031
22 | 2682051.2964 | 1219617.9008
23 | 2682152.4165 | 1219526.762
24 | 2681994.8486 | 1219497.7166
25 | 2682047.3976 | 1219636.6174
26 | 2681984.7898 | 1219485.6744
27 | 2681990.9832 | 1219503.7617
28 | 2682000.3879 | 1219488.4235
29 | 2682082.4936 | 1219366.6928
30 | 2682086.2434 | 1219362.1012
31 | 2682106.7704 | 1219339.7438
32 | 2681971.0276 | 1219542.7551
33 | 2681967.893 | 1219549.6925
34 | 2681977.893 | 1219202.7204
35 | 2681985.0662 | 1219177.7846
36 | 2682007.0224 | 1219087.6659
37 | 2682705.6567 | 1219264.3785
38 | 2682288.1353 | 1219178.4295
39 | 2682276.8424 | 1219189.3764
40 | 2682364.67 | 1218985.1761
41 | 2682290.0114 | 1219197.7569
42 | 2682374.9276 | 1218986.3419
43 | 2682331.8118 | 1218851.3552
44 | 2682306.7364 | 1219202.703
45 | 2682323.7296 | 1219331.0961
46 | 2682112.0105 | 1219328.8513
47 | 2682286.1181 | 1218960.7968
48 | 2682373.9917 | 1218692.8695
49 | 2682378.4054 | 1218676.9972
50 | 2681874.0782 | 1218656.7416
51 | 2681934.5537 | 1218745.2649
52 | 2681888.5839 | 1218624.1193
53 | 2681678.32 | 1218750.1617
54 | 2682057.7882 | 1218691.8442
55 | 2682048.2359 | 1218627.4345
56 | 2682098.1175 | 1218802.7765
57 | 2682061.1515 | 1218599.4323
58 | 2682064.4207 | 1218910.0585
59 | 2682160.5287 | 1218675.8301
60 | 2682046.7078 | 1218991.8941
61 | 2681391.3305 | 1218659.6999
62 | 2681396.7452 | 1218672.8002
63 | 2681474.4197 | 1218780.0903
64 | 2681504.4394 | 1218809.965
65 | 2681297.1194 | 1218959.9658
66 | 2681522.3522 | 1218830.4928
67 | 2681543.1093 | 1218767.3325
68 | 2681519.1911 | 1219494.7553
69 | 2681496.8471 | 1219510.6811
70 | 2681255.1132 | 1219349.6068
71 | 2681283.229 | 1218977.2767
72 | 2681157.6558 | 1219199.0617
73 | 2681168.0168 | 1219209.3605
74 | 2682023.8578 | 1219062.7599
75 | 2682092.125 | 1219021.5425
76 | 2682196.9875 | 1218857.6314
77 | 2682134.8446 | 1219000.1794
78 | 2682184.2537 | 1218804.6762
79 | 2682255.2159 | 1218797.8841
80 | 2682384.5876 | 1218654.765
81 | 2682254.6008 | 1218634.1446
82 | 2681522.3522 | 1218830.4928

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98363 | -0.31511 | 0.00013631 | 3.4163e-05
1 | 0.98364 | -0.31488 | 0.000156 | 3.9097e-05
2 | 0.98355 | -0.31677 | 0 | 0
3 | 0.98368 | -0.31408 | 0.00045845 | 0.0001149
4 | 0.98386 | -0.31051 | 0.00028782 | 7.2134e-05
5 | 0.98355 | -0.31693 | 0 | 0
6 | 0.98353 | -0.31728 | 0 | 0
7 | 0.98352 | -0.31746 | 0.00019569 | 4.9045e-05
8 | 0.98317 | -0.32363 | 0.0012544 | 0.00031438
9 | 0.98359 | -0.31537 | 0.00066653 | 0.00016705
10 | 0.98292 | -0.32856 | 0 | 0
11 | 0.98486 | -0.29075 | 0 | 0
12 | 0.98098 | -0.36647 | 0 | 0
13 | 0.98473 | -0.29319 | 0.00026272 | 6.5843e-05
14 | 0.98737 | -0.24194 | 0 | 0
15 | 0.98438 | -0.30012 | 0.00059133 | 0.0001482
16 | 0.98808 | -0.22821 | 0.0075585 | 0.0018943
17 | 0.98731 | -0.24314 | 0.0015384 | 0.00038555
18 | 0.98435 | -0.30072 | 0.0032414 | 0.00081236
19 | 0.97072 | -0.56801 | 0.0030796 | 0.00077181
20 | 0.97064 | -0.56962 | 0 | 0
21 | 0.97103 | -0.56187 | 0 | 0
22 | 0.9706 | -0.57055 | 0.0018498 | 0.0004636
23 | 0.9706 | -0.5704 | 0.0003539 | 8.8695e-05
24 | 0.97127 | -0.55729 | 0 | 0
25 | 0.97059 | -0.57066 | 0.00030569 | 7.6613e-05
26 | 0.97126 | -0.55734 | 0.00014923 | 3.7401e-05
27 | 0.97124 | -0.55779 | 0.00030259 | 7.5836e-05
28 | 0.97136 | -0.55539 | 0.00015236 | 3.8186e-05
29 | 0.97269 | -0.52912 | 0.00012358 | 3.0973e-05
30 | 0.97274 | -0.52805 | 0.00029371 | 7.3611e-05
31 | 0.97303 | -0.52232 | 0.00013352 | 3.3464e-05
32 | 0.9711 | -0.56061 | 0.0027393 | 0.00068654
33 | 0.97109 | -0.56071 | 0.00073252 | 0.00018359
34 | 0.98934 | -0.20448 | 8.5281e-05 | 2.1373e-05
35 | 0.98934 | -0.20444 | 8.5128e-05 | 2.1335e-05
36 | 0.98935 | -0.20415 | 0.0001137 | 2.8497e-05
37 | 0.98352 | -0.31741 | 0.00012369 | 3.1e-05
38 | 0.9773 | -0.43826 | 0.0001609 | 4.0324e-05
39 | 0.97712 | -0.44179 | 0 | 0
40 | 0.97972 | -0.39108 | 0.00010095 | 2.5301e-05
41 | 0.97694 | -0.44533 | 0.00040498 | 0.0001015
42 | 0.97971 | -0.39111 | 0.00014703 | 3.685e-05
43 | 0.9814 | -0.35824 | 0 | 0
44 | 0.97674 | -0.44929 | 0.00071406 | 0.00017896
45 | 0.97535 | -0.47659 | 0 | 0
46 | 0.97315 | -0.52004 | 0.00093801 | 0.00023509
47 | 0.98138 | -0.35876 | 0.00023983 | 6.0108e-05
48 | 0.98338 | -0.31978 | 0.00031106 | 7.7959e-05
49 | 0.98358 | -0.31583 | 0.00057955 | 0.00014525
50 | 0.99452 | -0.10467 | 0 | 0
51 | 0.99345 | -0.12515 | 0 | 0
52 | 0.99445 | -0.10607 | 0.0022316 | 0.00055928
53 | 0.9967 | -0.062852 | 0.0030347 | 0.00076058
54 | 0.99224 | -0.14851 | 0.00022789 | 5.7115e-05
55 | 0.99221 | -0.14908 | 0.00024056 | 6.0289e-05
56 | 0.9912 | -0.16852 | 0 | 0
57 | 0.9922 | -0.14922 | 0.00024707 | 6.1922e-05
58 | 0.99018 | -0.18819 | 0.00012376 | 3.1016e-05
59 | 0.99116 | -0.16925 | 0.00027552 | 6.9053e-05
60 | 0.98945 | -0.20223 | 0 | 0
61 | 0.99759 | -0.045853 | 0.00059113 | 0.00014815
62 | 0.99759 | -0.045706 | 0.00012496 | 3.1317e-05
63 | 0.99768 | -0.043989 | 0 | 0
64 | 0.9991 | -0.016997 | 0 | 0
65 | 0.98957 | -0.19939 | 0.0023663 | 0.00059306
66 | 1 | 0 | -0.067014 | -0.016662
67 | 0.99826 | -0.033037 | 0.0040791 | 0.0010223
68 | 0.9779 | -0.42691 | 0.0020158 | 0.00050521
69 | 0.97795 | -0.4259 | 0.0036902 | 0.00092485
70 | 0.97949 | -0.39571 | 0 | 0
71 | 0.98956 | -0.19964 | 0.00061992 | 0.00015537
72 | 0.98053 | -0.37522 | 0.0062717 | 0.0015718
73 | 0.98039 | -0.378 | 0.0047325 | 0.0011861
74 | 0.98936 | -0.204 | 0 | 0
75 | 0.98928 | -0.20558 | 0.00016064 | 4.026e-05
76 | 0.98778 | -0.23441 | 0 | 0
77 | 0.98924 | -0.20641 | 0.00087514 | 0.00021933
78 | 0.98777 | -0.23473 | 0.00019876 | 4.9814e-05
79 | 0.98686 | -0.25225 | 0 | 0
80 | 0.98388 | -0.31007 | 0 | 0
81 | 0.98659 | -0.25765 | 0.0017031 | 0.00042685
82 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00045573 | -0.0001048 | 0.00045574 | 0.00010447 | 4.6693e-09 | -3.3274e-07 | 0.00068619 | 0.00068608 | 0.00068619 | 0.98363 | -0.31511 | 0.98364 | -0.31488 | 0.18851
1 | 0.00031942 | 7.0634e-05 | -0.00031939 | -7.4059e-05 | 2.3471e-08 | -3.4246e-06 | 0.00048004 | 0.00048115 | 0.00048115 | 0.98363 | -0.31511 | 0.98355 | -0.31677 | 0.13218
2 | -0.00061174 | -0.00014356 | 0.00061176 | 0.00014269 | 2.2385e-08 | -8.7727e-07 | 0.00092204 | 0.00092174 | 0.00092204 | 0.98364 | -0.31488 | 0.98368 | -0.31408 | 0.25331
3 | 0.0001957 | 4.6593e-05 | -0.0001957 | -4.7148e-05 | 1.4335e-09 | -5.5536e-07 | 0.00029522 | 0.00029541 | 0.00029541 | 0.98355 | -0.31677 | 0.98355 | -0.31693 | 0.081156
4 | 0.0001237 | 2.7466e-05 | -0.00012369 | -3.0248e-05 | 2.8575e-09 | -2.7815e-06 | 0.00018595 | 0.00018687 | 0.00018687 | 0.98355 | -0.31677 | 0.98353 | -0.31728 | 0.051339
5 | -0.0010702 | -0.00025758 | 0.0010704 | 0.00025541 | 1.7596e-07 | -2.1722e-06 | 0.0016152 | 0.0016144 | 0.0016152 | 0.98368 | -0.31408 | 0.98386 | -0.31051 | 0.44373
6 | -0.0013582 | -0.00032754 | 0.0013582 | 0.00032734 | 2.756e-08 | -2.0453e-07 | 0.0020497 | 0.0020496 | 0.0020497 | 0.98386 | -0.31051 | 0.98388 | -0.31007 | 0.5631
7 | 0.0001957 | 4.7148e-05 | -0.00019569 | -4.9045e-05 | 4.9111e-09 | -1.8972e-06 | 0.00029541 | 0.00029607 | 0.00029607 | 0.98355 | -0.31693 | 0.98352 | -0.31746 | 0.081339
8 | 0.00012369 | 3.0248e-05 | -0.00012369 | -3.1e-05 | 7.7803e-10 | -7.524e-07 | 0.00018687 | 0.00018714 | 0.00018714 | 0.98353 | -0.31728 | 0.98352 | -0.31741 | 0.051412
9 | -0.01802 | -0.0045295 | 0.018027 | 0.0045338 | 7.1097e-06 | 4.227e-06 | 0.027278 | 0.027278 | 0.027278 | 0.98317 | -0.32363 | 0.98359 | -0.31537 | 7.494
10 | 0.016766 | 0.0042151 | -0.016762 | -0.0042128 | 3.9467e-06 | 2.3187e-06 | 0.02538 | 0.02538 | 0.02538 | 0.98317 | -0.32363 | 0.98292 | -0.32856 | 6.9725
11 | -0.018694 | -0.0047008 | 0.018716 | 0.004714 | 2.2013e-05 | 1.3156e-05 | 0.028287 | 0.028286 | 0.028287 | 0.98359 | -0.31537 | 0.98486 | -0.29075 | 7.771
12 | 0.016762 | 0.0042128 | -0.016732 | -0.004195 | 3.0279e-05 | 1.7793e-05 | 0.02538 | 0.02538 | 0.02538 | 0.98292 | -0.32856 | 0.98098 | -0.36647 | 6.9727
13 | 0.0040972 | 0.0010257 | -0.0040968 | -0.0010259 | 4.7707e-07 | -1.171e-07 | 0.0061901 | 0.0061902 | 0.0061902 | 0.98486 | -0.29075 | 0.98473 | -0.29319 | 1.7006
14 | -0.022813 | -0.0057397 | 0.022867 | 0.0057723 | 5.3335e-05 | 3.2608e-05 | 0.034476 | 0.034476 | 0.034476 | 0.98486 | -0.29075 | 0.98737 | -0.24194 | 9.4715
15 | 0.016732 | 0.004195 | -0.016725 | -0.0041909 | 6.9738e-06 | 4.0989e-06 | 0.02538 | 0.025381 | 0.025381 | 0.98098 | -0.36647 | 0.98053 | -0.37522 | 6.9727
16 | 0.003834 | 0.00096002 | -0.0038328 | -0.00096049 | 1.2648e-06 | -4.6845e-07 | 0.0057933 | 0.0057937 | 0.0057937 | 0.98473 | -0.29319 | 0.98438 | -0.30012 | 1.5917
17 | -0.024405 | -0.0061574 | 0.024421 | 0.0061672 | 1.6047e-05 | 9.8655e-06 | 0.036794 | 0.036794 | 0.036794 | 0.98737 | -0.24194 | 0.98808 | -0.22821 | 10.1083
18 | 0.0015385 | 0.00038505 | -0.0015384 | -0.00038555 | 8.816e-08 | -5.0293e-07 | 0.0023184 | 0.0023186 | 0.0023186 | 0.98737 | -0.24194 | 0.98731 | -0.24314 | 0.63697
19 | 0.0032414 | 0.00081229 | -0.0032414 | -0.00081236 | 9.1697e-08 | -7.0785e-08 | 0.0048998 | 0.0048999 | 0.0048999 | 0.98438 | -0.30012 | 0.98435 | -0.30072 | 1.3461
20 | -0.03198 | -0.0080616 | 0.032024 | 0.0080892 | 4.4173e-05 | 2.762e-05 | 0.048177 | 0.048177 | 0.048177 | 0.98808 | -0.22821 | 0.98957 | -0.19939 | 13.2354
21 | 0.0025097 | 0.00062669 | -0.0025095 | -0.00062699 | 1.9187e-07 | -3.0472e-07 | 0.0038462 | 0.0038464 | 0.0038464 | 0.97072 | -0.56801 | 0.97064 | -0.56962 | 1.0567
22 | -0.0055892 | -0.0013985 | 0.0055909 | 0.0013988 | 1.6348e-06 | 3.1169e-07 | 0.0085669 | 0.0085666 | 0.0085669 | 0.97072 | -0.56801 | 0.97103 | -0.56187 | 2.3535
23 | 0.0021556 | 0.00053975 | -0.0021555 | -0.00053998 | 9.559e-08 | -2.2736e-07 | 0.0033043 | 0.0033044 | 0.0033044 | 0.97064 | -0.56962 | 0.9706 | -0.57055 | 0.90782
24 | 0.00035391 | 8.7244e-05 | -0.0003539 | -8.8695e-05 | 1.3024e-08 | -1.4514e-06 | 0.00054203 | 0.00054255 | 0.00054255 | 0.97064 | -0.56962 | 0.9706 | -0.5704 | 0.14905
25 | -0.0055909 | -0.0013988 | 0.0055921 | 0.001399 | 1.2164e-06 | 2.3158e-07 | 0.0085666 | 0.0085664 | 0.0085666 | 0.97103 | -0.56187 | 0.97127 | -0.55729 | 2.3535
26 | 0.00030569 | 7.6378e-05 | -0.00030569 | -7.6613e-05 | 1.5744e-09 | -2.3528e-07 | 0.00046857 | 0.00046866 | 0.00046866 | 0.9706 | -0.57055 | 0.97059 | -0.57066 | 0.12875
27 | 0.00014923 | 3.7207e-05 | -0.00014923 | -3.7401e-05 | 3.0747e-10 | -1.9399e-07 | 0.00022856 | 0.00022863 | 0.00022863 | 0.97127 | -0.55729 | 0.97126 | -0.55734 | 0.062811
28 | 0.003775 | 0.0009456 | -0.0037749 | -0.00094563 | 8.9994e-08 | -3.1203e-08 | 0.0057833 | 0.0057833 | 0.0057833 | 0.97127 | -0.55729 | 0.97124 | -0.55779 | 1.5888
29 | -0.0095163 | -0.0023818 | 0.0095172 | 0.0023823 | 8.6222e-07 | 4.1791e-07 | 0.014578 | 0.014578 | 0.014578 | 0.97127 | -0.55729 | 0.97136 | -0.55539 | 4.005
30 | 0.0034723 | 0.00086979 | -0.0034719 | -0.00087004 | 4.6601e-07 | -2.4509e-07 | 0.0053197 | 0.0053199 | 0.0053199 | 0.97124 | -0.55779 | 0.9711 | -0.56061 | 1.4615
31 | -0.0096695 | -0.0024204 | 0.0096816 | 0.0024264 | 1.2101e-05 | 5.9213e-06 | 0.014812 | 0.014811 | 0.014812 | 0.97136 | -0.55539 | 0.97269 | -0.52912 | 4.0691
32 | -0.0098052 | -0.0024573 | 0.0098057 | 0.0024576 | 5.002e-07 | 2.4654e-07 | 0.015 | 0.015 | 0.015 | 0.97269 | -0.52912 | 0.97274 | -0.52805 | 4.1209
33 | -0.010099 | -0.0025312 | 0.010102 | 0.0025326 | 2.7603e-06 | 1.3837e-06 | 0.015449 | 0.015449 | 0.015449 | 0.97274 | -0.52805 | 0.97303 | -0.52232 | 4.2443
34 | -0.010236 | -0.002566 | 0.010237 | 0.0025666 | 1.1106e-06 | 5.6066e-07 | 0.015653 | 0.015653 | 0.015653 | 0.97303 | -0.52232 | 0.97315 | -0.52004 | 4.3004
35 | 0.00073252 | 0.0001835 | -0.00073252 | -0.00018359 | 3.5966e-09 | -9.1882e-08 | 0.0011224 | 0.0011224 | 0.0011224 | 0.9711 | -0.56061 | 0.97109 | -0.56071 | 0.30837
36 | -8.5281e-05 | -2.1373e-05 | 8.5281e-05 | 2.104e-05 | 1.6025e-10 | -3.3374e-07 | 0.00012827 | 0.00012815 | 0.00012827 | 0.98934 | -0.20448 | 0.98934 | -0.20444 | 0.035238
37 | -0.00017041 | -4.2375e-05 | 0.00017041 | 4.1178e-05 | 2.2923e-09 | -1.1965e-06 | 0.00025619 | 0.00025577 | 0.00025619 | 0.98934 | -0.20444 | 0.98935 | -0.20415 | 0.070381
38 | -0.00028411 | -6.9675e-05 | 0.00028412 | 6.9289e-05 | 2.0601e-09 | -3.8612e-07 | 0.00042678 | 0.00042664 | 0.00042678 | 0.98935 | -0.20415 | 0.98936 | -0.204 | 0.11725
39 | 0.012338 | 0.0031055 | -0.012336 | -0.0031044 | 2.0825e-06 | 1.1357e-06 | 0.01879 | 0.018791 | 0.018791 | 0.9773 | -0.43826 | 0.97712 | -0.44179 | 5.1622
40 | -0.012499 | -0.0031459 | 0.012527 | 0.0031613 | 2.8242e-05 | 1.5464e-05 | 0.019035 | 0.019034 | 0.019035 | 0.9773 | -0.43826 | 0.97972 | -0.39108 | 5.2295
41 | 0.012336 | 0.0031044 | -0.012334 | -0.0031033 | 2.0878e-06 | 1.1387e-06 | 0.018791 | 0.018791 | 0.018791 | 0.97712 | -0.44179 | 0.97694 | -0.44533 | 5.1622
42 | -0.012775 | -0.0032233 | 0.012795 | 0.0032344 | 2.0123e-05 | 1.1082e-05 | 0.019411 | 0.01941 | 0.019411 | 0.97972 | -0.39108 | 0.9814 | -0.35824 | 5.3327
43 | 0.00014703 | 3.672e-05 | -0.00014703 | -3.685e-05 | 1.9303e-10 | -1.2988e-07 | 0.00022327 | 0.00022332 | 0.00022332 | 0.97972 | -0.39108 | 0.97971 | -0.39111 | 0.061351
44 | 0.011929 | 0.0030018 | -0.011927 | -0.0030005 | 2.2565e-06 | 1.2161e-06 | 0.018174 | 0.018174 | 0.018174 | 0.97694 | -0.44533 | 0.97674 | -0.44929 | 4.9928
45 | 0.00023984 | 5.8602e-05 | -0.00023983 | -6.0108e-05 | 5.9154e-09 | -1.5057e-06 | 0.00036312 | 0.00036365 | 0.00036365 | 0.9814 | -0.35824 | 0.98138 | -0.35876 | 0.099904
46 | -0.013035 | -0.003293 | 0.013059 | 0.0033063 | 2.4073e-05 | 1.3328e-05 | 0.019774 | 0.019773 | 0.019774 | 0.9814 | -0.35824 | 0.98338 | -0.31978 | 5.4323
47 | 0.011213 | 0.0028216 | -0.011198 | -0.0028139 | 1.4608e-05 | 7.6816e-06 | 0.017086 | 0.017087 | 0.017087 | 0.97674 | -0.44929 | 0.97535 | -0.47659 | 4.6941
48 | 0.011198 | 0.0028139 | -0.011175 | -0.0028017 | 2.3182e-05 | 1.22e-05 | 0.017087 | 0.017088 | 0.017088 | 0.97535 | -0.47659 | 0.97315 | -0.52004 | 4.6944
49 | -0.01337 | -0.0033843 | 0.013373 | 0.0033857 | 2.5317e-06 | 1.4112e-06 | 0.020243 | 0.020243 | 0.020243 | 0.98338 | -0.31978 | 0.98358 | -0.31583 | 5.5614
50 | -0.013952 | -0.003531 | 0.013956 | 0.0035331 | 3.8599e-06 | 2.1774e-06 | 0.02112 | 0.02112 | 0.02112 | 0.98358 | -0.31583 | 0.98388 | -0.31007 | 5.8022
51 | 0.019826 | 0.005022 | -0.019806 | -0.0050126 | 1.9484e-05 | 9.4121e-06 | 0.029682 | 0.029684 | 0.029684 | 0.99452 | -0.10467 | 0.99345 | -0.12515 | 4.0774
52 | 0.0022317 | 0.00055891 | -0.0022316 | -0.00055928 | 1.4922e-07 | -3.6759e-07 | 0.003339 | 0.0033391 | 0.0033391 | 0.99452 | -0.10467 | 0.99445 | -0.10607 | 0.91735
53 | -0.022057 | -0.0055809 | 0.022102 | 0.0056037 | 4.4344e-05 | 2.2739e-05 | 0.033021 | 0.033019 | 0.033021 | 0.99452 | -0.10467 | 0.9967 | -0.062852 | 4.5359
54 | 0.019806 | 0.0050126 | -0.019784 | -0.0050019 | 2.2191e-05 | 1.0728e-05 | 0.029684 | 0.029685 | 0.029685 | 0.99345 | -0.12515 | 0.99224 | -0.14851 | 4.0776
55 | -0.025137 | -0.0063642 | 0.025173 | 0.0063837 | 3.6032e-05 | 1.9502e-05 | 0.03755 | 0.037549 | 0.03755 | 0.9967 | -0.062852 | 0.99826 | -0.033037 | 5.158
56 | 0.00048764 | 0.00012097 | -0.00048763 | -0.00012181 | 1.3118e-08 | -8.3714e-07 | 0.00073086 | 0.00073116 | 0.00073116 | 0.99224 | -0.14851 | 0.99221 | -0.14908 | 0.20087
57 | 0.019069 | 0.0048238 | -0.01905 | -0.0048151 | 1.8292e-05 | 8.6318e-06 | 0.028612 | 0.028613 | 0.028613 | 0.99224 | -0.14851 | 0.9912 | -0.16852 | 3.9304
58 | 0.00024707 | 6.1521e-05 | -0.00024707 | -6.1922e-05 | 1.6029e-09 | -4.0123e-07 | 0.0003704 | 0.00037054 | 0.00037054 | 0.99221 | -0.14908 | 0.9922 | -0.14922 | 0.1018
59 | 0.018775 | 0.004748 | -0.018757 | -0.0047397 | 1.7696e-05 | 8.2695e-06 | 0.0282 | 0.028201 | 0.028201 | 0.9912 | -0.16852 | 0.99018 | -0.18819 | 3.8738
60 | 0.00027553 | 6.7159e-05 | -0.00027552 | -6.9053e-05 | 9.4428e-09 | -1.8939e-06 | 0.00041297 | 0.00041364 | 0.00041364 | 0.9912 | -0.16852 | 0.99116 | -0.16925 | 0.11364
61 | 0.018633 | 0.0047087 | -0.018621 | -0.0047029 | 1.2539e-05 | 5.8344e-06 | 0.028015 | 0.028016 | 0.028016 | 0.99018 | -0.18819 | 0.98945 | -0.20223 | 3.8484
62 | 0.017301 | 0.0043766 | -0.017274 | -0.0043649 | 2.6683e-05 | 1.1692e-05 | 0.026033 | 0.026034 | 0.026034 | 0.98945 | -0.20223 | 0.98778 | -0.23441 | 3.5762
63 | 0.0013201 | 0.00032628 | -0.00132 | -0.00032717 | 1.1008e-07 | -8.8742e-07 | 0.0019837 | 0.001984 | 0.001984 | 0.98945 | -0.20223 | 0.98936 | -0.204 | 0.54506
64 | -0.00059113 | -0.00014815 | 0.00059114 | 0.00014797 | 4.1325e-09 | -1.8243e-07 | 0.00088174 | 0.00088168 | 0.00088174 | 0.99759 | -0.045853 | 0.99759 | -0.045706 | 0.24224
65 | -0.00071609 | -0.00017929 | 0.00071615 | 0.00017754 | 5.8308e-08 | -1.7435e-06 | 0.0010681 | 0.0010674 | 0.0010681 | 0.99759 | -0.045706 | 0.99768 | -0.043989 | 0.29342
66 | -0.035989 | -0.0091797 | 0.036036 | 0.0092092 | 4.6977e-05 | 2.9498e-05 | 0.053733 | 0.053733 | 0.053733 | 0.99768 | -0.043989 | 0.9991 | -0.016997 | 14.7618
67 | 0.035273 | 0.0090022 | -0.03501 | -0.0088373 | 0.00026271 | 0.00016486 | 0.052666 | 0.052667 | 0.052667 | 0.99768 | -0.043989 | 0.98957 | -0.19939 | 14.4689
68 | -0.06531 | -0.016628 | 0.065364 | 0.016662 | 5.3577e-05 | 3.3499e-05 | 0.097361 | 0.097361 | 0.097361 | 0.9991 | -0.016997 | 1 | 0 | 13.3738
69 | 0.029274 | 0.0074188 | -0.029252 | -0.0074061 | 2.2544e-05 | 1.2775e-05 | 0.043629 | 0.043629 | 0.043629 | 0.9991 | -0.016997 | 0.99826 | -0.033037 | 5.993
70 | 0.00061993 | 0.00015509 | -0.00061992 | -0.00015537 | 7.2317e-09 | -2.8051e-07 | 0.00093209 | 0.00093219 | 0.00093219 | 0.98957 | -0.19939 | 0.98956 | -0.19964 | 0.2561
71 | -0.0020158 | -0.00050521 | 0.0020159 | 0.00050493 | 9.7202e-08 | -2.8345e-07 | 0.0030674 | 0.0030672 | 0.0030674 | 0.9779 | -0.42691 | 0.97795 | -0.4259 | 0.84268
72 | -0.0057061 | -0.0014298 | 0.0057143 | 0.0014314 | 8.2099e-06 | 1.6039e-06 | 0.0086821 | 0.0086808 | 0.0086821 | 0.97795 | -0.4259 | 0.97949 | -0.39571 | 2.3852
73 | -0.0057143 | -0.0014314 | 0.0057191 | 0.0014323 | 4.8214e-06 | 9.3604e-07 | 0.0086808 | 0.00868 | 0.0086808 | 0.97949 | -0.39571 | 0.98039 | -0.378 | 2.3848
74 | 0.010453 | 0.0026191 | -0.010452 | -0.0026184 | 1.3846e-06 | 7.0108e-07 | 0.015863 | 0.015863 | 0.015863 | 0.98053 | -0.37522 | 0.98039 | -0.378 | 4.358
75 | 0.0010359 | 0.00025788 | -0.0010358 | -0.00025893 | 7.7893e-08 | -1.0495e-06 | 0.0015574 | 0.0015578 | 0.0015578 | 0.98936 | -0.204 | 0.98928 | -0.20558 | 0.42796
76 | 0.00087517 | 0.00021867 | -0.00087514 | -0.00021933 | 3.4445e-08 | -6.5862e-07 | 0.0013162 | 0.0013164 | 0.0013164 | 0.98928 | -0.20558 | 0.98924 | -0.20641 | 0.36165
77 | 0.00019876 | 4.869e-05 | -0.00019876 | -4.9814e-05 | 2.9525e-09 | -1.1238e-06 | 0.00029902 | 0.00029942 | 0.00029942 | 0.98778 | -0.23441 | 0.98777 | -0.23473 | 0.082258
78 | 0.017075 | 0.0043162 | -0.017061 | -0.0043099 | 1.4594e-05 | 6.3346e-06 | 0.025735 | 0.025737 | 0.025737 | 0.98778 | -0.23441 | 0.98686 | -0.25225 | 3.5352
79 | 0.0017036 | 0.00042487 | -0.0017031 | -0.00042685 | 4.3715e-07 | -1.9775e-06 | 0.002568 | 0.0025688 | 0.0025688 | 0.98686 | -0.25225 | 0.98659 | -0.25765 | 0.7057
80 | 0.015357 | 0.003885 | -0.015314 | -0.0038605 | 4.2491e-05 | 2.4506e-05 | 0.023169 | 0.02317 | 0.02317 | 0.98686 | -0.25225 | 0.98388 | -0.31007 | 6.3653

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.072337 | 0.017996

## res_load
| p_mw | q_mvar
0 | 0.00013631 | 3.4163e-05
1 | 0.000156 | 3.9097e-05
2 | 0.00045845 | 0.0001149
3 | 0.00028782 | 7.2134e-05
4 | 0.00019569 | 4.9045e-05
5 | 0.0012544 | 0.00031438
6 | 0.00066653 | 0.00016705
7 | 0.00026272 | 6.5843e-05
8 | 0.00059133 | 0.0001482
9 | 0.0075585 | 0.0018943
10 | 0.0015384 | 0.00038555
11 | 0.0032414 | 0.00081236
12 | 0.0030796 | 0.00077181
13 | 0.0018498 | 0.0004636
14 | 0.0003539 | 8.8695e-05
15 | 0.00030569 | 7.6613e-05
16 | 0.00014923 | 3.7401e-05
17 | 0.00030259 | 7.5836e-05
18 | 0.00015236 | 3.8186e-05
19 | 0.00012358 | 3.0973e-05
20 | 0.00029371 | 7.3611e-05
21 | 0.00013352 | 3.3464e-05
22 | 0.0027393 | 0.00068654
23 | 0.00073252 | 0.00018359
24 | 8.5281e-05 | 2.1373e-05
25 | 8.5128e-05 | 2.1335e-05
26 | 0.0001137 | 2.8497e-05
27 | 0.00012369 | 3.1e-05
28 | 0.0001609 | 4.0324e-05
29 | 0.00010095 | 2.5301e-05
30 | 0.00040498 | 0.0001015
31 | 0.00014703 | 3.685e-05
32 | 0.00071406 | 0.00017896
33 | 0.00093801 | 0.00023509
34 | 0.00023983 | 6.0108e-05
35 | 0.00031106 | 7.7959e-05
36 | 0.00057955 | 0.00014525
37 | 0.0022316 | 0.00055928
38 | 0.0030347 | 0.00076058
39 | 0.00022789 | 5.7115e-05
40 | 0.00024056 | 6.0289e-05
41 | 0.00024707 | 6.1922e-05
42 | 0.00012376 | 3.1016e-05
43 | 0.00027552 | 6.9053e-05
44 | 0.00059113 | 0.00014815
45 | 0.00012496 | 3.1317e-05
46 | 0.0023663 | 0.00059306
47 | 0.005323 | 0.0013341
48 | 0.0040791 | 0.0010223
49 | 0.0020158 | 0.00050521
50 | 0.0036902 | 0.00092485
51 | 0.00061992 | 0.00015537
52 | 0.0062717 | 0.0015718
53 | 0.0047325 | 0.0011861
54 | 0.00016064 | 4.026e-05
55 | 0.00087514 | 0.00021933
56 | 0.00019876 | 4.9814e-05
57 | 0.0017031 | 0.00042685

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1