## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1710-5_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1710-5_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1710-5_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1710-5_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1710-5_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1710-5_0_8_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1710-5_0_8_node_102 | 0.4 | n |  | TRUE
7 | bus_LV_1710-5_0_8_node_105 | 0.4 | n |  | TRUE
8 | bus_LV_1710-5_0_8_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1710-5_0_8_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1710-5_0_8_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1710-5_0_8_node_122 | 0.4 | n |  | TRUE
12 | bus_LV_1710-5_0_8_node_70 | 0.4 | n |  | TRUE
13 | bus_LV_1710-5_0_8_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1710-5_0_8_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1710-5_0_8_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1710-5_0_8_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1710-5_0_8_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1710-5_0_8_node_61 | 0.4 | n |  | TRUE
19 | bus_LV_1710-5_0_8_node_60 | 0.4 | n |  | TRUE
20 | bus_LV_1710-5_0_8_node_73 | 0.4 | n |  | TRUE
21 | bus_LV_1710-5_0_8_node_71 | 0.4 | n |  | TRUE
22 | bus_LV_1710-5_0_8_node_83 | 0.4 | n |  | TRUE
23 | bus_LV_1710-5_0_8_node_62 | 0.4 | n |  | TRUE
24 | bus_LV_1710-5_0_8_node_63 | 0.4 | n |  | TRUE
25 | bus_LV_1710-5_0_8_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_1710-5_0_8_node_55 | 0.4 | n |  | TRUE
27 | bus_LV_1710-5_0_8_node_76 | 0.4 | n |  | TRUE
28 | bus_LV_1710-5_0_8_node_72 | 0.4 | n |  | TRUE
29 | bus_LV_1710-5_0_8_node_84 | 0.4 | n |  | TRUE
30 | bus_LV_1710-5_0_8_node_86 | 0.4 | n |  | TRUE
31 | bus_LV_1710-5_0_8_node_85 | 0.4 | n |  | TRUE
32 | bus_LV_1710-5_0_8_node_15 | 0.4 | n |  | TRUE
33 | bus_LV_1710-5_0_8_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_1710-5_0_8_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_1710-5_0_8_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_1710-5_0_8_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_1710-5_0_8_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_1710-5_0_8_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_1710-5_0_8_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_1710-5_0_8_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_1710-5_0_8_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_1710-5_0_8_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_1710-5_0_8_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_1710-5_0_8_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_1710-5_0_8_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_1710-5_0_8_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_1710-5_0_8_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_1710-5_0_8_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_1710-5_0_8_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_1710-5_0_8_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_1710-5_0_8_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_1710-5_0_8_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_1710-5_0_8_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_1710-5_0_8_node_53 | 0.4 | n |  | TRUE
55 | bus_LV_1710-5_0_8_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_1710-5_0_8_node_34 | 0.4 | n |  | TRUE
57 | bus_LV_1710-5_0_8_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_1710-5_0_8_node_66 | 0.4 | n |  | TRUE
59 | bus_LV_1710-5_0_8_node_64 | 0.4 | n |  | TRUE
60 | bus_LV_1710-5_0_8_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_1710-5_0_8_node_69 | 0.4 | n |  | TRUE
62 | bus_LV_1710-5_0_8_node_68 | 0.4 | n |  | TRUE
63 | bus_LV_1710-5_0_8_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_1710-5_0_8_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_1710-5_0_8_node_38 | 0.4 | n |  | TRUE
66 | bus_LV_1710-5_0_8_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_1710-5_0_8_node_56 | 0.4 | n |  | TRUE
68 | bus_LV_1710-5_0_8_node_44 | 0.4 | n |  | TRUE
69 | bus_LV_1710-5_0_8_node_45 | 0.4 | n |  | TRUE
70 | bus_LV_1710-5_0_8_node_46 | 0.4 | n |  | TRUE
71 | bus_LV_1710-5_0_8_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_1710-5_0_8_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_1710-5_0_8_node_118 | 0.4 | n |  | TRUE
74 | bus_LV_1710-5_0_8_node_119 | 0.4 | n |  | TRUE
75 | bus_LV_1710-5_0_8_node_49 | 0.4 | n |  | TRUE
76 | bus_LV_1710-5_0_8_node_50 | 0.4 | n |  | TRUE
77 | bus_LV_1710-5_0_8_node_51 | 0.4 | n |  | TRUE
78 | bus_LV_1710-5_0_8_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_1710-5_0_8_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_1710-5_0_8_node_65 | 0.4 | n |  | TRUE
81 | bus_LV_1710-5_0_8_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_1710-5_0_8_node_115 | 0.4 | n |  | TRUE
83 | bus_LV_1710-5_0_8_node_117 | 0.4 | n |  | TRUE
84 | bus_LV_1710-5_0_8_node_114 | 0.4 | n |  | TRUE
85 | bus_LV_1710-5_0_8_node_82 | 0.4 | n |  | TRUE
86 | bus_LV_1710-5_0_8_node_81 | 0.4 | n |  | TRUE
87 | bus_LV_1710-5_0_8_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_1710-5_0_8_node_79 | 0.4 | n |  | TRUE
89 | bus_LV_1710-5_0_8_node_80 | 0.4 | n |  | TRUE
90 | bus_LV_1710-5_0_8_node_94 | 0.4 | n |  | TRUE
91 | bus_LV_1710-5_0_8_node_87 | 0.4 | n |  | TRUE
92 | bus_LV_1710-5_0_8_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_1710-5_0_8_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_1710-5_0_8_node_90 | 0.4 | n |  | TRUE
95 | bus_LV_1710-5_0_8_node_91 | 0.4 | n |  | TRUE
96 | bus_LV_1710-5_0_8_node_93 | 0.4 | n |  | TRUE
97 | bus_LV_1710-5_0_8_node_95 | 0.4 | n |  | TRUE
98 | bus_LV_1710-5_0_8_node_96 | 0.4 | n |  | TRUE
99 | bus_LV_1710-5_0_8_node_112 | 0.4 | n |  | TRUE
100 | bus_LV_1710-5_0_8_node_111 | 0.4 | n |  | TRUE
101 | bus_LV_1710-5_0_8_node_116 | 0.4 | n |  | TRUE
102 | bus_LV_1710-5_0_8_node_113 | 0.4 | n |  | TRUE
103 | bus_LV_1710-5_0_8_node_110 | 0.4 | n |  | TRUE
104 | bus_LV_1710-5_0_8_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_1710-5_0_8_node_98 | 0.4 | n |  | TRUE
106 | bus_LV_1710-5_0_8_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_1710-5_0_8_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_1710-5_0_8_node_101 | 0.4 | n |  | TRUE
109 | bus_LV_1710-5_0_8_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_1710-5_0_8_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_1710-5_0_8_node_106 | 0.4 | n |  | TRUE
112 | bus_LV_1710-5_0_8_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_1710-5_0_8_node_108 | 0.4 | n |  | TRUE
114 | bus_LV_1710-5_0_8_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_1710-5_0_8_node_120 | 0.4 | n |  | TRUE
116 | bus_LV_1710-5_0_8_node_121 | 0.4 | n |  | TRUE
117 | bus_MV_1_0_node_178 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1710-5_0_8_load_0 | 0 | 0.00040786 | 0.00010222 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1710-5_0_8_load_1 | 1 | 0.0017956 | 0.00045002 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1710-5_0_8_load_2 | 2 | 0.015968 | 0.0040019 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1710-5_0_8_load_3 | 3 | 0.0079651 | 0.0019962 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1710-5_0_8_load_5 | 5 | 0.0030783 | 0.00077149 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1710-5_0_8_load_102 | 6 | 0.0053236 | 0.0013342 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1710-5_0_8_load_6 | 8 | 0.01096 | 0.002747 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1710-5_0_8_load_9 | 10 | 0.0087361 | 0.0021895 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1710-5_0_8_load_122 | 11 | 0.0027937 | 0.00070017 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1710-5_0_8_load_70 | 12 | 0.019926 | 0.0049939 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1710-5_0_8_load_11 | 14 | 0.010729 | 0.002689 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1710-5_0_8_load_14 | 17 | 0.0042023 | 0.0010532 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1710-5_0_8_load_60 | 19 | 0.001464 | 0.00036692 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1710-5_0_8_load_73 | 20 | 0.010395 | 0.0026053 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1710-5_0_8_load_71 | 21 | 0.017444 | 0.0043718 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1710-5_0_8_load_62 | 23 | 0.0048677 | 0.00122 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1710-5_0_8_load_63 | 24 | 0.003448 | 0.00086416 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1710-5_0_8_load_59 | 25 | 0.0033015 | 0.00082743 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1710-5_0_8_load_55 | 26 | 0.0033501 | 0.00083961 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1710-5_0_8_load_76 | 27 | 0.0061803 | 0.0015489 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1710-5_0_8_load_72 | 28 | 0.010327 | 0.0025881 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1710-5_0_8_load_86 | 30 | 0.0052364 | 0.0013124 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1710-5_0_8_load_85 | 31 | 0.0071713 | 0.0017973 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1710-5_0_8_load_15 | 32 | 0.0033136 | 0.00083048 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1710-5_0_8_load_16 | 33 | 0.0026415 | 0.00066201 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1710-5_0_8_load_18 | 34 | 0.0021888 | 0.00054857 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1710-5_0_8_load_19 | 35 | 0.00094139 | 0.00023594 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1710-5_0_8_load_21 | 37 | 0.0095604 | 0.0023961 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1710-5_0_8_load_22 | 38 | 0.0016161 | 0.00040503 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1710-5_0_8_load_35 | 40 | 0.003665 | 0.00091854 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1710-5_0_8_load_30 | 41 | 0.0052208 | 0.0013085 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1710-5_0_8_load_23 | 44 | 0.0022859 | 0.0005729 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1710-5_0_8_load_24 | 45 | 0.003011 | 0.00075463 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1710-5_0_8_load_26 | 46 | 0.0035172 | 0.0008815 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1710-5_0_8_load_32 | 50 | 0.0085822 | 0.0021509 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1710-5_0_8_load_36 | 52 | 0.0059429 | 0.0014894 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1710-5_0_8_load_52 | 53 | 0.0067234 | 0.001685 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1710-5_0_8_load_53 | 54 | 0.014283 | 0.0035796 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1710-5_0_8_load_47 | 55 | 0.032679 | 0.0081901 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1710-5_0_8_load_34 | 56 | 0.0091686 | 0.0022979 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1710-5_0_8_load_37 | 57 | 0.0061951 | 0.0015526 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1710-5_0_8_load_66 | 58 | 0.0032351 | 0.00081079 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1710-5_0_8_load_64 | 59 | 0.0019522 | 0.00048927 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1710-5_0_8_load_69 | 61 | 0.0098384 | 0.0024657 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1710-5_0_8_load_68 | 62 | 0.0090784 | 0.0022753 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1710-5_0_8_load_40 | 63 | 0.0089575 | 0.002245 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1710-5_0_8_load_38 | 65 | 0.0051095 | 0.0012806 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1710-5_0_8_load_43 | 66 | 0.0068007 | 0.0017044 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1710-5_0_8_load_56 | 67 | 0.0053787 | 0.001348 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1710-5_0_8_load_45 | 69 | 0.0009883 | 0.00024769 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1710-5_0_8_load_57 | 71 | 0.0048003 | 0.0012031 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1710-5_0_8_load_58 | 72 | 0.0010839 | 0.00027166 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1710-5_0_8_load_118 | 73 | 0.0011667 | 0.0002924 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1710-5_0_8_load_119 | 74 | 0.00076613 | 0.00019201 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1710-5_0_8_load_49 | 75 | 0.0015757 | 0.0003949 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1710-5_0_8_load_50 | 76 | 0.0022506 | 0.00056404 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1710-5_0_8_load_51 | 77 | 0.0034978 | 0.00087662 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1710-5_0_8_load_54 | 78 | 0.0031477 | 0.00078889 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1710-5_0_8_load_67 | 79 | 0.0066344 | 0.0016627 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1710-5_0_8_load_65 | 80 | 0.0024829 | 0.00062228 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1710-5_0_8_load_77 | 81 | 0.00529 | 0.0013258 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1710-5_0_8_load_115 | 82 | 0.0024019 | 0.00060197 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1710-5_0_8_load_117 | 83 | 0.0016417 | 0.00041146 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1710-5_0_8_load_114 | 84 | 0.00067069 | 0.00016809 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1710-5_0_8_load_82 | 85 | 0.0064909 | 0.0016268 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1710-5_0_8_load_81 | 86 | 0.0058022 | 0.0014542 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1710-5_0_8_load_78 | 87 | 0.0054491 | 0.0013657 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1710-5_0_8_load_79 | 88 | 0.0046256 | 0.0011593 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1710-5_0_8_load_80 | 89 | 0.0056985 | 0.0014282 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1710-5_0_8_load_94 | 90 | 0.038453 | 0.0096372 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1710-5_0_8_load_87 | 91 | 0.0040911 | 0.0010253 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1710-5_0_8_load_88 | 92 | 0.0020927 | 0.00052449 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1710-5_0_8_load_89 | 93 | 0.0044271 | 0.0011095 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1710-5_0_8_load_90 | 94 | 0.0041742 | 0.0010462 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1710-5_0_8_load_91 | 95 | 0.0050566 | 0.0012673 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1710-5_0_8_load_96 | 98 | 0.0047711 | 0.0011957 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1710-5_0_8_load_112 | 99 | 0.0066277 | 0.0016611 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1710-5_0_8_load_111 | 100 | 0.00084036 | 0.00021061 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1710-5_0_8_load_113 | 102 | 0.0032275 | 0.00080889 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1710-5_0_8_load_110 | 103 | 0.0066936 | 0.0016776 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1710-5_0_8_load_97 | 104 | 0.01333 | 0.0033408 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1710-5_0_8_load_98 | 105 | 0.014634 | 0.0036677 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1710-5_0_8_load_99 | 106 | 0.014957 | 0.0037486 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1710-5_0_8_load_100 | 107 | 0.0043615 | 0.0010931 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1710-5_0_8_load_101 | 108 | 0.0032095 | 0.00080438 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1710-5_0_8_load_103 | 109 | 0.004005 | 0.0010038 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1710-5_0_8_load_104 | 110 | 0.0030349 | 0.00076061 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1710-5_0_8_load_106 | 111 | 0.0040711 | 0.0010203 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1710-5_0_8_load_108 | 113 | 0.0017097 | 0.00042849 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1710-5_0_8_load_109 | 114 | 0.0012915 | 0.00032367 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1710-5_0_8_load_120 | 115 | 0.0021959 | 0.00055033 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1710-5_0_8_load_121 | 116 | 0.0092303 | 0.0023133 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1710-5_0_8_line_0 |  | 0 | 1 | 0.025195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1710-5_0_8_line_1 |  | 0 | 2 | 0.031665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1710-5_0_8_line_2 |  | 1 | 3 | 0.036183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1710-5_0_8_line_3 |  | 2 | 4 | 0.0039623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1710-5_0_8_line_4 |  | 4 | 5 | 0.062297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1710-5_0_8_line_5 |  | 5 | 6 | 0.031818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1710-5_0_8_line_6 |  | 6 | 7 | 0.070013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1710-5_0_8_line_7 |  | 7 | 111 | 0.074568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1710-5_0_8_line_8 |  | 7 | 112 | 0.071103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1710-5_0_8_line_9 |  | 8 | 9 | 0.021518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1710-5_0_8_line_10 |  | 9 | 10 | 0.033502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1710-5_0_8_line_11 |  | 10 | 13 | 0.0047346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1710-5_0_8_line_12 |  | 11 | 12 | 0.047002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1710-5_0_8_line_13 |  | 12 | 62 | 0.014409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1710-5_0_8_line_14 |  | 13 | 14 | 0.0076088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1710-5_0_8_line_15 |  | 13 | 15 | 0.072904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1710-5_0_8_line_16 |  | 13 | 16 | 0.058654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1710-5_0_8_line_17 |  | 14 | 17 | 0.03972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1710-5_0_8_line_18 |  | 15 | 18 | 0.056387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1710-5_0_8_line_19 |  | 15 | 19 | 0.04697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1710-5_0_8_line_20 |  | 16 | 20 | 0.018761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1710-5_0_8_line_21 |  | 16 | 21 | 0.0016928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1710-5_0_8_line_22 |  | 17 | 22 | 0.067603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1710-5_0_8_line_23 |  | 18 | 23 | 0.037652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1710-5_0_8_line_24 |  | 18 | 24 | 0.0078132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1710-5_0_8_line_25 |  | 19 | 25 | 0.025125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1710-5_0_8_line_26 |  | 20 | 27 | 0.018992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1710-5_0_8_line_27 |  | 21 | 28 | 0.032969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1710-5_0_8_line_28 |  | 22 | 29 | 0.034314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1710-5_0_8_line_29 |  | 23 | 82 | 0.093315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1710-5_0_8_line_30 |  | 24 | 81 | 0.024969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1710-5_0_8_line_31 |  | 25 | 26 | 0.025951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1710-5_0_8_line_32 |  | 26 | 78 | 0.0066795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1710-5_0_8_line_33 |  | 27 | 85 | 0.011373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1710-5_0_8_line_34 |  | 29 | 30 | 0.030266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1710-5_0_8_line_35 |  | 30 | 31 | 0.0065901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1710-5_0_8_line_36 |  | 31 | 91 | 0.013858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1710-5_0_8_line_37 |  | 32 | 33 | 0.030431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1710-5_0_8_line_38 |  | 33 | 34 | 0.023144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1710-5_0_8_line_39 |  | 34 | 35 | 0.016482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1710-5_0_8_line_40 |  | 35 | 36 | 0.0098401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1710-5_0_8_line_41 |  | 36 | 37 | 0.018163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1710-5_0_8_line_42 |  | 36 | 38 | 0.02616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_1710-5_0_8_line_43 |  | 37 | 39 | 0.015669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_1710-5_0_8_line_44 |  | 38 | 40 | 0.058614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_1710-5_0_8_line_45 |  | 39 | 41 | 0.037389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1710-5_0_8_line_46 |  | 39 | 42 | 0.019317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_1710-5_0_8_line_47 |  | 40 | 43 | 0.049098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1710-5_0_8_line_48 |  | 41 | 52 | 0.0067185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1710-5_0_8_line_49 |  | 42 | 47 | 0.045848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_1710-5_0_8_line_50 |  | 42 | 44 | 0.0021958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1710-5_0_8_line_51 |  | 43 | 63 | 0.0093354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1710-5_0_8_line_52 |  | 43 | 64 | 0.019819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1710-5_0_8_line_53 |  | 44 | 45 | 0.016159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1710-5_0_8_line_54 |  | 45 | 46 | 0.020905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1710-5_0_8_line_55 |  | 46 | 48 | 0.01484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1710-5_0_8_line_56 |  | 47 | 49 | 0.033944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1710-5_0_8_line_57 |  | 47 | 50 | 0.054114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_1710-5_0_8_line_58 |  | 48 | 51 | 0.021051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1710-5_0_8_line_59 |  | 49 | 53 | 0.013759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1710-5_0_8_line_60 |  | 49 | 54 | 0.0036887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1710-5_0_8_line_61 |  | 50 | 55 | 0.0076773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_1710-5_0_8_line_62 |  | 51 | 56 | 0.034343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1710-5_0_8_line_63 |  | 52 | 57 | 0.014765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1710-5_0_8_line_64 |  | 53 | 58 | 0.008266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1710-5_0_8_line_65 |  | 54 | 59 | 0.028532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1710-5_0_8_line_66 |  | 55 | 60 | 0.017847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_1710-5_0_8_line_67 |  | 56 | 61 | 0.010167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1710-5_0_8_line_68 |  | 57 | 65 | 0.0027777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1710-5_0_8_line_69 |  | 58 | 79 | 0.00072294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1710-5_0_8_line_70 |  | 59 | 80 | 0.0058682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1710-5_0_8_line_71 |  | 60 | 75 | 0.031682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_1710-5_0_8_line_72 |  | 60 | 76 | 0.017032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1710-5_0_8_line_73 |  | 61 | 62 | 0.02131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1710-5_0_8_line_74 |  | 64 | 66 | 0.030817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1710-5_0_8_line_75 |  | 66 | 67 | 0.026551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1710-5_0_8_line_76 |  | 67 | 71 | 0.01338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1710-5_0_8_line_77 |  | 68 | 69 | 0.011172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1710-5_0_8_line_78 |  | 68 | 70 | 0.038691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1710-5_0_8_line_79 |  | 69 | 72 | 0.011847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1710-5_0_8_line_80 |  | 70 | 73 | 0.023188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1710-5_0_8_line_81 |  | 71 | 72 | 0.022228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1710-5_0_8_line_82 |  | 73 | 74 | 0.0019386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1710-5_0_8_line_83 |  | 74 | 115 | 0.011705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1710-5_0_8_line_84 |  | 75 | 77 | 0.021781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_1710-5_0_8_line_85 |  | 77 | 78 | 0.016581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_1710-5_0_8_line_86 |  | 82 | 83 | 0.020523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1710-5_0_8_line_87 |  | 82 | 84 | 0.017819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_1710-5_0_8_line_88 |  | 84 | 101 | 0.004826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_1710-5_0_8_line_89 |  | 85 | 86 | 0.0029386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1710-5_0_8_line_90 |  | 86 | 88 | 0.024712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1710-5_0_8_line_91 |  | 87 | 88 | 0.0023899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1710-5_0_8_line_92 |  | 87 | 89 | 0.010565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1710-5_0_8_line_93 |  | 90 | 91 | 0.039469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1710-5_0_8_line_94 |  | 91 | 92 | 0.018278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1710-5_0_8_line_95 |  | 92 | 93 | 0.0077561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1710-5_0_8_line_96 |  | 93 | 94 | 0.0094982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1710-5_0_8_line_97 |  | 94 | 95 | 0.030559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1710-5_0_8_line_98 |  | 96 | 97 | 0.013847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_1710-5_0_8_line_99 |  | 96 | 98 | 0.025192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_1710-5_0_8_line_100 |  | 97 | 99 | 0.028565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_1710-5_0_8_line_101 |  | 97 | 100 | 0.017068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1710-5_0_8_line_102 |  | 98 | 101 | 0.0039639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_1710-5_0_8_line_103 |  | 99 | 102 | 0.012873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_1710-5_0_8_line_104 |  | 100 | 103 | 0.0061342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1710-5_0_8_line_105 |  | 102 | 112 | 0.069785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_1710-5_0_8_line_106 |  | 103 | 114 | 0.028197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1710-5_0_8_line_107 |  | 104 | 105 | 0.074483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1710-5_0_8_line_108 |  | 104 | 106 | 0.0073724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1710-5_0_8_line_109 |  | 105 | 107 | 0.035433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1710-5_0_8_line_110 |  | 107 | 108 | 0.0063642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1710-5_0_8_line_111 |  | 108 | 109 | 0.023671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1710-5_0_8_line_112 |  | 109 | 110 | 0.0017688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1710-5_0_8_line_113 |  | 110 | 111 | 0.023267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1710-5_0_8_line_114 |  | 113 | 114 | 0.024189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1710-5_0_8_line_115 |  | 115 | 116 | 0.0017988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1710-5_0_8_trafo_12 | 0.63 MVA 20/0.4 kV | 117 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2682311.0894 | 1216893.7712 | 2682311.4677 | 1216900.4586 | 2682311.1464 | 1216906.6805 | 2682308.7764 | 1216914.4529 | 2682306.9429 | 1216918.166
1 | 2682311.0894 | 1216893.7712 | 2682311.0894 | 1216893.7712 | 2682307.3044 | 1216882.5115 | 2682303.0208 | 1216872.7237 | 2682301.7155 | 1216867.7357 | 2682300.9946 | 1216863.8565 | 2682300.9946 | 1216863.8565
2 | 2682280.7419 | 1216942.2281 | 2682281.4619 | 1216941.705 | 2682290.6163 | 1216935.8052 | 2682295.1514 | 1216932.8881 | 2682299.519 | 1216928.9013 | 2682303.6592 | 1216923.7885 | 2682306.1753 | 1216919.7205 | 2682306.9429 | 1216918.166
3 | 2682300.5023 | 1216859.9249 | 2682300.9946 | 1216863.8565
4 | 2682300.5023 | 1216859.9249 | 2682298.6275 | 1216847.2462 | 2682295.8425 | 1216814.7085 | 2682295.3386 | 1216803.3718 | 2682296.5136 | 1216798.0239
5 | 2682296.5136 | 1216798.0239 | 2682297.3479 | 1216794.2268 | 2682305.2868 | 1216770.265 | 2682305.7781 | 1216767.623
6 | 2682313.937 | 1216698.1257 | 2682310.01 | 1216739.9991 | 2682307.8212 | 1216756.6355 | 2682305.7781 | 1216767.623
7 | 2682313.937 | 1216698.1257 | 2682306.1409 | 1216698.0069 | 2682294.5863 | 1216705.5857 | 2682261.6322 | 1216726.0444 | 2682251.2864 | 1216735.7191
8 | 2682276.6278 | 1216669.425 | 2682285.3583 | 1216669.5123 | 2682292.031 | 1216669.6044 | 2682300.8099 | 1216669.4922 | 2682307.681 | 1216668.4197 | 2682314.3864 | 1216665.5993 | 2682315.7068 | 1216674.4456 | 2682313.937 | 1216698.1257
9 | 2682003.9655 | 1216903.1333 | 2681983.2301 | 1216897.3823
10 | 2682003.9655 | 1216903.1333 | 2682016.6726 | 1216872.1347
11 | 2682018.4684 | 1216867.7539 | 2682016.6726 | 1216872.1347
12 | 2681893.058 | 1216832.751 | 2681905.2349 | 1216878.1483
13 | 2681893.058 | 1216832.751 | 2681880.22 | 1216826.2081
14 | 2682018.4684 | 1216867.7539 | 2682025.045 | 1216863.9275
15 | 2682009.6944 | 1216798.5987 | 2682009.7036 | 1216807.8605 | 2682019.2192 | 1216827.5599 | 2682019.3793 | 1216842.9501 | 2682023.4048 | 1216854.4242 | 2682018.4684 | 1216867.7539
16 | 2682018.4684 | 1216867.7539 | 2682023.4048 | 1216854.4242 | 2682047.3811 | 1216817.0072
17 | 2682025.045 | 1216863.9275 | 2682033.4776 | 1216859.0214 | 2682052.0052 | 1216868.2602 | 2682060.5031 | 1216871.9407
18 | 2682009.6944 | 1216798.5987 | 2682026.7819 | 1216765.2117 | 2682043.4575 | 1216756.2353
19 | 2682009.6944 | 1216798.5987 | 2681997.5447 | 1216791.538 | 2681982.3924 | 1216781.4229 | 2681972.3481 | 1216770.6904
20 | 2682047.3811 | 1216817.0072 | 2682061.5542 | 1216829.2993
21 | 2682047.3811 | 1216817.0072 | 2682048.2088 | 1216815.5305
22 | 2682102.9686 | 1216915.4598 | 2682103.941 | 1216909.914 | 2682091.9098 | 1216900.8868 | 2682074.1236 | 1216891.3022 | 2682074.403 | 1216883.1451 | 2682069.2663 | 1216875.7361 | 2682060.5031 | 1216871.9407
23 | 2682071.6006 | 1216732.7516 | 2682052.9884 | 1216753.3312 | 2682043.4575 | 1216756.2353
24 | 2682043.4575 | 1216756.2353 | 2682045.7735 | 1216748.7732
25 | 2681955.1857 | 1216752.3407 | 2681972.3481 | 1216770.6904
26 | 2682061.5542 | 1216829.2993 | 2682071.5044 | 1216834.5286 | 2682078.9881 | 1216832.5081 | 2682078.9881 | 1216832.5081
27 | 2682048.2088 | 1216815.5305 | 2682064.329 | 1216786.771
28 | 2682102.9686 | 1216915.4598 | 2682104.621 | 1216915.6605 | 2682109.1687 | 1216916.2235 | 2682117.9988 | 1216914.5662 | 2682120.2898 | 1216912.5076 | 2682123.5648 | 1216909.5618 | 2682130.0973 | 1216899.9788
29 | 2682146.6688 | 1216677.3226 | 2682071.6006 | 1216732.7516
30 | 2682053.1746 | 1216724.9262 | 2682045.7735 | 1216748.7732
31 | 2681955.1857 | 1216752.3407 | 2681937.2495 | 1216742.0207 | 2681936.133 | 1216736.8831
32 | 2681934.7145 | 1216730.3559 | 2681934.7145 | 1216730.3559 | 2681936.133 | 1216736.8831
33 | 2682085.9531 | 1216823.8631 | 2682084.8183 | 1216827.0626 | 2682078.9881 | 1216832.5081
34 | 2682160.2191 | 1216897.0303 | 2682130.0973 | 1216899.9788
35 | 2682163.2543 | 1216891.1808 | 2682160.2191 | 1216897.0303
36 | 2682163.2543 | 1216891.1808 | 2682169.6368 | 1216878.8802
37 | 2681746.3918 | 1216807.3649 | 2681759.9601 | 1216780.1267
38 | 2681759.9601 | 1216780.1267 | 2681761.5464 | 1216776.9423 | 2681770.213 | 1216759.3771
39 | 2681770.213 | 1216759.3771 | 2681777.506 | 1216744.596
40 | 2681781.86 | 1216735.7716 | 2681777.506 | 1216744.596
41 | 2681781.86 | 1216735.7716 | 2681797.4124 | 1216745.1536
42 | 2681781.86 | 1216735.7716 | 2681793.5886 | 1216712.3882
43 | 2681810.829 | 1216753.2473 | 2681797.4124 | 1216745.1536
44 | 2681830.2503 | 1216666.7123 | 2681824.7101 | 1216672.9738 | 2681802.8828 | 1216700.4812 | 2681801.1289 | 1216702.6919 | 2681794.2721 | 1216711.0256 | 2681793.5886 | 1216712.3882
45 | 2681810.829 | 1216753.2473 | 2681825.2659 | 1216730.3525 | 2681831.5962 | 1216722.1991
46 | 2681826.0346 | 1216765.0415 | 2681818.2841 | 1216757.7414 | 2681810.829 | 1216753.2473
47 | 2681867.3428 | 1216634.9007 | 2681859.565 | 1216639.5191 | 2681837.0347 | 1216659.0449 | 2681830.2503 | 1216666.7123
48 | 2681831.5962 | 1216722.1991 | 2681835.7164 | 1216716.8923
49 | 2681854.9393 | 1216729.7151 | 2681849.4166 | 1216733.7864 | 2681826.0346 | 1216765.0415
50 | 2681826.0346 | 1216765.0415 | 2681827.4386 | 1216766.7298
51 | 2681867.3428 | 1216634.9007 | 2681864.0432 | 1216629.6852 | 2681864.4205 | 1216626.5439
52 | 2681884.7772 | 1216625.4116 | 2681875.0747 | 1216630.3038 | 2681867.3428 | 1216634.9007
53 | 2681834.7491 | 1216780.7582 | 2681832.4133 | 1216772.7119 | 2681827.4386 | 1216766.7298
54 | 2681834.7491 | 1216780.7582 | 2681836.0816 | 1216785.3484 | 2681837.3923 | 1216797.1631 | 2681836.4584 | 1216801.2974
55 | 2681833.1885 | 1216815.7732 | 2681836.4584 | 1216801.2974
56 | 2681854.9393 | 1216729.7151 | 2681867.0489 | 1216736.3969 | 2681885.0625 | 1216745.517
57 | 2681854.9393 | 1216729.7151 | 2681860.7045 | 1216721.2553 | 2681862.1806 | 1216708.3226 | 2681865.7158 | 1216688.6471 | 2681876.2624 | 1216686.0193
58 | 2681828.9117 | 1216836.3836 | 2681833.1885 | 1216815.7732
59 | 2681885.0625 | 1216745.517 | 2681878.4033 | 1216757.5573
60 | 2681885.0625 | 1216745.517 | 2681888.3158 | 1216747.2554
61 | 2681883.712 | 1216684.1632 | 2681876.2624 | 1216686.0193
62 | 2681828.9117 | 1216836.3836 | 2681842.0431 | 1216841.6229 | 2681854.9442 | 1216844.2907 | 2681859.0115 | 1216838.5556
63 | 2681835.7164 | 1216716.8923 | 2681838.5219 | 1216713.2788 | 2681837.0614 | 1216703.1939
64 | 2681878.4033 | 1216757.5573 | 2681874.4027 | 1216764.7907
65 | 2681888.3158 | 1216747.2554 | 2681913.4806 | 1216760.7025
66 | 2681901.0292 | 1216679.8486 | 2681883.712 | 1216684.1632
67 | 2681864.8932 | 1216830.2622 | 2681859.0115 | 1216838.5556
68 | 2681836.6633 | 1216700.4448 | 2681837.0614 | 1216703.1939
69 | 2681874.4027 | 1216764.7907 | 2681874.0528 | 1216765.4233
70 | 2681918.6562 | 1216763.4682 | 2681913.4806 | 1216760.7025
71 | 2681901.0292 | 1216679.8486 | 2681916.7433 | 1216702.1459 | 2681913.7229 | 1216705.3509 | 2681913.7229 | 1216705.3509
72 | 2681917.6002 | 1216675.718 | 2681901.0292 | 1216679.8486
73 | 2681880.22 | 1216826.2081 | 2681879.4487 | 1216825.8151 | 2681871.312 | 1216821.2114 | 2681864.8932 | 1216830.2622
74 | 2681884.7772 | 1216625.4116 | 2681897.107 | 1216629.3503 | 2681914.8931 | 1216631.1142
75 | 2681914.8931 | 1216631.1142 | 2681921.5756 | 1216631.777 | 2681931.9107 | 1216632.2415 | 2681941.3487 | 1216631.2483
76 | 2681941.3487 | 1216631.2483 | 2681941.6284 | 1216631.2189 | 2681953.6584 | 1216626.0364
77 | 2681973.3072 | 1216586.9586 | 2681973.4575 | 1216595.8998 | 2681972.4463 | 1216597.8869
78 | 2681973.3072 | 1216586.9586 | 2681993.1519 | 1216572.2885 | 2681995.9857 | 1216569.4144 | 2682002.8293 | 1216562.0704
79 | 2681967.0731 | 1216608.4452 | 2681972.4463 | 1216597.8869
80 | 2682002.8293 | 1216562.0704 | 2682006.7933 | 1216569.7522 | 2682006.8076 | 1216572.0206 | 2682004.2495 | 1216584.0268
81 | 2681953.6584 | 1216626.0364 | 2681953.6584 | 1216626.0364 | 2681964.7875 | 1216612.9363 | 2681967.0731 | 1216608.4452
82 | 2682004.2495 | 1216584.0268 | 2682003.926 | 1216585.5454 | 2682003.8156 | 1216585.9152
83 | 2682000.4683 | 1216597.1314 | 2682003.8156 | 1216585.9152
84 | 2681913.7229 | 1216705.3509 | 2681912.5411 | 1216712.8841 | 2681922.0281 | 1216723.3897
85 | 2681922.0281 | 1216723.3897 | 2681929.5704 | 1216731.7417 | 2681934.7145 | 1216730.3559
86 | 2682146.6688 | 1216677.3226 | 2682144.8556 | 1216668.2848 | 2682145.2143 | 1216656.9854
87 | 2682156.4566 | 1216692.0532 | 2682153.6207 | 1216688.9859 | 2682146.8732 | 1216678.3414 | 2682146.6688 | 1216677.3226
88 | 2682159.7328 | 1216695.5967 | 2682156.4566 | 1216692.0532
89 | 2682086.9355 | 1216821.0936 | 2682085.9531 | 1216823.8631
90 | 2682095.1965 | 1216797.8029 | 2682086.9355 | 1216821.0936
91 | 2682095.9955 | 1216795.5505 | 2682095.1965 | 1216797.8029
92 | 2682099.5272 | 1216785.5933 | 2682095.9955 | 1216795.5505
93 | 2682169.6368 | 1216878.8802 | 2682134.2665 | 1216861.3663
94 | 2682169.6368 | 1216878.8802 | 2682178.055 | 1216862.6563
95 | 2682181.6272 | 1216855.7718 | 2682178.055 | 1216862.6563
96 | 2682181.6272 | 1216855.7718 | 2682185.5457 | 1216848.22 | 2682185.4779 | 1216847.232
97 | 2682185.4779 | 1216847.232 | 2682184.4267 | 1216831.916 | 2682182.8142 | 1216823.3214 | 2682183.6814 | 1216816.9176
98 | 2682176.7229 | 1216713.3871 | 2682174.4685 | 1216714.9904 | 2682167.2755 | 1216723.4413
99 | 2682167.2755 | 1216723.4413 | 2682163.1905 | 1216715.7466 | 2682160.4032 | 1216699.5035
100 | 2682176.7229 | 1216713.3871 | 2682200.0326 | 1216696.8754
101 | 2682176.7229 | 1216713.3871 | 2682182.433 | 1216719.4142 | 2682189.2984 | 1216724.8646
102 | 2682159.7328 | 1216695.5967 | 2682160.4032 | 1216699.5035
103 | 2682211.2937 | 1216690.6379 | 2682200.0326 | 1216696.8754
104 | 2682189.2984 | 1216724.8646 | 2682194.1026 | 1216728.6787
105 | 2682276.6278 | 1216669.425 | 2682259.0027 | 1216670.6826 | 2682247.4469 | 1216673.4027 | 2682236.598 | 1216676.6219 | 2682211.2937 | 1216690.6379
106 | 2682209.6536 | 1216749.9087 | 2682210.2116 | 1216745.5034 | 2682206.6767 | 1216738.6612 | 2682194.1026 | 1216728.6787
107 | 2682249.2042 | 1216896.4987 | 2682253.014 | 1216891.0455 | 2682244.9825 | 1216873.9012 | 2682242.556 | 1216857.1789 | 2682245.0107 | 1216825.2719
108 | 2682244.9819 | 1216902.5423 | 2682249.2042 | 1216896.4987
109 | 2682245.0107 | 1216825.2719 | 2682245.045 | 1216824.8252 | 2682245.3004 | 1216789.8412
110 | 2682245.3004 | 1216789.8412 | 2682245.3469 | 1216783.4772
111 | 2682246.0816 | 1216759.8313 | 2682245.4624 | 1216767.6487 | 2682245.3469 | 1216783.4772
112 | 2682246.0816 | 1216759.8313 | 2682246.2213 | 1216758.068
113 | 2682246.2213 | 1216758.068 | 2682247.3107 | 1216744.3144 | 2682251.2864 | 1216735.7191 | 2682251.2864 | 1216735.7191
114 | 2682206.6142 | 1216773.9062 | 2682209.6536 | 1216749.9087
115 | 2681999.9539 | 1216598.8551 | 2682000.4683 | 1216597.1314

## bus_geodata
| x | y | coords
0 | 2682311.0894 | 1216893.7712
1 | 2682306.9429 | 1216918.166
2 | 2682300.9946 | 1216863.8565
3 | 2682280.7419 | 1216942.2281
4 | 2682300.5023 | 1216859.9249
5 | 2682296.5136 | 1216798.0239
6 | 2682305.7781 | 1216767.623
7 | 2682313.937 | 1216698.1257
8 | 2681983.2301 | 1216897.3823
9 | 2682003.9655 | 1216903.1333
10 | 2682016.6726 | 1216872.1347
11 | 2681905.2349 | 1216878.1483
12 | 2681893.058 | 1216832.751
13 | 2682018.4684 | 1216867.7539
14 | 2682025.045 | 1216863.9275
15 | 2682009.6944 | 1216798.5987
16 | 2682047.3811 | 1216817.0072
17 | 2682060.5031 | 1216871.9407
18 | 2682043.4575 | 1216756.2353
19 | 2681972.3481 | 1216770.6904
20 | 2682061.5542 | 1216829.2993
21 | 2682048.2088 | 1216815.5305
22 | 2682102.9686 | 1216915.4598
23 | 2682071.6006 | 1216732.7516
24 | 2682045.7735 | 1216748.7732
25 | 2681955.1857 | 1216752.3407
26 | 2681936.133 | 1216736.8831
27 | 2682078.9881 | 1216832.5081
28 | 2682064.329 | 1216786.771
29 | 2682130.0973 | 1216899.9788
30 | 2682160.2191 | 1216897.0303
31 | 2682163.2543 | 1216891.1808
32 | 2681746.3918 | 1216807.3649
33 | 2681759.9601 | 1216780.1267
34 | 2681770.213 | 1216759.3771
35 | 2681777.506 | 1216744.596
36 | 2681781.86 | 1216735.7716
37 | 2681797.4124 | 1216745.1536
38 | 2681793.5887 | 1216712.3882
39 | 2681810.829 | 1216753.2473
40 | 2681830.2503 | 1216666.7123
41 | 2681831.5962 | 1216722.1991
42 | 2681826.0346 | 1216765.0415
43 | 2681867.3428 | 1216634.9007
44 | 2681827.4386 | 1216766.7298
45 | 2681834.7491 | 1216780.7582
46 | 2681836.4584 | 1216801.2974
47 | 2681854.9393 | 1216729.7151
48 | 2681833.1885 | 1216815.7732
49 | 2681885.0625 | 1216745.517
50 | 2681876.2624 | 1216686.0193
51 | 2681828.9117 | 1216836.3836
52 | 2681835.7164 | 1216716.8923
53 | 2681878.4033 | 1216757.5573
54 | 2681888.3158 | 1216747.2554
55 | 2681883.712 | 1216684.1632
56 | 2681859.0115 | 1216838.5556
57 | 2681837.0614 | 1216703.1939
58 | 2681874.4027 | 1216764.7907
59 | 2681913.4806 | 1216760.7025
60 | 2681901.0292 | 1216679.8486
61 | 2681864.8932 | 1216830.2622
62 | 2681880.22 | 1216826.2081
63 | 2681864.4205 | 1216626.5439
64 | 2681884.7772 | 1216625.4116
65 | 2681836.6633 | 1216700.4448
66 | 2681914.8931 | 1216631.1142
67 | 2681941.3487 | 1216631.2483
68 | 2681973.3072 | 1216586.9586
69 | 2681972.4463 | 1216597.8869
70 | 2682002.8293 | 1216562.0704
71 | 2681953.6584 | 1216626.0364
72 | 2681967.0731 | 1216608.4452
73 | 2682004.2495 | 1216584.0268
74 | 2682003.8156 | 1216585.9152
75 | 2681913.7228 | 1216705.3509
76 | 2681917.6002 | 1216675.718
77 | 2681922.0281 | 1216723.3897
78 | 2681934.7145 | 1216730.3559
79 | 2681874.0528 | 1216765.4233
80 | 2681918.6562 | 1216763.4682
81 | 2682053.1746 | 1216724.9262
82 | 2682146.6688 | 1216677.3226
83 | 2682145.2143 | 1216656.9854
84 | 2682156.4566 | 1216692.0532
85 | 2682085.9531 | 1216823.8631
86 | 2682086.9355 | 1216821.0936
87 | 2682095.9955 | 1216795.5505
88 | 2682095.1965 | 1216797.8029
89 | 2682099.5272 | 1216785.5933
90 | 2682134.2665 | 1216861.3663
91 | 2682169.6368 | 1216878.8802
92 | 2682178.055 | 1216862.6563
93 | 2682181.6272 | 1216855.7718
94 | 2682185.4779 | 1216847.232
95 | 2682183.6814 | 1216816.9176
96 | 2682167.2755 | 1216723.4413
97 | 2682176.7229 | 1216713.3871
98 | 2682160.4032 | 1216699.5035
99 | 2682200.0326 | 1216696.8754
100 | 2682189.2984 | 1216724.8646
101 | 2682159.7328 | 1216695.5967
102 | 2682211.2937 | 1216690.6379
103 | 2682194.1026 | 1216728.6787
104 | 2682249.2042 | 1216896.4987
105 | 2682245.0107 | 1216825.2719
106 | 2682244.9819 | 1216902.5423
107 | 2682245.3004 | 1216789.8412
108 | 2682245.3469 | 1216783.4772
109 | 2682246.0816 | 1216759.8313
110 | 2682246.2213 | 1216758.068
111 | 2682251.2864 | 1216735.7191
112 | 2682276.6278 | 1216669.425
113 | 2682206.6142 | 1216773.9062
114 | 2682209.6536 | 1216749.9087
115 | 2682000.4683 | 1216597.1314
116 | 2681999.9539 | 1216598.8551
117 | 2682043.4575 | 1216756.2353

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97841 | -0.41473 | 0.00040786 | 0.00010222
1 | 0.97819 | -0.41921 | 0.0017956 | 0.00045002
2 | 0.97871 | -0.40887 | 0.015968 | 0.0040019
3 | 0.97792 | -0.42446 | 0.0079651 | 0.0019962
4 | 0.97881 | -0.40698 | 0 | 0
5 | 0.98032 | -0.3774 | 0.0030783 | 0.00077149
6 | 0.98118 | -0.36056 | 0.0053236 | 0.0013342
7 | 0.98342 | -0.31687 | 0 | 0
8 | 0.9934 | -0.12591 | 0.01096 | 0.002747
9 | 0.99362 | -0.12174 | 0 | 0
10 | 0.99395 | -0.11526 | 0.0087361 | 0.0021895
11 | 0.97362 | -0.50861 | 0.0027937 | 0.00070017
12 | 0.97374 | -0.5062 | 0.019926 | 0.0049939
13 | 0.99404 | -0.11362 | 0 | 0
14 | 0.99344 | -0.12512 | 0.010729 | 0.002689
15 | 1 | 0 | -0.57088 | -0.14624
16 | 0.99014 | -0.18884 | 0 | 0
17 | 0.99068 | -0.17781 | 0.0042023 | 0.0010532
18 | 0.99757 | -0.045871 | 0 | 0
19 | 0.99648 | -0.066437 | 0.001464 | 0.00036692
20 | 0.98938 | -0.20374 | 0.010395 | 0.0026053
21 | 0.9901 | -0.18967 | 0.017444 | 0.0043718
22 | 0.98626 | -0.26309 | 0 | 0
23 | 0.99605 | -0.074697 | 0.0048677 | 0.00122
24 | 0.99751 | -0.047067 | 0.003448 | 0.00086416
25 | 0.99461 | -0.10195 | 0.0033015 | 0.00082743
26 | 0.9927 | -0.13827 | 0.0033501 | 0.00083961
27 | 0.98878 | -0.21533 | 0.0061803 | 0.0015489
28 | 0.98979 | -0.19573 | 0.010327 | 0.0025881
29 | 0.98401 | -0.30666 | 0 | 0
30 | 0.98203 | -0.34526 | 0.0052364 | 0.0013124
31 | 0.98163 | -0.35306 | 0.0071713 | 0.0017973
32 | 0.97885 | -0.40592 | 0.0033136 | 0.00083048
33 | 0.97895 | -0.40408 | 0.0026415 | 0.00066201
34 | 0.97907 | -0.40158 | 0.0021888 | 0.00054857
35 | 0.9792 | -0.39914 | 0.00094139 | 0.00023594
36 | 0.97928 | -0.39751 | 0 | 0
37 | 0.97959 | -0.39138 | 0.0095604 | 0.0023961
38 | 0.9789 | -0.40491 | 0.0016161 | 0.00040503
39 | 0.97991 | -0.38518 | 0 | 0
40 | 0.97767 | -0.42895 | 0.003665 | 0.00091854
41 | 0.97913 | -0.40044 | 0.0052208 | 0.0013085
42 | 0.98044 | -0.37493 | 0 | 0
43 | 0.97578 | -0.46606 | 0 | 0
44 | 0.98031 | -0.3773 | 0.0022859 | 0.0005729
45 | 0.97945 | -0.39412 | 0.003011 | 0.00075463
46 | 0.9784 | -0.41478 | 0.0035172 | 0.0008815
47 | 0.98253 | -0.33417 | 0 | 0
48 | 0.97769 | -0.42852 | 0 | 0
49 | 0.98142 | -0.35583 | 0 | 0
50 | 0.98559 | -0.27484 | 0.0085822 | 0.0021509
51 | 0.9767 | -0.44804 | 0 | 0
52 | 0.97903 | -0.40255 | 0.0059429 | 0.0014894
53 | 0.98121 | -0.35996 | 0.0067234 | 0.001685
54 | 0.98136 | -0.35708 | 0.014283 | 0.0035796
55 | 0.98605 | -0.26606 | 0.032679 | 0.0081901
56 | 0.97507 | -0.47997 | 0.0091686 | 0.0022979
57 | 0.97887 | -0.40559 | 0.0061951 | 0.0015526
58 | 0.98114 | -0.36144 | 0.0032351 | 0.00081079
59 | 0.98124 | -0.35937 | 0.0019522 | 0.00048927
60 | 0.98728 | -0.2422 | 0 | 0
61 | 0.97468 | -0.48774 | 0.0098384 | 0.0024657
62 | 0.97405 | -0.50018 | 0.0090784 | 0.0022753
63 | 0.9757 | -0.4676 | 0.0089575 | 0.002245
64 | 0.97518 | -0.47783 | 0 | 0
65 | 0.97886 | -0.40585 | 0.0051095 | 0.0012806
66 | 0.97425 | -0.49616 | 0.0068007 | 0.0017044
67 | 0.97362 | -0.50866 | 0.0053787 | 0.001348
68 | 0.97275 | -0.52583 | 0 | 0
69 | 0.97289 | -0.52308 | 0.0009883 | 0.00024769
70 | 0.97226 | -0.53536 | 0 | 0
71 | 0.97336 | -0.51364 | 0.0048003 | 0.0012031
72 | 0.97304 | -0.51995 | 0.0010839 | 0.00027166
73 | 0.97198 | -0.54107 | 0.0011667 | 0.0002924
74 | 0.97195 | -0.5415 | 0.00076613 | 0.00019201
75 | 0.9895 | -0.19957 | 0.0015757 | 0.0003949
76 | 0.98725 | -0.24289 | 0.0022506 | 0.00056404
77 | 0.99103 | -0.17017 | 0.0034978 | 0.00087662
78 | 0.99222 | -0.14751 | 0.0031477 | 0.00078889
79 | 0.98113 | -0.36153 | 0.0066344 | 0.0016627
80 | 0.98123 | -0.35964 | 0.0024829 | 0.00062228
81 | 0.99739 | -0.049381 | 0.00529 | 0.0013258
82 | 0.99242 | -0.14384 | 0.0024019 | 0.00060197
83 | 0.99238 | -0.14443 | 0.0016417 | 0.00041146
84 | 0.99174 | -0.15667 | 0.00067069 | 0.00016809
85 | 0.98849 | -0.22102 | 0.0064909 | 0.0016268
86 | 0.98843 | -0.22215 | 0.0058022 | 0.0014542
87 | 0.98805 | -0.22958 | 0.0054491 | 0.0013657
88 | 0.98807 | -0.22911 | 0.0046256 | 0.0011593
89 | 0.98799 | -0.23066 | 0.0056985 | 0.0014282
90 | 0.97948 | -0.39522 | 0.038453 | 0.0096372
91 | 0.98089 | -0.36768 | 0.0040911 | 0.0010253
92 | 0.98062 | -0.3729 | 0.0020927 | 0.00052449
93 | 0.98052 | -0.37482 | 0.0044271 | 0.0011095
94 | 0.98044 | -0.37641 | 0.0041742 | 0.0010462
95 | 0.9803 | -0.37921 | 0.0050566 | 0.0012673
96 | 0.99051 | -0.18035 | 0 | 0
97 | 0.99001 | -0.18991 | 0 | 0
98 | 0.99141 | -0.16297 | 0.0047711 | 0.0011957
99 | 0.98907 | -0.20788 | 0.0066277 | 0.0016611
100 | 0.98984 | -0.19311 | 0.00084036 | 0.00021061
101 | 0.99156 | -0.16013 | 0 | 0
102 | 0.98867 | -0.21548 | 0.0032275 | 0.00080889
103 | 0.98979 | -0.19417 | 0.0066936 | 0.0016776
104 | 0.97304 | -0.52002 | 0.01333 | 0.0033408
105 | 0.975 | -0.48131 | 0.014634 | 0.0036677
106 | 0.97293 | -0.52205 | 0.014957 | 0.0037486
107 | 0.97642 | -0.45346 | 0.0043615 | 0.0010931
108 | 0.9767 | -0.44796 | 0.0032095 | 0.00080438
109 | 0.97781 | -0.42615 | 0.004005 | 0.0010038
110 | 0.9779 | -0.42439 | 0.0030349 | 0.00076061
111 | 0.97914 | -0.40002 | 0.0040711 | 0.0010203
112 | 0.9866 | -0.25545 | 0 | 0
113 | 0.98967 | -0.19641 | 0.0017097 | 0.00042849
114 | 0.98971 | -0.19567 | 0.0012915 | 0.00032367
115 | 0.97183 | -0.54397 | 0.0021959 | 0.00055033
116 | 0.97181 | -0.54428 | 0.0092303 | 0.0023133
117 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0097648 | 0.0024481 | -0.0097627 | -0.0024471 | 2.0838e-06 | 1.0173e-06 | 0.014851 | 0.014851 | 0.014851 | 0.97841 | -0.41473 | 0.97819 | -0.41921 | 4.08
1 | -0.010173 | -0.0025503 | 0.010175 | 0.0025517 | 2.8422e-06 | 1.4212e-06 | 0.015471 | 0.015471 | 0.015471 | 0.97841 | -0.41473 | 0.97871 | -0.40887 | 4.2504
2 | 0.0079671 | 0.0019971 | -0.0079651 | -0.0019962 | 1.993e-06 | 8.2147e-07 | 0.01212 | 0.01212 | 0.01212 | 0.97819 | -0.41921 | 0.97792 | -0.42446 | 3.3296
3 | -0.026143 | -0.0065537 | 0.026146 | 0.0065551 | 2.3476e-06 | 1.4527e-06 | 0.039748 | 0.039748 | 0.039748 | 0.97871 | -0.40887 | 0.97881 | -0.40698 | 10.9199
4 | -0.026146 | -0.0065551 | 0.026183 | 0.006578 | 3.6909e-05 | 2.2838e-05 | 0.039748 | 0.039748 | 0.039748 | 0.97881 | -0.40698 | 0.98032 | -0.3774 | 10.9199
5 | -0.029261 | -0.0073495 | 0.029284 | 0.0073641 | 2.3543e-05 | 1.4666e-05 | 0.044421 | 0.044421 | 0.044421 | 0.98032 | -0.3774 | 0.98118 | -0.36056 | 12.2035
6 | -0.034608 | -0.0086983 | 0.03468 | 0.0087438 | 7.2348e-05 | 4.5416e-05 | 0.052494 | 0.052494 | 0.052494 | 0.98118 | -0.36056 | 0.98342 | -0.31687 | 14.4214
7 | 0.062099 | 0.015753 | -0.061851 | -0.015596 | 0.00024724 | 0.00015729 | 0.09403 | 0.09403 | 0.09403 | 0.98342 | -0.31687 | 0.97914 | -0.40002 | 25.8324
8 | -0.096779 | -0.024497 | 0.097065 | 0.024678 | 0.00028622 | 0.00018137 | 0.14652 | 0.14652 | 0.14652 | 0.98342 | -0.31687 | 0.9866 | -0.25545 | 20.1268
9 | -0.01096 | -0.002747 | 0.010963 | 0.0027481 | 2.175e-06 | 1.1134e-06 | 0.016418 | 0.016418 | 0.016418 | 0.9934 | -0.12591 | 0.99362 | -0.12174 | 4.5104
10 | -0.010963 | -0.0027481 | 0.010966 | 0.0027498 | 3.3862e-06 | 1.7331e-06 | 0.016418 | 0.016417 | 0.016418 | 0.99362 | -0.12174 | 0.99395 | -0.11526 | 4.5103
11 | -0.019702 | -0.0049393 | 0.019704 | 0.0049402 | 1.5447e-06 | 9.2722e-07 | 0.029496 | 0.029496 | 0.029496 | 0.99395 | -0.11526 | 0.99404 | -0.11362 | 8.1033
12 | -0.0027937 | -0.00070017 | 0.002794 | 0.00069979 | 3.2131e-07 | -3.7897e-07 | 0.0042697 | 0.0042695 | 0.0042697 | 0.97362 | -0.50861 | 0.97374 | -0.5062 | 1.173
13 | -0.02272 | -0.0056937 | 0.022726 | 0.0056977 | 6.5133e-06 | 3.9892e-06 | 0.034719 | 0.034719 | 0.034719 | 0.97374 | -0.5062 | 0.97405 | -0.50018 | 9.5382
14 | 0.086567 | 0.022055 | -0.086519 | -0.022025 | 4.8009e-05 | 3.0627e-05 | 0.12971 | 0.12971 | 0.12971 | 0.99404 | -0.11362 | 0.99344 | -0.12512 | 35.6358
15 | -0.17901 | -0.045353 | 0.18 | 0.04598 | 0.00098287 | 0.00062714 | 0.26815 | 0.26815 | 0.26815 | 0.99404 | -0.11362 | 1 | 0 | 36.8333
16 | 0.072743 | 0.018357 | -0.072482 | -0.018191 | 0.00026102 | 0.0001663 | 0.10894 | 0.10894 | 0.10894 | 0.99404 | -0.11362 | 0.99014 | -0.18884 | 29.9276
17 | 0.07579 | 0.019336 | -0.075598 | -0.019213 | 0.00019237 | 0.0001226 | 0.11364 | 0.11364 | 0.11364 | 0.99344 | -0.12512 | 0.99068 | -0.17781 | 31.2208
18 | 0.14206 | 0.036531 | -0.14175 | -0.036331 | 0.00031595 | 0.0002 | 0.21172 | 0.21172 | 0.21172 | 1 | 0 | 0.99757 | -0.045871 | 19.3885
19 | 0.24717 | 0.063726 | -0.24638 | -0.063218 | 0.00079698 | 0.00050822 | 0.36843 | 0.36843 | 0.36843 | 1 | 0 | 0.99648 | -0.066437 | 33.7393
20 | 0.044707 | 0.011229 | -0.044675 | -0.011209 | 3.1767e-05 | 2.0089e-05 | 0.067196 | 0.067196 | 0.067196 | 0.99014 | -0.18884 | 0.98938 | -0.20374 | 18.4604
21 | 0.027774 | 0.0069621 | -0.027773 | -0.0069614 | 1.106e-06 | 6.8608e-07 | 0.041741 | 0.041741 | 0.041741 | 0.99014 | -0.18884 | 0.9901 | -0.18967 | 11.4672
22 | 0.071395 | 0.01816 | -0.071103 | -0.017974 | 0.00029205 | 0.00018605 | 0.10733 | 0.10733 | 0.10733 | 0.99068 | -0.17781 | 0.98626 | -0.26309 | 29.4868
23 | 0.13301 | 0.03414 | -0.13282 | -0.034023 | 0.0001858 | 0.00011744 | 0.19869 | 0.19869 | 0.19869 | 0.99757 | -0.045871 | 0.99605 | -0.074697 | 18.1948
24 | 0.0087391 | 0.0021902 | -0.0087386 | -0.00219 | 4.9787e-07 | 2.1664e-07 | 0.013036 | 0.013036 | 0.013036 | 0.99757 | -0.045871 | 0.99751 | -0.047067 | 3.5812
25 | 0.24491 | 0.062851 | -0.24449 | -0.062583 | 0.00042127 | 0.00026863 | 0.36625 | 0.36625 | 0.36625 | 0.99648 | -0.066437 | 0.99461 | -0.10195 | 33.5391
26 | 0.03428 | 0.0086035 | -0.034261 | -0.0085917 | 1.8935e-05 | 1.1874e-05 | 0.051561 | 0.051562 | 0.051562 | 0.98938 | -0.20374 | 0.98878 | -0.21533 | 14.1652
27 | 0.01033 | 0.0025896 | -0.010327 | -0.0025881 | 2.9797e-06 | 1.4831e-06 | 0.015524 | 0.015525 | 0.015525 | 0.9901 | -0.18967 | 0.98979 | -0.19573 | 4.265
28 | 0.071103 | 0.017974 | -0.070955 | -0.01788 | 0.00014824 | 9.4436e-05 | 0.10733 | 0.10733 | 0.10733 | 0.98626 | -0.26309 | 0.98401 | -0.30666 | 29.4869
29 | 0.12795 | 0.032803 | -0.12753 | -0.032533 | 0.00042738 | 0.0002699 | 0.19142 | 0.19142 | 0.19142 | 0.99605 | -0.074697 | 0.99242 | -0.14384 | 17.529
30 | 0.0052905 | 0.0013258 | -0.00529 | -0.0013258 | 5.832e-07 | 4.7341e-08 | 0.007892 | 0.0078921 | 0.0078921 | 0.99751 | -0.047067 | 0.99739 | -0.049381 | 2.1682
31 | 0.24119 | 0.061755 | -0.24077 | -0.061485 | 0.00042346 | 0.00027001 | 0.36131 | 0.36131 | 0.36131 | 0.99461 | -0.10195 | 0.9927 | -0.13827 | 33.0868
32 | 0.23742 | 0.060646 | -0.23731 | -0.060578 | 0.00010599 | 6.7573e-05 | 0.35629 | 0.35629 | 0.35629 | 0.9927 | -0.13827 | 0.99222 | -0.14751 | 32.627
33 | 0.028081 | 0.0070427 | -0.028073 | -0.007038 | 7.6166e-06 | 4.7288e-06 | 0.042261 | 0.042261 | 0.042261 | 0.98878 | -0.21533 | 0.98849 | -0.22102 | 11.6101
34 | 0.070955 | 0.01788 | -0.070824 | -0.017796 | 0.00013075 | 8.3297e-05 | 0.10733 | 0.10733 | 0.10733 | 0.98401 | -0.30666 | 0.98203 | -0.34526 | 29.4869
35 | 0.065588 | 0.016484 | -0.065564 | -0.016468 | 2.4416e-05 | 1.5543e-05 | 0.099398 | 0.099398 | 0.099398 | 0.98203 | -0.34526 | 0.98163 | -0.35306 | 27.3071
36 | 0.058392 | 0.014671 | -0.058351 | -0.014645 | 4.0727e-05 | 2.589e-05 | 0.088527 | 0.088527 | 0.088527 | 0.98163 | -0.35306 | 0.98089 | -0.36768 | 24.3207
37 | -0.0033136 | -0.00083048 | 0.0033139 | 0.00083028 | 2.8955e-07 | -1.9725e-07 | 0.0050373 | 0.0050371 | 0.0050373 | 0.97885 | -0.40592 | 0.97895 | -0.40408 | 1.3839
38 | -0.0059554 | -0.0014923 | 0.0059561 | 0.0014925 | 7.1119e-07 | 1.6413e-07 | 0.0090522 | 0.0090521 | 0.0090522 | 0.97895 | -0.40408 | 0.97907 | -0.40158 | 2.4869
39 | -0.0081449 | -0.002041 | 0.0081459 | 0.0020414 | 9.4711e-07 | 3.9884e-07 | 0.012379 | 0.012379 | 0.012379 | 0.97907 | -0.40158 | 0.9792 | -0.39914 | 3.4007
40 | -0.0090873 | -0.0022774 | 0.009088 | 0.0022777 | 7.0367e-07 | 3.2656e-07 | 0.013809 | 0.013809 | 0.013809 | 0.9792 | -0.39914 | 0.97928 | -0.39751 | 3.7937
41 | -0.055967 | -0.01411 | 0.055984 | 0.01412 | 1.6431e-05 | 9.8303e-06 | 0.085072 | 0.085072 | 0.085072 | 0.97928 | -0.39751 | 0.97959 | -0.39138 | 7.7905
42 | 0.046879 | 0.011833 | -0.046863 | -0.011823 | 1.6606e-05 | 9.6411e-06 | 0.071263 | 0.071263 | 0.071263 | 0.97928 | -0.39751 | 0.9789 | -0.40491 | 6.5259
43 | -0.065544 | -0.016516 | 0.065563 | 0.016528 | 1.9427e-05 | 1.1842e-05 | 0.099594 | 0.099594 | 0.099594 | 0.97959 | -0.39138 | 0.97991 | -0.38518 | 9.1203
44 | 0.045246 | 0.011418 | -0.045194 | -0.011386 | 5.2032e-05 | 3.1828e-05 | 0.068807 | 0.068807 | 0.068807 | 0.9789 | -0.40491 | 0.97767 | -0.42895 | 9.4515
45 | 0.022488 | 0.005643 | -0.022472 | -0.005633 | 1.6353e-05 | 9.995e-06 | 0.034151 | 0.034151 | 0.034151 | 0.97991 | -0.38518 | 0.97913 | -0.40044 | 9.3822
46 | -0.088052 | -0.022171 | 0.088095 | 0.022198 | 4.3192e-05 | 2.6913e-05 | 0.13375 | 0.13374 | 0.13375 | 0.97991 | -0.38518 | 0.98044 | -0.37493 | 12.2477
47 | 0.041529 | 0.010468 | -0.041456 | -0.010421 | 7.3608e-05 | 4.6495e-05 | 0.063229 | 0.063229 | 0.063229 | 0.97767 | -0.42895 | 0.97578 | -0.46606 | 17.3707
48 | 0.017251 | 0.0043245 | -0.017249 | -0.0043235 | 1.7317e-06 | 1.0238e-06 | 0.026217 | 0.026217 | 0.026217 | 0.97913 | -0.40044 | 0.97903 | -0.40255 | 7.2025
49 | -0.14802 | -0.037334 | 0.14831 | 0.037517 | 0.00028945 | 0.00018351 | 0.22474 | 0.22474 | 0.22474 | 0.98044 | -0.37493 | 0.98253 | -0.33417 | 20.5803
50 | 0.059926 | 0.015136 | -0.059919 | -0.015131 | 6.8175e-06 | 4.3355e-06 | 0.090992 | 0.090992 | 0.090992 | 0.98044 | -0.37493 | 0.98031 | -0.3773 | 24.9978
51 | 0.0089581 | 0.0022453 | -0.0089575 | -0.002245 | 6.533e-07 | 3.0151e-07 | 0.013661 | 0.013661 | 0.013661 | 0.97578 | -0.46606 | 0.9757 | -0.4676 | 3.753
52 | 0.032498 | 0.0081758 | -0.032479 | -0.0081644 | 1.8261e-05 | 1.144e-05 | 0.049568 | 0.049569 | 0.049569 | 0.97578 | -0.46606 | 0.97518 | -0.47783 | 13.6177
53 | 0.057633 | 0.014559 | -0.057587 | -0.014529 | 4.6417e-05 | 2.9504e-05 | 0.087522 | 0.087522 | 0.087522 | 0.98031 | -0.3773 | 0.97945 | -0.39412 | 24.0446
54 | 0.054576 | 0.013774 | -0.054522 | -0.01374 | 5.3939e-05 | 3.4258e-05 | 0.082948 | 0.082948 | 0.082948 | 0.97945 | -0.39412 | 0.9784 | -0.41478 | 22.7879
55 | 0.051005 | 0.012859 | -0.050971 | -0.012837 | 3.3511e-05 | 2.1261e-05 | 0.077599 | 0.077599 | 0.077599 | 0.9784 | -0.41478 | 0.97769 | -0.42852 | 21.3184
56 | 0.035353 | 0.0088755 | -0.035316 | -0.0088525 | 3.6497e-05 | 2.2929e-05 | 0.053546 | 0.053547 | 0.053547 | 0.98253 | -0.33417 | 0.98142 | -0.35583 | 14.7106
57 | -0.18366 | -0.046393 | 0.18419 | 0.046726 | 0.00052383 | 0.00033319 | 0.27828 | 0.27828 | 0.27828 | 0.98253 | -0.33417 | 0.98559 | -0.27484 | 25.4838
58 | 0.050971 | 0.012837 | -0.050924 | -0.012807 | 4.7535e-05 | 3.0159e-05 | 0.077599 | 0.077599 | 0.077599 | 0.97769 | -0.42852 | 0.9767 | -0.44804 | 21.3184
59 | 0.016597 | 0.0041608 | -0.016594 | -0.0041589 | 3.2673e-06 | 1.9173e-06 | 0.025164 | 0.025164 | 0.025164 | 0.98142 | -0.35583 | 0.98121 | -0.35996 | 6.9133
60 | 0.01872 | 0.0046917 | -0.018718 | -0.0046911 | 1.1143e-06 | 6.6654e-07 | 0.028382 | 0.028382 | 0.028382 | 0.98142 | -0.35583 | 0.98136 | -0.35708 | 7.7974
61 | -0.19277 | -0.048877 | 0.19285 | 0.048929 | 8.1399e-05 | 5.1802e-05 | 0.29124 | 0.29124 | 0.29124 | 0.98559 | -0.27484 | 0.98605 | -0.26606 | 26.6702
62 | 0.050924 | 0.012807 | -0.050846 | -0.012758 | 7.755e-05 | 4.9203e-05 | 0.077599 | 0.077599 | 0.077599 | 0.9767 | -0.44804 | 0.97507 | -0.47997 | 21.3184
63 | 0.011306 | 0.0028341 | -0.011305 | -0.0028332 | 1.6351e-06 | 8.6081e-07 | 0.017185 | 0.017185 | 0.017185 | 0.97903 | -0.40255 | 0.97887 | -0.40559 | 4.721
64 | 0.0098702 | 0.0024739 | -0.0098695 | -0.0024735 | 6.945e-07 | 3.4008e-07 | 0.014968 | 0.014968 | 0.014968 | 0.98121 | -0.35996 | 0.98114 | -0.36144 | 4.1122
65 | 0.0044356 | 0.0011114 | -0.0044352 | -0.0011115 | 4.8399e-07 | -5.0699e-08 | 0.0067256 | 0.0067257 | 0.0067257 | 0.98136 | -0.35708 | 0.98124 | -0.35937 | 1.8477
66 | -0.22553 | -0.057119 | 0.22579 | 0.057284 | 0.00025872 | 0.0001649 | 0.34055 | 0.34055 | 0.34055 | 0.98605 | -0.26606 | 0.98728 | -0.2422 | 31.1863
67 | 0.041677 | 0.01046 | -0.041662 | -0.01045 | 1.5426e-05 | 9.7459e-06 | 0.063607 | 0.063607 | 0.063607 | 0.97507 | -0.47997 | 0.97468 | -0.48774 | 17.4746
68 | 0.0051096 | 0.0012806 | -0.0051095 | -0.0012806 | 6.2843e-08 | 5.3019e-09 | 0.0077673 | 0.0077673 | 0.0077673 | 0.97887 | -0.40559 | 0.97886 | -0.40585 | 2.1339
69 | 0.0066344 | 0.0016627 | -0.0066344 | -0.0016627 | 2.7447e-08 | 8.4361e-09 | 0.010062 | 0.010062 | 0.010062 | 0.98114 | -0.36144 | 0.98113 | -0.36153 | 2.7643
70 | 0.002483 | 0.00062223 | -0.0024829 | -0.00062228 | 3.1199e-08 | -5.4157e-08 | 0.0037653 | 0.0037653 | 0.0037653 | 0.98124 | -0.35937 | 0.98123 | -0.35964 | 1.0344
71 | -0.22804 | -0.057848 | 0.22851 | 0.058146 | 0.0004685 | 0.00029862 | 0.34395 | 0.34395 | 0.34395 | 0.98728 | -0.2422 | 0.9895 | -0.19957 | 31.4969
72 | 0.0022506 | 0.00056387 | -0.0022506 | -0.00056404 | 7.349e-08 | -1.7076e-07 | 0.003392 | 0.0033921 | 0.0033921 | 0.98728 | -0.2422 | 0.98725 | -0.24289 | 0.9319
73 | 0.031824 | 0.0079847 | -0.031805 | -0.0079729 | 1.8866e-05 | 1.1809e-05 | 0.048587 | 0.048588 | 0.048588 | 0.97468 | -0.48774 | 0.97405 | -0.50018 | 13.3482
74 | 0.032479 | 0.0081644 | -0.032451 | -0.0081466 | 2.8395e-05 | 1.7788e-05 | 0.049569 | 0.049569 | 0.049569 | 0.97518 | -0.47783 | 0.97425 | -0.49616 | 13.6178
75 | 0.02565 | 0.0064422 | -0.025635 | -0.0064327 | 1.5285e-05 | 9.4523e-06 | 0.039182 | 0.039182 | 0.039182 | 0.97425 | -0.49616 | 0.97362 | -0.50866 | 10.7642
76 | 0.020256 | 0.0050847 | -0.020251 | -0.0050818 | 4.8098e-06 | 2.9119e-06 | 0.030961 | 0.030961 | 0.030961 | 0.97362 | -0.50866 | 0.97336 | -0.51364 | 8.5059
77 | -0.01337 | -0.0033544 | 0.013372 | 0.0033554 | 1.7528e-06 | 9.8306e-07 | 0.020454 | 0.020454 | 0.020454 | 0.97275 | -0.52583 | 0.97289 | -0.52308 | 5.6192
78 | 0.01337 | 0.0033544 | -0.013364 | -0.003351 | 6.0702e-06 | 3.4049e-06 | 0.020454 | 0.020454 | 0.020454 | 0.97275 | -0.52583 | 0.97226 | -0.53536 | 5.6193
79 | -0.01436 | -0.0036031 | 0.014363 | 0.0036043 | 2.1435e-06 | 1.2247e-06 | 0.021966 | 0.021966 | 0.021966 | 0.97289 | -0.52308 | 0.97304 | -0.51995 | 6.0345
80 | 0.013364 | 0.003351 | -0.013361 | -0.003349 | 3.6381e-06 | 2.0409e-06 | 0.020454 | 0.020454 | 0.020454 | 0.97226 | -0.53536 | 0.97198 | -0.54107 | 5.6193
81 | 0.015451 | 0.0038787 | -0.015447 | -0.003876 | 4.6517e-06 | 2.7009e-06 | 0.023623 | 0.023623 | 0.023623 | 0.97336 | -0.51364 | 0.97304 | -0.51995 | 6.4899
82 | 0.012194 | 0.0030566 | -0.012194 | -0.0030564 | 2.5336e-07 | 1.3812e-07 | 0.018668 | 0.018668 | 0.018668 | 0.97198 | -0.54107 | 0.97195 | -0.5415 | 5.1286
83 | 0.011428 | 0.0028644 | -0.011426 | -0.0028637 | 1.3435e-06 | 7.1481e-07 | 0.017495 | 0.017495 | 0.017495 | 0.97195 | -0.5415 | 0.97183 | -0.54397 | 4.8064
84 | -0.23008 | -0.058541 | 0.23041 | 0.058749 | 0.00032653 | 0.00020814 | 0.34631 | 0.34631 | 0.34631 | 0.9895 | -0.19957 | 0.99103 | -0.17017 | 31.7138
85 | -0.23391 | -0.059626 | 0.23416 | 0.059789 | 0.00025617 | 0.00016331 | 0.35157 | 0.35157 | 0.35157 | 0.99103 | -0.17017 | 0.99222 | -0.14751 | 32.1947
86 | 0.0016418 | 0.00041123 | -0.0016417 | -0.00041146 | 4.6636e-08 | -2.3532e-07 | 0.0024616 | 0.0024617 | 0.0024617 | 0.99242 | -0.14384 | 0.99238 | -0.14443 | 0.67629
87 | 0.12348 | 0.03152 | -0.12341 | -0.031472 | 7.6526e-05 | 4.8286e-05 | 0.18535 | 0.18535 | 0.18535 | 0.99242 | -0.14384 | 0.99174 | -0.15667 | 16.9738
88 | 0.12274 | 0.031304 | -0.12272 | -0.031291 | 2.0501e-05 | 1.2934e-05 | 0.18435 | 0.18435 | 0.18435 | 0.99174 | -0.15667 | 0.99156 | -0.16013 | 16.8817
89 | 0.021582 | 0.0054112 | -0.021581 | -0.0054105 | 1.1632e-06 | 7.068e-07 | 0.03249 | 0.03249 | 0.03249 | 0.98849 | -0.22102 | 0.98843 | -0.22215 | 8.9258
90 | 0.015779 | 0.0039564 | -0.015774 | -0.0039533 | 5.2295e-06 | 3.0302e-06 | 0.023755 | 0.023755 | 0.023755 | 0.98843 | -0.22215 | 0.98807 | -0.22911 | 6.5261
91 | -0.011148 | -0.0027939 | 0.011148 | 0.002794 | 2.5261e-07 | 1.3106e-07 | 0.016789 | 0.016789 | 0.016789 | 0.98805 | -0.22958 | 0.98807 | -0.22911 | 4.6123
92 | 0.0056988 | 0.0014282 | -0.0056985 | -0.0014282 | 2.9183e-07 | 5.147e-08 | 0.0085825 | 0.0085826 | 0.0085826 | 0.98805 | -0.22958 | 0.98799 | -0.23066 | 2.3579
93 | -0.038453 | -0.0096372 | 0.038503 | 0.009669 | 5.0508e-05 | 3.1828e-05 | 0.058417 | 0.058417 | 0.058417 | 0.97948 | -0.39522 | 0.98089 | -0.36768 | 16.0486
94 | 0.015757 | 0.0039508 | -0.015753 | -0.0039485 | 3.9166e-06 | 2.276e-06 | 0.023904 | 0.023904 | 0.023904 | 0.98089 | -0.36768 | 0.98062 | -0.3729 | 6.5672
95 | 0.01366 | 0.0034241 | -0.013659 | -0.0034234 | 1.2498e-06 | 7.0201e-07 | 0.020729 | 0.020729 | 0.020729 | 0.98062 | -0.3729 | 0.98052 | -0.37482 | 5.6948
96 | 0.0092321 | 0.0023138 | -0.0092314 | -0.0023135 | 6.9916e-07 | 3.2767e-07 | 0.01401 | 0.014011 | 0.014011 | 0.98052 | -0.37482 | 0.98044 | -0.37641 | 3.849
97 | 0.0050572 | 0.0012673 | -0.0050566 | -0.0012673 | 6.751e-07 | 4.6742e-08 | 0.0076753 | 0.0076755 | 0.0076755 | 0.98044 | -0.37641 | 0.9803 | -0.37921 | 2.1086
98 | 0.11783 | 0.030022 | -0.11777 | -0.029988 | 5.4342e-05 | 3.4244e-05 | 0.17719 | 0.17719 | 0.17719 | 0.99051 | -0.18035 | 0.99001 | -0.18991 | 16.226
99 | -0.11783 | -0.030022 | 0.11793 | 0.030084 | 9.8866e-05 | 6.23e-05 | 0.17719 | 0.17719 | 0.17719 | 0.99051 | -0.18035 | 0.99141 | -0.16297 | 16.226
100 | 0.10724 | 0.027347 | -0.10714 | -0.027288 | 9.2958e-05 | 5.8392e-05 | 0.16135 | 0.16135 | 0.16135 | 0.99001 | -0.18991 | 0.98907 | -0.20788 | 14.7757
101 | 0.010538 | 0.0026409 | -0.010536 | -0.0026401 | 1.6056e-06 | 8.0815e-07 | 0.015838 | 0.015838 | 0.015838 | 0.99001 | -0.18991 | 0.98984 | -0.19311 | 4.3512
102 | -0.1227 | -0.03128 | 0.12272 | 0.031291 | 1.6839e-05 | 1.0623e-05 | 0.18435 | 0.18435 | 0.18435 | 0.99141 | -0.16297 | 0.99156 | -0.16013 | 16.8817
103 | 0.10052 | 0.025627 | -0.10048 | -0.025604 | 3.6875e-05 | 2.3104e-05 | 0.15138 | 0.15138 | 0.15138 | 0.98907 | -0.20788 | 0.98867 | -0.21548 | 13.8626
104 | 0.0096956 | 0.0024295 | -0.0096951 | -0.0024292 | 4.8866e-07 | 2.339e-07 | 0.014575 | 0.014575 | 0.014575 | 0.98984 | -0.19311 | 0.98979 | -0.19417 | 4.0041
105 | 0.097252 | 0.024795 | -0.097065 | -0.024678 | 0.00018727 | 0.00011718 | 0.14652 | 0.14652 | 0.14652 | 0.98867 | -0.21548 | 0.9866 | -0.25545 | 13.4178
106 | 0.0030014 | 0.00075166 | -0.0030012 | -0.00075189 | 2.1527e-07 | -2.246e-07 | 0.004512 | 0.0045122 | 0.0045122 | 0.98979 | -0.19417 | 0.98971 | -0.19567 | 1.2396
107 | -0.028288 | -0.0070902 | 0.028341 | 0.0071227 | 5.2271e-05 | 3.2526e-05 | 0.04326 | 0.04326 | 0.04326 | 0.97304 | -0.52002 | 0.975 | -0.48131 | 11.8846
108 | 0.014958 | 0.0037494 | -0.014957 | -0.0037486 | 1.4467e-06 | 8.3433e-07 | 0.022875 | 0.022875 | 0.022875 | 0.97304 | -0.52002 | 0.97293 | -0.52205 | 6.2845
109 | -0.042975 | -0.01079 | 0.043032 | 0.010827 | 5.717e-05 | 3.6146e-05 | 0.065594 | 0.065594 | 0.065594 | 0.975 | -0.48131 | 0.97642 | -0.45346 | 18.0204
110 | -0.047394 | -0.01192 | 0.047406 | 0.011928 | 1.2455e-05 | 7.8915e-06 | 0.072241 | 0.072241 | 0.072241 | 0.97642 | -0.45346 | 0.9767 | -0.44796 | 19.8464
111 | -0.050616 | -0.012732 | 0.050668 | 0.012765 | 5.2808e-05 | 3.35e-05 | 0.077131 | 0.077131 | 0.077131 | 0.9767 | -0.44796 | 0.97781 | -0.42615 | 21.1897
112 | -0.054673 | -0.013769 | 0.054678 | 0.013772 | 4.5943e-06 | 2.9182e-06 | 0.083225 | 0.083225 | 0.083225 | 0.97781 | -0.42615 | 0.9779 | -0.42439 | 22.8641
113 | -0.057713 | -0.014533 | 0.05778 | 0.014576 | 6.7327e-05 | 4.2797e-05 | 0.087843 | 0.087843 | 0.087843 | 0.9779 | -0.42439 | 0.97914 | -0.40002 | 24.1328
114 | -0.0017097 | -0.00042849 | 0.0017098 | 0.00042822 | 5.9938e-08 | -2.7248e-07 | 0.0025706 | 0.0025705 | 0.0025706 | 0.98967 | -0.19641 | 0.98971 | -0.19567 | 0.70621
115 | 0.0092304 | 0.0023134 | -0.0092303 | -0.0023133 | 1.3474e-07 | 6.3946e-08 | 0.014133 | 0.014133 | 0.014133 | 0.97183 | -0.54397 | 0.97181 | -0.54428 | 3.8827

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57088 | 0.14624

## res_load
| p_mw | q_mvar
0 | 0.00040786 | 0.00010222
1 | 0.0017956 | 0.00045002
2 | 0.015968 | 0.0040019
3 | 0.0079651 | 0.0019962
4 | 0.0030783 | 0.00077149
5 | 0.0053236 | 0.0013342
6 | 0.01096 | 0.002747
7 | 0.0087361 | 0.0021895
8 | 0.0027937 | 0.00070017
9 | 0.019926 | 0.0049939
10 | 0.010729 | 0.002689
11 | 0.0042023 | 0.0010532
12 | 0.001464 | 0.00036692
13 | 0.010395 | 0.0026053
14 | 0.017444 | 0.0043718
15 | 0.0048677 | 0.00122
16 | 0.003448 | 0.00086416
17 | 0.0033015 | 0.00082743
18 | 0.0033501 | 0.00083961
19 | 0.0061803 | 0.0015489
20 | 0.010327 | 0.0025881
21 | 0.0052364 | 0.0013124
22 | 0.0071713 | 0.0017973
23 | 0.0033136 | 0.00083048
24 | 0.0026415 | 0.00066201
25 | 0.0021888 | 0.00054857
26 | 0.00094139 | 0.00023594
27 | 0.0095604 | 0.0023961
28 | 0.0016161 | 0.00040503
29 | 0.003665 | 0.00091854
30 | 0.0052208 | 0.0013085
31 | 0.0022859 | 0.0005729
32 | 0.003011 | 0.00075463
33 | 0.0035172 | 0.0008815
34 | 0.0085822 | 0.0021509
35 | 0.0059429 | 0.0014894
36 | 0.0067234 | 0.001685
37 | 0.014283 | 0.0035796
38 | 0.032679 | 0.0081901
39 | 0.0091686 | 0.0022979
40 | 0.0061951 | 0.0015526
41 | 0.0032351 | 0.00081079
42 | 0.0019522 | 0.00048927
43 | 0.0098384 | 0.0024657
44 | 0.0090784 | 0.0022753
45 | 0.0089575 | 0.002245
46 | 0.0051095 | 0.0012806
47 | 0.0068007 | 0.0017044
48 | 0.0053787 | 0.001348
49 | 0.0009883 | 0.00024769
50 | 0.0048003 | 0.0012031
51 | 0.0010839 | 0.00027166
52 | 0.0011667 | 0.0002924
53 | 0.00076613 | 0.00019201
54 | 0.0015757 | 0.0003949
55 | 0.0022506 | 0.00056404
56 | 0.0034978 | 0.00087662
57 | 0.0031477 | 0.00078889
58 | 0.0066344 | 0.0016627
59 | 0.0024829 | 0.00062228
60 | 0.00529 | 0.0013258
61 | 0.0024019 | 0.00060197
62 | 0.0016417 | 0.00041146
63 | 0.00067069 | 0.00016809
64 | 0.0064909 | 0.0016268
65 | 0.0058022 | 0.0014542
66 | 0.0054491 | 0.0013657
67 | 0.0046256 | 0.0011593
68 | 0.0056985 | 0.0014282
69 | 0.038453 | 0.0096372
70 | 0.0040911 | 0.0010253
71 | 0.0020927 | 0.00052449
72 | 0.0044271 | 0.0011095
73 | 0.0041742 | 0.0010462
74 | 0.0050566 | 0.0012673
75 | 0.0047711 | 0.0011957
76 | 0.0066277 | 0.0016611
77 | 0.00084036 | 0.00021061
78 | 0.0032275 | 0.00080889
79 | 0.0066936 | 0.0016776
80 | 0.01333 | 0.0033408
81 | 0.014634 | 0.0036677
82 | 0.014957 | 0.0037486
83 | 0.0043615 | 0.0010931
84 | 0.0032095 | 0.00080438
85 | 0.004005 | 0.0010038
86 | 0.0030349 | 0.00076061
87 | 0.0040711 | 0.0010203
88 | 0.0017097 | 0.00042849
89 | 0.0012915 | 0.00032367
90 | 0.0021959 | 0.00055033
91 | 0.0092303 | 0.0023133

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1