## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1710-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1710-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1710-8_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1710-8_0_4_node_33 | 0.4 | n |  | TRUE
4 | bus_LV_1710-8_0_4_node_34 | 0.4 | n |  | TRUE
5 | bus_LV_1710-8_0_4_node_32 | 0.4 | n |  | TRUE
6 | bus_LV_1710-8_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1710-8_0_4_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_1710-8_0_4_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_1710-8_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1710-8_0_4_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_1710-8_0_4_node_31 | 0.4 | n |  | TRUE
12 | bus_LV_1710-8_0_4_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_1710-8_0_4_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_1710-8_0_4_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_1710-8_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1710-8_0_4_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_1710-8_0_4_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_1710-8_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1710-8_0_4_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1710-8_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1710-8_0_4_node_7 | 0.4 | n |  | TRUE
22 | bus_LV_1710-8_0_4_node_8 | 0.4 | n |  | TRUE
23 | bus_LV_1710-8_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1710-8_0_4_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1710-8_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1710-8_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1710-8_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1710-8_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1710-8_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1710-8_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1710-8_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1710-8_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_1710-8_0_4_node_84 | 0.4 | n |  | TRUE
34 | bus_LV_1710-8_0_4_node_120 | 0.4 | n |  | TRUE
35 | bus_LV_1710-8_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_1710-8_0_4_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1710-8_0_4_node_85 | 0.4 | n |  | TRUE
38 | bus_LV_1710-8_0_4_node_83 | 0.4 | n |  | TRUE
39 | bus_LV_1710-8_0_4_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_1710-8_0_4_node_82 | 0.4 | n |  | TRUE
41 | bus_LV_1710-8_0_4_node_86 | 0.4 | n |  | TRUE
42 | bus_LV_1710-8_0_4_node_87 | 0.4 | n |  | TRUE
43 | bus_LV_1710-8_0_4_node_88 | 0.4 | n |  | TRUE
44 | bus_LV_1710-8_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_1710-8_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_1710-8_0_4_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_1710-8_0_4_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_1710-8_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_1710-8_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_1710-8_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_1710-8_0_4_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_1710-8_0_4_node_61 | 0.4 | n |  | TRUE
53 | bus_LV_1710-8_0_4_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_1710-8_0_4_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_1710-8_0_4_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_1710-8_0_4_node_46 | 0.4 | n |  | TRUE
57 | bus_LV_1710-8_0_4_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_1710-8_0_4_node_102 | 0.4 | n |  | TRUE
59 | bus_LV_1710-8_0_4_node_119 | 0.4 | n |  | TRUE
60 | bus_LV_1710-8_0_4_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_1710-8_0_4_node_118 | 0.4 | n |  | TRUE
62 | bus_LV_1710-8_0_4_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_1710-8_0_4_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_1710-8_0_4_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_1710-8_0_4_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_1710-8_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_1710-8_0_4_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_1710-8_0_4_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_1710-8_0_4_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_1710-8_0_4_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_1710-8_0_4_node_101 | 0.4 | n |  | TRUE
72 | bus_LV_1710-8_0_4_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_1710-8_0_4_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_1710-8_0_4_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_1710-8_0_4_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_1710-8_0_4_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_1710-8_0_4_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_1710-8_0_4_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_1710-8_0_4_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_1710-8_0_4_node_80 | 0.4 | n |  | TRUE
81 | bus_LV_1710-8_0_4_node_79 | 0.4 | n |  | TRUE
82 | bus_LV_1710-8_0_4_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_1710-8_0_4_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_1710-8_0_4_node_111 | 0.4 | n |  | TRUE
85 | bus_LV_1710-8_0_4_node_65 | 0.4 | n |  | TRUE
86 | bus_LV_1710-8_0_4_node_72 | 0.4 | n |  | TRUE
87 | bus_LV_1710-8_0_4_node_69 | 0.4 | n |  | TRUE
88 | bus_LV_1710-8_0_4_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_1710-8_0_4_node_73 | 0.4 | n |  | TRUE
90 | bus_LV_1710-8_0_4_node_74 | 0.4 | n |  | TRUE
91 | bus_LV_1710-8_0_4_node_75 | 0.4 | n |  | TRUE
92 | bus_LV_1710-8_0_4_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_1710-8_0_4_node_77 | 0.4 | n |  | TRUE
94 | bus_LV_1710-8_0_4_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_1710-8_0_4_node_96 | 0.4 | n |  | TRUE
96 | bus_LV_1710-8_0_4_node_89 | 0.4 | n |  | TRUE
97 | bus_LV_1710-8_0_4_node_90 | 0.4 | n |  | TRUE
98 | bus_LV_1710-8_0_4_node_91 | 0.4 | n |  | TRUE
99 | bus_LV_1710-8_0_4_node_92 | 0.4 | n |  | TRUE
100 | bus_LV_1710-8_0_4_node_100 | 0.4 | n |  | TRUE
101 | bus_LV_1710-8_0_4_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_1710-8_0_4_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_1710-8_0_4_node_95 | 0.4 | n |  | TRUE
104 | bus_LV_1710-8_0_4_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_1710-8_0_4_node_98 | 0.4 | n |  | TRUE
106 | bus_LV_1710-8_0_4_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_1710-8_0_4_node_112 | 0.4 | n |  | TRUE
108 | bus_LV_1710-8_0_4_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_1710-8_0_4_node_104 | 0.4 | n |  | TRUE
110 | bus_LV_1710-8_0_4_node_105 | 0.4 | n |  | TRUE
111 | bus_LV_1710-8_0_4_node_106 | 0.4 | n |  | TRUE
112 | bus_LV_1710-8_0_4_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_1710-8_0_4_node_107 | 0.4 | n |  | TRUE
114 | bus_LV_1710-8_0_4_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_1710-8_0_4_node_116 | 0.4 | n |  | TRUE
116 | bus_LV_1710-8_0_4_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_1710-8_0_4_node_114 | 0.4 | n |  | TRUE
118 | bus_LV_1710-8_0_4_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_1710-8_0_4_node_113 | 0.4 | n |  | TRUE
120 | bus_MV_1_0_node_54 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1710-8_0_4_load_0 | 0 | 0.0035344 | 0.00088581 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1710-8_0_4_load_33 | 3 | 0.01096 | 0.0027468 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1710-8_0_4_load_34 | 4 | 0.0038206 | 0.00095753 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1710-8_0_4_load_32 | 5 | 0.0064986 | 0.0016287 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1710-8_0_4_load_3 | 7 | 0.0072961 | 0.0018286 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1710-8_0_4_load_16 | 8 | 0.0036555 | 0.00091616 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1710-8_0_4_load_9 | 9 | 0.0018436 | 0.00046204 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1710-8_0_4_load_4 | 10 | 0.0052884 | 0.0013254 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1710-8_0_4_load_31 | 11 | 0.007309 | 0.0018318 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1710-8_0_4_load_29 | 12 | 0.0047447 | 0.0011891 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1710-8_0_4_load_5 | 13 | 0.0063183 | 0.0015835 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1710-8_0_4_load_10 | 15 | 0.0026162 | 0.00065569 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1710-8_0_4_load_30 | 16 | 0.011121 | 0.0027871 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1710-8_0_4_load_25 | 17 | 0.0078861 | 0.0019764 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1710-8_0_4_load_11 | 18 | 0.0060589 | 0.0015185 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1710-8_0_4_load_26 | 19 | 0.01121 | 0.0028094 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1710-8_0_4_load_17 | 20 | 0.0016226 | 0.00040666 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1710-8_0_4_load_7 | 21 | 0.0037315 | 0.00093521 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1710-8_0_4_load_8 | 22 | 0.0038215 | 0.00095775 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1710-8_0_4_load_12 | 23 | 0.0022534 | 0.00056474 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1710-8_0_4_load_14 | 25 | 0.0022594 | 0.00056625 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1710-8_0_4_load_15 | 26 | 0.0056794 | 0.0014234 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1710-8_0_4_load_18 | 27 | 0.0012824 | 0.0003214 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1710-8_0_4_load_20 | 28 | 0.0059282 | 0.0014857 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1710-8_0_4_load_21 | 30 | 0.0045556 | 0.0011418 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1710-8_0_4_load_24 | 31 | 0.0022373 | 0.00056072 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1710-8_0_4_load_23 | 32 | 0.00069235 | 0.00017352 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1710-8_0_4_load_120 | 34 | 0.0050796 | 0.0012731 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1710-8_0_4_load_28 | 35 | 0.0072049 | 0.0018057 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1710-8_0_4_load_22 | 36 | 0.011612 | 0.0029101 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1710-8_0_4_load_85 | 37 | 0.014178 | 0.0035532 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1710-8_0_4_load_83 | 38 | 0.0055276 | 0.0013853 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1710-8_0_4_load_40 | 39 | 0.0099406 | 0.0024913 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1710-8_0_4_load_82 | 40 | 0.0030969 | 0.00077615 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1710-8_0_4_load_86 | 41 | 0.0055317 | 0.0013864 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1710-8_0_4_load_87 | 42 | 0.00076911 | 0.00019276 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1710-8_0_4_load_88 | 43 | 0.0096802 | 0.0024261 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1710-8_0_4_load_41 | 44 | 0.0066618 | 0.0016696 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1710-8_0_4_load_35 | 45 | 0.0052967 | 0.0013275 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1710-8_0_4_load_36 | 46 | 0.009975 | 0.0025 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1710-8_0_4_load_37 | 47 | 0.003804 | 0.00095338 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1710-8_0_4_load_42 | 50 | 0.0015876 | 0.00039789 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1710-8_0_4_load_61 | 52 | 0.012377 | 0.003102 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1710-8_0_4_load_59 | 53 | 0.0021804 | 0.00054646 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1710-8_0_4_load_45 | 55 | 0.0018068 | 0.00045282 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1710-8_0_4_load_46 | 56 | 0.0048646 | 0.0012192 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1710-8_0_4_load_102 | 58 | 0.0051829 | 0.001299 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1710-8_0_4_load_119 | 59 | 0.0061125 | 0.0015319 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1710-8_0_4_load_52 | 60 | 0.0076522 | 0.0019178 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1710-8_0_4_load_48 | 62 | 0.0026724 | 0.00066977 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1710-8_0_4_load_49 | 63 | 0.0026409 | 0.00066188 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1710-8_0_4_load_50 | 64 | 0.0027577 | 0.00069116 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1710-8_0_4_load_51 | 65 | 0.0021202 | 0.00053138 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1710-8_0_4_load_53 | 66 | 0.0027456 | 0.00068811 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1710-8_0_4_load_55 | 68 | 0.0028862 | 0.00072335 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1710-8_0_4_load_56 | 69 | 0.003681 | 0.00092254 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1710-8_0_4_load_57 | 70 | 0.0019883 | 0.00049831 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1710-8_0_4_load_101 | 71 | 0.0027083 | 0.00067877 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1710-8_0_4_load_58 | 72 | 0.002049 | 0.00051352 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1710-8_0_4_load_60 | 73 | 0.0050286 | 0.0012603 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1710-8_0_4_load_62 | 74 | 0.0027341 | 0.00068523 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1710-8_0_4_load_67 | 76 | 0.040218 | 0.01008 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1710-8_0_4_load_70 | 78 | 0.0044322 | 0.0011108 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1710-8_0_4_load_80 | 80 | 0.0017014 | 0.00042642 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1710-8_0_4_load_79 | 81 | 0.0056631 | 0.0014193 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1710-8_0_4_load_66 | 82 | 0.0024271 | 0.00060829 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1710-8_0_4_load_64 | 83 | 0.002125 | 0.00053259 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1710-8_0_4_load_111 | 84 | 0.00218 | 0.00054636 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1710-8_0_4_load_65 | 85 | 0.001868 | 0.00046817 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1710-8_0_4_load_72 | 86 | 0.004318 | 0.0010822 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1710-8_0_4_load_69 | 87 | 0.0037384 | 0.00093694 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1710-8_0_4_load_71 | 88 | 0.0024524 | 0.00061463 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1710-8_0_4_load_73 | 89 | 0.0016043 | 0.00040208 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1710-8_0_4_load_74 | 90 | 0.001317 | 0.00033007 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1710-8_0_4_load_75 | 91 | 0.0011667 | 0.00029241 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1710-8_0_4_load_76 | 92 | 0.0047776 | 0.0011974 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1710-8_0_4_load_78 | 94 | 0.0039648 | 0.00099367 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1710-8_0_4_load_96 | 95 | 0.0046474 | 0.0011648 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1710-8_0_4_load_90 | 97 | 0.0028065 | 0.00070339 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1710-8_0_4_load_91 | 98 | 0.0026467 | 0.00066333 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1710-8_0_4_load_92 | 99 | 0.0058907 | 0.0014764 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1710-8_0_4_load_100 | 100 | 0.0013907 | 0.00034855 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1710-8_0_4_load_93 | 101 | 0.0050197 | 0.0012581 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1710-8_0_4_load_94 | 102 | 0.0053167 | 0.0013325 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1710-8_0_4_load_95 | 103 | 0.0052559 | 0.0013172 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1710-8_0_4_load_97 | 104 | 0.0052601 | 0.0013183 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1710-8_0_4_load_98 | 105 | 0.0086823 | 0.002176 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1710-8_0_4_load_99 | 106 | 0.0018925 | 0.00047432 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1710-8_0_4_load_112 | 107 | 0.0025434 | 0.00063745 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1710-8_0_4_load_103 | 108 | 0.0077031 | 0.0019306 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1710-8_0_4_load_104 | 109 | 0.0045445 | 0.001139 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1710-8_0_4_load_105 | 110 | 0.0078205 | 0.00196 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1710-8_0_4_load_106 | 111 | 0.0031212 | 0.00078226 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1710-8_0_4_load_108 | 112 | 0.0043432 | 0.0010885 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1710-8_0_4_load_107 | 113 | 0.013124 | 0.0032893 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1710-8_0_4_load_109 | 114 | 0.003458 | 0.00086665 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1710-8_0_4_load_116 | 115 | 0.0035128 | 0.00088039 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1710-8_0_4_load_110 | 116 | 0.0026261 | 0.00065817 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1710-8_0_4_load_115 | 118 | 0.0068918 | 0.0017272 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1710-8_0_4_load_113 | 119 | 0.0046226 | 0.0011585 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 73 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1710-8_0_4_line_0 |  | 0 | 1 | 0.01301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1710-8_0_4_line_1 |  | 1 | 2 | 0.022527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1710-8_0_4_line_2 |  | 2 | 6 | 0.033899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1710-8_0_4_line_3 |  | 2 | 7 | 0.022217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1710-8_0_4_line_4 |  | 3 | 4 | 0.023244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1710-8_0_4_line_5 |  | 3 | 5 | 0.00074239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1710-8_0_4_line_6 |  | 5 | 11 | 0.024957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1710-8_0_4_line_7 |  | 6 | 8 | 0.012822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1710-8_0_4_line_8 |  | 6 | 9 | 0.011665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1710-8_0_4_line_9 |  | 7 | 10 | 0.0078557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1710-8_0_4_line_10 |  | 8 | 20 | 0.017321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1710-8_0_4_line_11 |  | 9 | 21 | 0.019012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1710-8_0_4_line_12 |  | 9 | 11 | 0.053247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1710-8_0_4_line_13 |  | 10 | 13 | 0.030297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1710-8_0_4_line_14 |  | 11 | 12 | 0.0058021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1710-8_0_4_line_15 |  | 12 | 14 | 0.02523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1710-8_0_4_line_16 |  | 13 | 15 | 0.0038835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1710-8_0_4_line_17 |  | 14 | 16 | 0.027509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1710-8_0_4_line_18 |  | 14 | 17 | 0.0025426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1710-8_0_4_line_19 |  | 15 | 18 | 0.020541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1710-8_0_4_line_20 |  | 16 | 39 | 0.024322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1710-8_0_4_line_21 |  | 17 | 19 | 0.016371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1710-8_0_4_line_22 |  | 18 | 23 | 0.0096629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1710-8_0_4_line_23 |  | 19 | 35 | 0.01362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1710-8_0_4_line_24 |  | 21 | 22 | 0.00066786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1710-8_0_4_line_25 |  | 23 | 24 | 0.02255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1710-8_0_4_line_26 |  | 24 | 25 | 0.0095699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1710-8_0_4_line_27 |  | 24 | 26 | 0.0064064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1710-8_0_4_line_28 |  | 25 | 27 | 0.025015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1710-8_0_4_line_29 |  | 26 | 28 | 0.013418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1710-8_0_4_line_30 |  | 27 | 29 | 0.020017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1710-8_0_4_line_31 |  | 28 | 30 | 0.020601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1710-8_0_4_line_32 |  | 29 | 31 | 0.054551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1710-8_0_4_line_33 |  | 30 | 36 | 0.011896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1710-8_0_4_line_34 |  | 31 | 34 | 0.018438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1710-8_0_4_line_35 |  | 32 | 33 | 0.018564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1710-8_0_4_line_36 |  | 33 | 37 | 0.026382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1710-8_0_4_line_37 |  | 33 | 38 | 0.018072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1710-8_0_4_line_38 |  | 37 | 41 | 0.055717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1710-8_0_4_line_39 |  | 38 | 40 | 0.022394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1710-8_0_4_line_40 |  | 39 | 44 | 0.015899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1710-8_0_4_line_41 |  | 40 | 79 | 0.0038479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1710-8_0_4_line_42 |  | 41 | 42 | 0.040622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1710-8_0_4_line_43 |  | 42 | 43 | 0.018576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1710-8_0_4_line_44 |  | 44 | 52 | 0.030971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1710-8_0_4_line_45 |  | 45 | 46 | 0.011648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1710-8_0_4_line_46 |  | 45 | 47 | 0.0085093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1710-8_0_4_line_47 |  | 46 | 48 | 0.039888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1710-8_0_4_line_48 |  | 48 | 49 | 0.017071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1710-8_0_4_line_49 |  | 49 | 50 | 0.028757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1710-8_0_4_line_50 |  | 50 | 51 | 0.014852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1710-8_0_4_line_51 |  | 51 | 54 | 0.015425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1710-8_0_4_line_52 |  | 52 | 53 | 0.027016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1710-8_0_4_line_53 |  | 53 | 73 | 0.0020271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1710-8_0_4_line_54 |  | 53 | 68 | 0.046192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1710-8_0_4_line_55 |  | 54 | 55 | 0.014118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1710-8_0_4_line_56 |  | 55 | 56 | 0.041982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1710-8_0_4_line_57 |  | 56 | 57 | 0.033363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1710-8_0_4_line_58 |  | 57 | 58 | 0.019746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1710-8_0_4_line_59 |  | 57 | 59 | 0.039346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1710-8_0_4_line_60 |  | 58 | 60 | 0.017068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1710-8_0_4_line_61 |  | 59 | 61 | 0.021233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1710-8_0_4_line_62 |  | 60 | 64 | 0.036089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1710-8_0_4_line_63 |  | 61 | 113 | 0.01421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1710-8_0_4_line_64 |  | 62 | 63 | 0.013329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1710-8_0_4_line_65 |  | 62 | 64 | 0.017729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1710-8_0_4_line_66 |  | 63 | 65 | 0.0059361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1710-8_0_4_line_67 |  | 65 | 66 | 0.0058112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1710-8_0_4_line_68 |  | 66 | 67 | 0.014772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1710-8_0_4_line_69 |  | 67 | 68 | 0.02746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1710-8_0_4_line_70 |  | 67 | 69 | 0.020654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1710-8_0_4_line_71 |  | 68 | 70 | 0.023775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_1710-8_0_4_line_72 |  | 69 | 71 | 0.035887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1710-8_0_4_line_73 |  | 70 | 72 | 0.019029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_1710-8_0_4_line_74 |  | 72 | 74 | 0.013548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_1710-8_0_4_line_75 |  | 74 | 75 | 0.026387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_1710-8_0_4_line_76 |  | 75 | 82 | 0.012115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1710-8_0_4_line_77 |  | 75 | 83 | 0.021516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_1710-8_0_4_line_78 |  | 76 | 77 | 0.034559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1710-8_0_4_line_79 |  | 77 | 87 | 0.017824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_1710-8_0_4_line_80 |  | 77 | 78 | 0.040149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_1710-8_0_4_line_81 |  | 78 | 79 | 0.0089605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_1710-8_0_4_line_82 |  | 79 | 80 | 0.0071312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_1710-8_0_4_line_83 |  | 80 | 81 | 0.032609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1710-8_0_4_line_84 |  | 81 | 94 | 0.022073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1710-8_0_4_line_85 |  | 82 | 84 | 0.0013816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1710-8_0_4_line_86 |  | 83 | 85 | 0.0060364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_1710-8_0_4_line_87 |  | 84 | 107 | 0.022577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1710-8_0_4_line_88 |  | 85 | 86 | 0.055493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_1710-8_0_4_line_89 |  | 86 | 89 | 0.015111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1710-8_0_4_line_90 |  | 86 | 88 | 0.036549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_1710-8_0_4_line_91 |  | 87 | 88 | 0.011087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_1710-8_0_4_line_92 |  | 90 | 91 | 0.021079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1710-8_0_4_line_93 |  | 90 | 92 | 0.0037933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1710-8_0_4_line_94 |  | 91 | 93 | 0.049087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1710-8_0_4_line_95 |  | 92 | 94 | 0.027042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1710-8_0_4_line_96 |  | 93 | 95 | 0.049439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1710-8_0_4_line_97 |  | 95 | 103 | 0.0037059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1710-8_0_4_line_98 |  | 96 | 97 | 0.019326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1710-8_0_4_line_99 |  | 96 | 98 | 0.0096752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1710-8_0_4_line_100 |  | 97 | 99 | 0.01439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1710-8_0_4_line_101 |  | 98 | 100 | 0.014371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1710-8_0_4_line_102 |  | 99 | 101 | 0.022977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1710-8_0_4_line_103 |  | 100 | 106 | 0.030473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1710-8_0_4_line_104 |  | 101 | 102 | 0.0044569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1710-8_0_4_line_105 |  | 102 | 103 | 0.024354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1710-8_0_4_line_106 |  | 104 | 105 | 0.0076329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1710-8_0_4_line_107 |  | 104 | 106 | 0.05813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1710-8_0_4_line_108 |  | 107 | 119 | 0.006812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1710-8_0_4_line_109 |  | 108 | 109 | 0.02604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1710-8_0_4_line_110 |  | 108 | 110 | 0.0016769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1710-8_0_4_line_111 |  | 109 | 111 | 0.0030123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1710-8_0_4_line_112 |  | 111 | 112 | 0.010397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1710-8_0_4_line_113 |  | 112 | 114 | 0.012555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1710-8_0_4_line_114 |  | 112 | 115 | 0.044335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1710-8_0_4_line_115 |  | 114 | 116 | 0.023228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1710-8_0_4_line_116 |  | 116 | 117 | 0.010893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1710-8_0_4_line_117 |  | 117 | 118 | 0.0063669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1710-8_0_4_line_118 |  | 117 | 119 | 0.019235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1710-8_0_4_trafo_60 | 0.63 MVA 20/0.4 kV | 120 | 73 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2681785.1179 | 1217438.0132 | 2681783.5286 | 1217445.941 | 2681782.2429 | 1217450.5598 | 2681782.1497 | 1217450.6503
1 | 2681785.1179 | 1217438.0132 | 2681806.916 | 1217443.9384
2 | 2681832.5835 | 1217422.9658 | 2681827.4793 | 1217430.3339 | 2681820.9017 | 1217436.0808 | 2681813.2948 | 1217438.8449 | 2681806.916 | 1217443.9384
3 | 2681806.916 | 1217443.9384 | 2681814.5247 | 1217447.1339 | 2681820.1098 | 1217450.624 | 2681826.1172 | 1217454.909
4 | 2681814.9167 | 1217359.1677 | 2681792.5848 | 1217352.7218
5 | 2681814.9167 | 1217359.1677 | 2681815.63 | 1217359.3735
6 | 2681815.63 | 1217359.3735 | 2681821.2348 | 1217360.9913 | 2681839.4246 | 1217366.8921
7 | 2681832.5835 | 1217422.9658 | 2681844.3924 | 1217427.9616
8 | 2681832.5835 | 1217422.9658 | 2681822.3687 | 1217417.3332
9 | 2681826.1172 | 1217454.909 | 2681832.5126 | 1217459.4709
10 | 2681860.3448 | 1217434.7103 | 2681844.3924 | 1217427.9616
11 | 2681822.3687 | 1217417.3332 | 2681820.5279 | 1217416.3181 | 2681803.9525 | 1217412.9695
12 | 2681839.4246 | 1217366.8921 | 2681822.3687 | 1217417.3332
13 | 2681832.5126 | 1217459.4709 | 2681857.1776 | 1217477.0643
14 | 2681844.9435 | 1217368.6825 | 2681839.4246 | 1217366.8921
15 | 2681868.942 | 1217376.4677 | 2681844.9435 | 1217368.6825
16 | 2681860.3392 | 1217479.3195 | 2681857.1776 | 1217477.0643
17 | 2681868.942 | 1217376.4677 | 2681871.1244 | 1217371.2387 | 2681866.3216 | 1217349.9304
18 | 2681868.942 | 1217376.4677 | 2681871.361 | 1217377.2508
19 | 2681877.5102 | 1217490.4608 | 2681877.5102 | 1217490.4608 | 2681873.4505 | 1217488.6705 | 2681867.6315 | 1217484.5211 | 2681860.3392 | 1217479.3195
20 | 2681865.7075 | 1217325.7523 | 2681865.1138 | 1217344.5718 | 2681866.3216 | 1217349.9304
21 | 2681871.361 | 1217377.2508 | 2681873.031 | 1217377.7914 | 2681883.7117 | 1217367.8148
22 | 2681887.0871 | 1217491.6358 | 2681882.3344 | 1217491.3165 | 2681877.5102 | 1217490.4608
23 | 2681893.665 | 1217358.5177 | 2681883.7117 | 1217367.8148
24 | 2681803.2978 | 1217412.8372 | 2681803.9525 | 1217412.9695
25 | 2681909.5863 | 1217493.1477 | 2681887.0871 | 1217491.6358
26 | 2681909.5863 | 1217493.1477 | 2681919.1349 | 1217493.7844
27 | 2681909.5863 | 1217493.1477 | 2681913.9554 | 1217497.8331 | 2681913.9554 | 1217497.8331
28 | 2681919.1349 | 1217493.7844 | 2681922.8217 | 1217494.0302 | 2681927.29 | 1217493.1577 | 2681930.1176 | 1217492.3516 | 2681932.8644 | 1217490.7994 | 2681935.5934 | 1217488.3353 | 2681937.5004 | 1217484.9148 | 2681938.7047 | 1217482.0807
29 | 2681913.9554 | 1217497.8331 | 2681922.8896 | 1217499.5792 | 2681927.1238 | 1217500.4068
30 | 2681948.1948 | 1217464.6707 | 2681947.2802 | 1217465.4808 | 2681944.4367 | 1217469.0997 | 2681942.404 | 1217473.3746 | 2681938.7047 | 1217482.0807
31 | 2681927.1238 | 1217500.4068 | 2681931.8238 | 1217501.3254 | 2681941.1454 | 1217504.7113 | 2681943.7143 | 1217510.0168
32 | 2681948.1948 | 1217464.6707 | 2681946.0162 | 1217460.2378 | 2681935.3336 | 1217422.7773 | 2681933.9431 | 1217420.6568 | 2681931.8011 | 1217419.6377 | 2681929.053 | 1217420.1781 | 2681926.9894 | 1217422.2845
33 | 2681942.3221 | 1217521.8166 | 2681943.2198 | 1217516.7145 | 2681943.7143 | 1217510.0168
34 | 2681917.6229 | 1217438.1662 | 2681926.9894 | 1217422.2845
35 | 2682008.849 | 1217429.1147 | 2682003.1799 | 1217438.8987 | 2682000.0007 | 1217443.736 | 2681998.9581 | 1217444.7692
36 | 2682008.849 | 1217429.1147 | 2682014.5842 | 1217432.7294 | 2682017.4938 | 1217436.4496 | 2682017.036 | 1217444.3374 | 2682018.0885 | 1217448.9439 | 2682020.0651 | 1217450.0269
37 | 2682008.849 | 1217429.1147 | 2682015.1294 | 1217412.1695
38 | 2682038.712 | 1217468.3125 | 2682043.1995 | 1217460.7083 | 2682047.2706 | 1217452.3033 | 2682046.8621 | 1217446.138 | 2682041.7042 | 1217443.0539 | 2682035.9599 | 1217443.4084 | 2682031.3364 | 1217449.4821 | 2682026.9832 | 1217451.3567 | 2682022.293 | 1217451.2477 | 2682020.0651 | 1217450.0269
39 | 2682015.1294 | 1217412.1695 | 2682016.1345 | 1217409.4575 | 2682018.9116 | 1217395.7867 | 2682019.1763 | 1217390.2413
40 | 2681865.7075 | 1217325.7523 | 2681865.7999 | 1217322.8224 | 2681868.0126 | 1217316.4931 | 2681870.6019 | 1217310.9361 | 2681870.6819 | 1217310.8315
41 | 2682019.3597 | 1217386.3978 | 2682019.1763 | 1217390.2413
42 | 2682041.435 | 1217503.9349 | 2682035.9313 | 1217500.0565 | 2682032.3972 | 1217489.8678 | 2682033.1177 | 1217477.792 | 2682038.712 | 1217468.3125
43 | 2682041.435 | 1217503.9349 | 2682041.435 | 1217503.9349 | 2682047.9345 | 1217503.3128 | 2682052.1797 | 1217498.8016 | 2682055.3378 | 1217493.8741
44 | 2681870.6819 | 1217310.8315 | 2681901.1253 | 1217305.1405
45 | 2681814.5137 | 1217290.1254 | 2681806.6481 | 1217298.7166
46 | 2681820.2597 | 1217283.8492 | 2681814.5137 | 1217290.1254
47 | 2681771.58 | 1217283.2919 | 2681775.2401 | 1217288.7679 | 2681780.2557 | 1217292.2835 | 2681793.4614 | 1217295.9116 | 2681806.6481 | 1217298.7166 | 2681806.6481 | 1217298.7166
48 | 2681784.0169 | 1217271.5881 | 2681779.0179 | 1217276.823 | 2681771.58 | 1217283.2919
49 | 2681784.0169 | 1217271.5881 | 2681787.6642 | 1217265.8344 | 2681790.1816 | 1217260.5321 | 2681791.4415 | 1217256.1353 | 2681793.7922 | 1217244.8768
50 | 2681796.9277 | 1217230.3603 | 2681795.2447 | 1217237.9199 | 2681793.7922 | 1217244.8768
51 | 2681796.9277 | 1217230.3603 | 2681799.1884 | 1217223.2977 | 2681802.583 | 1217216.0395
52 | 2681901.1253 | 1217305.1405 | 2681905.1685 | 1217304.8292 | 2681913.8106 | 1217305.7596 | 2681928.0728 | 1217306.1949
53 | 2681928.0728 | 1217306.1949 | 2681930.0989 | 1217306.2567
54 | 2681904.8035 | 1217266.2925 | 2681928.0728 | 1217306.1949
55 | 2681802.583 | 1217216.0395 | 2681810.372 | 1217216.6246 | 2681815.0825 | 1217212.4299
56 | 2681815.0825 | 1217212.4299 | 2681846.4351 | 1217184.5099
57 | 2681869.3699 | 1217160.2863 | 2681847.4191 | 1217183.6336 | 2681846.4351 | 1217184.5099
58 | 2681869.3699 | 1217160.2863 | 2681879.7131 | 1217157.8824 | 2681886.8319 | 1217163.595
59 | 2681869.3699 | 1217160.2863 | 2681875.8667 | 1217144.9766 | 2681881.5451 | 1217133.4136 | 2681881.7883 | 1217130.0814 | 2681883.139 | 1217127.3759 | 2681885.0056 | 1217124.4533
60 | 2681886.8319 | 1217163.595 | 2681889.7989 | 1217174.7543 | 2681889.2965 | 1217180.2522
61 | 2681896.6957 | 1217107.7047 | 2681893.9121 | 1217109.1675 | 2681890.9494 | 1217112.0509 | 2681889.9671 | 1217116.6849 | 2681885.0056 | 1217124.4533
62 | 2681871.4253 | 1217210.5194 | 2681882.4258 | 1217198.035 | 2681888.6908 | 1217186.8804 | 2681889.2965 | 1217180.2522
63 | 2681896.6957 | 1217107.7047 | 2681896.6737 | 1217109.3055 | 2681897.2179 | 1217110.5916 | 2681901.3628 | 1217115.0404 | 2681904.0664 | 1217119.4026 | 2681904.0664 | 1217119.4026
64 | 2681861.3313 | 1217224.8185 | 2681861.3313 | 1217224.8185 | 2681860.8064 | 1217231.5269 | 2681861.5438 | 1217238.0858
65 | 2681861.3313 | 1217224.8185 | 2681863.3762 | 1217219.6543 | 2681871.4253 | 1217210.5194
66 | 2681861.5438 | 1217238.0858 | 2681861.5438 | 1217238.0858 | 2681864.2179 | 1217243.3854
67 | 2681867.3317 | 1217248.229 | 2681865.8599 | 1217246.6396 | 2681864.2179 | 1217243.3854
68 | 2681879.328 | 1217256.0419 | 2681872.3983 | 1217253.7007 | 2681867.3317 | 1217248.229
69 | 2681879.328 | 1217256.0419 | 2681904.8035 | 1217266.2925
70 | 2681879.328 | 1217256.0419 | 2681891.6641 | 1217239.4763
71 | 2681904.8035 | 1217266.2925 | 2681909.7404 | 1217268.2789 | 2681918.4984 | 1217265.1973 | 2681923.1361 | 1217257.2879
72 | 2681891.6641 | 1217239.4763 | 2681913.0984 | 1217210.693
73 | 2681923.1361 | 1217257.2879 | 2681932.7612 | 1217240.8727
74 | 2681932.7612 | 1217240.8727 | 2681939.6137 | 1217229.1859
75 | 2681962.2744 | 1217236.4801 | 2681958.9946 | 1217233.722 | 2681948.4815 | 1217226.406 | 2681939.6137 | 1217229.1859
76 | 2681962.2744 | 1217236.4801 | 2681970.7753 | 1217227.8479
77 | 2681962.2744 | 1217236.4801 | 2681978.7615 | 1217250.3038
78 | 2682022.7724 | 1217340.3476 | 2682013.3168 | 1217340.6177 | 2682010.9936 | 1217339.5183 | 2681990.6347 | 1217329.8691
79 | 2682022.7724 | 1217340.3476 | 2682022.8521 | 1217334.0112 | 2682021.3051 | 1217322.6283
80 | 2682022.7724 | 1217340.3476 | 2682022.7063 | 1217345.1499 | 2682014.1489 | 1217367.3023 | 2682013.8448 | 1217376.7044 | 2682014.9287 | 1217378.6095
81 | 2682019.3597 | 1217386.3978 | 2682014.9287 | 1217378.6095
82 | 2682019.3597 | 1217386.3978 | 2682019.5099 | 1217379.2682
83 | 2682028.1529 | 1217348.3677 | 2682027.462 | 1217349.3292 | 2682024.1633 | 1217355.121 | 2682022.037 | 1217361.2291 | 2682020.9011 | 1217365.4273 | 2682019.8832 | 1217370.9837 | 2682019.5789 | 1217375.9939 | 2682019.5099 | 1217379.2682
84 | 2682028.1529 | 1217348.3677 | 2682031.7656 | 1217343.34 | 2682039.7658 | 1217329.6204
85 | 2681970.7753 | 1217227.8479 | 2681971.7448 | 1217226.8635
86 | 2681983.3872 | 1217254.1821 | 2681978.7615 | 1217250.3038
87 | 2681971.7448 | 1217226.8635 | 2681987.5863 | 1217210.7775
88 | 2681983.3872 | 1217254.1821 | 2682033.8451 | 1217277.2789
89 | 2682033.8451 | 1217277.2789 | 2682034.5947 | 1217275.1783 | 2682041.0797 | 1217264.0491
90 | 2682033.8451 | 1217277.2789 | 2682026.8007 | 1217297.0188 | 2682021.9558 | 1217311.8365
91 | 2682021.3051 | 1217322.6283 | 2682020.4601 | 1217316.4111 | 2682021.9558 | 1217311.8365
92 | 2682055.2987 | 1217302.9829 | 2682062.0206 | 1217291.4555 | 2682064.6905 | 1217288.3235 | 2682067.2264 | 1217285.7415
93 | 2682055.2987 | 1217302.9829 | 2682053.3879 | 1217306.2598
94 | 2682114.1044 | 1217277.4858 | 2682107.4174 | 1217278.4721 | 2682092.7207 | 1217278.3696 | 2682085.0331 | 1217278.1413 | 2682080.844 | 1217278.5728 | 2682076.6012 | 1217279.5929 | 2682073.2053 | 1217280.858 | 2682070.1698 | 1217282.9732 | 2682067.3624 | 1217285.603 | 2682067.2264 | 1217285.7415
95 | 2682053.3879 | 1217306.2598 | 2682039.7658 | 1217329.6204
96 | 2682114.1044 | 1217277.4858 | 2682139.8526 | 1217319.6908
97 | 2682139.8526 | 1217319.6908 | 2682137.232 | 1217322.3112
98 | 2682106.3705 | 1217384.7168 | 2682099.2646 | 1217374.7902 | 2682097.6049 | 1217367.8678
99 | 2682106.3705 | 1217384.7168 | 2682112.9049 | 1217377.5816
100 | 2682099.0522 | 1217353.9142 | 2682098.2362 | 1217355.2186 | 2682096.8094 | 1217364.5496 | 2682097.6049 | 1217367.8678
101 | 2682122.6109 | 1217366.9834 | 2682112.9049 | 1217377.5816
102 | 2682099.0522 | 1217353.9142 | 2682109.2984 | 1217337.5371 | 2682112.4883 | 1217335.7458
103 | 2682122.6109 | 1217366.9834 | 2682124.6613 | 1217364.7445 | 2682136.0098 | 1217353.8381 | 2682143.5521 | 1217351.9297 | 2682147.3958 | 1217352.6851
104 | 2682112.4883 | 1217335.7458 | 2682116.3744 | 1217333.5635
105 | 2682137.232 | 1217322.3112 | 2682130.9139 | 1217328.629 | 2682119.0383 | 1217332.0676 | 2682116.3744 | 1217333.5635
106 | 2682152.7619 | 1217400.5891 | 2682147.1778 | 1217405.793
107 | 2682152.7619 | 1217400.5891 | 2682157.0417 | 1217396.6007 | 2682161.6242 | 1217386.3571 | 2682161.8505 | 1217370.5053 | 2682159.4171 | 1217360.3317 | 2682152.191 | 1217353.6276 | 2682147.3958 | 1217352.6851
108 | 2681992.3661 | 1217205.924 | 2681987.5863 | 1217210.7775
109 | 2681929.3937 | 1217155.3118 | 2681933.0153 | 1217158.6041 | 2681941.2919 | 1217161.8312 | 2681943.6855 | 1217162.231 | 2681948.5405 | 1217165.2775 | 2681951.5361 | 1217168.0823
110 | 2681928.1529 | 1217154.1838 | 2681929.3937 | 1217155.3118
111 | 2681953.7349 | 1217170.1411 | 2681953.7349 | 1217170.1411 | 2681951.5361 | 1217168.0823
112 | 2681953.7349 | 1217170.1411 | 2681958.4257 | 1217173.5411 | 2681962.8098 | 1217174.9468 | 2681962.8098 | 1217174.9468
113 | 2681962.8098 | 1217174.9468 | 2681966.7131 | 1217175.423 | 2681970.2235 | 1217178.5289 | 2681973.9678 | 1217179.74
114 | 2681962.8098 | 1217174.9468 | 2681981.0355 | 1217134.5311
115 | 2681996.3296 | 1217184.8661 | 2681990.7574 | 1217182.0469 | 2681985.1116 | 1217181.291 | 2681975.8244 | 1217180.3404 | 2681973.9678 | 1217179.74
116 | 2682004.9612 | 1217191.493 | 2681996.8343 | 1217185.1215 | 2681996.3296 | 1217184.8661
117 | 2682004.9612 | 1217191.493 | 2682007.1849 | 1217194.8592 | 2682007.9211 | 1217197.0725
118 | 2682004.9612 | 1217191.493 | 2682003.7152 | 1217193.7663 | 2682001.5788 | 1217196.194 | 2681999.7718 | 1217198.404 | 2681992.3661 | 1217205.924

## bus_geodata
| x | y | coords
0 | 2681782.1497 | 1217450.6503
1 | 2681785.1179 | 1217438.0132
2 | 2681806.916 | 1217443.9384
3 | 2681814.9167 | 1217359.1677
4 | 2681792.5848 | 1217352.7218
5 | 2681815.63 | 1217359.3735
6 | 2681832.5835 | 1217422.9658
7 | 2681826.1172 | 1217454.909
8 | 2681844.3924 | 1217427.9616
9 | 2681822.3687 | 1217417.3332
10 | 2681832.5126 | 1217459.4709
11 | 2681839.4246 | 1217366.8921
12 | 2681844.9435 | 1217368.6825
13 | 2681857.1776 | 1217477.0643
14 | 2681868.942 | 1217376.4677
15 | 2681860.3392 | 1217479.3195
16 | 2681866.3216 | 1217349.9304
17 | 2681871.361 | 1217377.2508
18 | 2681877.5102 | 1217490.4608
19 | 2681883.7117 | 1217367.8148
20 | 2681860.3448 | 1217434.7103
21 | 2681803.9525 | 1217412.9695
22 | 2681803.2978 | 1217412.8372
23 | 2681887.0871 | 1217491.6358
24 | 2681909.5863 | 1217493.1477
25 | 2681919.1349 | 1217493.7844
26 | 2681913.9554 | 1217497.8331
27 | 2681938.7047 | 1217482.0807
28 | 2681927.1238 | 1217500.4068
29 | 2681948.1948 | 1217464.6707
30 | 2681943.7143 | 1217510.0168
31 | 2681926.9894 | 1217422.2845
32 | 2681998.9581 | 1217444.7692
33 | 2682008.849 | 1217429.1147
34 | 2681917.6229 | 1217438.1662
35 | 2681893.665 | 1217358.5177
36 | 2681942.3221 | 1217521.8166
37 | 2682020.0651 | 1217450.0269
38 | 2682015.1294 | 1217412.1695
39 | 2681865.7075 | 1217325.7523
40 | 2682019.1763 | 1217390.2413
41 | 2682038.712 | 1217468.3125
42 | 2682041.435 | 1217503.9349
43 | 2682055.3378 | 1217493.8741
44 | 2681870.6819 | 1217310.8315
45 | 2681814.5136 | 1217290.1254
46 | 2681806.6481 | 1217298.7166
47 | 2681820.2597 | 1217283.8492
48 | 2681771.58 | 1217283.2919
49 | 2681784.0169 | 1217271.5881
50 | 2681793.7922 | 1217244.8768
51 | 2681796.9277 | 1217230.3603
52 | 2681901.1253 | 1217305.1405
53 | 2681928.0728 | 1217306.1949
54 | 2681802.583 | 1217216.0395
55 | 2681815.0825 | 1217212.4299
56 | 2681846.4351 | 1217184.5099
57 | 2681869.3699 | 1217160.2863
58 | 2681886.8319 | 1217163.595
59 | 2681885.0056 | 1217124.4533
60 | 2681889.2965 | 1217180.2522
61 | 2681896.6957 | 1217107.7047
62 | 2681861.3313 | 1217224.8185
63 | 2681861.5438 | 1217238.0858
64 | 2681871.4253 | 1217210.5194
65 | 2681864.2179 | 1217243.3854
66 | 2681867.3317 | 1217248.229
67 | 2681879.328 | 1217256.0419
68 | 2681904.8035 | 1217266.2925
69 | 2681891.6641 | 1217239.4763
70 | 2681923.1361 | 1217257.2879
71 | 2681913.0984 | 1217210.693
72 | 2681932.7612 | 1217240.8727
73 | 2681930.0989 | 1217306.2567
74 | 2681939.6137 | 1217229.1859
75 | 2681962.2744 | 1217236.4801
76 | 2681990.6347 | 1217329.8691
77 | 2682022.7724 | 1217340.3476
78 | 2682014.9287 | 1217378.6095
79 | 2682019.3597 | 1217386.3978
80 | 2682019.5099 | 1217379.2682
81 | 2682028.1529 | 1217348.3677
82 | 2681970.7753 | 1217227.8479
83 | 2681978.7615 | 1217250.3038
84 | 2681971.7448 | 1217226.8635
85 | 2681983.3872 | 1217254.1821
86 | 2682033.8451 | 1217277.2789
87 | 2682021.3051 | 1217322.6283
88 | 2682021.9558 | 1217311.8365
89 | 2682041.0797 | 1217264.0491
90 | 2682055.2987 | 1217302.9829
91 | 2682067.2264 | 1217285.7415
92 | 2682053.3879 | 1217306.2598
93 | 2682114.1044 | 1217277.4858
94 | 2682039.7658 | 1217329.6204
95 | 2682139.8526 | 1217319.6908
96 | 2682106.3705 | 1217384.7168
97 | 2682097.6049 | 1217367.8678
98 | 2682112.9049 | 1217377.5816
99 | 2682099.0522 | 1217353.9142
100 | 2682122.6109 | 1217366.9834
101 | 2682112.4883 | 1217335.7458
102 | 2682116.3744 | 1217333.5635
103 | 2682137.232 | 1217322.3112
104 | 2682152.7619 | 1217400.5891
105 | 2682147.1778 | 1217405.793
106 | 2682147.3958 | 1217352.6851
107 | 2681987.5863 | 1217210.7775
108 | 2681929.3937 | 1217155.3118
109 | 2681951.5361 | 1217168.0823
110 | 2681928.1529 | 1217154.1838
111 | 2681953.7349 | 1217170.1411
112 | 2681962.8098 | 1217174.9468
113 | 2681904.0664 | 1217119.4026
114 | 2681973.9678 | 1217179.74
115 | 2681981.0355 | 1217134.5311
116 | 2681996.3296 | 1217184.8661
117 | 2682004.9612 | 1217191.493
118 | 2682007.9211 | 1217197.0725
119 | 2681992.3661 | 1217205.924
120 | 2681901.1253 | 1217305.1405

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98312 | -0.32402 | 0.0035344 | 0.00088581
1 | 0.98316 | -0.32319 | 0 | 0
2 | 0.98324 | -0.32176 | 0 | 0
3 | 0.99011 | -0.18897 | 0.01096 | 0.0027468
4 | 0.99003 | -0.19055 | 0.0038206 | 0.00095753
5 | 0.99012 | -0.18878 | 0.0064986 | 0.0016287
6 | 0.9855 | -0.27785 | 0 | 0
7 | 0.98182 | -0.34922 | 0.0072961 | 0.0018286
8 | 0.98544 | -0.27906 | 0.0036555 | 0.00091616
9 | 0.98633 | -0.26168 | 0.0018436 | 0.00046204
10 | 0.98138 | -0.35792 | 0.0052884 | 0.0013254
11 | 0.99061 | -0.17934 | 0.007309 | 0.0018318
12 | 0.99122 | -0.16747 | 0.0047447 | 0.0011891
13 | 0.97981 | -0.38861 | 0.0063183 | 0.0015835
14 | 0.99402 | -0.1139 | 0 | 0
15 | 0.97963 | -0.3921 | 0.0026162 | 0.00065569
16 | 0.99588 | -0.078464 | 0.011121 | 0.0027871
17 | 0.99396 | -0.11508 | 0.0078861 | 0.0019764
18 | 0.97874 | -0.40964 | 0.0060589 | 0.0015185
19 | 0.99368 | -0.1204 | 0.01121 | 0.0028094
20 | 0.98541 | -0.27957 | 0.0016226 | 0.00040666
21 | 0.9862 | -0.26425 | 0.0037315 | 0.00093521
22 | 0.9862 | -0.2643 | 0.0038215 | 0.00095775
23 | 0.97837 | -0.41683 | 0.0022534 | 0.00056474
24 | 0.97756 | -0.43271 | 0 | 0
25 | 0.97746 | -0.4346 | 0.0022594 | 0.00056625
26 | 0.9774 | -0.43595 | 0.0056794 | 0.0014234
27 | 0.97726 | -0.43853 | 0.0012824 | 0.0003214
28 | 0.97712 | -0.44136 | 0.0059282 | 0.0014857
29 | 0.97713 | -0.4412 | 0 | 0
30 | 0.97681 | -0.44745 | 0.0045556 | 0.0011418
31 | 0.97676 | -0.44849 | 0.0022373 | 0.00056072
32 | 0.98391 | -0.30848 | 0.00069235 | 0.00017352
33 | 0.98393 | -0.30825 | 0 | 0
34 | 0.97667 | -0.45021 | 0.0050796 | 0.0012731
35 | 0.99359 | -0.12213 | 0.0072049 | 0.0018057
36 | 0.97668 | -0.44997 | 0.011612 | 0.0029101
37 | 0.98319 | -0.32259 | 0.014178 | 0.0035532
38 | 0.98444 | -0.29821 | 0.0055276 | 0.0013853
39 | 0.99676 | -0.061654 | 0.0099406 | 0.0024913
40 | 0.98519 | -0.28357 | 0.0030969 | 0.00077615
41 | 0.98237 | -0.33866 | 0.0055317 | 0.0013864
42 | 0.98198 | -0.34633 | 0.00076911 | 0.00019276
43 | 0.98181 | -0.34958 | 0.0096802 | 0.0024261
44 | 0.99737 | -0.049989 | 0.0066618 | 0.0016696
45 | 0.98313 | -0.3248 | 0.0052967 | 0.0013275
46 | 0.98323 | -0.32289 | 0.009975 | 0.0025
47 | 0.9831 | -0.32539 | 0.003804 | 0.00095338
48 | 0.98393 | -0.30918 | 0 | 0
49 | 0.98423 | -0.30332 | 0 | 0
50 | 0.98474 | -0.29345 | 0.0015876 | 0.00039789
51 | 0.98502 | -0.28794 | 0 | 0
52 | 0.99861 | -0.026405 | 0.012377 | 0.003102
53 | 0.99977 | -0.0044221 | 0.0021804 | 0.00054646
54 | 0.98532 | -0.28221 | 0 | 0
55 | 0.98559 | -0.27698 | 0.0018068 | 0.00045282
56 | 0.98645 | -0.26006 | 0.0048646 | 0.0012192
57 | 0.9873 | -0.24374 | 0 | 0
58 | 0.98814 | -0.2273 | 0.0051829 | 0.001299
59 | 0.9866 | -0.25728 | 0.0061125 | 0.0015319
60 | 0.98895 | -0.21154 | 0.0076522 | 0.0019178
61 | 0.98634 | -0.26227 | 0 | 0
62 | 0.99194 | -0.15386 | 0.0026724 | 0.00066977
63 | 0.99274 | -0.13856 | 0.0026409 | 0.00066188
64 | 0.99093 | -0.17341 | 0.0027577 | 0.00069116
65 | 0.9931 | -0.13148 | 0.0021202 | 0.00053138
66 | 0.99348 | -0.12433 | 0.0027456 | 0.00068811
67 | 0.99446 | -0.10547 | 0 | 0
68 | 0.99645 | -0.067438 | 0.0028862 | 0.00072335
69 | 0.99434 | -0.1078 | 0.003681 | 0.00092254
70 | 0.99518 | -0.091493 | 0.0019883 | 0.00049831
71 | 0.99425 | -0.10951 | 0.0027083 | 0.00067877
72 | 0.99418 | -0.11062 | 0.002049 | 0.00051352
73 | 1 | 0 | -0.50875 | -0.12965
74 | 0.99347 | -0.12414 | 0.0027341 | 0.00068523
75 | 0.99211 | -0.15021 | 0 | 0
76 | 0.98531 | -0.28144 | 0.040218 | 0.01008
77 | 0.98659 | -0.25652 | 0 | 0
78 | 0.98555 | -0.27655 | 0.0044322 | 0.0011108
79 | 0.98533 | -0.28084 | 0 | 0
80 | 0.98511 | -0.28516 | 0.0017014 | 0.00042642
81 | 0.98311 | -0.32372 | 0.0056631 | 0.0014193
82 | 0.99149 | -0.16219 | 0.0024271 | 0.00060829
83 | 0.99128 | -0.1662 | 0.002125 | 0.00053259
84 | 0.99142 | -0.1635 | 0.00218 | 0.00054636
85 | 0.99105 | -0.17063 | 0.001868 | 0.00046817
86 | 0.98895 | -0.21101 | 0.004318 | 0.0010822
87 | 0.98721 | -0.24443 | 0.0037384 | 0.00093694
88 | 0.98761 | -0.23674 | 0.0024524 | 0.00061463
89 | 0.98892 | -0.21144 | 0.0016043 | 0.00040208
90 | 0.98028 | -0.37864 | 0.001317 | 0.00033007
91 | 0.9793 | -0.39777 | 0.0011667 | 0.00029241
92 | 0.98047 | -0.37511 | 0.0047776 | 0.0011974
93 | 0.97707 | -0.44142 | 0 | 0
94 | 0.98188 | -0.34766 | 0.0039648 | 0.00099367
95 | 0.97482 | -0.48559 | 0.0046474 | 0.0011648
96 | 0.97237 | -0.53391 | 0 | 0
97 | 0.97273 | -0.52683 | 0.0028065 | 0.00070339
98 | 0.97219 | -0.53746 | 0.0026467 | 0.00066333
99 | 0.97303 | -0.52082 | 0.0058907 | 0.0014764
100 | 0.97196 | -0.54203 | 0.0013907 | 0.00034855
101 | 0.97364 | -0.50874 | 0.0050197 | 0.0012581
102 | 0.97378 | -0.50599 | 0.0053167 | 0.0013325
103 | 0.97467 | -0.48859 | 0.0052559 | 0.0013172
104 | 0.97075 | -0.56591 | 0.0052601 | 0.0013183
105 | 0.97069 | -0.56714 | 0.0086823 | 0.002176
106 | 0.97151 | -0.55093 | 0.0018925 | 0.00047432
107 | 0.99036 | -0.18402 | 0.0025434 | 0.00063745
108 | 0.98717 | -0.24605 | 0.0077031 | 0.0019306
109 | 0.98754 | -0.23883 | 0.0045445 | 0.001139
110 | 0.98716 | -0.24629 | 0.0078205 | 0.00196
111 | 0.9876 | -0.23775 | 0.0031212 | 0.00078226
112 | 0.98782 | -0.23344 | 0.0043432 | 0.0010885
113 | 0.98617 | -0.26561 | 0.013124 | 0.0032893
114 | 0.98817 | -0.22648 | 0.003458 | 0.00086665
115 | 0.98767 | -0.23622 | 0.0035128 | 0.00088039
116 | 0.98891 | -0.21218 | 0.0026261 | 0.00065817
117 | 0.98928 | -0.20498 | 0 | 0
118 | 0.98924 | -0.20576 | 0.0068918 | 0.0017272
119 | 0.99006 | -0.18991 | 0.0046226 | 0.0011585
120 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0035344 | -0.00088581 | 0.0035345 | 0.00088573 | 1.3962e-07 | -7.562e-08 | 0.0053496 | 0.0053495 | 0.0053496 | 0.98312 | -0.32402 | 0.98316 | -0.32319 | 1.4697
1 | -0.0035345 | -0.00088573 | 0.0035348 | 0.0008856 | 2.4174e-07 | -1.3098e-07 | 0.0053495 | 0.0053494 | 0.0053495 | 0.98316 | -0.32319 | 0.98324 | -0.32176 | 1.4696
2 | -0.072311 | -0.01824 | 0.072464 | 0.018337 | 0.00015236 | 9.7078e-05 | 0.10948 | 0.10948 | 0.10948 | 0.98324 | -0.32176 | 0.9855 | -0.27785 | 30.0761
3 | 0.068777 | 0.017355 | -0.068686 | -0.017297 | 9.0335e-05 | 5.7533e-05 | 0.10413 | 0.10413 | 0.10413 | 0.98324 | -0.32176 | 0.98182 | -0.34922 | 28.6065
4 | 0.0038209 | 0.00095741 | -0.0038206 | -0.00095753 | 2.8741e-07 | -1.1497e-07 | 0.0057422 | 0.0057424 | 0.0057424 | 0.99011 | -0.18897 | 0.99003 | -0.19055 | 1.5776
5 | -0.014781 | -0.0037042 | 0.014781 | 0.0037043 | 1.3737e-07 | 7.8369e-08 | 0.022213 | 0.022213 | 0.022213 | 0.99011 | -0.18897 | 0.99012 | -0.18878 | 6.1026
6 | -0.021279 | -0.005333 | 0.021289 | 0.0053388 | 9.5713e-06 | 5.8045e-06 | 0.03198 | 0.03198 | 0.03198 | 0.99012 | -0.18878 | 0.99061 | -0.17934 | 8.7857
7 | 0.0052785 | 0.0013227 | -0.0052782 | -0.0013226 | 3.0543e-07 | 3.2111e-08 | 0.00797 | 0.00797 | 0.00797 | 0.9855 | -0.27785 | 0.98544 | -0.27906 | 2.1896
8 | -0.077742 | -0.01966 | 0.077803 | 0.019698 | 6.0338e-05 | 3.8468e-05 | 0.11745 | 0.11745 | 0.11745 | 0.9855 | -0.27785 | 0.98633 | -0.26168 | 32.2656
9 | 0.06139 | 0.015469 | -0.061365 | -0.015452 | 2.5517e-05 | 1.6232e-05 | 0.09307 | 0.09307 | 0.09307 | 0.98182 | -0.34922 | 0.98138 | -0.35792 | 25.5687
10 | 0.0016227 | 0.00040647 | -0.0016226 | -0.00040666 | 3.8995e-08 | -1.9571e-07 | 0.0024501 | 0.0024502 | 0.0024502 | 0.98544 | -0.27906 | 0.98541 | -0.27957 | 0.67314
11 | 0.0075539 | 0.0018933 | -0.007553 | -0.001893 | 9.2596e-07 | 3.4999e-07 | 0.011396 | 0.011396 | 0.011396 | 0.98633 | -0.26168 | 0.9862 | -0.26425 | 3.1308
12 | -0.0872 | -0.022054 | 0.087546 | 0.022274 | 0.00034593 | 0.00022072 | 0.13162 | 0.13162 | 0.13162 | 0.98633 | -0.26168 | 0.99061 | -0.17934 | 36.1605
13 | 0.056076 | 0.014127 | -0.055994 | -0.014075 | 8.2185e-05 | 5.2216e-05 | 0.085052 | 0.085052 | 0.085052 | 0.98138 | -0.35792 | 0.97981 | -0.38861 | 23.3659
14 | -0.11614 | -0.029445 | 0.11621 | 0.029487 | 6.6316e-05 | 4.2368e-05 | 0.17458 | 0.17458 | 0.17458 | 0.99061 | -0.17934 | 0.99122 | -0.16747 | 47.9623
15 | -0.12095 | -0.030677 | 0.12127 | 0.030876 | 0.00031238 | 0.00019959 | 0.18171 | 0.18171 | 0.18171 | 0.99122 | -0.16747 | 0.99402 | -0.1139 | 49.919
16 | 0.049676 | 0.012491 | -0.049667 | -0.012486 | 8.2917e-06 | 5.2578e-06 | 0.075456 | 0.075456 | 0.075456 | 0.97981 | -0.38861 | 0.97963 | -0.3921 | 20.7297
17 | -0.14757 | -0.037472 | 0.14783 | 0.037632 | 0.00025212 | 0.00016064 | 0.22109 | 0.22109 | 0.22109 | 0.99402 | -0.1139 | 0.99588 | -0.078464 | 30.3691
18 | 0.026308 | 0.0065955 | -0.026306 | -0.0065946 | 1.4788e-06 | 9.1346e-07 | 0.039382 | 0.039382 | 0.039382 | 0.99402 | -0.1139 | 0.99396 | -0.11508 | 10.8193
19 | 0.047051 | 0.01183 | -0.047012 | -0.011805 | 3.936e-05 | 2.4932e-05 | 0.071482 | 0.071482 | 0.071482 | 0.97963 | -0.3921 | 0.97874 | -0.40964 | 19.638
20 | -0.15895 | -0.040419 | 0.15908 | 0.040501 | 0.00012884 | 8.1188e-05 | 0.2377 | 0.2377 | 0.2377 | 0.99588 | -0.078464 | 0.99676 | -0.061654 | 16.3258
21 | 0.01842 | 0.0046181 | -0.018415 | -0.0046154 | 4.6685e-06 | 2.7757e-06 | 0.027576 | 0.027576 | 0.027576 | 0.99396 | -0.11508 | 0.99368 | -0.1204 | 7.5759
22 | 0.040953 | 0.010287 | -0.040939 | -0.010278 | 1.4051e-05 | 8.8712e-06 | 0.062271 | 0.062271 | 0.062271 | 0.97874 | -0.40964 | 0.97837 | -0.41683 | 17.1073
23 | 0.0072055 | 0.0018059 | -0.0072049 | -0.0018057 | 5.9465e-07 | 2.0416e-07 | 0.01079 | 0.01079 | 0.01079 | 0.99368 | -0.1204 | 0.99359 | -0.12213 | 2.9643
24 | 0.0038215 | 0.00095775 | -0.0038215 | -0.00095775 | 8.3265e-09 | -3.1926e-09 | 0.005766 | 0.005766 | 0.005766 | 0.9862 | -0.26425 | 0.9862 | -0.2643 | 1.5841
25 | 0.038685 | 0.0097131 | -0.038656 | -0.0096947 | 2.928e-05 | 1.8456e-05 | 0.058844 | 0.058844 | 0.058844 | 0.97837 | -0.41683 | 0.97756 | -0.43271 | 16.1658
26 | 0.010865 | 0.002724 | -0.010864 | -0.0027235 | 9.8164e-07 | 5.0828e-07 | 0.016539 | 0.016539 | 0.016539 | 0.97756 | -0.43271 | 0.97746 | -0.4346 | 4.5437
27 | 0.027791 | 0.0069707 | -0.027787 | -0.006968 | 4.2996e-06 | 2.6714e-06 | 0.042305 | 0.042305 | 0.042305 | 0.97756 | -0.43271 | 0.9774 | -0.43595 | 11.6222
28 | 0.0086047 | 0.0021572 | -0.0086031 | -0.0021565 | 1.6097e-06 | 7.1672e-07 | 0.013099 | 0.0131 | 0.0131 | 0.97746 | -0.4346 | 0.97726 | -0.43853 | 3.5988
29 | 0.022107 | 0.0055446 | -0.022102 | -0.0055411 | 5.7002e-06 | 3.48e-06 | 0.033658 | 0.033658 | 0.033658 | 0.9774 | -0.43595 | 0.97712 | -0.44136 | 9.2468
30 | 0.0073207 | 0.0018351 | -0.0073198 | -0.0018348 | 9.3271e-07 | 3.4616e-07 | 0.011147 | 0.011147 | 0.011147 | 0.97726 | -0.43853 | 0.97713 | -0.4412 | 3.0624
31 | 0.016173 | 0.0040554 | -0.016169 | -0.0040526 | 4.6867e-06 | 2.7415e-06 | 0.02463 | 0.024631 | 0.024631 | 0.97712 | -0.44136 | 0.97681 | -0.44745 | 6.7666
32 | 0.0073198 | 0.0018348 | -0.0073173 | -0.0018338 | 2.5419e-06 | 9.4377e-07 | 0.011147 | 0.011147 | 0.011147 | 0.97713 | -0.4412 | 0.97676 | -0.44849 | 3.0624
33 | 0.011613 | 0.0029109 | -0.011612 | -0.0029101 | 1.3962e-06 | 7.4465e-07 | 0.017691 | 0.017691 | 0.017691 | 0.97681 | -0.44745 | 0.97668 | -0.44997 | 4.8601
34 | 0.00508 | 0.0012731 | -0.0050796 | -0.0012731 | 4.1411e-07 | 3.4268e-08 | 0.0077389 | 0.007739 | 0.007739 | 0.97676 | -0.44849 | 0.97667 | -0.45021 | 2.1261
35 | -0.00069235 | -0.00017352 | 0.00069236 | 0.00017329 | 7.6317e-09 | -2.3089e-07 | 0.0010471 | 0.001047 | 0.0010471 | 0.98391 | -0.30848 | 0.98393 | -0.30825 | 0.28766
36 | 0.030197 | 0.0075811 | -0.030176 | -0.0075683 | 2.0637e-05 | 1.2873e-05 | 0.045672 | 0.045672 | 0.045672 | 0.98393 | -0.30825 | 0.98319 | -0.32259 | 12.5473
37 | -0.030889 | -0.0077544 | 0.030904 | 0.0077637 | 1.4792e-05 | 9.237e-06 | 0.046719 | 0.046719 | 0.046719 | 0.98393 | -0.30825 | 0.98444 | -0.29821 | 12.8349
38 | 0.015999 | 0.004015 | -0.015986 | -0.0040079 | 1.2252e-05 | 7.1351e-06 | 0.024215 | 0.024215 | 0.024215 | 0.98319 | -0.32259 | 0.98237 | -0.33866 | 6.6526
39 | -0.036432 | -0.009149 | 0.036457 | 0.009165 | 2.5472e-05 | 1.6017e-05 | 0.055074 | 0.055074 | 0.055074 | 0.98444 | -0.29821 | 0.98519 | -0.28357 | 15.1303
40 | -0.16902 | -0.042992 | 0.16911 | 0.043052 | 9.506e-05 | 6.0009e-05 | 0.25254 | 0.25254 | 0.25254 | 0.99676 | -0.061654 | 0.99737 | -0.049989 | 17.3449
41 | -0.039554 | -0.0099412 | 0.039559 | 0.0099444 | 5.1517e-06 | 3.2481e-06 | 0.059752 | 0.059752 | 0.059752 | 0.98519 | -0.28357 | 0.98533 | -0.28084 | 16.4153
42 | 0.010455 | 0.0026215 | -0.010451 | -0.0026196 | 3.8203e-06 | 1.9309e-06 | 0.015836 | 0.015836 | 0.015836 | 0.98237 | -0.33866 | 0.98198 | -0.34633 | 4.3507
43 | 0.0096817 | 0.0024268 | -0.0096802 | -0.0024261 | 1.4994e-06 | 7.2465e-07 | 0.014671 | 0.014671 | 0.014671 | 0.98198 | -0.34633 | 0.98181 | -0.34958 | 4.0305
44 | -0.17577 | -0.044722 | 0.17597 | 0.044848 | 0.00020004 | 0.00012641 | 0.26248 | 0.26248 | 0.26248 | 0.99737 | -0.049989 | 0.99861 | -0.026405 | 18.0275
45 | -0.0091008 | -0.0022808 | 0.0091017 | 0.0022812 | 8.2876e-07 | 3.8269e-07 | 0.013774 | 0.013774 | 0.013774 | 0.98313 | -0.3248 | 0.98323 | -0.32289 | 3.7842
46 | 0.0038041 | 0.00095334 | -0.003804 | -0.00095338 | 1.0579e-07 | -4.0196e-08 | 0.0057577 | 0.0057577 | 0.0057577 | 0.98313 | -0.3248 | 0.9831 | -0.32539 | 1.5818
47 | -0.019077 | -0.0047812 | 0.019089 | 0.0047886 | 1.2468e-05 | 7.473e-06 | 0.028871 | 0.02887 | 0.028871 | 0.98323 | -0.32289 | 0.98393 | -0.30918 | 7.9315
48 | -0.019089 | -0.0047886 | 0.019094 | 0.0047918 | 5.3357e-06 | 3.198e-06 | 0.02887 | 0.02887 | 0.02887 | 0.98393 | -0.30918 | 0.98423 | -0.30332 | 7.9314
49 | -0.019094 | -0.0047918 | 0.019103 | 0.0047972 | 8.9882e-06 | 5.3868e-06 | 0.02887 | 0.02887 | 0.02887 | 0.98423 | -0.30332 | 0.98474 | -0.29345 | 7.9314
50 | -0.020691 | -0.0051951 | 0.020697 | 0.0051984 | 5.4455e-06 | 3.2961e-06 | 0.031269 | 0.031269 | 0.031269 | 0.98474 | -0.29345 | 0.98502 | -0.28794 | 8.5904
51 | -0.020697 | -0.0051984 | 0.020702 | 0.0052018 | 5.6557e-06 | 3.4232e-06 | 0.031269 | 0.031269 | 0.031269 | 0.98502 | -0.28794 | 0.98532 | -0.28221 | 8.5904
52 | -0.18835 | -0.04795 | 0.18855 | 0.048076 | 0.00019988 | 0.00012651 | 0.28092 | 0.28092 | 0.28092 | 0.99861 | -0.026405 | 0.99977 | -0.0044221 | 19.2942
53 | -0.507 | -0.12958 | 0.5071 | 0.12965 | 0.00010847 | 6.9313e-05 | 0.75549 | 0.75549 | 0.75549 | 0.99977 | -0.0044221 | 1 | 0 | 51.8878
54 | 0.31626 | 0.080961 | -0.3153 | -0.080347 | 0.00096198 | 0.00061325 | 0.47132 | 0.47132 | 0.47132 | 0.99977 | -0.0044221 | 0.99645 | -0.067438 | 32.3709
55 | -0.020702 | -0.0052018 | 0.020707 | 0.005205 | 5.1766e-06 | 3.1331e-06 | 0.031269 | 0.031269 | 0.031269 | 0.98532 | -0.28221 | 0.98559 | -0.27698 | 8.5904
56 | -0.022514 | -0.0056578 | 0.022532 | 0.0056689 | 1.8196e-05 | 1.111e-05 | 0.033997 | 0.033997 | 0.033997 | 0.98559 | -0.27698 | 0.98645 | -0.26006 | 9.3398
57 | -0.027397 | -0.0068881 | 0.027418 | 0.0069013 | 2.1376e-05 | 1.3254e-05 | 0.041335 | 0.041334 | 0.041335 | 0.98645 | -0.26006 | 0.9873 | -0.24374 | 11.3557
58 | -0.046673 | -0.011733 | 0.04671 | 0.011756 | 3.6654e-05 | 2.3206e-05 | 0.070356 | 0.070356 | 0.070356 | 0.9873 | -0.24374 | 0.98814 | -0.2273 | 19.3287
59 | 0.019255 | 0.0048316 | -0.019242 | -0.0048241 | 1.2428e-05 | 7.4509e-06 | 0.029022 | 0.029022 | 0.029022 | 0.9873 | -0.24374 | 0.9866 | -0.25728 | 7.9731
60 | -0.051893 | -0.013055 | 0.051932 | 0.01308 | 3.9101e-05 | 2.4806e-05 | 0.078161 | 0.078161 | 0.078161 | 0.98814 | -0.2273 | 0.98895 | -0.21154 | 21.4728
61 | 0.01313 | 0.0032922 | -0.013127 | -0.0032904 | 3.1226e-06 | 1.7274e-06 | 0.019803 | 0.019803 | 0.019803 | 0.9866 | -0.25728 | 0.98634 | -0.26227 | 5.4404
62 | -0.059584 | -0.014998 | 0.059693 | 0.015067 | 0.00010883 | 6.9187e-05 | 0.089675 | 0.089675 | 0.089675 | 0.98895 | -0.21154 | 0.99093 | -0.17341 | 24.6359
63 | 0.013127 | 0.0032904 | -0.013124 | -0.0032893 | 2.0897e-06 | 1.1561e-06 | 0.019803 | 0.019803 | 0.019803 | 0.98634 | -0.26227 | 0.98617 | -0.26561 | 5.4404
64 | -0.065181 | -0.016465 | 0.065229 | 0.016495 | 4.7833e-05 | 3.0441e-05 | 0.097825 | 0.097825 | 0.097825 | 0.99194 | -0.15386 | 0.99274 | -0.13856 | 26.8749
65 | 0.062509 | 0.015795 | -0.06245 | -0.015758 | 5.8517e-05 | 3.7222e-05 | 0.093816 | 0.093816 | 0.093816 | 0.99194 | -0.15386 | 0.99093 | -0.17341 | 25.7736
66 | -0.06787 | -0.017157 | 0.067893 | 0.017172 | 2.3061e-05 | 1.4682e-05 | 0.10178 | 0.10178 | 0.10178 | 0.99274 | -0.13856 | 0.9931 | -0.13148 | 27.9624
67 | -0.070013 | -0.017703 | 0.070037 | 0.017719 | 2.4007e-05 | 1.5289e-05 | 0.10496 | 0.10496 | 0.10496 | 0.9931 | -0.13148 | 0.99348 | -0.12433 | 28.8351
68 | -0.072783 | -0.018407 | 0.072849 | 0.018449 | 6.5901e-05 | 4.1985e-05 | 0.10907 | 0.10907 | 0.10907 | 0.99348 | -0.12433 | 0.99446 | -0.10547 | 29.9649
69 | -0.079239 | -0.02005 | 0.079384 | 0.020142 | 0.00014493 | 9.2397e-05 | 0.11863 | 0.11863 | 0.11863 | 0.99446 | -0.10547 | 0.99645 | -0.067438 | 32.5917
70 | 0.0063903 | 0.0016012 | -0.0063896 | -0.001601 | 7.0813e-07 | 1.8526e-07 | 0.0095617 | 0.0095618 | 0.0095618 | 0.99446 | -0.10547 | 0.99434 | -0.1078 | 2.6269
71 | 0.23303 | 0.059482 | -0.23276 | -0.05931 | 0.00027051 | 0.00017189 | 0.34838 | 0.34838 | 0.34838 | 0.99645 | -0.067438 | 0.99518 | -0.091493 | 23.927
72 | 0.0027086 | 0.00067845 | -0.0027083 | -0.00067877 | 2.211e-07 | -3.2396e-07 | 0.0040532 | 0.0040534 | 0.0040534 | 0.99434 | -0.1078 | 0.99425 | -0.10951 | 1.1136
73 | 0.23077 | 0.058812 | -0.23056 | -0.058676 | 0.00021283 | 0.00013523 | 0.3454 | 0.3454 | 0.3454 | 0.99518 | -0.091493 | 0.99418 | -0.11062 | 23.7228
74 | 0.22851 | 0.058163 | -0.22836 | -0.058068 | 0.00014885 | 9.4561e-05 | 0.34234 | 0.34234 | 0.34234 | 0.99418 | -0.11062 | 0.99347 | -0.12414 | 23.5122
75 | 0.22563 | 0.057383 | -0.22535 | -0.057203 | 0.00028302 | 0.00017977 | 0.33824 | 0.33824 | 0.33824 | 0.99347 | -0.12414 | 0.99211 | -0.15021 | 23.231
76 | 0.055984 | 0.014102 | -0.055952 | -0.014082 | 3.2052e-05 | 2.0357e-05 | 0.083993 | 0.083993 | 0.083993 | 0.99211 | -0.15021 | 0.99149 | -0.16219 | 23.0749
77 | 0.16936 | 0.043101 | -0.16923 | -0.043019 | 0.00013039 | 8.234e-05 | 0.25425 | 0.25425 | 0.25425 | 0.99211 | -0.15021 | 0.99128 | -0.1662 | 17.4623
78 | -0.040218 | -0.01008 | 0.040266 | 0.01011 | 4.7809e-05 | 3.0157e-05 | 0.060738 | 0.060738 | 0.060738 | 0.98531 | -0.28144 | 0.98659 | -0.25652 | 16.6862
79 | -0.15243 | -0.038542 | 0.15252 | 0.038597 | 8.8412e-05 | 5.5672e-05 | 0.23002 | 0.23002 | 0.23002 | 0.98659 | -0.25652 | 0.98721 | -0.24443 | 15.7979
80 | 0.11216 | 0.028432 | -0.11205 | -0.028365 | 0.00010786 | 6.6983e-05 | 0.16928 | 0.16928 | 0.16928 | 0.98659 | -0.25652 | 0.98555 | -0.27655 | 11.6265
81 | 0.10762 | 0.027254 | -0.1076 | -0.02724 | 2.2207e-05 | 1.3756e-05 | 0.16259 | 0.16259 | 0.16259 | 0.98555 | -0.27655 | 0.98533 | -0.28084 | 11.1669
82 | 0.068039 | 0.017296 | -0.068025 | -0.017287 | 1.4141e-05 | 8.8684e-06 | 0.10284 | 0.10284 | 0.10284 | 0.98533 | -0.28084 | 0.98511 | -0.28516 | 14.1261
83 | 0.066324 | 0.016861 | -0.066201 | -0.016782 | 0.00012294 | 7.8268e-05 | 0.10027 | 0.10027 | 0.10027 | 0.98511 | -0.28516 | 0.98311 | -0.32372 | 27.5462
84 | 0.060538 | 0.015363 | -0.060468 | -0.015319 | 6.9598e-05 | 4.4264e-05 | 0.091697 | 0.091697 | 0.091697 | 0.98311 | -0.32372 | 0.98188 | -0.34766 | 25.1915
85 | 0.053525 | 0.013474 | -0.053521 | -0.013471 | 3.3449e-06 | 2.1229e-06 | 0.08035 | 0.08035 | 0.08035 | 0.99149 | -0.16219 | 0.99142 | -0.1635 | 22.0742
86 | 0.16711 | 0.042486 | -0.16707 | -0.042464 | 3.567e-05 | 2.2518e-05 | 0.25106 | 0.25106 | 0.25106 | 0.99128 | -0.1662 | 0.99105 | -0.17063 | 17.2432
87 | 0.051342 | 0.012925 | -0.051291 | -0.012893 | 5.0299e-05 | 3.1901e-05 | 0.077078 | 0.077078 | 0.077078 | 0.99142 | -0.1635 | 0.99036 | -0.18402 | 21.1754
88 | 0.1652 | 0.041995 | -0.16488 | -0.041793 | 0.00032064 | 0.00020235 | 0.24826 | 0.24826 | 0.24826 | 0.99105 | -0.17063 | 0.98895 | -0.21101 | 17.0507
89 | 0.0016044 | 0.00040191 | -0.0016043 | -0.00040208 | 3.3021e-08 | -1.7275e-07 | 0.0024139 | 0.002414 | 0.002414 | 0.98895 | -0.21101 | 0.98892 | -0.21144 | 0.66319
90 | 0.15896 | 0.040309 | -0.15876 | -0.040185 | 0.00019629 | 0.00012375 | 0.23935 | 0.23935 | 0.23935 | 0.98895 | -0.21101 | 0.98761 | -0.23674 | 16.4387
91 | -0.15625 | -0.039534 | 0.15631 | 0.039571 | 5.7722e-05 | 3.6375e-05 | 0.23565 | 0.23565 | 0.23565 | 0.98721 | -0.24443 | 0.98761 | -0.23674 | 16.1849
92 | 0.050326 | 0.012745 | -0.050279 | -0.012715 | 4.6185e-05 | 2.9293e-05 | 0.076439 | 0.076439 | 0.076439 | 0.98028 | -0.37864 | 0.9793 | -0.39777 | 20.9997
93 | -0.051643 | -0.013075 | 0.051651 | 0.01308 | 8.7519e-06 | 5.5534e-06 | 0.078438 | 0.078438 | 0.078438 | 0.98028 | -0.37864 | 0.98047 | -0.37511 | 21.5489
94 | 0.049113 | 0.012423 | -0.04901 | -0.012358 | 0.00010262 | 6.5062e-05 | 0.074666 | 0.074666 | 0.074666 | 0.9793 | -0.39777 | 0.97707 | -0.44142 | 20.5127
95 | -0.056429 | -0.014278 | 0.056503 | 0.014325 | 7.4459e-05 | 4.7312e-05 | 0.085688 | 0.085688 | 0.085688 | 0.98047 | -0.37511 | 0.98188 | -0.34766 | 23.5408
96 | 0.04901 | 0.012358 | -0.048907 | -0.012292 | 0.00010336 | 6.5533e-05 | 0.074666 | 0.074666 | 0.074666 | 0.97707 | -0.44142 | 0.97482 | -0.48559 | 20.5128
97 | 0.044259 | 0.011128 | -0.044253 | -0.011124 | 6.3454e-06 | 4.0149e-06 | 0.067572 | 0.067572 | 0.067572 | 0.97482 | -0.48559 | 0.97467 | -0.48859 | 18.5638
98 | -0.019897 | -0.0049946 | 0.019903 | 0.0049986 | 6.7202e-06 | 4.0611e-06 | 0.030451 | 0.030451 | 0.030451 | 0.97237 | -0.53391 | 0.97273 | -0.52683 | 8.3656
99 | 0.019897 | 0.0049946 | -0.019893 | -0.0049925 | 3.3643e-06 | 2.0331e-06 | 0.030451 | 0.030451 | 0.030451 | 0.97237 | -0.53391 | 0.97219 | -0.53746 | 8.3656
100 | -0.02271 | -0.005702 | 0.022716 | 0.005706 | 6.5142e-06 | 3.9904e-06 | 0.034744 | 0.034744 | 0.034744 | 0.97273 | -0.52683 | 0.97303 | -0.52082 | 9.5451
101 | 0.017247 | 0.0043292 | -0.017243 | -0.004327 | 3.756e-06 | 2.2257e-06 | 0.0264 | 0.0264 | 0.0264 | 0.97219 | -0.53746 | 0.97196 | -0.54203 | 7.2527
102 | -0.028607 | -0.0071823 | 0.028624 | 0.0071926 | 1.6494e-05 | 1.027e-05 | 0.043752 | 0.043752 | 0.043752 | 0.97303 | -0.52082 | 0.97364 | -0.50874 | 12.0199
103 | 0.015852 | 0.0039784 | -0.015845 | -0.0039745 | 6.7316e-06 | 3.9307e-06 | 0.024271 | 0.024271 | 0.024271 | 0.97196 | -0.54203 | 0.97151 | -0.55093 | 6.6678
104 | -0.033643 | -0.0084507 | 0.033648 | 0.0084535 | 4.4198e-06 | 2.7732e-06 | 0.051424 | 0.051424 | 0.051424 | 0.97364 | -0.50874 | 0.97378 | -0.50599 | 14.1275
105 | -0.038965 | -0.009786 | 0.038997 | 0.0098064 | 3.2384e-05 | 2.0423e-05 | 0.059548 | 0.059548 | 0.059548 | 0.97378 | -0.50599 | 0.97467 | -0.48859 | 16.3594
106 | 0.0086828 | 0.0021762 | -0.0086823 | -0.002176 | 5.0705e-07 | 2.3015e-07 | 0.01331 | 0.01331 | 0.01331 | 0.97075 | -0.56591 | 0.97069 | -0.56714 | 3.6565
107 | -0.013943 | -0.0034945 | 0.013953 | 0.0035002 | 9.9572e-06 | 5.6534e-06 | 0.021372 | 0.021372 | 0.021372 | 0.97075 | -0.56591 | 0.97151 | -0.55093 | 5.8716
108 | 0.048748 | 0.012256 | -0.048734 | -0.012247 | 1.3709e-05 | 8.6861e-06 | 0.073257 | 0.073257 | 0.073257 | 0.99036 | -0.18402 | 0.99006 | -0.18991 | 20.1255
109 | -0.015524 | -0.0038906 | 0.015529 | 0.0038937 | 5.3468e-06 | 3.0889e-06 | 0.0234 | 0.0234 | 0.0234 | 0.98717 | -0.24605 | 0.98754 | -0.23883 | 6.4285
110 | 0.0078206 | 0.00196 | -0.0078205 | -0.00196 | 8.7388e-08 | 3.449e-08 | 0.011788 | 0.011788 | 0.011788 | 0.98717 | -0.24605 | 0.98716 | -0.24629 | 3.2386
111 | -0.020074 | -0.0050327 | 0.020075 | 0.0050333 | 1.0335e-06 | 6.2287e-07 | 0.030247 | 0.030247 | 0.030247 | 0.98754 | -0.23883 | 0.9876 | -0.23775 | 8.3097
112 | -0.023196 | -0.0058155 | 0.023201 | 0.0058184 | 4.7626e-06 | 2.915e-06 | 0.03495 | 0.03495 | 0.03495 | 0.9876 | -0.23775 | 0.98782 | -0.23344 | 9.6016
113 | -0.031057 | -0.0077871 | 0.031067 | 0.0077935 | 1.0305e-05 | 6.4343e-06 | 0.046784 | 0.046784 | 0.046784 | 0.98782 | -0.23344 | 0.98817 | -0.22648 | 12.8529
114 | 0.0035133 | 0.00088012 | -0.0035128 | -0.00088039 | 4.6564e-07 | -2.6946e-07 | 0.0052921 | 0.0052923 | 0.0052923 | 0.98782 | -0.23344 | 0.98767 | -0.23622 | 1.4539
115 | -0.034525 | -0.0086602 | 0.034549 | 0.0086749 | 2.3545e-05 | 1.4771e-05 | 0.051992 | 0.051991 | 0.051992 | 0.98817 | -0.22648 | 0.98891 | -0.21218 | 14.2834
116 | -0.037175 | -0.0093331 | 0.037188 | 0.0093411 | 1.2783e-05 | 8.0416e-06 | 0.055943 | 0.055943 | 0.055943 | 0.98891 | -0.21218 | 0.98928 | -0.20498 | 15.3689
117 | 0.0068921 | 0.0017273 | -0.0068918 | -0.0017272 | 2.5659e-07 | 8.247e-08 | 0.010367 | 0.010367 | 0.010367 | 0.98928 | -0.20498 | 0.98924 | -0.20576 | 2.848
118 | -0.04408 | -0.011068 | 0.044111 | 0.011089 | 3.1716e-05 | 2.0051e-05 | 0.06631 | 0.066309 | 0.06631 | 0.98928 | -0.20498 | 0.99006 | -0.18991 | 18.2169

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.51378 | 0.13091

## res_load
| p_mw | q_mvar
0 | 0.0035344 | 0.00088581
1 | 0.01096 | 0.0027468
2 | 0.0038206 | 0.00095753
3 | 0.0064986 | 0.0016287
4 | 0.0072961 | 0.0018286
5 | 0.0036555 | 0.00091616
6 | 0.0018436 | 0.00046204
7 | 0.0052884 | 0.0013254
8 | 0.007309 | 0.0018318
9 | 0.0047447 | 0.0011891
10 | 0.0063183 | 0.0015835
11 | 0.0026162 | 0.00065569
12 | 0.011121 | 0.0027871
13 | 0.0078861 | 0.0019764
14 | 0.0060589 | 0.0015185
15 | 0.01121 | 0.0028094
16 | 0.0016226 | 0.00040666
17 | 0.0037315 | 0.00093521
18 | 0.0038215 | 0.00095775
19 | 0.0022534 | 0.00056474
20 | 0.0022594 | 0.00056625
21 | 0.0056794 | 0.0014234
22 | 0.0012824 | 0.0003214
23 | 0.0059282 | 0.0014857
24 | 0.0045556 | 0.0011418
25 | 0.0022373 | 0.00056072
26 | 0.00069235 | 0.00017352
27 | 0.0050796 | 0.0012731
28 | 0.0072049 | 0.0018057
29 | 0.011612 | 0.0029101
30 | 0.014178 | 0.0035532
31 | 0.0055276 | 0.0013853
32 | 0.0099406 | 0.0024913
33 | 0.0030969 | 0.00077615
34 | 0.0055317 | 0.0013864
35 | 0.00076911 | 0.00019276
36 | 0.0096802 | 0.0024261
37 | 0.0066618 | 0.0016696
38 | 0.0052967 | 0.0013275
39 | 0.009975 | 0.0025
40 | 0.003804 | 0.00095338
41 | 0.0015876 | 0.00039789
42 | 0.012377 | 0.003102
43 | 0.0021804 | 0.00054646
44 | 0.0018068 | 0.00045282
45 | 0.0048646 | 0.0012192
46 | 0.0051829 | 0.001299
47 | 0.0061125 | 0.0015319
48 | 0.0076522 | 0.0019178
49 | 0.0026724 | 0.00066977
50 | 0.0026409 | 0.00066188
51 | 0.0027577 | 0.00069116
52 | 0.0021202 | 0.00053138
53 | 0.0027456 | 0.00068811
54 | 0.0028862 | 0.00072335
55 | 0.003681 | 0.00092254
56 | 0.0019883 | 0.00049831
57 | 0.0027083 | 0.00067877
58 | 0.002049 | 0.00051352
59 | 0.0050286 | 0.0012603
60 | 0.0027341 | 0.00068523
61 | 0.040218 | 0.01008
62 | 0.0044322 | 0.0011108
63 | 0.0017014 | 0.00042642
64 | 0.0056631 | 0.0014193
65 | 0.0024271 | 0.00060829
66 | 0.002125 | 0.00053259
67 | 0.00218 | 0.00054636
68 | 0.001868 | 0.00046817
69 | 0.004318 | 0.0010822
70 | 0.0037384 | 0.00093694
71 | 0.0024524 | 0.00061463
72 | 0.0016043 | 0.00040208
73 | 0.001317 | 0.00033007
74 | 0.0011667 | 0.00029241
75 | 0.0047776 | 0.0011974
76 | 0.0039648 | 0.00099367
77 | 0.0046474 | 0.0011648
78 | 0.0028065 | 0.00070339
79 | 0.0026467 | 0.00066333
80 | 0.0058907 | 0.0014764
81 | 0.0013907 | 0.00034855
82 | 0.0050197 | 0.0012581
83 | 0.0053167 | 0.0013325
84 | 0.0052559 | 0.0013172
85 | 0.0052601 | 0.0013183
86 | 0.0086823 | 0.002176
87 | 0.0018925 | 0.00047432
88 | 0.0025434 | 0.00063745
89 | 0.0077031 | 0.0019306
90 | 0.0045445 | 0.001139
91 | 0.0078205 | 0.00196
92 | 0.0031212 | 0.00078226
93 | 0.0043432 | 0.0010885
94 | 0.013124 | 0.0032893
95 | 0.003458 | 0.00086665
96 | 0.0035128 | 0.00088039
97 | 0.0026261 | 0.00065817
98 | 0.0068918 | 0.0017272
99 | 0.0046226 | 0.0011585

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1