## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_181-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_181-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_181-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_181-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_181-3_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_181-3_0_4_node_252 | 0.4 | n |  | TRUE
6 | bus_LV_181-3_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_181-3_0_4_node_67 | 0.4 | n |  | TRUE
8 | bus_LV_181-3_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_181-3_0_4_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_181-3_0_4_node_103 | 0.4 | n |  | TRUE
11 | bus_LV_181-3_0_4_node_65 | 0.4 | n |  | TRUE
12 | bus_LV_181-3_0_4_node_64 | 0.4 | n |  | TRUE
13 | bus_LV_181-3_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_181-3_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_181-3_0_4_node_35 | 0.4 | n |  | TRUE
16 | bus_LV_181-3_0_4_node_113 | 0.4 | n |  | TRUE
17 | bus_LV_181-3_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_181-3_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_181-3_0_4_node_135 | 0.4 | n |  | TRUE
20 | bus_LV_181-3_0_4_node_85 | 0.4 | n |  | TRUE
21 | bus_LV_181-3_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_181-3_0_4_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_181-3_0_4_node_76 | 0.4 | n |  | TRUE
24 | bus_LV_181-3_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_181-3_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_181-3_0_4_node_89 | 0.4 | n |  | TRUE
27 | bus_LV_181-3_0_4_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_181-3_0_4_node_127 | 0.4 | n |  | TRUE
29 | bus_LV_181-3_0_4_node_131 | 0.4 | n |  | TRUE
30 | bus_LV_181-3_0_4_node_96 | 0.4 | n |  | TRUE
31 | bus_LV_181-3_0_4_node_66 | 0.4 | n |  | TRUE
32 | bus_LV_181-3_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_181-3_0_4_node_114 | 0.4 | n |  | TRUE
34 | bus_LV_181-3_0_4_node_116 | 0.4 | n |  | TRUE
35 | bus_LV_181-3_0_4_node_147 | 0.4 | n |  | TRUE
36 | bus_LV_181-3_0_4_node_136 | 0.4 | n |  | TRUE
37 | bus_LV_181-3_0_4_node_119 | 0.4 | n |  | TRUE
38 | bus_LV_181-3_0_4_node_118 | 0.4 | n |  | TRUE
39 | bus_LV_181-3_0_4_node_152 | 0.4 | n |  | TRUE
40 | bus_LV_181-3_0_4_node_139 | 0.4 | n |  | TRUE
41 | bus_LV_181-3_0_4_node_124 | 0.4 | n |  | TRUE
42 | bus_LV_181-3_0_4_node_46 | 0.4 | n |  | TRUE
43 | bus_LV_181-3_0_4_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_181-3_0_4_node_74 | 0.4 | n |  | TRUE
45 | bus_LV_181-3_0_4_node_112 | 0.4 | n |  | TRUE
46 | bus_LV_181-3_0_4_node_87 | 0.4 | n |  | TRUE
47 | bus_LV_181-3_0_4_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_181-3_0_4_node_117 | 0.4 | n |  | TRUE
49 | bus_LV_181-3_0_4_node_132 | 0.4 | n |  | TRUE
50 | bus_LV_181-3_0_4_node_133 | 0.4 | n |  | TRUE
51 | bus_LV_181-3_0_4_node_123 | 0.4 | n |  | TRUE
52 | bus_LV_181-3_0_4_node_122 | 0.4 | n |  | TRUE
53 | bus_LV_181-3_0_4_node_130 | 0.4 | n |  | TRUE
54 | bus_LV_181-3_0_4_node_126 | 0.4 | n |  | TRUE
55 | bus_LV_181-3_0_4_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_181-3_0_4_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_181-3_0_4_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_181-3_0_4_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_181-3_0_4_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_181-3_0_4_node_108 | 0.4 | n |  | TRUE
61 | bus_LV_181-3_0_4_node_72 | 0.4 | n |  | TRUE
62 | bus_LV_181-3_0_4_node_109 | 0.4 | n |  | TRUE
63 | bus_LV_181-3_0_4_node_269 | 0.4 | n |  | TRUE
64 | bus_LV_181-3_0_4_node_101 | 0.4 | n |  | TRUE
65 | bus_LV_181-3_0_4_node_265 | 0.4 | n |  | TRUE
66 | bus_LV_181-3_0_4_node_264 | 0.4 | n |  | TRUE
67 | bus_LV_181-3_0_4_node_100 | 0.4 | n |  | TRUE
68 | bus_LV_181-3_0_4_node_71 | 0.4 | n |  | TRUE
69 | bus_LV_181-3_0_4_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_181-3_0_4_node_111 | 0.4 | n |  | TRUE
71 | bus_LV_181-3_0_4_node_110 | 0.4 | n |  | TRUE
72 | bus_LV_181-3_0_4_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_181-3_0_4_node_50 | 0.4 | n |  | TRUE
74 | bus_LV_181-3_0_4_node_47 | 0.4 | n |  | TRUE
75 | bus_LV_181-3_0_4_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_181-3_0_4_node_93 | 0.4 | n |  | TRUE
77 | bus_LV_181-3_0_4_node_91 | 0.4 | n |  | TRUE
78 | bus_LV_181-3_0_4_node_43 | 0.4 | n |  | TRUE
79 | bus_LV_181-3_0_4_node_45 | 0.4 | n |  | TRUE
80 | bus_LV_181-3_0_4_node_69 | 0.4 | n |  | TRUE
81 | bus_LV_181-3_0_4_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_181-3_0_4_node_80 | 0.4 | n |  | TRUE
83 | bus_LV_181-3_0_4_node_77 | 0.4 | n |  | TRUE
84 | bus_LV_181-3_0_4_node_81 | 0.4 | n |  | TRUE
85 | bus_LV_181-3_0_4_node_128 | 0.4 | n |  | TRUE
86 | bus_LV_181-3_0_4_node_125 | 0.4 | n |  | TRUE
87 | bus_LV_181-3_0_4_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_181-3_0_4_node_57 | 0.4 | n |  | TRUE
89 | bus_LV_181-3_0_4_node_88 | 0.4 | n |  | TRUE
90 | bus_LV_181-3_0_4_node_99 | 0.4 | n |  | TRUE
91 | bus_LV_181-3_0_4_node_95 | 0.4 | n |  | TRUE
92 | bus_LV_181-3_0_4_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_181-3_0_4_node_90 | 0.4 | n |  | TRUE
94 | bus_LV_181-3_0_4_node_58 | 0.4 | n |  | TRUE
95 | bus_LV_181-3_0_4_node_60 | 0.4 | n |  | TRUE
96 | bus_LV_181-3_0_4_node_62 | 0.4 | n |  | TRUE
97 | bus_LV_181-3_0_4_node_63 | 0.4 | n |  | TRUE
98 | bus_LV_181-3_0_4_node_61 | 0.4 | n |  | TRUE
99 | bus_LV_181-3_0_4_node_83 | 0.4 | n |  | TRUE
100 | bus_LV_181-3_0_4_node_84 | 0.4 | n |  | TRUE
101 | bus_LV_181-3_0_4_node_86 | 0.4 | n |  | TRUE
102 | bus_LV_181-3_0_4_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_181-3_0_4_node_73 | 0.4 | n |  | TRUE
104 | bus_LV_181-3_0_4_node_75 | 0.4 | n |  | TRUE
105 | bus_LV_181-3_0_4_node_79 | 0.4 | n |  | TRUE
106 | bus_LV_181-3_0_4_node_266 | 0.4 | n |  | TRUE
107 | bus_LV_181-3_0_4_node_94 | 0.4 | n |  | TRUE
108 | bus_LV_181-3_0_4_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_181-3_0_4_node_105 | 0.4 | n |  | TRUE
110 | bus_LV_181-3_0_4_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_181-3_0_4_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_181-3_0_4_node_129 | 0.4 | n |  | TRUE
113 | bus_LV_181-3_0_4_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_181-3_0_4_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_181-3_0_4_node_115 | 0.4 | n |  | TRUE
116 | bus_LV_181-3_0_4_node_146 | 0.4 | n |  | TRUE
117 | bus_LV_181-3_0_4_node_120 | 0.4 | n |  | TRUE
118 | bus_LV_181-3_0_4_node_121 | 0.4 | n |  | TRUE
119 | bus_LV_181-3_0_4_node_262 | 0.4 | n |  | TRUE
120 | bus_LV_181-3_0_4_node_263 | 0.4 | n |  | TRUE
121 | bus_LV_181-3_0_4_node_261 | 0.4 | n |  | TRUE
122 | bus_LV_181-3_0_4_node_137 | 0.4 | n |  | TRUE
123 | bus_LV_181-3_0_4_node_138 | 0.4 | n |  | TRUE
124 | bus_LV_181-3_0_4_node_150 | 0.4 | n |  | TRUE
125 | bus_LV_181-3_0_4_node_144 | 0.4 | n |  | TRUE
126 | bus_LV_181-3_0_4_node_140 | 0.4 | n |  | TRUE
127 | bus_LV_181-3_0_4_node_141 | 0.4 | n |  | TRUE
128 | bus_LV_181-3_0_4_node_142 | 0.4 | n |  | TRUE
129 | bus_LV_181-3_0_4_node_143 | 0.4 | n |  | TRUE
130 | bus_LV_181-3_0_4_node_145 | 0.4 | n |  | TRUE
131 | bus_LV_181-3_0_4_node_151 | 0.4 | n |  | TRUE
132 | bus_LV_181-3_0_4_node_148 | 0.4 | n |  | TRUE
133 | bus_LV_181-3_0_4_node_149 | 0.4 | n |  | TRUE
134 | bus_LV_181-3_0_4_node_153 | 0.4 | n |  | TRUE
135 | bus_MV_26_0_node_175 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_181-3_0_4_load_0 | 0 | 0.0017051 | 0.00042735 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_181-3_0_4_load_3 | 3 | 0.00057398 | 0.00014385 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_181-3_0_4_load_252 | 5 | 0.00045863 | 0.00011494 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_181-3_0_4_load_67 | 7 | 0.0028331 | 0.00071005 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_181-3_0_4_load_103 | 10 | 0.0036052 | 0.00090354 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_181-3_0_4_load_64 | 12 | 0.010864 | 0.0027228 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_181-3_0_4_load_35 | 15 | 0.00032583 | 8.166e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_181-3_0_4_load_113 | 16 | 0.00031373 | 7.8629e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_181-3_0_4_load_135 | 19 | 0.0010018 | 0.00025107 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_181-3_0_4_load_85 | 20 | 0.0022026 | 0.00055202 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_181-3_0_4_load_76 | 23 | 0.0087306 | 0.0021881 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_181-3_0_4_load_24 | 24 | 0.0020915 | 0.00052417 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_181-3_0_4_load_22 | 25 | 0.0051538 | 0.0012917 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_181-3_0_4_load_89 | 26 | 0.0015126 | 0.0003791 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_181-3_0_4_load_131 | 29 | 0.00021036 | 5.2721e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_181-3_0_4_load_66 | 31 | 0.021103 | 0.005289 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_181-3_0_4_load_147 | 35 | 0.0011411 | 0.00028599 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_181-3_0_4_load_119 | 37 | 0.00037325 | 9.3544e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_181-3_0_4_load_118 | 38 | 0.0012619 | 0.00031626 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_181-3_0_4_load_152 | 39 | 0.00073249 | 0.00018358 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_181-3_0_4_load_139 | 40 | 0.002244 | 0.00056241 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_181-3_0_4_load_124 | 41 | 0.00084486 | 0.00021174 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_181-3_0_4_load_42 | 43 | 0.0021351 | 0.0005351 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_181-3_0_4_load_112 | 45 | 0.00013129 | 3.2905e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_181-3_0_4_load_36 | 47 | 0.0017377 | 0.00043551 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_181-3_0_4_load_117 | 48 | 0.00036919 | 9.2528e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_181-3_0_4_load_133 | 50 | 0.00015373 | 3.8529e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_181-3_0_4_load_123 | 51 | 0.0011137 | 0.00027911 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_181-3_0_4_load_122 | 52 | 0.00013498 | 3.383e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_181-3_0_4_load_130 | 53 | 0.00012685 | 3.1792e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_181-3_0_4_load_126 | 54 | 0.00010788 | 2.7038e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_181-3_0_4_load_37 | 55 | 0.0060803 | 0.0015239 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_181-3_0_4_load_38 | 56 | 0.0076116 | 0.0019076 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_181-3_0_4_load_108 | 60 | 0.0020274 | 0.00050812 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_181-3_0_4_load_109 | 62 | 0.0075761 | 0.0018987 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_181-3_0_4_load_269 | 63 | 0.0026158 | 0.00065557 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_181-3_0_4_load_265 | 65 | 0.0038311 | 0.00096015 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_181-3_0_4_load_264 | 66 | 0.0026704 | 0.00066926 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_181-3_0_4_load_71 | 68 | 0.0029 | 0.00072681 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_181-3_0_4_load_111 | 70 | 0.00029433 | 7.3766e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_181-3_0_4_load_110 | 71 | 0.006989 | 0.0017516 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_181-3_0_4_load_50 | 73 | 0.0054946 | 0.0013771 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_181-3_0_4_load_47 | 74 | 0.0051259 | 0.0012847 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_181-3_0_4_load_91 | 77 | 0.0006465 | 0.00016203 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_181-3_0_4_load_43 | 78 | 0.0058687 | 0.0014708 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_181-3_0_4_load_69 | 80 | 0.018294 | 0.0045848 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_181-3_0_4_load_77 | 83 | 0.0024924 | 0.00062466 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_181-3_0_4_load_81 | 84 | 0.0025708 | 0.00064431 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_181-3_0_4_load_128 | 85 | 0.0012039 | 0.00030174 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_181-3_0_4_load_125 | 86 | 0.00011141 | 2.7923e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_181-3_0_4_load_78 | 87 | 0.0017161 | 0.0004301 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_181-3_0_4_load_57 | 88 | 0.0010547 | 0.00026434 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_181-3_0_4_load_99 | 90 | 0.0019448 | 0.00048741 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_181-3_0_4_load_95 | 91 | 0.00076163 | 0.00019088 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_181-3_0_4_load_92 | 92 | 0.0033608 | 0.0008423 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_181-3_0_4_load_90 | 93 | 0.00046226 | 0.00011585 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_181-3_0_4_load_58 | 94 | 0.013604 | 0.0034096 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_181-3_0_4_load_62 | 96 | 0.0054336 | 0.0013618 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_181-3_0_4_load_63 | 97 | 0.0016905 | 0.00042367 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_181-3_0_4_load_61 | 98 | 0.0083855 | 0.0021016 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_181-3_0_4_load_83 | 99 | 0.0017612 | 0.00044141 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_181-3_0_4_load_86 | 101 | 0.0034295 | 0.00085952 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_181-3_0_4_load_82 | 102 | 0.0020091 | 0.00050352 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_181-3_0_4_load_73 | 103 | 0.0038292 | 0.00095969 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_181-3_0_4_load_266 | 106 | 0.0041283 | 0.0010347 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_181-3_0_4_load_94 | 107 | 0.0024484 | 0.00061362 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_181-3_0_4_load_105 | 109 | 0.00077639 | 0.00019458 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_181-3_0_4_load_97 | 110 | 0.0023303 | 0.00058403 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_181-3_0_4_load_98 | 111 | 0.0018314 | 0.00045898 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_181-3_0_4_load_129 | 112 | 0.0051281 | 0.0012852 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_181-3_0_4_load_106 | 113 | 0.0031966 | 0.00080115 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_181-3_0_4_load_107 | 114 | 0.00092954 | 0.00023297 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_181-3_0_4_load_115 | 115 | 0.0031641 | 0.00079301 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_181-3_0_4_load_146 | 116 | 0.00080488 | 0.00020172 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_181-3_0_4_load_120 | 117 | 0.0011455 | 0.00028709 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_181-3_0_4_load_263 | 120 | 0.00087588 | 0.00021952 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_181-3_0_4_load_261 | 121 | 0.0011782 | 0.00029527 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_181-3_0_4_load_137 | 122 | 0.0001822 | 4.5664e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_181-3_0_4_load_150 | 124 | 0.00052194 | 0.00013081 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_181-3_0_4_load_144 | 125 | 0.00034399 | 8.6213e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_181-3_0_4_load_140 | 126 | 0.00096496 | 0.00024184 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_181-3_0_4_load_141 | 127 | 0.00063941 | 0.00016025 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_181-3_0_4_load_142 | 128 | 0.00075697 | 0.00018971 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_181-3_0_4_load_143 | 129 | 0.00016629 | 4.1676e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_181-3_0_4_load_145 | 130 | 0.00093888 | 0.00023531 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_181-3_0_4_load_151 | 131 | 0.0011571 | 0.00029 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_181-3_0_4_load_148 | 132 | 0.0012835 | 0.00032167 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_181-3_0_4_load_149 | 133 | 0.00036981 | 9.2683e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_181-3_0_4_load_153 | 134 | 0.0043249 | 0.0010839 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_181-3_0_4_line_0 |  | 0 | 1 | 0.0077257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_181-3_0_4_line_1 |  | 0 | 2 | 0.024788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_181-3_0_4_line_2 |  | 1 | 3 | 0.011643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_181-3_0_4_line_3 |  | 2 | 4 | 0.8499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_181-3_0_4_line_4 |  | 3 | 5 | 0.034618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_181-3_0_4_line_5 |  | 4 | 11 | 0.08704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_181-3_0_4_line_6 |  | 4 | 12 | 0.011513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_181-3_0_4_line_7 |  | 4 | 6 | 0.031316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_181-3_0_4_line_8 |  | 6 | 7 | 0.012691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_181-3_0_4_line_9 |  | 8 | 9 | 0.024827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_181-3_0_4_line_10 |  | 8 | 10 | 0.072046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_181-3_0_4_line_11 |  | 9 | 11 | 0.031475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_181-3_0_4_line_12 |  | 9 | 26 | 0.0067982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_181-3_0_4_line_13 |  | 10 | 30 | 0.012462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_181-3_0_4_line_14 |  | 11 | 31 | 0.036431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_181-3_0_4_line_15 |  | 13 | 14 | 0.02131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_181-3_0_4_line_16 |  | 13 | 15 | 0.015269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_181-3_0_4_line_17 |  | 14 | 16 | 0.035197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_181-3_0_4_line_18 |  | 15 | 32 | 0.0081088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_181-3_0_4_line_19 |  | 17 | 18 | 0.13719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_181-3_0_4_line_20 |  | 17 | 19 | 0.037347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_181-3_0_4_line_21 |  | 18 | 20 | 0.014002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_181-3_0_4_line_22 |  | 18 | 21 | 0.14111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_181-3_0_4_line_23 |  | 18 | 22 | 0.032881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_181-3_0_4_line_24 |  | 18 | 23 | 0.024833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_181-3_0_4_line_25 |  | 19 | 36 | 0.017441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_181-3_0_4_line_26 |  | 20 | 41 | 0.016273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_181-3_0_4_line_27 |  | 21 | 24 | 0.054301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_181-3_0_4_line_28 |  | 21 | 25 | 0.018681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_181-3_0_4_line_29 |  | 22 | 42 | 0.039141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_181-3_0_4_line_30 |  | 22 | 43 | 0.010746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_181-3_0_4_line_31 |  | 23 | 44 | 0.014527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_181-3_0_4_line_32 |  | 24 | 45 | 0.00028285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_181-3_0_4_line_33 |  | 25 | 32 | 0.024386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_181-3_0_4_line_34 |  | 26 | 46 | 0.0095467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_181-3_0_4_line_35 |  | 27 | 28 | 0.086739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_181-3_0_4_line_36 |  | 27 | 29 | 0.0056093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_181-3_0_4_line_37 |  | 28 | 53 | 0.029411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_181-3_0_4_line_38 |  | 28 | 54 | 0.015214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_181-3_0_4_line_39 |  | 29 | 49 | 0.011857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_181-3_0_4_line_40 |  | 30 | 108 | 0.058824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_181-3_0_4_line_41 |  | 30 | 76 | 0.029096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_181-3_0_4_line_42 |  | 32 | 47 | 0.032874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_181-3_0_4_line_43 |  | 33 | 34 | 0.026449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_181-3_0_4_line_44 |  | 33 | 35 | 0.073662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_181-3_0_4_line_45 |  | 34 | 115 | 0.039292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_181-3_0_4_line_46 |  | 34 | 48 | 0.020751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_181-3_0_4_line_47 |  | 35 | 116 | 0.031403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_181-3_0_4_line_48 |  | 36 | 122 | 0.018419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_181-3_0_4_line_49 |  | 36 | 123 | 0.072434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_181-3_0_4_line_50 |  | 36 | 40 | 0.05667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_181-3_0_4_line_51 |  | 37 | 38 | 0.024175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_181-3_0_4_line_52 |  | 38 | 117 | 0.44354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_181-3_0_4_line_53 |  | 39 | 40 | 0.025624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_181-3_0_4_line_54 |  | 41 | 104 | 0.0049873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_181-3_0_4_line_55 |  | 42 | 82 | 0.023002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_181-3_0_4_line_56 |  | 42 | 83 | 0.028004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_181-3_0_4_line_57 |  | 43 | 78 | 0.041449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_181-3_0_4_line_58 |  | 44 | 103 | 0.022461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_181-3_0_4_line_59 |  | 46 | 89 | 0.032873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_181-3_0_4_line_60 |  | 46 | 101 | 0.038384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_181-3_0_4_line_61 |  | 47 | 48 | 0.0168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_181-3_0_4_line_62 |  | 49 | 50 | 0.029318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_181-3_0_4_line_63 |  | 50 | 70 | 0.025352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_181-3_0_4_line_64 |  | 51 | 52 | 0.047098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_181-3_0_4_line_65 |  | 52 | 104 | 0.02034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_181-3_0_4_line_66 |  | 53 | 112 | 0.014025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_181-3_0_4_line_67 |  | 54 | 86 | 0.023622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_181-3_0_4_line_68 |  | 55 | 56 | 0.024321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_181-3_0_4_line_69 |  | 55 | 57 | 0.016353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_181-3_0_4_line_70 |  | 56 | 58 | 0.014141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_181-3_0_4_line_71 |  | 57 | 59 | 0.00121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_181-3_0_4_line_72 |  | 58 | 60 | 0.017532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_181-3_0_4_line_73 |  | 58 | 61 | 0.021869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_181-3_0_4_line_74 |  | 59 | 62 | 0.014405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_181-3_0_4_line_75 |  | 60 | 63 | 0.0017227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_181-3_0_4_line_76 |  | 61 | 67 | 0.035893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_181-3_0_4_line_77 |  | 61 | 68 | 0.01117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_181-3_0_4_line_78 |  | 61 | 64 | 0.069963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_181-3_0_4_line_79 |  | 64 | 65 | 0.01072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_181-3_0_4_line_80 |  | 64 | 66 | 0.017906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_181-3_0_4_line_81 |  | 65 | 105 | 0.0027228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_181-3_0_4_line_82 |  | 67 | 90 | 0.01192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_181-3_0_4_line_83 |  | 67 | 73 | 0.021674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_181-3_0_4_line_84 |  | 68 | 96 | 0.0084188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_181-3_0_4_line_85 |  | 69 | 70 | 0.10618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_181-3_0_4_line_86 |  | 69 | 71 | 0.054295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_181-3_0_4_line_87 |  | 72 | 73 | 0.0010939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_181-3_0_4_line_88 |  | 72 | 74 | 0.030365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_181-3_0_4_line_89 |  | 75 | 76 | 0.026319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_181-3_0_4_line_90 |  | 75 | 77 | 0.0176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_181-3_0_4_line_91 |  | 76 | 91 | 0.022839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_181-3_0_4_line_92 |  | 77 | 92 | 0.012056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_181-3_0_4_line_93 |  | 78 | 79 | 0.019365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_181-3_0_4_line_94 |  | 79 | 80 | 0.015527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_181-3_0_4_line_95 |  | 79 | 81 | 0.048905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_181-3_0_4_line_96 |  | 81 | 84 | 0.030447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_181-3_0_4_line_97 |  | 82 | 85 | 0.018145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_181-3_0_4_line_98 |  | 82 | 86 | 0.026162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_181-3_0_4_line_99 |  | 83 | 87 | 0.010932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_181-3_0_4_line_100 |  | 84 | 102 | 0.0067708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_181-3_0_4_line_101 |  | 87 | 105 | 0.025097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_181-3_0_4_line_102 |  | 88 | 89 | 0.042507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_181-3_0_4_line_103 |  | 89 | 93 | 0.023375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_181-3_0_4_line_104 |  | 90 | 111 | 0.024654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_181-3_0_4_line_105 |  | 93 | 107 | 0.007373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_181-3_0_4_line_106 |  | 94 | 95 | 0.026888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_181-3_0_4_line_107 |  | 95 | 96 | 0.020038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_181-3_0_4_line_108 |  | 95 | 97 | 0.0021169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_181-3_0_4_line_109 |  | 97 | 100 | 0.028575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_181-3_0_4_line_110 |  | 98 | 99 | 0.0238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_181-3_0_4_line_111 |  | 99 | 100 | 0.012194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_181-3_0_4_line_112 |  | 100 | 101 | 0.0038673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_181-3_0_4_line_113 |  | 105 | 106 | 0.027668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_181-3_0_4_line_114 |  | 108 | 109 | 0.006162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_181-3_0_4_line_115 |  | 109 | 113 | 0.12812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_181-3_0_4_line_116 |  | 110 | 111 | 0.026929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_181-3_0_4_line_117 |  | 113 | 114 | 0.021321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_181-3_0_4_line_118 |  | 116 | 132 | 0.15599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_181-3_0_4_line_119 |  | 117 | 118 | 0.02771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_181-3_0_4_line_120 |  | 118 | 119 | 0.057386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_181-3_0_4_line_121 |  | 119 | 120 | 0.21809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_181-3_0_4_line_122 |  | 119 | 121 | 0.046524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_181-3_0_4_line_123 |  | 121 | 134 | 0.039726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_181-3_0_4_line_124 |  | 123 | 124 | 0.024294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_181-3_0_4_line_125 |  | 124 | 125 | 0.016402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_181-3_0_4_line_126 |  | 125 | 128 | 0.0067648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_181-3_0_4_line_127 |  | 126 | 127 | 0.006215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_181-3_0_4_line_128 |  | 126 | 128 | 0.0081198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_181-3_0_4_line_129 |  | 127 | 129 | 0.0057893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_181-3_0_4_line_130 |  | 129 | 130 | 0.022557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_181-3_0_4_line_131 |  | 130 | 131 | 0.0019976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_181-3_0_4_line_132 |  | 132 | 133 | 0.27914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_181-3_0_4_line_133 |  | 133 | 134 | 0.011698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_181-3_0_4_trafo_46 | 0.63 MVA 20/0.4 kV | 135 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2707029.2612 | 1251951.2352 | 2707027.8328 | 1251954.6677 | 2707026.3981 | 1251958.41
1 | 2707015.9979 | 1251980.8864 | 2707023.8954 | 1251964.9383 | 2707026.3981 | 1251958.41
2 | 2707029.2612 | 1251951.2352 | 2707018.4793 | 1251946.8409
3 | 2706495.089 | 1252601.9059 | 2706498.2185 | 1252594.9343 | 2706481.77 | 1252584.9416 | 2706504.4043 | 1252557.3705 | 2706537.5431 | 1252521.5482 | 2706560.6926 | 1252496.4108 | 2706573.5017 | 1252480.8952 | 2706599.7529 | 1252444.0708 | 2706629.2185 | 1252400.6213 | 2706641.2382 | 1252383.2791 | 2706664.6127 | 1252346.9592 | 2706675.6717 | 1252325.9745 | 2706686.6538 | 1252300.0401 | 2706699.0032 | 1252264.4224 | 2706707.3702 | 1252245.3909 | 2706712.7485 | 1252235.5465 | 2706723.2273 | 1252218.2878 | 2706737.8192 | 1252199.8246 | 2706749.7099 | 1252186.3278 | 2706765.3628 | 1252172.2428 | 2706790.5613 | 1252153.326 | 2706833.7874 | 1252124.7042 | 2706965.2429 | 1252038.3834 | 2706977.6151 | 1252028.3652 | 2706988.8829 | 1252017.6377 | 2707001.7129 | 1252002.7573 | 2707011.546 | 1251988.3009 | 2707015.9979 | 1251980.8864
4 | 2707017.3248 | 1251917.4466 | 2707009.9999 | 1251937.6874 | 2707011.4812 | 1251941.3505 | 2707014.9858 | 1251945.4171 | 2707018.4793 | 1251946.8409
5 | 2706495.089 | 1252601.9059 | 2706477.9653 | 1252608.8927 | 2706432.7745 | 1252660.6006
6 | 2706495.089 | 1252601.9059 | 2706492.1626 | 1252608.9146 | 2706489.9565 | 1252612.1527
7 | 2706495.089 | 1252601.9059 | 2706498.2185 | 1252594.9343 | 2706505.7083 | 1252589.3532 | 2706509.6773 | 1252575.5801
8 | 2706509.6773 | 1252575.5801 | 2706512.688 | 1252576.8908 | 2706521.0194 | 1252581.2599
9 | 2706407.1905 | 1252669.2369 | 2706417.1594 | 1252657.5843 | 2706409.9257 | 1252651.4383
10 | 2706409.9257 | 1252651.4383 | 2706386.1487 | 1252646.4628 | 2706376.682 | 1252646.137 | 2706352.7825 | 1252650.0778 | 2706342.4218 | 1252650.3587 | 2706338.9311 | 1252649.1476
11 | 2706407.1905 | 1252669.2369 | 2706411.655 | 1252672.8089 | 2706422.3742 | 1252661.8258 | 2706432.7745 | 1252660.6006
12 | 2706407.1905 | 1252669.2369 | 2706402.4844 | 1252674.1429
13 | 2706328.4044 | 1252642.8455 | 2706333.938 | 1252647.4152 | 2706338.9311 | 1252649.1476
14 | 2706432.7745 | 1252660.6006 | 2706433.2508 | 1252666.4361 | 2706439.971 | 1252678.4666 | 2706454.6987 | 1252686.541
15 | 2706660.0382 | 1252846.7724 | 2706660.7355 | 1252851.6333 | 2706661.7903 | 1252855.0885 | 2706664.5977 | 1252861.8111 | 2706667.4032 | 1252866.5433
16 | 2706660.0382 | 1252846.7724 | 2706675.1083 | 1252849.2301
17 | 2706667.4032 | 1252866.5433 | 2706663.8232 | 1252876.7316 | 2706663.8694 | 1252880.8691 | 2706663.7551 | 1252890.1413 | 2706659.0074 | 1252900.0503
18 | 2706683.1115 | 1252850.5353 | 2706675.1083 | 1252849.2301
19 | 2706607.8575 | 1252748.9091 | 2706611.3586 | 1252749.8061 | 2706644.5846 | 1252754.3745 | 2706646.8456 | 1252754.5598 | 2706653.1898 | 1252754.7519 | 2706659.3799 | 1252753.8626 | 2706669.4508 | 1252748.295 | 2706679.0726 | 1252740.4285 | 2706685.9654 | 1252731.1228 | 2706688.682 | 1252724.4552 | 2706691.3913 | 1252717.7763 | 2706712.4768 | 1252721.7148 | 2706726.2332 | 1252722.7301
20 | 2706726.2332 | 1252722.7301 | 2706747.2469 | 1252725.2107 | 2706760.4843 | 1252726.5503 | 2706763.3666 | 1252726.5218
21 | 2706607.8575 | 1252748.9091 | 2706607.0513 | 1252762.8877
22 | 2706607.8575 | 1252748.9091 | 2706611.3586 | 1252749.8061 | 2706644.5846 | 1252754.3745 | 2706646.8456 | 1252754.5598 | 2706653.1898 | 1252754.7519 | 2706659.3799 | 1252753.8626 | 2706660.3103 | 1252759.1949 | 2706660.0557 | 1252795.531 | 2706660.0176 | 1252801.8354 | 2706659.9638 | 1252809.0069 | 2706659.8937 | 1252819.6032 | 2706672.3821 | 1252820.6066 | 2706683.0569 | 1252821.7331
23 | 2706574.9361 | 1252747.5379 | 2706589.0448 | 1252747.4361 | 2706607.8575 | 1252748.9091
24 | 2706607.8575 | 1252748.9091 | 2706611.5763 | 1252731.4284 | 2706612.8074 | 1252724.5772
25 | 2706780.8066 | 1252726.3497 | 2706763.3666 | 1252726.5218
26 | 2706606.1144 | 1252779.1333 | 2706607.0513 | 1252762.8877
27 | 2706683.0569 | 1252821.7331 | 2706696.761 | 1252769.1896
28 | 2706683.0569 | 1252821.7331 | 2706691.0595 | 1252826.2253 | 2706695.9469 | 1252834.3755
29 | 2706535.8678 | 1252751.3717 | 2706561.4185 | 1252748.7735 | 2706574.9361 | 1252747.5379
30 | 2706574.9361 | 1252747.5379 | 2706574.7025 | 1252744.1643 | 2706574.5386 | 1252738.1787 | 2706574.7888 | 1252736.8256
31 | 2706615.3764 | 1252710.2796 | 2706612.8074 | 1252724.5772
32 | 2706696.8324 | 1252768.9159 | 2706696.761 | 1252769.1896
33 | 2706683.1115 | 1252850.5353 | 2706690.9211 | 1252849.8198 | 2706692.873 | 1252846.6301 | 2706695.8684 | 1252838.7332 | 2706695.9469 | 1252834.3755
34 | 2706395.8756 | 1252681.0322 | 2706402.4844 | 1252674.1429
35 | 2706539.9752 | 1252838.1051 | 2706539.2138 | 1252913.9642 | 2706537.5111 | 1252924.6979
36 | 2706537.5111 | 1252924.6979 | 2706534.6226 | 1252929.5063
37 | 2706539.9752 | 1252838.1051 | 2706510.6192 | 1252839.9082
38 | 2706539.9752 | 1252838.1051 | 2706540.1292 | 1252822.8915
39 | 2706528.5167 | 1252939.6706 | 2706534.6226 | 1252929.5063
40 | 2706328.4044 | 1252642.8455 | 2706324.3423 | 1252634.9328 | 2706322.466 | 1252625.5137 | 2706323.2477 | 1252618.1329 | 2706325.9209 | 1252610.9194 | 2706337.33 | 1252588.417
41 | 2706328.4044 | 1252642.8455 | 2706324.5607 | 1252650.0935 | 2706318.8933 | 1252670.2082
42 | 2706683.1115 | 1252850.5353 | 2706692.0992 | 1252858.9929 | 2706711.2469 | 1252866.4054
43 | 2706737.7034 | 1252889.8951 | 2706736.562 | 1252893.7555 | 2706721.2315 | 1252910.1593
44 | 2706721.2315 | 1252910.1593 | 2706727.6119 | 1252914.6112 | 2706746.7311 | 1252921.6614 | 2706761.7498 | 1252924.6456 | 2706785.7286 | 1252928.8145 | 2706791.5608 | 1252928.3128
45 | 2706737.7034 | 1252889.8951 | 2706750.8469 | 1252885.9509 | 2706754.9713 | 1252882.8338 | 2706758.8356 | 1252862.8035
46 | 2706737.7034 | 1252889.8951 | 2706735.5624 | 1252882.2169 | 2706726.3441 | 1252873.3658
47 | 2706821.0817 | 1252918.4308 | 2706809.5931 | 1252923.8406 | 2706798.1258 | 1252927.7482 | 2706791.5608 | 1252928.3128
48 | 2706780.8066 | 1252726.3497 | 2706777.4808 | 1252744.4659
49 | 2706780.8066 | 1252726.3497 | 2706782.3152 | 1252726.3991 | 2706790.2159 | 1252726.0857 | 2706806.3175 | 1252723.0402 | 2706829.2914 | 1252717.6945 | 2706836.2339 | 1252716.9412 | 2706846.469 | 1252718.1824 | 2706852.0548 | 1252720.2515
50 | 2706780.8066 | 1252726.3497 | 2706783.487 | 1252707.0489 | 2706782.4374 | 1252696.6104 | 2706779.0119 | 1252691.5223 | 2706759.7695 | 1252684.2833
51 | 2706808.5342 | 1253035.2862 | 2706799.4367 | 1253039.9966 | 2706787.1798 | 1253046.6167
52 | 2707232.9734 | 1253036.2526 | 2707228.592 | 1253036.1677 | 2707204.3299 | 1253034.3382 | 2707190.8055 | 1253033.4706 | 2707180.7025 | 1253034.5553 | 2707164.6402 | 1253037.9675 | 2707136.4614 | 1253044.8746 | 2707120.8029 | 1253048.4944 | 2707106.4904 | 1253049.8924 | 2707059.715 | 1253051.3703 | 2707042.101 | 1253050.8628 | 2707027.7801 | 1253048.5466 | 2707001.1008 | 1253042.6599 | 2706965.1358 | 1253034.3925 | 2706944.8941 | 1253028.0998 | 2706909.5803 | 1253015.1074 | 2706883.3304 | 1253005.07 | 2706867.929 | 1253001.9785 | 2706858.7005 | 1253002.7015 | 2706850.9229 | 1253006.253 | 2706826.6656 | 1253025.8983 | 2706808.5342 | 1253035.2862
53 | 2706735.7867 | 1252675.2609 | 2706759.7695 | 1252684.2833
54 | 2706605.8272 | 1252784.1123 | 2706606.1144 | 1252779.1333
55 | 2706542.468 | 1252773.4083 | 2706539.4566 | 1252762.9123 | 2706537.1914 | 1252755.8325 | 2706535.8678 | 1252751.3717
56 | 2706535.8678 | 1252751.3717 | 2706508.2499 | 1252756.0048
57 | 2706578.0201 | 1252695.5876 | 2706576.8381 | 1252725.7433 | 2706574.7888 | 1252736.8256
58 | 2706615.3764 | 1252710.2796 | 2706618.3414 | 1252688.0156
59 | 2706395.8756 | 1252681.0322 | 2706373.9013 | 1252705.5353
60 | 2706395.8756 | 1252681.0322 | 2706399.0223 | 1252684.4359 | 2706402.2841 | 1252692.768 | 2706401.3816 | 1252717.5522
61 | 2706726.3441 | 1252873.3658 | 2706724.3966 | 1252871.4959 | 2706711.2469 | 1252866.4054
62 | 2706528.5167 | 1252939.6706 | 2706522.472 | 1252943.3983 | 2706514.4393 | 1252943.9321 | 2706500.3044 | 1252944.8727
63 | 2706500.3044 | 1252944.8727 | 2706475.0086 | 1252946.5562
64 | 2706602.4882 | 1252804.1768 | 2706599.2849 | 1252823.4266 | 2706598.2787 | 1252830.6811 | 2706595.6503 | 1252850.7696
65 | 2706605.8272 | 1252784.1123 | 2706602.4882 | 1252804.1768
66 | 2706510.6192 | 1252839.9082 | 2706496.6206 | 1252840.768
67 | 2706541.7653 | 1252799.3929 | 2706540.2757 | 1252808.4085 | 2706540.1292 | 1252822.8915
68 | 2706380.1451 | 1252843.9298 | 2706386.4534 | 1252831.5299 | 2706390.3734 | 1252823.8162 | 2706391.1696 | 1252822.2505
69 | 2706372.7301 | 1252858.5054 | 2706380.1451 | 1252843.9298
70 | 2706397.5795 | 1252809.6452 | 2706391.1696 | 1252822.2505
71 | 2706372.1823 | 1252859.5853 | 2706372.7301 | 1252858.5054
72 | 2706397.5795 | 1252809.6452 | 2706411.3755 | 1252816.0092 | 2706413.4691 | 1252817.0523
73 | 2706397.5795 | 1252809.6452 | 2706405.5611 | 1252796.4222 | 2706403.5761 | 1252794.3182 | 2706401.6824 | 1252791.3373
74 | 2706372.1823 | 1252859.5853 | 2706362.7153 | 1252870.4426
75 | 2706415.0111 | 1252817.8205 | 2706413.4691 | 1252817.0523
76 | 2706401.6824 | 1252791.3373 | 2706395.0217 | 1252792.7967 | 2706375.3986 | 1252799.0494 | 2706367.591 | 1252802.5899
77 | 2706401.6824 | 1252791.3373 | 2706400.1325 | 1252786.8614 | 2706399.5769 | 1252784.1826 | 2706399.0818 | 1252780.5183
78 | 2706401.6824 | 1252791.3373 | 2706403.5761 | 1252794.3182 | 2706405.5611 | 1252796.4222 | 2706415.57 | 1252785.0483 | 2706428.7116 | 1252777.4337 | 2706436.8653 | 1252773.9551 | 2706443.9614 | 1252771.3694 | 2706449.6899 | 1252769.2817 | 2706455.4034 | 1252767.1938 | 2706459.7767 | 1252765.7601
79 | 2706459.7767 | 1252765.7601 | 2706470.1705 | 1252763.1359
80 | 2706459.7767 | 1252765.7601 | 2706462.3034 | 1252783.4866
81 | 2706472.8104 | 1252762.4694 | 2706470.1705 | 1252763.1359
82 | 2706367.591 | 1252802.5899 | 2706368.4878 | 1252790.7032
83 | 2706367.591 | 1252802.5899 | 2706347.8509 | 1252811.5402
84 | 2706399.325 | 1252772.1106 | 2706399.0106 | 1252779.9912 | 2706399.0818 | 1252780.5183
85 | 2706373.303 | 1252960.1873 | 2706431.3803 | 1252963.1661 | 2706441.4191 | 1252958.9319 | 2706447.7855 | 1252954.5205 | 2706457.614 | 1252947.7138 | 2706475.0086 | 1252946.5562
86 | 2706373.303 | 1252960.1873 | 2706371.9837 | 1252946.6637 | 2706380.3223 | 1252922.3826 | 2706387.8524 | 1252909.3698
87 | 2706346.8546 | 1252811.9919 | 2706347.8509 | 1252811.5402
88 | 2706346.8546 | 1252811.9919 | 2706328.6911 | 1252787.6583
89 | 2706304.9202 | 1252692.1753 | 2706312.1956 | 1252683.8101 | 2706316.0034 | 1252677.718 | 2706317.9472 | 1252672.8711 | 2706318.8933 | 1252670.2082
90 | 2706304.9202 | 1252692.1753 | 2706318.2508 | 1252703.667
91 | 2706318.8933 | 1252670.2082 | 2706340.0946 | 1252678.7017
92 | 2706327.382 | 1252711.5385 | 2706318.2508 | 1252703.667
93 | 2706578.7785 | 1252676.2379 | 2706578.0201 | 1252695.5876
94 | 2706578.7785 | 1252676.2379 | 2706578.1445 | 1252660.725
95 | 2706578.7785 | 1252676.2379 | 2706529.8766 | 1252672.422
96 | 2706529.8766 | 1252672.422 | 2706526.5383 | 1252696.8707 | 2706523.4242 | 1252701.7298
97 | 2706560.2683 | 1252769.9034 | 2706554.5279 | 1252770.9677 | 2706551.7084 | 1252772.0401 | 2706542.468 | 1252773.4083
98 | 2706542.468 | 1252773.4083 | 2706543.4338 | 1252779.2972 | 2706542.7745 | 1252793.2856 | 2706541.7653 | 1252799.3929
99 | 2706508.2499 | 1252756.0048 | 2706497.4688 | 1252757.8135
100 | 2706517.4456 | 1252700.5102 | 2706521.331 | 1252702.7041 | 2706523.4242 | 1252701.7298
101 | 2706472.8104 | 1252762.4694 | 2706488.5136 | 1252759.3158 | 2706497.4688 | 1252757.8135
102 | 2706373.9013 | 1252705.5353 | 2706345.5134 | 1252737.173
103 | 2706373.9013 | 1252705.5353 | 2706355.6417 | 1252690.9418
104 | 2706368.4878 | 1252790.7032 | 2706370.3427 | 1252766.1193
105 | 2706352.9914 | 1252684.2427 | 2706353.6783 | 1252688.0247 | 2706355.4402 | 1252690.7808 | 2706355.6417 | 1252690.9418
106 | 2706400.1235 | 1252752.0885 | 2706426.9901 | 1252753.1579
107 | 2706400.1235 | 1252752.0885 | 2706399.325 | 1252772.1106
108 | 2706400.1235 | 1252752.0885 | 2706400.2006 | 1252749.973
109 | 2706401.2409 | 1252721.417 | 2706400.2006 | 1252749.973
110 | 2706436.4053 | 1252720.6645 | 2706421.831 | 1252719.7521 | 2706417.9429 | 1252722.3288 | 2706413.4172 | 1252722.0817
111 | 2706401.2409 | 1252721.417 | 2706413.4172 | 1252722.0817
112 | 2706401.2409 | 1252721.417 | 2706401.3816 | 1252717.5522
113 | 2706472.8104 | 1252762.4694 | 2706469.8073 | 1252747.3142 | 2706474.9132 | 1252736.2136
114 | 2706337.33 | 1252588.417 | 2706339.9095 | 1252582.8209
115 | 2706339.9095 | 1252582.8209 | 2706344.4065 | 1252573.0649 | 2706349.7502 | 1252555.0128 | 2706351.3484 | 1252544.1993 | 2706351.9855 | 1252484.7847 | 2706350.9103 | 1252472.789 | 2706348.4186 | 1252456.8261
116 | 2706370.3427 | 1252766.1193 | 2706371.1972 | 1252754.7935 | 2706360.0546 | 1252743.9167
117 | 2706343.7077 | 1252436.0429 | 2706344.234 | 1252438.1188 | 2706347.8642 | 1252453.274 | 2706348.4186 | 1252456.8261
118 | 2706821.0817 | 1252918.4308 | 2706828.2203 | 1252915.0693 | 2706859.6268 | 1252897.8661 | 2706877.6465 | 1252891.397 | 2706892.6537 | 1252892.5131 | 2706918.2717 | 1252898.28 | 2706936.0678 | 1252902.1044 | 2706969.7044 | 1252902.0685
119 | 2707260.6554 | 1253035.6477 | 2707246.2392 | 1253036.5096 | 2707232.9734 | 1253036.2526
120 | 2707317.8051 | 1253035.2045 | 2707313.3333 | 1253036.658 | 2707304.4732 | 1253035.3742 | 2707290.8542 | 1253034.3156 | 2707270.1649 | 1253034.8303 | 2707260.6554 | 1253035.6477
121 | 2707446.9174 | 1252995.8014 | 2707452.4294 | 1253001.4949 | 2707461.4174 | 1253004.4603 | 2707469.6622 | 1253005.5441 | 2707477.2589 | 1253008.2397 | 2707481.7037 | 1253010.3554 | 2707482.8765 | 1253013.1011 | 2707482.0816 | 1253016.1447 | 2707478.4303 | 1253020.6266 | 2707474.6635 | 1253021.9038 | 2707466.7537 | 1253022.7387 | 2707456.2541 | 1253024.0494 | 2707452.0858 | 1253025.4082 | 2707445.5547 | 1253027.2134 | 2707438.6624 | 1253027.7111 | 2707432.611 | 1253028.0349 | 2707419.5814 | 1253029.4332 | 2707412.4674 | 1253031.7505 | 2707409.0815 | 1253032.8344 | 2707377.5087 | 1253048.3303 | 2707365.7802 | 1253049.9858 | 2707354.008 | 1253045.7245 | 2707336.6476 | 1253039.9719 | 2707317.8051 | 1253035.2045
122 | 2707317.8051 | 1253035.2045 | 2707309.5169 | 1253030.684 | 2707294.6219 | 1253022.9857 | 2707275.438 | 1253016.298
123 | 2707275.438 | 1253016.298 | 2707273.6592 | 1253015.6779 | 2707253.0076 | 1253012.8573 | 2707243.8727 | 1253010.0785 | 2707237.68 | 1253005.9349
124 | 2706852.0548 | 1252720.2515 | 2706855.1334 | 1252721.9751 | 2706859.0076 | 1252727.7052 | 2706863.0461 | 1252740.9522
125 | 2706870.2025 | 1252755.4969 | 2706865.314 | 1252748.3913 | 2706863.0461 | 1252740.9522
126 | 2706870.2025 | 1252755.4969 | 2706874.0368 | 1252761.0701
127 | 2706880.494 | 1252765.9931 | 2706885.4364 | 1252769.7613
128 | 2706880.494 | 1252765.9931 | 2706874.0368 | 1252761.0701 | 2706874.0368 | 1252761.0701
129 | 2706890.0403 | 1252773.2713 | 2706885.4364 | 1252769.7613
130 | 2706890.0403 | 1252773.2713 | 2706892.2628 | 1252774.9658 | 2706908.805 | 1252785.7772
131 | 2706910.4772 | 1252786.8701 | 2706908.805 | 1252785.7772
132 | 2707227.8295 | 1252999.6419 | 2707216.0773 | 1252993.3062 | 2707200.0517 | 1252984.6758 | 2707182.7577 | 1252979.8256 | 2707167.4775 | 1252977.5473 | 2707118.2341 | 1252970.2286 | 2707102.8543 | 1252965.947 | 2707089.7489 | 1252960.6836 | 2706995.504 | 1252909.6836 | 2706984.3889 | 1252904.5343 | 2706969.776 | 1252902.0684 | 2706969.7044 | 1252902.0685
133 | 2707237.68 | 1253005.9349 | 2707230.1218 | 1253000.8776 | 2707227.8295 | 1252999.6419

## bus_geodata
| x | y | coords
0 | 2707026.3981 | 1251958.41
1 | 2707029.2612 | 1251951.2352
2 | 2707015.9979 | 1251980.8864
3 | 2707018.4793 | 1251946.8409
4 | 2706495.089 | 1252601.9059
5 | 2707017.3248 | 1251917.4466
6 | 2706509.6773 | 1252575.5801
7 | 2706521.0194 | 1252581.2599
8 | 2706409.9257 | 1252651.4383
9 | 2706407.1905 | 1252669.2369
10 | 2706338.9311 | 1252649.1476
11 | 2706432.7745 | 1252660.6006
12 | 2706489.9565 | 1252612.1527
13 | 2706660.0382 | 1252846.7724
14 | 2706667.4032 | 1252866.5433
15 | 2706675.1083 | 1252849.2301
16 | 2706659.0074 | 1252900.0503
17 | 2706726.2332 | 1252722.7301
18 | 2706607.8575 | 1252748.9091
19 | 2706763.3666 | 1252726.5218
20 | 2706607.0513 | 1252762.8877
21 | 2706683.0569 | 1252821.7331
22 | 2706574.9361 | 1252747.5379
23 | 2706612.8074 | 1252724.5772
24 | 2706696.761 | 1252769.1896
25 | 2706695.9469 | 1252834.3755
26 | 2706402.4844 | 1252674.1429
27 | 2706537.5111 | 1252924.6979
28 | 2706539.9752 | 1252838.1051
29 | 2706534.6226 | 1252929.5063
30 | 2706328.4044 | 1252642.8455
31 | 2706454.6987 | 1252686.541
32 | 2706683.1114 | 1252850.5353
33 | 2706721.2315 | 1252910.1593
34 | 2706737.7034 | 1252889.8951
35 | 2706791.5608 | 1252928.3128
36 | 2706780.8066 | 1252726.3497
37 | 2706787.1798 | 1253046.6167
38 | 2706808.5342 | 1253035.2862
39 | 2706735.7867 | 1252675.2609
40 | 2706759.7695 | 1252684.2833
41 | 2706606.1144 | 1252779.1333
42 | 2706535.8678 | 1252751.3717
43 | 2706574.7888 | 1252736.8256
44 | 2706615.3764 | 1252710.2796
45 | 2706696.8324 | 1252768.9159
46 | 2706395.8756 | 1252681.0322
47 | 2706711.2469 | 1252866.4054
48 | 2706726.3441 | 1252873.3658
49 | 2706528.5167 | 1252939.6706
50 | 2706500.3044 | 1252944.8727
51 | 2706595.6503 | 1252850.7696
52 | 2706602.4882 | 1252804.1768
53 | 2706510.6192 | 1252839.9082
54 | 2706540.1292 | 1252822.8915
55 | 2706380.1451 | 1252843.9298
56 | 2706391.1696 | 1252822.2505
57 | 2706372.7301 | 1252858.5054
58 | 2706397.5795 | 1252809.6452
59 | 2706372.1823 | 1252859.5853
60 | 2706413.4691 | 1252817.0523
61 | 2706401.6824 | 1252791.3373
62 | 2706362.7153 | 1252870.4426
63 | 2706415.0111 | 1252817.8205
64 | 2706459.7767 | 1252765.7601
65 | 2706470.1705 | 1252763.1359
66 | 2706462.3034 | 1252783.4866
67 | 2706367.591 | 1252802.5899
68 | 2706399.0818 | 1252780.5183
69 | 2706373.303 | 1252960.1873
70 | 2706475.0086 | 1252946.5562
71 | 2706387.8524 | 1252909.3698
72 | 2706346.8546 | 1252811.9919
73 | 2706347.8509 | 1252811.5402
74 | 2706328.6911 | 1252787.6583
75 | 2706304.9202 | 1252692.1753
76 | 2706318.8933 | 1252670.2082
77 | 2706318.2508 | 1252703.667
78 | 2706578.0201 | 1252695.5876
79 | 2706578.7785 | 1252676.2379
80 | 2706578.1445 | 1252660.725
81 | 2706529.8766 | 1252672.422
82 | 2706542.468 | 1252773.4083
83 | 2706508.2499 | 1252756.0048
84 | 2706523.4242 | 1252701.7298
85 | 2706560.2683 | 1252769.9034
86 | 2706541.7653 | 1252799.3929
87 | 2706497.4688 | 1252757.8135
88 | 2706345.5134 | 1252737.173
89 | 2706373.9013 | 1252705.5353
90 | 2706368.4878 | 1252790.7032
91 | 2706340.0946 | 1252678.7017
92 | 2706327.382 | 1252711.5385
93 | 2706355.6417 | 1252690.9418
94 | 2706426.9901 | 1252753.1579
95 | 2706400.1235 | 1252752.0885
96 | 2706399.325 | 1252772.1106
97 | 2706400.2006 | 1252749.973
98 | 2706436.4053 | 1252720.6645
99 | 2706413.4172 | 1252722.0817
100 | 2706401.2409 | 1252721.417
101 | 2706401.3816 | 1252717.5522
102 | 2706517.4456 | 1252700.5102
103 | 2706618.3414 | 1252688.0156
104 | 2706605.8272 | 1252784.1123
105 | 2706472.8104 | 1252762.4694
106 | 2706474.9132 | 1252736.2136
107 | 2706352.9914 | 1252684.2427
108 | 2706337.33 | 1252588.417
109 | 2706339.9095 | 1252582.8209
110 | 2706360.0546 | 1252743.9167
111 | 2706370.3427 | 1252766.1193
112 | 2706496.6206 | 1252840.768
113 | 2706348.4186 | 1252456.8261
114 | 2706343.7077 | 1252436.0429
115 | 2706758.8356 | 1252862.8035
116 | 2706821.0817 | 1252918.4308
117 | 2707232.9734 | 1253036.2526
118 | 2707260.6554 | 1253035.6477
119 | 2707317.8051 | 1253035.2045
120 | 2707446.9174 | 1252995.8014
121 | 2707275.438 | 1253016.298
122 | 2706777.4808 | 1252744.4659
123 | 2706852.0548 | 1252720.2515
124 | 2706863.0461 | 1252740.9522
125 | 2706870.2025 | 1252755.4969
126 | 2706880.494 | 1252765.9931
127 | 2706885.4364 | 1252769.7613
128 | 2706874.0368 | 1252761.0701
129 | 2706890.0403 | 1252773.2713
130 | 2706908.805 | 1252785.7772
131 | 2706910.4772 | 1252786.8701
132 | 2706969.7044 | 1252902.0685
133 | 2707227.8295 | 1252999.6419
134 | 2707237.68 | 1253005.9349
135 | 2706542.468 | 1252773.4083

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97228 | -0.5362 | 0.0017051 | 0.00042735
1 | 0.97227 | -0.53635 | 0 | 0
2 | 0.97234 | -0.53495 | 0 | 0
3 | 0.97226 | -0.53657 | 0.00057398 | 0.00014385
4 | 0.97451 | -0.4919 | 0 | 0
5 | 0.97224 | -0.53686 | 0.00045863 | 0.00011494
6 | 0.97443 | -0.49353 | 0 | 0
7 | 0.97439 | -0.49419 | 0.0028331 | 0.00071005
8 | 0.97663 | -0.45003 | 0 | 0
9 | 0.97694 | -0.44401 | 0 | 0
10 | 0.97574 | -0.46755 | 0.0036052 | 0.00090354
11 | 0.97584 | -0.46563 | 0 | 0
12 | 0.97439 | -0.4942 | 0.010864 | 0.0027228
13 | 0.99123 | -0.16873 | 0 | 0
14 | 0.99122 | -0.16885 | 0 | 0
15 | 0.99123 | -0.16864 | 0.00032583 | 8.166e-05
16 | 0.99121 | -0.16905 | 0.00031373 | 7.8629e-05
17 | 0.99423 | -0.11089 | 0 | 0
18 | 0.99544 | -0.087541 | 0 | 0
19 | 0.9939 | -0.11725 | 0.0010018 | 0.00025107
20 | 0.99538 | -0.0886 | 0.0022026 | 0.00055202
21 | 0.99206 | -0.15255 | 0 | 0
22 | 0.99702 | -0.057147 | 0 | 0
23 | 0.99515 | -0.093029 | 0.0087306 | 0.0021881
24 | 0.99195 | -0.15469 | 0.0020915 | 0.00052417
25 | 0.99166 | -0.16046 | 0.0051538 | 0.0012917
26 | 0.97726 | -0.43769 | 0.0015126 | 0.0003791
27 | 0.99833 | -0.032155 | 0 | 0
28 | 0.99893 | -0.020548 | 0 | 0
29 | 0.99829 | -0.032906 | 0.00021036 | 5.2721e-05
30 | 0.97563 | -0.46975 | 0 | 0
31 | 0.97512 | -0.47971 | 0.021103 | 0.005289
32 | 0.99124 | -0.16855 | 0 | 0
33 | 0.98983 | -0.19589 | 0 | 0
34 | 0.99014 | -0.18987 | 0 | 0
35 | 0.98896 | -0.21268 | 0.0011411 | 0.00028599
36 | 0.99376 | -0.11991 | 0 | 0
37 | 0.9833 | -0.32338 | 0.00037325 | 9.3544e-05
38 | 0.98331 | -0.32322 | 0.0012619 | 0.00031626
39 | 0.99359 | -0.12323 | 0.00073249 | 0.00018358
40 | 0.99361 | -0.12289 | 0.002244 | 0.00056241
41 | 0.99535 | -0.0892 | 0.00084486 | 0.00021174
42 | 1 | 0 | -0.2536 | -0.064329
43 | 0.99671 | -0.062968 | 0.0021351 | 0.0005351
44 | 0.9951 | -0.094008 | 0 | 0
45 | 0.99195 | -0.15469 | 0.00013129 | 3.2905e-05
46 | 0.97772 | -0.42857 | 0 | 0
47 | 0.99069 | -0.1791 | 0.0017377 | 0.00043551
48 | 0.99044 | -0.18398 | 0.00036919 | 9.2528e-05
49 | 0.99821 | -0.03445 | 0 | 0
50 | 0.99801 | -0.038268 | 0.00015373 | 3.8529e-05
51 | 0.99527 | -0.090681 | 0.0011137 | 0.00027911
52 | 0.99532 | -0.089757 | 0.00013498 | 3.383e-05
53 | 0.99879 | -0.023248 | 0.00012685 | 3.1792e-05
54 | 0.99911 | -0.017116 | 0.00010788 | 2.7038e-05
55 | 0.9841 | -0.30431 | 0.0060803 | 0.0015239
56 | 0.98441 | -0.29833 | 0.0076116 | 0.0019076
57 | 0.98399 | -0.30654 | 0 | 0
58 | 0.98468 | -0.29292 | 0 | 0
59 | 0.98398 | -0.3067 | 0 | 0
60 | 0.98461 | -0.29438 | 0.0020274 | 0.00050812
61 | 0.98521 | -0.28274 | 0 | 0
62 | 0.98388 | -0.30867 | 0.0075761 | 0.0018987
63 | 0.9846 | -0.29447 | 0.0026158 | 0.00065557
64 | 0.99403 | -0.11314 | 0 | 0
65 | 0.99541 | -0.086917 | 0.0038311 | 0.00096015
66 | 0.99398 | -0.11398 | 0.0026704 | 0.00066926
67 | 0.98465 | -0.29353 | 0 | 0
68 | 0.98424 | -0.30152 | 0.0029 | 0.00072681
69 | 0.99717 | -0.054508 | 0 | 0
70 | 0.99784 | -0.041502 | 0.00029433 | 7.3766e-05
71 | 0.99682 | -0.061163 | 0.006989 | 0.0017516
72 | 0.98444 | -0.29777 | 0 | 0
73 | 0.98444 | -0.29767 | 0.0054946 | 0.0013771
74 | 0.98429 | -0.30057 | 0.0051259 | 0.0012847
75 | 0.9754 | -0.47423 | 0 | 0
76 | 0.9755 | -0.4723 | 0 | 0
77 | 0.97534 | -0.47552 | 0.0006465 | 0.00016203
78 | 0.99563 | -0.083895 | 0.0058687 | 0.0014708
79 | 0.99523 | -0.091688 | 0 | 0
80 | 0.99497 | -0.096687 | 0.018294 | 0.0045848
81 | 0.99502 | -0.095632 | 0 | 0
82 | 0.9997 | -0.0057512 | 0 | 0
83 | 0.99804 | -0.036935 | 0.0024924 | 0.00062466
84 | 0.99489 | -0.098087 | 0.0025708 | 0.00064431
85 | 0.99968 | -0.0061323 | 0.0012039 | 0.00030174
86 | 0.99939 | -0.011746 | 0.00011141 | 2.7923e-05
87 | 0.99729 | -0.051154 | 0.0017161 | 0.0004301
88 | 0.97756 | -0.43177 | 0.0010547 | 0.00026434
89 | 0.9776 | -0.43095 | 0 | 0
90 | 0.98459 | -0.29484 | 0.0019448 | 0.00048741
91 | 0.97549 | -0.47262 | 0.00076163 | 0.00019088
92 | 0.9753 | -0.47626 | 0.0033608 | 0.0008423
93 | 0.97754 | -0.43219 | 0.00046226 | 0.00011585
94 | 0.98161 | -0.3527 | 0.013604 | 0.0034096
95 | 0.98194 | -0.34608 | 0 | 0
96 | 0.98353 | -0.31526 | 0.0054336 | 0.0013618
97 | 0.9818 | -0.34882 | 0.0016905 | 0.00042367
98 | 0.97965 | -0.39089 | 0.0083855 | 0.0021016
99 | 0.97983 | -0.38727 | 0.0017612 | 0.00044141
100 | 0.97995 | -0.38502 | 0 | 0
101 | 0.97973 | -0.38922 | 0.0034295 | 0.00085952
102 | 0.99488 | -0.098327 | 0.0020091 | 0.00050352
103 | 0.99502 | -0.095523 | 0.0038292 | 0.00095969
104 | 0.99534 | -0.08931 | 0 | 0
105 | 0.99559 | -0.0835 | 0 | 0
106 | 0.99548 | -0.085509 | 0.0041283 | 0.0010347
107 | 0.97752 | -0.43252 | 0.0024484 | 0.00061362
108 | 0.97536 | -0.47504 | 0 | 0
109 | 0.97533 | -0.4756 | 0.00077639 | 0.00019458
110 | 0.98443 | -0.29781 | 0.0023303 | 0.00058403
111 | 0.98449 | -0.29668 | 0.0018314 | 0.00045898
112 | 0.99873 | -0.024505 | 0.0051281 | 0.0012852
113 | 0.97484 | -0.48529 | 0.0031966 | 0.00080115
114 | 0.97482 | -0.48566 | 0.00092954 | 0.00023297
115 | 0.99002 | -0.19208 | 0.0031641 | 0.00079301
116 | 0.98863 | -0.21921 | 0.00080488 | 0.00020172
117 | 0.98398 | -0.31009 | 0.0011455 | 0.00028709
118 | 0.98405 | -0.30869 | 0 | 0
119 | 0.98419 | -0.3058 | 0 | 0
120 | 0.98402 | -0.30926 | 0.00087588 | 0.00021952
121 | 0.98435 | -0.30272 | 0.0011782 | 0.00029527
122 | 0.99376 | -0.11997 | 0.0001822 | 4.5664e-05
123 | 0.9934 | -0.12694 | 0 | 0
124 | 0.99328 | -0.1293 | 0.00052194 | 0.00013081
125 | 0.9932 | -0.13074 | 0.00034399 | 8.6213e-05
126 | 0.99315 | -0.13185 | 0.00096496 | 0.00024184
127 | 0.99313 | -0.13216 | 0.00063941 | 0.00016025
128 | 0.99317 | -0.13129 | 0.00075697 | 0.00018971
129 | 0.99312 | -0.1324 | 0.00016629 | 4.1676e-05
130 | 0.99307 | -0.13323 | 0.00093888 | 0.00023531
131 | 0.99307 | -0.13327 | 0.0011571 | 0.00029
132 | 0.98707 | -0.24945 | 0.0012835 | 0.00032167
133 | 0.98463 | -0.29732 | 0.00036981 | 9.2683e-05
134 | 0.98453 | -0.29925 | 0.0043249 | 0.0010839
135 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0010326 | 0.00025814 | -0.0010326 | -0.00025823 | 7.2339e-09 | -9.1184e-08 | 0.0015801 | 0.0015802 | 0.0015802 | 0.97228 | -0.5362 | 0.97227 | -0.53635 | 0.43412
1 | -0.0027378 | -0.00068549 | 0.0027379 | 0.00068529 | 1.6317e-07 | -2.0301e-07 | 0.0041898 | 0.0041897 | 0.0041898 | 0.97228 | -0.5362 | 0.97234 | -0.53495 | 1.151
2 | 0.0010326 | 0.00025823 | -0.0010326 | -0.00025837 | 1.0902e-08 | -1.3741e-07 | 0.0015802 | 0.0015802 | 0.0015802 | 0.97227 | -0.53635 | 0.97226 | -0.53657 | 0.43413
3 | -0.0027379 | -0.00068529 | 0.0027435 | 0.0006783 | 5.5894e-06 | -6.9881e-06 | 0.0041897 | 0.0041859 | 0.0041897 | 0.97234 | -0.53495 | 0.97451 | -0.4919 | 1.151
4 | 0.00045864 | 0.00011452 | -0.00045863 | -0.00011494 | 6.3948e-09 | -4.2521e-07 | 0.00070178 | 0.00070193 | 0.00070193 | 0.97226 | -0.53657 | 0.97224 | -0.53686 | 0.19284
5 | -0.016442 | -0.0041114 | 0.016463 | 0.0041235 | 2.0568e-05 | 1.2077e-05 | 0.025103 | 0.025102 | 0.025103 | 0.97451 | -0.4919 | 0.97584 | -0.46563 | 6.8964
6 | 0.010865 | 0.0027234 | -0.010864 | -0.0027228 | 1.1884e-06 | 6.1714e-07 | 0.016591 | 0.016591 | 0.016591 | 0.97451 | -0.4919 | 0.97439 | -0.4942 | 4.5579
7 | 0.0028334 | 0.0007097 | -0.0028332 | -0.00070994 | 2.1981e-07 | -2.4945e-07 | 0.0043263 | 0.0043265 | 0.0043265 | 0.97451 | -0.4919 | 0.97443 | -0.49353 | 1.1886
8 | 0.0028332 | 0.00070994 | -0.0028331 | -0.00071005 | 8.9085e-08 | -1.0107e-07 | 0.0043265 | 0.0043265 | 0.0043265 | 0.97443 | -0.49353 | 0.97439 | -0.49419 | 1.1886
9 | -0.013293 | -0.0033331 | 0.013297 | 0.0033352 | 3.8195e-06 | 2.1337e-06 | 0.020255 | 0.020255 | 0.020255 | 0.97663 | -0.45003 | 0.97694 | -0.44401 | 5.5645
10 | 0.013293 | 0.0033331 | -0.013282 | -0.0033269 | 1.1084e-05 | 6.193e-06 | 0.020255 | 0.020255 | 0.020255 | 0.97663 | -0.45003 | 0.97574 | -0.46755 | 5.5645
11 | 0.037619 | 0.0094455 | -0.03758 | -0.0094211 | 3.8761e-05 | 2.4413e-05 | 0.057305 | 0.057306 | 0.057306 | 0.97694 | -0.44401 | 0.97584 | -0.46563 | 15.7433
12 | -0.050916 | -0.012781 | 0.050932 | 0.01279 | 1.5336e-05 | 9.7296e-06 | 0.07756 | 0.07756 | 0.07756 | 0.97694 | -0.44401 | 0.97726 | -0.43769 | 21.3077
13 | 0.0096772 | 0.0024233 | -0.0096761 | -0.0024228 | 1.0177e-06 | 4.9567e-07 | 0.014757 | 0.014757 | 0.014757 | 0.97574 | -0.46755 | 0.97563 | -0.46975 | 4.0541
14 | 0.021118 | 0.0052976 | -0.021103 | -0.005289 | 1.4168e-05 | 8.6126e-06 | 0.032203 | 0.032203 | 0.032203 | 0.97584 | -0.46563 | 0.97512 | -0.47971 | 8.8471
15 | 0.00031374 | 7.7904e-05 | -0.00031374 | -7.8177e-05 | 1.771e-09 | -2.7355e-07 | 0.00047072 | 0.00047082 | 0.00047082 | 0.99123 | -0.16873 | 0.99122 | -0.16885 | 0.12935
16 | -0.00031374 | -7.7904e-05 | 0.00031374 | 7.7708e-05 | 1.2686e-09 | -1.9601e-07 | 0.00047072 | 0.00047065 | 0.00047072 | 0.99123 | -0.16873 | 0.99123 | -0.16864 | 0.12932
17 | 0.00031374 | 7.8177e-05 | -0.00031373 | -7.8629e-05 | 2.9268e-09 | -4.5182e-07 | 0.00047082 | 0.00047098 | 0.00047098 | 0.99122 | -0.16885 | 0.99121 | -0.16905 | 0.12939
18 | -0.00063957 | -0.00015937 | 0.00063957 | 0.00015927 | 2.801e-09 | -1.0273e-07 | 0.00095978 | 0.00095974 | 0.00095978 | 0.99123 | -0.16864 | 0.99124 | -0.16855 | 0.26368
19 | -0.0096577 | -0.0024193 | 0.0096684 | 0.0024244 | 1.0747e-05 | 5.0969e-06 | 0.014454 | 0.014453 | 0.014454 | 0.99423 | -0.11089 | 0.99544 | -0.087541 | 3.9708
20 | 0.0096577 | 0.0024193 | -0.0096547 | -0.0024179 | 2.9259e-06 | 1.3884e-06 | 0.014454 | 0.014454 | 0.014454 | 0.99423 | -0.11089 | 0.9939 | -0.11725 | 3.9709
21 | 0.0042965 | 0.0010756 | -0.0042963 | -0.0010756 | 2.1656e-07 | -4.3414e-08 | 0.0064221 | 0.0064222 | 0.0064222 | 0.99544 | -0.087541 | 0.99538 | -0.0886 | 1.7643
22 | 0.02622 | 0.0066155 | -0.026139 | -0.0065653 | 8.1358e-05 | 5.0241e-05 | 0.039211 | 0.039211 | 0.039211 | 0.99544 | -0.087541 | 0.99206 | -0.15255 | 10.7724
23 | -0.052749 | -0.013265 | 0.052826 | 0.013314 | 7.6694e-05 | 4.8656e-05 | 0.078867 | 0.078867 | 0.078867 | 0.99544 | -0.087541 | 0.99702 | -0.057147 | 21.6667
24 | 0.012564 | 0.0031494 | -0.01256 | -0.0031476 | 3.2846e-06 | 1.7794e-06 | 0.018781 | 0.018781 | 0.018781 | 0.99544 | -0.087541 | 0.99515 | -0.093029 | 5.1596
25 | 0.008653 | 0.0021668 | -0.0086519 | -0.0021663 | 1.0975e-06 | 4.7643e-07 | 0.012954 | 0.012954 | 0.012954 | 0.9939 | -0.11725 | 0.99376 | -0.11991 | 3.5589
26 | 0.0020937 | 0.00052362 | -0.0020936 | -0.0005238 | 5.9764e-08 | -1.7326e-07 | 0.0031295 | 0.0031295 | 0.0031295 | 0.99538 | -0.0886 | 0.99535 | -0.0892 | 0.85976
27 | 0.002223 | 0.00055652 | -0.0022228 | -0.00055707 | 2.2637e-07 | -5.5617e-07 | 0.0033341 | 0.0033343 | 0.0033343 | 0.99206 | -0.15255 | 0.99195 | -0.15469 | 0.91602
28 | 0.023916 | 0.0060088 | -0.023907 | -0.0060033 | 9.017e-06 | 5.5298e-06 | 0.035877 | 0.035878 | 0.035878 | 0.99206 | -0.15255 | 0.99166 | -0.16046 | 9.8565
29 | -0.083754 | -0.021083 | 0.083984 | 0.021229 | 0.00022946 | 0.00014634 | 0.12503 | 0.12503 | 0.12503 | 0.99702 | -0.057147 | 1 | 0 | 34.3498
30 | 0.030929 | 0.0077693 | -0.03092 | -0.007764 | 8.5885e-06 | 5.3565e-06 | 0.046167 | 0.046167 | 0.046167 | 0.99702 | -0.057147 | 0.99671 | -0.062968 | 12.6831
31 | 0.0038297 | 0.0009595 | -0.0038295 | -0.00095958 | 1.7862e-07 | -7.4405e-08 | 0.0057263 | 0.0057263 | 0.0057263 | 0.99515 | -0.093029 | 0.9951 | -0.094008 | 1.5732
32 | 0.00013129 | 3.2902e-05 | -0.00013129 | -3.2905e-05 | 4.1807e-12 | -3.6485e-09 | 0.00019695 | 0.00019695 | 0.00019695 | 0.99195 | -0.15469 | 0.99195 | -0.15469 | 0.054108
33 | 0.018753 | 0.0047116 | -0.018746 | -0.0047073 | 7.2435e-06 | 4.3214e-06 | 0.028144 | 0.028144 | 0.028144 | 0.99166 | -0.16046 | 0.99124 | -0.16855 | 7.7319
34 | -0.052444 | -0.01317 | 0.052467 | 0.013184 | 2.2834e-05 | 1.4494e-05 | 0.079863 | 0.079863 | 0.079863 | 0.97726 | -0.43769 | 0.97772 | -0.42857 | 21.9404
35 | -0.0076573 | -0.0019199 | 0.0076615 | 0.0019215 | 4.2371e-06 | 1.5769e-06 | 0.011414 | 0.011413 | 0.011414 | 0.99833 | -0.032155 | 0.99893 | -0.020548 | 3.1356
36 | 0.0076573 | 0.0019199 | -0.007657 | -0.0019198 | 2.7402e-07 | 1.0203e-07 | 0.011414 | 0.011414 | 0.011414 | 0.99833 | -0.032155 | 0.99829 | -0.032906 | 3.1356
37 | 0.0052559 | 0.0013171 | -0.0052552 | -0.001317 | 6.7606e-07 | 4.7698e-08 | 0.0078291 | 0.0078293 | 0.0078293 | 0.99893 | -0.020548 | 0.99879 | -0.023248 | 2.1509
38 | -0.012917 | -0.0032385 | 0.01292 | 0.0032397 | 2.1125e-06 | 1.1528e-06 | 0.019242 | 0.019242 | 0.019242 | 0.99893 | -0.020548 | 0.99911 | -0.017116 | 5.2863
39 | 0.0074467 | 0.0018671 | -0.0074461 | -0.0018669 | 5.4786e-07 | 1.9561e-07 | 0.0111 | 0.0111 | 0.0111 | 0.99829 | -0.032906 | 0.99821 | -0.03445 | 3.0495
40 | 0.0049058 | 0.0012281 | -0.0049046 | -0.0012281 | 1.2348e-06 | 5.593e-08 | 0.0074818 | 0.0074821 | 0.0074821 | 0.97563 | -0.46975 | 0.97536 | -0.47504 | 2.0555
41 | 0.0047703 | 0.0011947 | -0.0047697 | -0.0011947 | 5.7753e-07 | 6.3234e-09 | 0.0072753 | 0.0072754 | 0.0072754 | 0.97563 | -0.46975 | 0.9755 | -0.4723 | 1.9987
42 | 0.018106 | 0.004548 | -0.018097 | -0.0045426 | 9.1101e-06 | 5.4069e-06 | 0.027184 | 0.027185 | 0.027185 | 0.99124 | -0.16855 | 0.99069 | -0.1791 | 7.4683
43 | -0.012814 | -0.003215 | 0.012818 | 0.003217 | 3.6809e-06 | 2.0157e-06 | 0.019265 | 0.019264 | 0.019265 | 0.98983 | -0.19589 | 0.99014 | -0.18987 | 5.2925
44 | 0.012814 | 0.003215 | -0.012804 | -0.0032094 | 1.0252e-05 | 5.6152e-06 | 0.019265 | 0.019265 | 0.019265 | 0.98983 | -0.19589 | 0.98896 | -0.21268 | 5.2925
45 | 0.0031645 | 0.00079272 | -0.0031641 | -0.00079301 | 3.3324e-07 | -2.9204e-07 | 0.0047556 | 0.0047557 | 0.0047557 | 0.99014 | -0.18987 | 0.99002 | -0.19208 | 1.3065
46 | -0.015982 | -0.0040097 | 0.015987 | 0.0040123 | 4.4896e-06 | 2.6064e-06 | 0.02402 | 0.02402 | 0.02402 | 0.99014 | -0.18987 | 0.99044 | -0.18398 | 6.5989
47 | 0.011663 | 0.0029234 | -0.011659 | -0.0029215 | 3.6262e-06 | 1.918e-06 | 0.017548 | 0.017548 | 0.017548 | 0.98896 | -0.21268 | 0.98863 | -0.21921 | 4.8209
48 | 0.0001822 | 4.5425e-05 | -0.0001822 | -4.5664e-05 | 5.1394e-10 | -2.3831e-07 | 0.00027274 | 0.00027282 | 0.00027282 | 0.99376 | -0.11991 | 0.99376 | -0.11997 | 0.07495
49 | 0.0054927 | 0.0013757 | -0.0054909 | -0.0013755 | 1.8373e-06 | 2.3776e-07 | 0.0082242 | 0.0082246 | 0.0082246 | 0.99376 | -0.11991 | 0.9934 | -0.12694 | 2.2595
50 | 0.002977 | 0.0007452 | -0.0029765 | -0.00074566 | 4.2222e-07 | -4.6389e-07 | 0.0044572 | 0.0044575 | 0.0044575 | 0.99376 | -0.11991 | 0.99361 | -0.12289 | 1.2246
51 | -0.00037325 | -9.3544e-05 | 0.00037325 | 9.3239e-05 | 2.8917e-09 | -3.0481e-07 | 0.00056483 | 0.00056472 | 0.00056483 | 0.9833 | -0.32338 | 0.98331 | -0.32322 | 0.15517
52 | -0.0016351 | -0.0004095 | 0.0016361 | 0.00040452 | 1.0175e-06 | -4.9789e-06 | 0.0024743 | 0.0024723 | 0.0024743 | 0.98331 | -0.32322 | 0.98398 | -0.31009 | 0.67975
53 | -0.00073249 | -0.00018358 | 0.00073251 | 0.00018326 | 1.1562e-08 | -3.2448e-07 | 0.001097 | 0.0010969 | 0.001097 | 0.99359 | -0.12323 | 0.99361 | -0.12289 | 0.30137
54 | 0.0012487 | 0.00031205 | -0.0012487 | -0.00031212 | 6.5157e-09 | -6.0652e-08 | 0.0018665 | 0.0018665 | 0.0018665 | 0.99535 | -0.0892 | 0.99534 | -0.08931 | 0.51278
55 | 0.014354 | 0.0036023 | -0.01435 | -0.0036001 | 3.9357e-06 | 2.2172e-06 | 0.02136 | 0.021361 | 0.021361 | 1 | 0 | 0.9997 | -0.0057512 | 5.8683
56 | 0.15362 | 0.039498 | -0.15334 | -0.039322 | 0.0002752 | 0.00017539 | 0.22894 | 0.22894 | 0.22894 | 1 | 0 | 0.99804 | -0.036935 | 31.4473
57 | 0.028785 | 0.0072289 | -0.028756 | -0.007211 | 2.8712e-05 | 1.7836e-05 | 0.042979 | 0.042979 | 0.042979 | 0.99671 | -0.062968 | 0.99563 | -0.083895 | 11.8075
58 | 0.0038295 | 0.00095958 | -0.0038292 | -0.00095969 | 2.7619e-07 | -1.15e-07 | 0.0057263 | 0.0057264 | 0.0057264 | 0.9951 | -0.094008 | 0.99502 | -0.095523 | 1.5732
59 | 0.003966 | 0.00099293 | -0.0039656 | -0.00099305 | 4.4908e-07 | -1.2481e-07 | 0.0060356 | 0.0060358 | 0.0060358 | 0.97772 | -0.42857 | 0.9776 | -0.43095 | 1.6582
60 | -0.056433 | -0.014177 | 0.056539 | 0.014244 | 0.00010621 | 6.749e-05 | 0.085899 | 0.085899 | 0.085899 | 0.97772 | -0.42857 | 0.97973 | -0.38922 | 23.5986
61 | 0.01636 | 0.0041071 | -0.016356 | -0.0041049 | 3.8047e-06 | 2.2187e-06 | 0.024574 | 0.024575 | 0.024575 | 0.99069 | -0.1791 | 0.99044 | -0.18398 | 6.7512
62 | 0.0074461 | 0.0018669 | -0.0074448 | -0.0018664 | 1.3547e-06 | 4.838e-07 | 0.0111 | 0.0111 | 0.0111 | 0.99821 | -0.03445 | 0.99801 | -0.038268 | 3.0495
63 | 0.007291 | 0.0018279 | -0.0072899 | -0.0018275 | 1.1235e-06 | 3.8784e-07 | 0.010871 | 0.010871 | 0.010871 | 0.99801 | -0.038268 | 0.99784 | -0.041502 | 2.9866
64 | -0.0011137 | -0.00027911 | 0.0011137 | 0.00027853 | 4.8958e-08 | -5.8076e-07 | 0.001665 | 0.0016648 | 0.001665 | 0.99527 | -0.090681 | 0.99532 | -0.089757 | 0.45743
65 | -0.0012487 | -0.00031236 | 0.0012487 | 0.00031212 | 2.6576e-08 | -2.4736e-07 | 0.0018666 | 0.0018665 | 0.0018666 | 0.99532 | -0.089757 | 0.99534 | -0.08931 | 0.51281
66 | 0.0051284 | 0.0012852 | -0.0051281 | -0.0012852 | 3.0701e-07 | 1.2948e-08 | 0.0076403 | 0.0076404 | 0.0076404 | 0.99879 | -0.023248 | 0.99873 | -0.024505 | 2.099
67 | -0.013027 | -0.0032667 | 0.013031 | 0.0032686 | 3.3348e-06 | 1.8248e-06 | 0.019403 | 0.019403 | 0.019403 | 0.99911 | -0.017116 | 0.99939 | -0.011746 | 5.3305
68 | -0.013658 | -0.0034232 | 0.013662 | 0.0034254 | 3.8898e-06 | 2.1804e-06 | 0.020652 | 0.020651 | 0.020652 | 0.9841 | -0.30431 | 0.98441 | -0.29833 | 5.6735
69 | 0.0075776 | 0.0018993 | -0.0075768 | -0.001899 | 8.051e-07 | 3.0751e-07 | 0.011458 | 0.011458 | 0.011458 | 0.9841 | -0.30431 | 0.98399 | -0.30654 | 3.1478
70 | -0.021273 | -0.005333 | 0.021279 | 0.0053364 | 5.4837e-06 | 3.3298e-06 | 0.032157 | 0.032157 | 0.032157 | 0.98441 | -0.29833 | 0.98468 | -0.29292 | 8.8344
71 | 0.0075768 | 0.001899 | -0.0075768 | -0.001899 | 5.9571e-08 | 2.2755e-08 | 0.011458 | 0.011458 | 0.011458 | 0.98399 | -0.30654 | 0.98398 | -0.3067 | 3.1478
72 | 0.0046435 | 0.0011637 | -0.0046432 | -0.0011637 | 3.2373e-07 | -1.5812e-08 | 0.0070171 | 0.0070172 | 0.0070172 | 0.98468 | -0.29292 | 0.98461 | -0.29438 | 1.9278
73 | -0.025922 | -0.0065 | 0.025935 | 0.0065078 | 1.2585e-05 | 7.7762e-06 | 0.039174 | 0.039174 | 0.039174 | 0.98468 | -0.29292 | 0.98521 | -0.28274 | 10.7621
74 | 0.0075768 | 0.001899 | -0.0075761 | -0.0018987 | 7.0919e-07 | 2.7092e-07 | 0.011458 | 0.011458 | 0.011458 | 0.98398 | -0.3067 | 0.98388 | -0.30867 | 3.1478
75 | 0.0026158 | 0.00065556 | -0.0026158 | -0.00065557 | 1.0096e-08 | -1.5449e-08 | 0.0039532 | 0.0039532 | 0.0039532 | 0.98461 | -0.29438 | 0.9846 | -0.29447 | 1.086
76 | 0.016739 | 0.0041981 | -0.016731 | -0.004193 | 8.6042e-06 | 5.0499e-06 | 0.025283 | 0.025283 | 0.025283 | 0.98521 | -0.28274 | 0.98465 | -0.29353 | 6.946
77 | 0.094165 | 0.023837 | -0.094081 | -0.023783 | 8.483e-05 | 5.4149e-05 | 0.14231 | 0.14231 | 0.14231 | 0.98521 | -0.28274 | 0.98424 | -0.30152 | 39.0957
78 | -0.13684 | -0.034543 | 0.13796 | 0.03526 | 0.0011216 | 0.00071695 | 0.20677 | 0.20677 | 0.20677 | 0.98521 | -0.28274 | 0.99403 | -0.11314 | 56.8037
79 | -0.14063 | -0.035929 | 0.14081 | 0.036043 | 0.00017857 | 0.00011415 | 0.21076 | 0.21076 | 0.21076 | 0.99403 | -0.11314 | 0.99541 | -0.086917 | 57.9019
80 | 0.0026705 | 0.0006691 | -0.0026704 | -0.00066926 | 1.073e-07 | -1.6343e-07 | 0.0039975 | 0.0039976 | 0.0039976 | 0.99403 | -0.11314 | 0.99398 | -0.11398 | 1.0982
81 | -0.14464 | -0.037003 | 0.14467 | 0.037018 | 2.3927e-05 | 1.5243e-05 | 0.21649 | 0.21649 | 0.21649 | 0.99541 | -0.086917 | 0.99559 | -0.0835 | 29.7376
82 | 0.0061073 | 0.0015302 | -0.0061069 | -0.0015301 | 3.8077e-07 | 9.2077e-08 | 0.0092293 | 0.0092293 | 0.0092293 | 0.98465 | -0.29353 | 0.98459 | -0.29484 | 2.5355
83 | 0.010623 | 0.0026629 | -0.010621 | -0.0026618 | 2.0949e-06 | 1.0651e-06 | 0.016054 | 0.016054 | 0.016054 | 0.98465 | -0.29353 | 0.98444 | -0.29767 | 4.4105
84 | 0.091181 | 0.023056 | -0.09112 | -0.023017 | 6.0056e-05 | 3.8329e-05 | 0.13792 | 0.13792 | 0.13792 | 0.98424 | -0.30152 | 0.98353 | -0.31526 | 37.8912
85 | -0.0069912 | -0.0017523 | 0.0069956 | 0.0017537 | 4.3337e-06 | 1.3875e-06 | 0.010433 | 0.010432 | 0.010433 | 0.99717 | -0.054508 | 0.99784 | -0.041502 | 2.8661
86 | 0.0069912 | 0.0017523 | -0.006989 | -0.0017516 | 2.2161e-06 | 7.1029e-07 | 0.010433 | 0.010433 | 0.010433 | 0.99717 | -0.054508 | 0.99682 | -0.061163 | 2.8662
87 | -0.0051266 | -0.0012847 | 0.0051266 | 0.0012847 | 2.4633e-08 | 1.8567e-09 | 0.007749 | 0.007749 | 0.007749 | 0.98444 | -0.29777 | 0.98444 | -0.29767 | 2.1289
88 | 0.0051266 | 0.0012847 | -0.0051259 | -0.0012847 | 6.8376e-07 | 5.1602e-08 | 0.007749 | 0.0077492 | 0.0077492 | 0.98444 | -0.29777 | 0.98429 | -0.30057 | 2.1289
89 | -0.0040077 | -0.0010042 | 0.0040081 | 0.0010041 | 3.689e-07 | -9.2441e-08 | 0.0061138 | 0.0061137 | 0.0061138 | 0.9754 | -0.47423 | 0.9755 | -0.4723 | 1.6796
90 | 0.0040077 | 0.0010042 | -0.0040075 | -0.0010043 | 2.4671e-07 | -6.1776e-08 | 0.0061138 | 0.0061139 | 0.0061139 | 0.9754 | -0.47423 | 0.97534 | -0.47552 | 1.6796
91 | 0.00076165 | 0.00019061 | -0.00076163 | -0.00019088 | 1.156e-08 | -2.7773e-07 | 0.0011617 | 0.0011618 | 0.0011618 | 0.9755 | -0.4723 | 0.97549 | -0.47262 | 0.31918
92 | 0.003361 | 0.00084223 | -0.0033608 | -0.0008423 | 1.1886e-07 | -7.4378e-08 | 0.0051276 | 0.0051276 | 0.0051276 | 0.97534 | -0.47552 | 0.9753 | -0.47626 | 1.4087
93 | 0.022888 | 0.0057402 | -0.022879 | -0.005735 | 8.4977e-06 | 5.1868e-06 | 0.034208 | 0.034208 | 0.034208 | 0.99563 | -0.083895 | 0.99523 | -0.091688 | 9.3979
94 | 0.018298 | 0.0045874 | -0.018294 | -0.0045848 | 4.3583e-06 | 2.5876e-06 | 0.027359 | 0.027359 | 0.027359 | 0.99523 | -0.091688 | 0.99497 | -0.096687 | 7.5162
95 | 0.0045813 | 0.0011476 | -0.0045805 | -0.0011477 | 8.6045e-07 | -8.4668e-08 | 0.0068496 | 0.0068498 | 0.0068498 | 0.99523 | -0.091688 | 0.99502 | -0.095632 | 1.8818
96 | 0.0045805 | 0.0011477 | -0.0045799 | -0.0011478 | 5.3572e-07 | -5.2562e-08 | 0.0068498 | 0.0068499 | 0.0068499 | 0.99502 | -0.095632 | 0.99489 | -0.098087 | 1.8819
97 | 0.001204 | 0.00030151 | -0.0012039 | -0.00030174 | 2.1851e-08 | -2.2392e-07 | 0.001792 | 0.0017921 | 0.0017921 | 0.9997 | -0.0057512 | 0.99968 | -0.0061323 | 0.49232
98 | 0.013146 | 0.0032985 | -0.013142 | -0.0032965 | 3.7568e-06 | 2.0614e-06 | 0.019569 | 0.019569 | 0.019569 | 0.9997 | -0.0057512 | 0.99939 | -0.011746 | 5.376
99 | 0.15085 | 0.038698 | -0.15074 | -0.038631 | 0.00010397 | 6.6255e-05 | 0.22522 | 0.22522 | 0.22522 | 0.99804 | -0.036935 | 0.99729 | -0.051154 | 30.9369
100 | 0.0020091 | 0.00050345 | -0.0020091 | -0.00050352 | 2.2926e-08 | -7.325e-08 | 0.0030049 | 0.0030049 | 0.0030049 | 0.99489 | -0.098087 | 0.99488 | -0.098327 | 0.82552
101 | 0.14903 | 0.038201 | -0.14879 | -0.038053 | 0.0002333 | 0.00014866 | 0.22266 | 0.22266 | 0.22266 | 0.99729 | -0.051154 | 0.99559 | -0.0835 | 30.5852
102 | -0.0010547 | -0.00026434 | 0.0010548 | 0.00026383 | 4.1081e-08 | -5.0664e-07 | 0.0016055 | 0.0016053 | 0.0016055 | 0.97756 | -0.43177 | 0.9776 | -0.43095 | 0.44106
103 | 0.0029108 | 0.00072922 | -0.0029107 | -0.0007294 | 1.7207e-07 | -1.8294e-07 | 0.0044305 | 0.0044306 | 0.0044306 | 0.9776 | -0.43095 | 0.97754 | -0.43219 | 1.2172
104 | 0.0041621 | 0.0010427 | -0.0041618 | -0.0010427 | 3.658e-07 | -7.9406e-08 | 0.0062901 | 0.0062902 | 0.0062902 | 0.98459 | -0.29484 | 0.98449 | -0.29668 | 1.7281
105 | 0.0024484 | 0.00061355 | -0.0024484 | -0.00061362 | 3.8405e-08 | -6.7851e-08 | 0.0037269 | 0.003727 | 0.003727 | 0.97754 | -0.43219 | 0.97752 | -0.43252 | 1.0239
106 | -0.013604 | -0.0034096 | 0.013609 | 0.003412 | 4.2883e-06 | 2.4045e-06 | 0.020623 | 0.020623 | 0.020623 | 0.98161 | -0.3527 | 0.98194 | -0.34608 | 5.6657
107 | -0.08556 | -0.021575 | 0.085687 | 0.021656 | 0.00012641 | 8.065e-05 | 0.1297 | 0.1297 | 0.1297 | 0.98194 | -0.34608 | 0.98353 | -0.31526 | 35.6328
108 | 0.071952 | 0.018163 | -0.071942 | -0.018157 | 9.4457e-06 | 6.0185e-06 | 0.10908 | 0.10908 | 0.10908 | 0.98194 | -0.34608 | 0.9818 | -0.34882 | 29.9672
109 | 0.070252 | 0.017733 | -0.07013 | -0.017656 | 0.00012158 | 7.7452e-05 | 0.10652 | 0.10652 | 0.10652 | 0.9818 | -0.34882 | 0.97995 | -0.38502 | 29.2634
110 | -0.0083855 | -0.0021016 | 0.0083869 | 0.0021022 | 1.4479e-06 | 6.2692e-07 | 0.012737 | 0.012737 | 0.012737 | 0.97965 | -0.39089 | 0.97983 | -0.38727 | 3.4992
111 | -0.010148 | -0.0025436 | 0.010149 | 0.0025442 | 1.0861e-06 | 5.4151e-07 | 0.015412 | 0.015411 | 0.015412 | 0.97983 | -0.38727 | 0.97995 | -0.38502 | 4.2339
112 | 0.059981 | 0.015112 | -0.059969 | -0.015104 | 1.2038e-05 | 7.6555e-06 | 0.091107 | 0.091107 | 0.091107 | 0.97995 | -0.38502 | 0.97973 | -0.38922 | 25.0295
113 | 0.0041287 | 0.0010345 | -0.0041283 | -0.0010347 | 3.9509e-07 | -1.069e-07 | 0.0061707 | 0.0061709 | 0.0061709 | 0.99559 | -0.0835 | 0.99548 | -0.085509 | 1.6953
114 | 0.0049046 | 0.0012281 | -0.0049045 | -0.0012281 | 1.2936e-07 | 5.8854e-09 | 0.0074821 | 0.0074821 | 0.0074821 | 0.97536 | -0.47504 | 0.97533 | -0.4756 | 2.0555
115 | 0.0041281 | 0.0010335 | -0.0041262 | -0.0010339 | 1.9056e-06 | -3.7854e-07 | 0.0062976 | 0.0062982 | 0.0062982 | 0.97533 | -0.4756 | 0.97484 | -0.48529 | 1.7303
116 | -0.0023303 | -0.00058403 | 0.0023304 | 0.00058376 | 1.2529e-07 | -2.6222e-07 | 0.0035223 | 0.0035222 | 0.0035223 | 0.98443 | -0.29781 | 0.98449 | -0.29668 | 0.96768
117 | 0.00092956 | 0.00023271 | -0.00092954 | -0.00023297 | 1.6095e-08 | -2.5551e-07 | 0.0014188 | 0.0014189 | 0.0014189 | 0.97484 | -0.48529 | 0.97482 | -0.48566 | 0.38981
118 | 0.010854 | 0.0027197 | -0.010838 | -0.0027118 | 1.5613e-05 | 7.995e-06 | 0.016337 | 0.016337 | 0.016337 | 0.98863 | -0.21921 | 0.98707 | -0.24945 | 4.4883
119 | -0.0027816 | -0.00069161 | 0.0027818 | 0.00069137 | 1.837e-07 | -2.3444e-07 | 0.0042046 | 0.0042044 | 0.0042046 | 0.98398 | -0.31009 | 0.98405 | -0.30869 | 1.1551
120 | -0.0027818 | -0.00069137 | 0.0027822 | 0.00069089 | 3.8039e-07 | -4.8569e-07 | 0.0042044 | 0.0042042 | 0.0042044 | 0.98405 | -0.30869 | 0.98419 | -0.3058 | 1.1551
121 | 0.00087602 | 0.00021684 | -0.00087588 | -0.00021952 | 1.4336e-07 | -2.6792e-06 | 0.0013235 | 0.0013245 | 0.0013245 | 0.98419 | -0.3058 | 0.98402 | -0.30926 | 0.36387
122 | -0.0036582 | -0.00090772 | 0.0036588 | 0.00090747 | 5.3306e-07 | -2.5015e-07 | 0.0055277 | 0.0055275 | 0.0055277 | 0.98419 | -0.3058 | 0.98435 | -0.30272 | 1.5186
123 | -0.0048369 | -0.0012027 | 0.0048377 | 0.0012028 | 7.9571e-07 | 4.1649e-09 | 0.0073085 | 0.0073083 | 0.0073085 | 0.98435 | -0.30272 | 0.98453 | -0.29925 | 2.0078
124 | 0.0054909 | 0.0013755 | -0.0054903 | -0.0013754 | 6.1626e-07 | 7.9918e-08 | 0.0082246 | 0.0082247 | 0.0082247 | 0.9934 | -0.12694 | 0.99328 | -0.1293 | 2.2595
125 | 0.0049683 | 0.0012446 | -0.004968 | -0.0012446 | 3.4072e-07 | 5.7794e-09 | 0.0074428 | 0.0074428 | 0.0074428 | 0.99328 | -0.1293 | 0.9932 | -0.13074 | 2.0447
126 | 0.004624 | 0.0011584 | -0.0046239 | -0.0011584 | 1.2174e-07 | -9.6301e-09 | 0.0069275 | 0.0069275 | 0.0069275 | 0.9932 | -0.13074 | 0.99317 | -0.13129 | 1.9032
127 | 0.0029018 | 0.00072685 | -0.0029018 | -0.00072691 | 4.4054e-08 | -5.2227e-08 | 0.0043476 | 0.0043477 | 0.0043477 | 0.99315 | -0.13185 | 0.99313 | -0.13216 | 1.1944
128 | -0.0038668 | -0.0009687 | 0.0038669 | 0.00096866 | 1.022e-07 | -3.9667e-08 | 0.0057934 | 0.0057934 | 0.0057934 | 0.99315 | -0.13185 | 0.99317 | -0.13129 | 1.5916
129 | 0.0022624 | 0.00056666 | -0.0022624 | -0.00056672 | 2.4944e-08 | -5.8947e-08 | 0.0033896 | 0.0033897 | 0.0033897 | 0.99313 | -0.13216 | 0.99312 | -0.1324 | 0.93122
130 | 0.0020961 | 0.00052504 | -0.002096 | -0.00052528 | 8.3429e-08 | -2.3846e-07 | 0.0031405 | 0.0031406 | 0.0031406 | 0.99312 | -0.1324 | 0.99307 | -0.13323 | 0.8628
131 | 0.0011571 | 0.00028997 | -0.0011571 | -0.00029 | 2.2518e-09 | -2.4404e-08 | 0.0017338 | 0.0017338 | 0.0017338 | 0.99307 | -0.13323 | 0.99307 | -0.13327 | 0.47632
132 | 0.009555 | 0.0023901 | -0.0095333 | -0.0023797 | 2.1715e-05 | 1.0338e-05 | 0.014402 | 0.014404 | 0.014404 | 0.98707 | -0.24945 | 0.98463 | -0.29732 | 3.9571
133 | 0.0091634 | 0.0022871 | -0.0091626 | -0.0022867 | 8.4088e-07 | 3.8939e-07 | 0.013845 | 0.013845 | 0.013845 | 0.98463 | -0.29732 | 0.98453 | -0.29925 | 3.8036

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2536 | 0.064329

## res_load
| p_mw | q_mvar
0 | 0.0017051 | 0.00042735
1 | 0.00057398 | 0.00014385
2 | 0.00045863 | 0.00011494
3 | 0.0028331 | 0.00071005
4 | 0.0036052 | 0.00090354
5 | 0.010864 | 0.0027228
6 | 0.00032583 | 8.166e-05
7 | 0.00031373 | 7.8629e-05
8 | 0.0010018 | 0.00025107
9 | 0.0022026 | 0.00055202
10 | 0.0087306 | 0.0021881
11 | 0.0020915 | 0.00052417
12 | 0.0051538 | 0.0012917
13 | 0.0015126 | 0.0003791
14 | 0.00021036 | 5.2721e-05
15 | 0.021103 | 0.005289
16 | 0.0011411 | 0.00028599
17 | 0.00037325 | 9.3544e-05
18 | 0.0012619 | 0.00031626
19 | 0.00073249 | 0.00018358
20 | 0.002244 | 0.00056241
21 | 0.00084486 | 0.00021174
22 | 0.0021351 | 0.0005351
23 | 0.00013129 | 3.2905e-05
24 | 0.0017377 | 0.00043551
25 | 0.00036919 | 9.2528e-05
26 | 0.00015373 | 3.8529e-05
27 | 0.0011137 | 0.00027911
28 | 0.00013498 | 3.383e-05
29 | 0.00012685 | 3.1792e-05
30 | 0.00010788 | 2.7038e-05
31 | 0.0060803 | 0.0015239
32 | 0.0076116 | 0.0019076
33 | 0.0020274 | 0.00050812
34 | 0.0075761 | 0.0018987
35 | 0.0026158 | 0.00065557
36 | 0.0038311 | 0.00096015
37 | 0.0026704 | 0.00066926
38 | 0.0029 | 0.00072681
39 | 0.00029433 | 7.3766e-05
40 | 0.006989 | 0.0017516
41 | 0.0054946 | 0.0013771
42 | 0.0051259 | 0.0012847
43 | 0.0006465 | 0.00016203
44 | 0.0058687 | 0.0014708
45 | 0.018294 | 0.0045848
46 | 0.0024924 | 0.00062466
47 | 0.0025708 | 0.00064431
48 | 0.0012039 | 0.00030174
49 | 0.00011141 | 2.7923e-05
50 | 0.0017161 | 0.0004301
51 | 0.0010547 | 0.00026434
52 | 0.0019448 | 0.00048741
53 | 0.00076163 | 0.00019088
54 | 0.0033608 | 0.0008423
55 | 0.00046226 | 0.00011585
56 | 0.013604 | 0.0034096
57 | 0.0054336 | 0.0013618
58 | 0.0016905 | 0.00042367
59 | 0.0083855 | 0.0021016
60 | 0.0017612 | 0.00044141
61 | 0.0034295 | 0.00085952
62 | 0.0020091 | 0.00050352
63 | 0.0038292 | 0.00095969
64 | 0.0041283 | 0.0010347
65 | 0.0024484 | 0.00061362
66 | 0.00077639 | 0.00019458
67 | 0.0023303 | 0.00058403
68 | 0.0018314 | 0.00045898
69 | 0.0051281 | 0.0012852
70 | 0.0031966 | 0.00080115
71 | 0.00092954 | 0.00023297
72 | 0.0031641 | 0.00079301
73 | 0.00080488 | 0.00020172
74 | 0.0011455 | 0.00028709
75 | 0.00087588 | 0.00021952
76 | 0.0011782 | 0.00029527
77 | 0.0001822 | 4.5664e-05
78 | 0.00052194 | 0.00013081
79 | 0.00034399 | 8.6213e-05
80 | 0.00096496 | 0.00024184
81 | 0.00063941 | 0.00016025
82 | 0.00075697 | 0.00018971
83 | 0.00016629 | 4.1676e-05
84 | 0.00093888 | 0.00023531
85 | 0.0011571 | 0.00029
86 | 0.0012835 | 0.00032167
87 | 0.00036981 | 9.2683e-05
88 | 0.0043249 | 0.0010839

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1