## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_181-3_1_5_node_13 | 0.4 | n |  | TRUE
1 | bus_LV_181-3_1_5_node_25 | 0.4 | n |  | TRUE
2 | bus_LV_181-3_1_5_node_258 | 0.4 | n |  | TRUE
3 | bus_LV_181-3_1_5_node_17 | 0.4 | n |  | TRUE
4 | bus_LV_181-3_1_5_node_18 | 0.4 | n |  | TRUE
5 | bus_LV_181-3_1_5_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_181-3_1_5_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_181-3_1_5_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_181-3_1_5_node_154 | 0.4 | n |  | TRUE
9 | bus_LV_181-3_1_5_node_224 | 0.4 | n |  | TRUE
10 | bus_LV_181-3_1_5_node_134 | 0.4 | n |  | TRUE
11 | bus_LV_181-3_1_5_node_254 | 0.4 | n |  | TRUE
12 | bus_LV_181-3_1_5_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_181-3_1_5_node_172 | 0.4 | n |  | TRUE
14 | bus_LV_181-3_1_5_node_251 | 0.4 | n |  | TRUE
15 | bus_LV_181-3_1_5_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_181-3_1_5_node_171 | 0.4 | n |  | TRUE
17 | bus_LV_181-3_1_5_node_243 | 0.4 | n |  | TRUE
18 | bus_LV_181-3_1_5_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_181-3_1_5_node_240 | 0.4 | n |  | TRUE
20 | bus_LV_181-3_1_5_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_181-3_1_5_node_159 | 0.4 | n |  | TRUE
22 | bus_LV_181-3_1_5_node_157 | 0.4 | n |  | TRUE
23 | bus_LV_181-3_1_5_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_181-3_1_5_node_249 | 0.4 | n |  | TRUE
25 | bus_LV_181-3_1_5_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_181-3_1_5_node_232 | 0.4 | n |  | TRUE
27 | bus_LV_181-3_1_5_node_216 | 0.4 | n |  | TRUE
28 | bus_LV_181-3_1_5_node_235 | 0.4 | n |  | TRUE
29 | bus_LV_181-3_1_5_node_233 | 0.4 | n |  | TRUE
30 | bus_LV_181-3_1_5_node_155 | 0.4 | n |  | TRUE
31 | bus_LV_181-3_1_5_node_156 | 0.4 | n |  | TRUE
32 | bus_LV_181-3_1_5_node_217 | 0.4 | n |  | TRUE
33 | bus_LV_181-3_1_5_node_161 | 0.4 | n |  | TRUE
34 | bus_LV_181-3_1_5_node_162 | 0.4 | n |  | TRUE
35 | bus_LV_181-3_1_5_node_163 | 0.4 | n |  | TRUE
36 | bus_LV_181-3_1_5_node_164 | 0.4 | n |  | TRUE
37 | bus_LV_181-3_1_5_node_165 | 0.4 | n |  | TRUE
38 | bus_LV_181-3_1_5_node_179 | 0.4 | n |  | TRUE
39 | bus_LV_181-3_1_5_node_166 | 0.4 | n |  | TRUE
40 | bus_LV_181-3_1_5_node_167 | 0.4 | n |  | TRUE
41 | bus_LV_181-3_1_5_node_168 | 0.4 | n |  | TRUE
42 | bus_LV_181-3_1_5_node_169 | 0.4 | n |  | TRUE
43 | bus_LV_181-3_1_5_node_170 | 0.4 | n |  | TRUE
44 | bus_LV_181-3_1_5_node_186 | 0.4 | n |  | TRUE
45 | bus_LV_181-3_1_5_node_180 | 0.4 | n |  | TRUE
46 | bus_LV_181-3_1_5_node_212 | 0.4 | n |  | TRUE
47 | bus_LV_181-3_1_5_node_250 | 0.4 | n |  | TRUE
48 | bus_LV_181-3_1_5_node_173 | 0.4 | n |  | TRUE
49 | bus_LV_181-3_1_5_node_174 | 0.4 | n |  | TRUE
50 | bus_LV_181-3_1_5_node_175 | 0.4 | n |  | TRUE
51 | bus_LV_181-3_1_5_node_176 | 0.4 | n |  | TRUE
52 | bus_LV_181-3_1_5_node_177 | 0.4 | n |  | TRUE
53 | bus_LV_181-3_1_5_node_178 | 0.4 | n |  | TRUE
54 | bus_LV_181-3_1_5_node_268 | 0.4 | n |  | TRUE
55 | bus_LV_181-3_1_5_node_221 | 0.4 | n |  | TRUE
56 | bus_LV_181-3_1_5_node_215 | 0.4 | n |  | TRUE
57 | bus_LV_181-3_1_5_node_181 | 0.4 | n |  | TRUE
58 | bus_LV_181-3_1_5_node_182 | 0.4 | n |  | TRUE
59 | bus_LV_181-3_1_5_node_183 | 0.4 | n |  | TRUE
60 | bus_LV_181-3_1_5_node_184 | 0.4 | n |  | TRUE
61 | bus_LV_181-3_1_5_node_185 | 0.4 | n |  | TRUE
62 | bus_LV_181-3_1_5_node_189 | 0.4 | n |  | TRUE
63 | bus_LV_181-3_1_5_node_187 | 0.4 | n |  | TRUE
64 | bus_LV_181-3_1_5_node_188 | 0.4 | n |  | TRUE
65 | bus_LV_181-3_1_5_node_267 | 0.4 | n |  | TRUE
66 | bus_LV_181-3_1_5_node_190 | 0.4 | n |  | TRUE
67 | bus_LV_181-3_1_5_node_191 | 0.4 | n |  | TRUE
68 | bus_LV_181-3_1_5_node_193 | 0.4 | n |  | TRUE
69 | bus_LV_181-3_1_5_node_192 | 0.4 | n |  | TRUE
70 | bus_LV_181-3_1_5_node_194 | 0.4 | n |  | TRUE
71 | bus_LV_181-3_1_5_node_196 | 0.4 | n |  | TRUE
72 | bus_LV_181-3_1_5_node_210 | 0.4 | n |  | TRUE
73 | bus_LV_181-3_1_5_node_207 | 0.4 | n |  | TRUE
74 | bus_LV_181-3_1_5_node_223 | 0.4 | n |  | TRUE
75 | bus_LV_181-3_1_5_node_195 | 0.4 | n |  | TRUE
76 | bus_LV_181-3_1_5_node_236 | 0.4 | n |  | TRUE
77 | bus_LV_181-3_1_5_node_206 | 0.4 | n |  | TRUE
78 | bus_LV_181-3_1_5_node_225 | 0.4 | n |  | TRUE
79 | bus_LV_181-3_1_5_node_197 | 0.4 | n |  | TRUE
80 | bus_LV_181-3_1_5_node_198 | 0.4 | n |  | TRUE
81 | bus_LV_181-3_1_5_node_199 | 0.4 | n |  | TRUE
82 | bus_LV_181-3_1_5_node_200 | 0.4 | n |  | TRUE
83 | bus_LV_181-3_1_5_node_201 | 0.4 | n |  | TRUE
84 | bus_LV_181-3_1_5_node_230 | 0.4 | n |  | TRUE
85 | bus_LV_181-3_1_5_node_237 | 0.4 | n |  | TRUE
86 | bus_LV_181-3_1_5_node_202 | 0.4 | n |  | TRUE
87 | bus_LV_181-3_1_5_node_203 | 0.4 | n |  | TRUE
88 | bus_LV_181-3_1_5_node_204 | 0.4 | n |  | TRUE
89 | bus_LV_181-3_1_5_node_205 | 0.4 | n |  | TRUE
90 | bus_LV_181-3_1_5_node_208 | 0.4 | n |  | TRUE
91 | bus_LV_181-3_1_5_node_209 | 0.4 | n |  | TRUE
92 | bus_LV_181-3_1_5_node_211 | 0.4 | n |  | TRUE
93 | bus_LV_181-3_1_5_node_213 | 0.4 | n |  | TRUE
94 | bus_LV_181-3_1_5_node_214 | 0.4 | n |  | TRUE
95 | bus_LV_181-3_1_5_node_218 | 0.4 | n |  | TRUE
96 | bus_LV_181-3_1_5_node_219 | 0.4 | n |  | TRUE
97 | bus_LV_181-3_1_5_node_220 | 0.4 | n |  | TRUE
98 | bus_LV_181-3_1_5_node_222 | 0.4 | n |  | TRUE
99 | bus_LV_181-3_1_5_node_242 | 0.4 | n |  | TRUE
100 | bus_LV_181-3_1_5_node_234 | 0.4 | n |  | TRUE
101 | bus_LV_181-3_1_5_node_248 | 0.4 | n |  | TRUE
102 | bus_LV_181-3_1_5_node_226 | 0.4 | n |  | TRUE
103 | bus_LV_181-3_1_5_node_227 | 0.4 | n |  | TRUE
104 | bus_LV_181-3_1_5_node_228 | 0.4 | n |  | TRUE
105 | bus_LV_181-3_1_5_node_247 | 0.4 | n |  | TRUE
106 | bus_LV_181-3_1_5_node_229 | 0.4 | n |  | TRUE
107 | bus_LV_181-3_1_5_node_231 | 0.4 | n |  | TRUE
108 | bus_LV_181-3_1_5_node_245 | 0.4 | n |  | TRUE
109 | bus_LV_181-3_1_5_node_238 | 0.4 | n |  | TRUE
110 | bus_LV_181-3_1_5_node_239 | 0.4 | n |  | TRUE
111 | bus_LV_181-3_1_5_node_246 | 0.4 | n |  | TRUE
112 | bus_LV_181-3_1_5_node_244 | 0.4 | n |  | TRUE
113 | bus_LV_181-3_1_5_node_253 | 0.4 | n |  | TRUE
114 | bus_LV_181-3_1_5_node_255 | 0.4 | n |  | TRUE
115 | bus_LV_181-3_1_5_node_256 | 0.4 | n |  | TRUE
116 | bus_LV_181-3_1_5_node_257 | 0.4 | n |  | TRUE
117 | bus_LV_181-3_1_5_node_260 | 0.4 | n |  | TRUE
118 | bus_MV_26_0_node_178 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_181-3_1_5_load_258 | 2 | 0.0029415 | 0.00073721 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_181-3_1_5_load_17 | 3 | 0.0033173 | 0.00083138 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_181-3_1_5_load_18 | 4 | 0.0028966 | 0.00072597 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_181-3_1_5_load_19 | 5 | 0.0028635 | 0.00071766 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_181-3_1_5_load_20 | 6 | 0.0014793 | 0.00037075 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_181-3_1_5_load_21 | 7 | 0.00084318 | 0.00021132 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_181-3_1_5_load_154 | 8 | 0.0013727 | 0.00034403 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_181-3_1_5_load_254 | 11 | 0.00094406 | 0.0002366 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_181-3_1_5_load_251 | 14 | 0.0089701 | 0.0022481 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_181-3_1_5_load_243 | 17 | 0.00888 | 0.0022255 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_181-3_1_5_load_159 | 21 | 0.018332 | 0.0045944 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_181-3_1_5_load_157 | 22 | 0.010732 | 0.0026896 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_181-3_1_5_load_249 | 24 | 0.0013438 | 0.00033679 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_181-3_1_5_load_232 | 26 | 0.0042287 | 0.0010598 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_181-3_1_5_load_216 | 27 | 0.021106 | 0.0052897 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_181-3_1_5_load_235 | 28 | 0.00099142 | 0.00024847 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_181-3_1_5_load_233 | 29 | 0.0030329 | 0.00076013 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_181-3_1_5_load_155 | 30 | 0.012887 | 0.0032297 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_181-3_1_5_load_156 | 31 | 0.0010079 | 0.00025261 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_181-3_1_5_load_161 | 33 | 0.0020181 | 0.00050578 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_181-3_1_5_load_162 | 34 | 0.0018121 | 0.00045416 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_181-3_1_5_load_163 | 35 | 0.0018629 | 0.0004669 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_181-3_1_5_load_164 | 36 | 0.0017611 | 0.00044138 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_181-3_1_5_load_165 | 37 | 0.0015832 | 0.00039679 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_181-3_1_5_load_179 | 38 | 0.0019464 | 0.0004878 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_181-3_1_5_load_166 | 39 | 0.002101 | 0.00052656 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_181-3_1_5_load_167 | 40 | 0.0018194 | 0.00045599 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_181-3_1_5_load_169 | 42 | 0.0019029 | 0.00047692 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_181-3_1_5_load_170 | 43 | 0.0088802 | 0.0022256 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_181-3_1_5_load_186 | 44 | 0.0020082 | 0.00050329 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_181-3_1_5_load_212 | 46 | 0.0080502 | 0.0020176 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_181-3_1_5_load_250 | 47 | 0.0081514 | 0.0020429 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_181-3_1_5_load_173 | 48 | 0.0023192 | 0.00058124 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_181-3_1_5_load_174 | 49 | 0.0012031 | 0.00030152 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_181-3_1_5_load_176 | 51 | 0.0012465 | 0.00031241 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_181-3_1_5_load_177 | 52 | 0.0040578 | 0.001017 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_181-3_1_5_load_178 | 53 | 0.0038623 | 0.00096797 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_181-3_1_5_load_268 | 54 | 0.001372 | 0.00034384 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_181-3_1_5_load_221 | 55 | 0.0013987 | 0.00035056 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_181-3_1_5_load_215 | 56 | 0.0029608 | 0.00074204 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_181-3_1_5_load_181 | 57 | 0.0013876 | 0.00034776 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_181-3_1_5_load_182 | 58 | 0.0011815 | 0.00029612 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_181-3_1_5_load_183 | 59 | 0.0012106 | 0.00030339 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_181-3_1_5_load_184 | 60 | 0.0012078 | 0.00030271 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_181-3_1_5_load_185 | 61 | 0.0013563 | 0.00033992 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_181-3_1_5_load_189 | 62 | 0.0012834 | 0.00032166 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_181-3_1_5_load_187 | 63 | 0.0018309 | 0.00045886 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_181-3_1_5_load_188 | 64 | 0.0019312 | 0.000484 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_181-3_1_5_load_267 | 65 | 0.0012545 | 0.0003144 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_181-3_1_5_load_190 | 66 | 0.0051014 | 0.0012785 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_181-3_1_5_load_191 | 67 | 0.0060983 | 0.0015284 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_181-3_1_5_load_210 | 72 | 0.0031893 | 0.00079932 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_181-3_1_5_load_207 | 73 | 0.0062313 | 0.0015617 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_181-3_1_5_load_223 | 74 | 0.0020494 | 0.00051364 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_181-3_1_5_load_236 | 76 | 0.0057604 | 0.0014437 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_181-3_1_5_load_225 | 78 | 0.0007527 | 0.00018864 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_181-3_1_5_load_197 | 79 | 0.00056002 | 0.00014035 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_181-3_1_5_load_198 | 80 | 0.003795 | 0.00095112 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_181-3_1_5_load_199 | 81 | 0.0019243 | 0.00048227 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_181-3_1_5_load_200 | 82 | 0.0038749 | 0.00097115 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_181-3_1_5_load_201 | 83 | 0.00095222 | 0.00023865 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_181-3_1_5_load_237 | 85 | 0.0014865 | 0.00037255 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_181-3_1_5_load_202 | 86 | 0.0006971 | 0.00017471 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_181-3_1_5_load_203 | 87 | 0.0010051 | 0.0002519 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_181-3_1_5_load_204 | 88 | 0.00081776 | 0.00020495 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_181-3_1_5_load_205 | 89 | 0.0053455 | 0.0013397 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_181-3_1_5_load_208 | 90 | 0.0051107 | 0.0012809 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_181-3_1_5_load_209 | 91 | 0.0035685 | 0.00089435 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_181-3_1_5_load_211 | 92 | 0.0056212 | 0.0014088 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_181-3_1_5_load_213 | 93 | 0.0053884 | 0.0013505 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_181-3_1_5_load_214 | 94 | 0.0091997 | 0.0023057 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_181-3_1_5_load_219 | 96 | 0.001006 | 0.00025213 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_181-3_1_5_load_220 | 97 | 0.00093032 | 0.00023316 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_181-3_1_5_load_242 | 99 | 0.0017665 | 0.00044274 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_181-3_1_5_load_234 | 100 | 0.00059528 | 0.00014919 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_181-3_1_5_load_248 | 101 | 0.0078595 | 0.0019698 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_181-3_1_5_load_226 | 102 | 0.0054544 | 0.001367 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_181-3_1_5_load_227 | 103 | 0.0008829 | 0.00022128 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_181-3_1_5_load_228 | 104 | 0.0016638 | 0.00041699 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_181-3_1_5_load_229 | 106 | 0.0015389 | 0.00038569 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_181-3_1_5_load_231 | 107 | 0.002237 | 0.00056065 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_181-3_1_5_load_245 | 108 | 0.0010817 | 0.00027109 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_181-3_1_5_load_238 | 109 | 0.0028976 | 0.0007262 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_181-3_1_5_load_246 | 111 | 0.0039846 | 0.00099863 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_181-3_1_5_load_244 | 112 | 0.0094811 | 0.0023762 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_181-3_1_5_load_253 | 113 | 0.00093783 | 0.00023504 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_181-3_1_5_load_255 | 114 | 0.0084232 | 0.0021111 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_181-3_1_5_load_260 | 117 | 0.00227 | 0.00056891 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_181-3_1_5_line_0 |  | 0 | 1 | 0.079993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_181-3_1_5_line_1 |  | 0 | 2 | 0.096923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_181-3_1_5_line_2 |  | 1 | 10 | 0.10732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_181-3_1_5_line_3 |  | 1 | 11 | 0.038406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_181-3_1_5_line_4 |  | 2 | 115 | 0.024229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_181-3_1_5_line_5 |  | 3 | 4 | 0.022016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_181-3_1_5_line_6 |  | 3 | 5 | 0.027333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_181-3_1_5_line_7 |  | 4 | 6 | 0.0011726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_181-3_1_5_line_8 |  | 5 | 7 | 0.00475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_181-3_1_5_line_9 |  | 6 | 8 | 0.037917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_181-3_1_5_line_10 |  | 7 | 9 | 0.03657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_181-3_1_5_line_11 |  | 8 | 30 | 0.015552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_181-3_1_5_line_12 |  | 9 | 101 | 0.049805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_181-3_1_5_line_13 |  | 9 | 70 | 0.019882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_181-3_1_5_line_14 |  | 9 | 95 | 0.022197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_181-3_1_5_line_15 |  | 10 | 28 | 0.015298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_181-3_1_5_line_16 |  | 10 | 29 | 0.028418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_181-3_1_5_line_17 |  | 11 | 113 | 0.01149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_181-3_1_5_line_18 |  | 12 | 13 | 0.011497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_181-3_1_5_line_19 |  | 12 | 14 | 0.034834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_181-3_1_5_line_20 |  | 13 | 47 | 0.020325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_181-3_1_5_line_21 |  | 14 | 18 | 0.040924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_181-3_1_5_line_22 |  | 15 | 16 | 0.006679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_181-3_1_5_line_23 |  | 15 | 17 | 0.022636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_181-3_1_5_line_24 |  | 16 | 46 | 0.021465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_181-3_1_5_line_25 |  | 16 | 41 | 0.049532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_181-3_1_5_line_26 |  | 17 | 112 | 0.032427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_181-3_1_5_line_27 |  | 18 | 19 | 0.019275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_181-3_1_5_line_28 |  | 19 | 94 | 0.0024539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_181-3_1_5_line_29 |  | 20 | 21 | 0.062859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_181-3_1_5_line_30 |  | 20 | 22 | 0.016785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_181-3_1_5_line_31 |  | 21 | 32 | 0.041556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_181-3_1_5_line_32 |  | 23 | 24 | 0.043985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_181-3_1_5_line_33 |  | 23 | 25 | 0.029859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_181-3_1_5_line_34 |  | 23 | 26 | 0.050678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_181-3_1_5_line_35 |  | 24 | 95 | 0.020549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_181-3_1_5_line_36 |  | 25 | 27 | 0.0193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_181-3_1_5_line_37 |  | 26 | 84 | 0.006256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_181-3_1_5_line_38 |  | 27 | 32 | 0.030526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_181-3_1_5_line_39 |  | 28 | 106 | 0.023638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_181-3_1_5_line_40 |  | 29 | 100 | 0.021402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_181-3_1_5_line_41 |  | 30 | 31 | 0.012469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_181-3_1_5_line_42 |  | 33 | 34 | 0.0080394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_181-3_1_5_line_43 |  | 33 | 35 | 0.0119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_181-3_1_5_line_44 |  | 34 | 36 | 0.0092628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_181-3_1_5_line_45 |  | 35 | 37 | 0.018991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_181-3_1_5_line_46 |  | 37 | 38 | 0.009247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_181-3_1_5_line_47 |  | 38 | 45 | 0.014519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_181-3_1_5_line_48 |  | 39 | 40 | 0.0097217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_181-3_1_5_line_49 |  | 39 | 41 | 0.013412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_181-3_1_5_line_50 |  | 40 | 42 | 0.017933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_181-3_1_5_line_51 |  | 41 | 43 | 0.024004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_181-3_1_5_line_52 |  | 42 | 44 | 0.014328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_181-3_1_5_line_53 |  | 43 | 45 | 0.004268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_181-3_1_5_line_54 |  | 44 | 63 | 0.0064641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_181-3_1_5_line_55 |  | 45 | 56 | 0.018977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_181-3_1_5_line_56 |  | 46 | 92 | 0.0025454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_181-3_1_5_line_57 |  | 48 | 49 | 0.0088155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_181-3_1_5_line_58 |  | 48 | 50 | 0.019695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_181-3_1_5_line_59 |  | 49 | 51 | 0.0060052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_181-3_1_5_line_60 |  | 50 | 52 | 0.011613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_181-3_1_5_line_61 |  | 50 | 53 | 0.0018819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_181-3_1_5_line_62 |  | 51 | 54 | 0.0049331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_181-3_1_5_line_63 |  | 52 | 55 | 0.01178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_181-3_1_5_line_64 |  | 53 | 56 | 0.018689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_181-3_1_5_line_65 |  | 54 | 61 | 0.015833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_181-3_1_5_line_66 |  | 55 | 96 | 0.00057671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_181-3_1_5_line_67 |  | 57 | 58 | 1.2698e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_181-3_1_5_line_68 |  | 57 | 59 | 0.0056541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_181-3_1_5_line_69 |  | 58 | 60 | 0.0087791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_181-3_1_5_line_70 |  | 59 | 61 | 0.0052199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_181-3_1_5_line_71 |  | 60 | 62 | 0.00066956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_181-3_1_5_line_72 |  | 62 | 65 | 0.0051925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_181-3_1_5_line_73 |  | 63 | 64 | 0.0093752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_181-3_1_5_line_74 |  | 66 | 67 | 0.042929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_181-3_1_5_line_75 |  | 67 | 68 | 0.031039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_181-3_1_5_line_76 |  | 68 | 72 | 0.039193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_181-3_1_5_line_77 |  | 68 | 73 | 0.026183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_181-3_1_5_line_78 |  | 69 | 70 | 0.01495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_181-3_1_5_line_79 |  | 69 | 71 | 0.11533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_181-3_1_5_line_80 |  | 70 | 74 | 0.028772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_181-3_1_5_line_81 |  | 71 | 77 | 0.072325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_181-3_1_5_line_82 |  | 71 | 78 | 0.020512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_181-3_1_5_line_83 |  | 71 | 75 | 0.060129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_181-3_1_5_line_84 |  | 72 | 74 | 0.064119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_181-3_1_5_line_85 |  | 73 | 90 | 0.013222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_181-3_1_5_line_86 |  | 75 | 76 | 0.042678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_181-3_1_5_line_87 |  | 77 | 88 | 0.017144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_181-3_1_5_line_88 |  | 79 | 80 | 0.015022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_181-3_1_5_line_89 |  | 79 | 81 | 0.00090215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_181-3_1_5_line_90 |  | 80 | 82 | 0.019987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_181-3_1_5_line_91 |  | 81 | 83 | 0.020062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_181-3_1_5_line_92 |  | 82 | 84 | 0.037375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_181-3_1_5_line_93 |  | 83 | 85 | 0.0027517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_181-3_1_5_line_94 |  | 84 | 107 | 0.0046864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_181-3_1_5_line_95 |  | 85 | 109 | 0.019749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_181-3_1_5_line_96 |  | 86 | 87 | 0.032721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_181-3_1_5_line_97 |  | 86 | 88 | 0.018336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_181-3_1_5_line_98 |  | 87 | 89 | 0.0093101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_181-3_1_5_line_99 |  | 90 | 91 | 0.051235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_181-3_1_5_line_100 |  | 92 | 93 | 0.04691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_181-3_1_5_line_101 |  | 93 | 94 | 0.020241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_181-3_1_5_line_102 |  | 96 | 97 | 0.0098345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_181-3_1_5_line_103 |  | 97 | 98 | 0.02434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_181-3_1_5_line_104 |  | 98 | 99 | 0.019508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_181-3_1_5_line_105 |  | 98 | 100 | 0.0079848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_181-3_1_5_line_106 |  | 99 | 111 | 0.015039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_181-3_1_5_line_107 |  | 102 | 103 | 0.023809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_181-3_1_5_line_108 |  | 103 | 104 | 0.0089866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_181-3_1_5_line_109 |  | 104 | 105 | 0.029696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_181-3_1_5_line_110 |  | 105 | 110 | 0.055785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_181-3_1_5_line_111 |  | 105 | 111 | 0.0067282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_181-3_1_5_line_112 |  | 107 | 108 | 0.029259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_181-3_1_5_line_113 |  | 109 | 110 | 0.023359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_181-3_1_5_line_114 |  | 114 | 115 | 0.020206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_181-3_1_5_line_115 |  | 114 | 116 | 0.023249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_181-3_1_5_line_116 |  | 116 | 117 | 0.052064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_181-3_1_5_trafo_29 | 0.63 MVA 20/0.4 kV | 118 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2706406.8902 | 1253373.2825 | 2706420.2082 | 1253380.5499 | 2706430.6969 | 1253390.7132 | 2706434.1507 | 1253393.3775 | 2706455.6239 | 1253411.7227 | 2706459.5544 | 1253415.1628 | 2706464.8413 | 1253419.9729 | 2706468.6865 | 1253423.5338
1 | 2706468.6865 | 1253423.5338 | 2706476.0355 | 1253432.0172 | 2706481.1981 | 1253443.3192 | 2706485.6505 | 1253458.4338 | 2706486.723 | 1253473.9101 | 2706486.7364 | 1253485.3308 | 2706484.6833 | 1253494.5792 | 2706476.884 | 1253511.1303 | 2706475.3718 | 1253513.5021
2 | 2706301.9969 | 1253389.9796 | 2706305.0493 | 1253389.3672 | 2706308.1984 | 1253388.8344 | 2706311.587 | 1253387.9945 | 2706321.5158 | 1253385.6375 | 2706375.979 | 1253372.7936 | 2706384.7405 | 1253370.727 | 2706395.8414 | 1253371.1823 | 2706406.8902 | 1253373.2825
3 | 2706406.8902 | 1253373.2825 | 2706409.9449 | 1253344.4138 | 2706408.7664 | 1253335.1123
4 | 2706462.3463 | 1253533.9321 | 2706475.3718 | 1253513.5021
5 | 2706042.1865 | 1253470.5419 | 2706042.0563 | 1253468.4181 | 2706042.2284 | 1253448.5309
6 | 2706042.1865 | 1253470.5419 | 2706043.4462 | 1253491.0948 | 2706045.0813 | 1253497.6349
7 | 2706042.2284 | 1253448.5309 | 2706042.2386 | 1253447.3584
8 | 2706046.2334 | 1253502.243 | 2706045.0813 | 1253497.6349
9 | 2706042.2386 | 1253447.3584 | 2706042.5666 | 1253409.4432
10 | 2706055.2293 | 1253536.8653 | 2706054.7021 | 1253522.066 | 2706048.4955 | 1253511.2905 | 2706046.2334 | 1253502.243
11 | 2706042.5666 | 1253409.4432 | 2706042.7011 | 1253393.8914
12 | 2706055.2293 | 1253536.8653 | 2706060.4363 | 1253552.4601 | 2706063.0173 | 1253573.1009 | 2706062.5262 | 1253585.6535
13 | 2706055.2293 | 1253536.8653 | 2706045.0967 | 1253553.9867
14 | 2706071.6923 | 1253521.9256 | 2706055.2293 | 1253536.8653
15 | 2706301.9969 | 1253389.9796 | 2706301.9829 | 1253374.6812
16 | 2706301.9969 | 1253389.9796 | 2706291.5746 | 1253392.0832 | 2706281.0027 | 1253392.4272 | 2706273.842 | 1253391.6006
17 | 2706407.3221 | 1253323.7132 | 2706408.7664 | 1253335.1123
18 | 2706256.2029 | 1253567.3471 | 2706248.5003 | 1253558.7908
19 | 2706256.2029 | 1253567.3471 | 2706231.469 | 1253591.8758
20 | 2706248.5003 | 1253558.7908 | 2706250.962 | 1253556.611 | 2706263.1941 | 1253544.7525
21 | 2706202.4112 | 1253620.6926 | 2706231.469 | 1253591.8758
22 | 2706188.4964 | 1253515.88 | 2706181.8952 | 1253517.0181
23 | 2706181.8952 | 1253517.0181 | 2706177.6814 | 1253494.7775
24 | 2706188.4964 | 1253515.88 | 2706190.2048 | 1253537.2772
25 | 2706188.4964 | 1253515.88 | 2706212.3375 | 1253512.4713 | 2706222.8618 | 1253510.5584 | 2706220.8525 | 1253495.9438
26 | 2706167.3026 | 1253465.1032 | 2706169.9546 | 1253479.6626 | 2706176.1111 | 1253486.4896 | 2706177.6814 | 1253494.7775
27 | 2706191.107 | 1253605.9335 | 2706197.8782 | 1253612.5603 | 2706198.0739 | 1253615.9554 | 2706202.4112 | 1253620.6926
28 | 2706191.107 | 1253605.9335 | 2706190.6563 | 1253603.5214
29 | 2706153.2138 | 1253669.5506 | 2706156.1931 | 1253659.5403 | 2706143.6031 | 1253608.6604
30 | 2706153.2138 | 1253669.5506 | 2706140.7439 | 1253667.6145 | 2706136.6634 | 1253668.455
31 | 2706127.2861 | 1253571.773 | 2706137.0393 | 1253582.134 | 2706143.6031 | 1253608.6604
32 | 2706131.8852 | 1253500.8866 | 2706107.596 | 1253505.2995 | 2706089.3649 | 1253511.6285
33 | 2706122.4166 | 1253523.8912 | 2706127.1116 | 1253514.5789 | 2706133.6964 | 1253513.5182 | 2706132.7573 | 1253506.9627 | 2706131.8852 | 1253500.8866
34 | 2706131.8852 | 1253500.8866 | 2706129.4877 | 1253478.025 | 2706128.1869 | 1253458.3968 | 2706128.2883 | 1253450.3773
35 | 2706071.6923 | 1253521.9256 | 2706085.4822 | 1253512.9764 | 2706089.3649 | 1253511.6285
36 | 2706122.4166 | 1253523.8912 | 2706125.6505 | 1253536.3037 | 2706127.1306 | 1253542.6059
37 | 2706128.3674 | 1253444.1218 | 2706128.2883 | 1253450.3773
38 | 2706127.2861 | 1253571.773 | 2706131.5541 | 1253561.4411 | 2706127.1306 | 1253542.6059
39 | 2706301.9829 | 1253374.6812 | 2706301.9611 | 1253351.0429
40 | 2706253.548 | 1253385.212 | 2706258.792 | 1253387.8027 | 2706270.9634 | 1253391.2683 | 2706273.842 | 1253391.6006
41 | 2706042.809 | 1253381.4228 | 2706042.7011 | 1253393.8914
42 | 2706275.1533 | 1253460.6029 | 2706270.8758 | 1253462.1467 | 2706267.4807 | 1253462.9626
43 | 2706256.1414 | 1253459.934 | 2706261.9743 | 1253462.3539 | 2706266.8283 | 1253463.1194 | 2706267.4807 | 1253462.9626
44 | 2706275.1533 | 1253460.6029 | 2706283.866 | 1253457.4584
45 | 2706256.1414 | 1253459.934 | 2706252.9251 | 1253458.5996 | 2706245.8905 | 1253458.2287 | 2706237.8442 | 1253460.8558
46 | 2706229.0539 | 1253463.7257 | 2706237.8442 | 1253460.8558
47 | 2706215.252 | 1253468.2319 | 2706229.0539 | 1253463.7257
48 | 2706242.7182 | 1253488.3907 | 2706233.5293 | 1253491.5648
49 | 2706220.8525 | 1253495.9438 | 2706233.5293 | 1253491.5648
50 | 2706242.7182 | 1253488.3907 | 2706250.5978 | 1253485.6688 | 2706258.0727 | 1253485.892 | 2706260.1019 | 1253486.499
51 | 2706220.8525 | 1253495.9438 | 2706216.0974 | 1253472.4153
52 | 2706260.1019 | 1253486.499 | 2706270.4509 | 1253489.5948 | 2706273.9638 | 1253489.2973
53 | 2706215.252 | 1253468.2319 | 2706216.0974 | 1253472.4153
54 | 2706280.2181 | 1253487.8007 | 2706275.976 | 1253489.1269 | 2706273.9638 | 1253489.2973
55 | 2706215.252 | 1253468.2319 | 2706212.8857 | 1253449.4025
56 | 2706190.4073 | 1253539.8145 | 2706190.2048 | 1253537.2772
57 | 2706241.9927 | 1253429.9564 | 2706233.5315 | 1253432.4305
58 | 2706214.1455 | 1253428.9578 | 2706233.5315 | 1253432.4305
59 | 2706241.9927 | 1253429.9564 | 2706247.7565 | 1253428.2711 | 2706247.7565 | 1253428.2711
60 | 2706214.1455 | 1253428.9578 | 2706217.5341 | 1253417.85
61 | 2706214.1455 | 1253428.9578 | 2706213.9441 | 1253430.8289
62 | 2706247.7565 | 1253428.2711 | 2706252.6877 | 1253428.4095
63 | 2706223.7133 | 1253407.8676 | 2706217.85 | 1253416.8144 | 2706217.5341 | 1253417.85
64 | 2706213.9441 | 1253430.8289 | 2706212.3793 | 1253445.3729 | 2706212.8857 | 1253449.4025
65 | 2706268.2766 | 1253431.0691 | 2706254.3492 | 1253428.4562 | 2706252.6877 | 1253428.4095
66 | 2706224.0294 | 1253407.3852 | 2706223.7133 | 1253407.8676
67 | 2706278.9024 | 1253429.298 | 2706278.9143 | 1253429.2936
68 | 2706273.4719 | 1253430.6868 | 2706275.7233 | 1253430.4857 | 2706278.9024 | 1253429.298
69 | 2706287.1383 | 1253426.2213 | 2706278.9143 | 1253429.2936
70 | 2706273.4719 | 1253430.6868 | 2706268.5724 | 1253431.1246 | 2706268.2766 | 1253431.0691
71 | 2706287.1383 | 1253426.2213 | 2706287.7655 | 1253425.987
72 | 2706287.7655 | 1253425.987 | 2706290.691 | 1253424.8941 | 2706292.7516 | 1253424.7019
73 | 2706280.2181 | 1253487.8007 | 2706289.1662 | 1253485.0033
74 | 2705987.9703 | 1253594.9383 | 2705984.6253 | 1253601.5877 | 2705973.6922 | 1253612.0117 | 2705961.3807 | 1253619.7645 | 2705955.7917 | 1253621.4233
75 | 2705997.6128 | 1253566.2024 | 2705998.303 | 1253572.3308 | 2705993.1078 | 1253584.7257 | 2705987.9703 | 1253594.9383
76 | 2705997.6128 | 1253566.2024 | 2705998.3433 | 1253560.3885 | 2706003.1089 | 1253553.0233 | 2706005.1906 | 1253542.9746 | 2706005.2691 | 1253528.6757
77 | 2705997.6128 | 1253566.2024 | 2705991.2477 | 1253565.1209 | 2705987.954 | 1253569.9437 | 2705984.2383 | 1253571.7787 | 2705974.502 | 1253571.4299
78 | 2706037.4778 | 1253566.8608 | 2706045.0967 | 1253553.9867
79 | 2705975.157 | 1253663.8135 | 2705978.8957 | 1253656.0518 | 2705981.4093 | 1253652.227 | 2705984.0315 | 1253648.2373 | 2705987.2745 | 1253643.2913 | 2706023.5381 | 1253587.5615 | 2706037.4778 | 1253566.8608
80 | 2706045.0967 | 1253553.9867 | 2706041.7679 | 1253553.6046 | 2706034.8327 | 1253552.7464 | 2706029.3664 | 1253546.1432 | 2706024.1071 | 1253537.8021
81 | 2705975.157 | 1253663.8135 | 2705956.3719 | 1253695.948 | 2705932.9384 | 1253722.1725
82 | 2705975.157 | 1253663.8135 | 2705981.3236 | 1253667.1265 | 2705988.0492 | 1253675.8873 | 2705989.1819 | 1253678.0792
83 | 2705975.157 | 1253663.8135 | 2705978.8957 | 1253656.0518 | 2705981.4093 | 1253652.227 | 2705984.0315 | 1253648.2373 | 2705987.2745 | 1253643.2913 | 2706004.3257 | 1253649.4236 | 2706022.4078 | 1253648.1351
84 | 2706005.2691 | 1253528.6757 | 2706005.284 | 1253525.9624 | 2706002.7426 | 1253509.0031 | 2706002.8121 | 1253505.1234 | 2706003.9759 | 1253504.6105 | 2706006.2713 | 1253506.2307 | 2706015.431 | 1253524.0424 | 2706024.1071 | 1253537.8021
85 | 2705961.2885 | 1253570.9564 | 2705974.502 | 1253571.4299
86 | 2706022.4078 | 1253648.1351 | 2706008.3214 | 1253639.5315 | 2706005.8557 | 1253635.6286 | 2706006.0568 | 1253630.2946 | 2706014.1094 | 1253616.2175
87 | 2705932.9384 | 1253722.1725 | 2705945.8864 | 1253733.4087
88 | 2706158.922 | 1253378.7279 | 2706151.6377 | 1253391.8653
89 | 2706158.922 | 1253378.7279 | 2706159.3595 | 1253377.9389
90 | 2706144.0772 | 1253410.3343 | 2706149.8808 | 1253395.0339 | 2706151.6377 | 1253391.8653
91 | 2706168.8032 | 1253360.2612 | 2706168.0374 | 1253362.2881 | 2706159.3595 | 1253377.9389
92 | 2706128.3674 | 1253444.1218 | 2706136.9689 | 1253429.0747 | 2706144.0772 | 1253410.3343
93 | 2706168.8032 | 1253360.2612 | 2706169.7758 | 1253357.6871
94 | 2706128.3674 | 1253444.1218 | 2706128.4283 | 1253439.4358
95 | 2706174.5748 | 1253338.7107 | 2706173.8133 | 1253347.0014 | 2706169.7758 | 1253357.6871
96 | 2705940.5584 | 1253771.5417 | 2705946.477 | 1253759.6897 | 2705959.7348 | 1253745.4263
97 | 2705945.8864 | 1253733.4087 | 2705959.7348 | 1253745.4263 | 2705959.7348 | 1253745.4263
98 | 2705940.5584 | 1253771.5417 | 2705939.2448 | 1253774.1721 | 2705935.0907 | 1253779.0012
99 | 2705961.2885 | 1253570.9564 | 2705961.2885 | 1253570.9564 | 2705959.6389 | 1253574.5743 | 2705946.5314 | 1253577.887 | 2705929.7552 | 1253587.1612 | 2705917.1805 | 1253594.5218
100 | 2706186.5808 | 1253583.747 | 2706193.3829 | 1253577.0841 | 2706190.4073 | 1253539.8145
101 | 2706190.6563 | 1253603.5214 | 2706188.3321 | 1253591.0827 | 2706186.5155 | 1253583.8109 | 2706186.5808 | 1253583.747
102 | 2706229.6309 | 1253399.3267 | 2706228.5968 | 1253400.4159 | 2706224.0294 | 1253407.3852
103 | 2706246.3892 | 1253381.6753 | 2706229.6309 | 1253399.3267
104 | 2706246.3892 | 1253381.6753 | 2706238.2225 | 1253374.5786 | 2706232.5989 | 1253367.9549
105 | 2706246.3892 | 1253381.6753 | 2706253.548 | 1253385.212
106 | 2706222.8659 | 1253356.4908 | 2706232.5989 | 1253367.9549
107 | 2706247.6444 | 1253325.9137 | 2706265.5758 | 1253310.2503
108 | 2706240.8763 | 1253331.8257 | 2706247.6444 | 1253325.9137
109 | 2706218.5113 | 1253351.3618 | 2706240.8763 | 1253331.8257
110 | 2706176.7113 | 1253315.4499 | 2706183.0969 | 1253319.1896 | 2706186.622 | 1253321.2545 | 2706194.2399 | 1253325.7169 | 2706203.0941 | 1253332.7814 | 2706218.5113 | 1253351.3618
111 | 2706218.5113 | 1253351.3618 | 2706222.8659 | 1253356.4908
112 | 2706128.4283 | 1253439.4358 | 2706128.8085 | 1253410.1793
113 | 2706176.7113 | 1253315.4499 | 2706174.5748 | 1253338.7107
114 | 2706462.3463 | 1253533.9321 | 2706445.8852 | 1253522.214
115 | 2706426.9447 | 1253508.731 | 2706445.8852 | 1253522.214
116 | 2706426.9447 | 1253508.731 | 2706456.1378 | 1253465.6212

## bus_geodata
| x | y | coords
0 | 2706468.6865 | 1253423.5338
1 | 2706406.8902 | 1253373.2825
2 | 2706475.3718 | 1253513.5021
3 | 2706042.1865 | 1253470.5419
4 | 2706042.2284 | 1253448.5309
5 | 2706045.0813 | 1253497.6349
6 | 2706042.2386 | 1253447.3584
7 | 2706046.2334 | 1253502.243
8 | 2706042.5666 | 1253409.4432
9 | 2706055.2293 | 1253536.8653
10 | 2706301.9969 | 1253389.9796
11 | 2706408.7664 | 1253335.1123
12 | 2706256.2029 | 1253567.3471
13 | 2706248.5003 | 1253558.7908
14 | 2706231.469 | 1253591.8758
15 | 2706181.8952 | 1253517.0181
16 | 2706188.4964 | 1253515.88
17 | 2706177.6814 | 1253494.7775
18 | 2706202.4112 | 1253620.6926
19 | 2706191.107 | 1253605.9335
20 | 2706153.2138 | 1253669.5506
21 | 2706143.6031 | 1253608.6604
22 | 2706136.6634 | 1253668.455
23 | 2706131.8852 | 1253500.8866
24 | 2706089.3649 | 1253511.6285
25 | 2706122.4166 | 1253523.8912
26 | 2706128.2883 | 1253450.3773
27 | 2706127.1306 | 1253542.6059
28 | 2706301.9829 | 1253374.6812
29 | 2706273.842 | 1253391.6006
30 | 2706042.7011 | 1253393.8914
31 | 2706042.809 | 1253381.4228
32 | 2706127.2861 | 1253571.773
33 | 2706267.4807 | 1253462.9626
34 | 2706275.1533 | 1253460.6029
35 | 2706256.1414 | 1253459.934
36 | 2706283.866 | 1253457.4584
37 | 2706237.8442 | 1253460.8558
38 | 2706229.0539 | 1253463.7257
39 | 2706233.5293 | 1253491.5648
40 | 2706242.7182 | 1253488.3907
41 | 2706220.8525 | 1253495.9438
42 | 2706260.1019 | 1253486.499
43 | 2706216.0974 | 1253472.4153
44 | 2706273.9638 | 1253489.2973
45 | 2706215.252 | 1253468.2319
46 | 2706190.2048 | 1253537.2772
47 | 2706263.1941 | 1253544.7525
48 | 2706233.5315 | 1253432.4305
49 | 2706241.9927 | 1253429.9564
50 | 2706214.1454 | 1253428.9578
51 | 2706247.7565 | 1253428.2711
52 | 2706217.5341 | 1253417.85
53 | 2706213.9441 | 1253430.8289
54 | 2706252.6877 | 1253428.4095
55 | 2706223.7133 | 1253407.8676
56 | 2706212.8857 | 1253449.4025
57 | 2706278.9024 | 1253429.298
58 | 2706278.9143 | 1253429.2936
59 | 2706273.4719 | 1253430.6868
60 | 2706287.1383 | 1253426.2213
61 | 2706268.2766 | 1253431.0691
62 | 2706287.7655 | 1253425.987
63 | 2706280.2181 | 1253487.8007
64 | 2706289.1662 | 1253485.0033
65 | 2706292.7516 | 1253424.7019
66 | 2705955.7917 | 1253621.4233
67 | 2705987.9703 | 1253594.9383
68 | 2705997.6128 | 1253566.2024
69 | 2706037.4778 | 1253566.8608
70 | 2706045.0967 | 1253553.9867
71 | 2705975.157 | 1253663.8135
72 | 2706005.2691 | 1253528.6757
73 | 2705974.502 | 1253571.4299
74 | 2706024.1071 | 1253537.8021
75 | 2706022.4078 | 1253648.1351
76 | 2706014.1094 | 1253616.2175
77 | 2705932.9384 | 1253722.1725
78 | 2705989.1819 | 1253678.0792
79 | 2706158.922 | 1253378.7279
80 | 2706151.6377 | 1253391.8653
81 | 2706159.3595 | 1253377.9389
82 | 2706144.0772 | 1253410.3343
83 | 2706168.8032 | 1253360.2612
84 | 2706128.3674 | 1253444.1218
85 | 2706169.7758 | 1253357.6871
86 | 2705959.7348 | 1253745.4263
87 | 2705940.5584 | 1253771.5417
88 | 2705945.8864 | 1253733.4087
89 | 2705935.0907 | 1253779.0012
90 | 2705961.2885 | 1253570.9564
91 | 2705917.1805 | 1253594.5218
92 | 2706190.4073 | 1253539.8145
93 | 2706186.5808 | 1253583.747
94 | 2706190.6563 | 1253603.5214
95 | 2706071.6923 | 1253521.9256
96 | 2706224.0294 | 1253407.3852
97 | 2706229.6309 | 1253399.3267
98 | 2706246.3892 | 1253381.6753
99 | 2706232.5989 | 1253367.9549
100 | 2706253.548 | 1253385.212
101 | 2706062.5262 | 1253585.6535
102 | 2706265.5758 | 1253310.2503
103 | 2706247.6444 | 1253325.9137
104 | 2706240.8763 | 1253331.8257
105 | 2706218.5113 | 1253351.3618
106 | 2706301.9611 | 1253351.0429
107 | 2706128.4283 | 1253439.4358
108 | 2706128.8085 | 1253410.1793
109 | 2706174.5748 | 1253338.7107
110 | 2706176.7113 | 1253315.4499
111 | 2706222.8659 | 1253356.4908
112 | 2706167.3027 | 1253465.1032
113 | 2706407.3221 | 1253323.7132
114 | 2706445.8852 | 1253522.214
115 | 2706462.3463 | 1253533.9321
116 | 2706426.9447 | 1253508.731
117 | 2706456.1378 | 1253465.6212
118 | 2706188.4964 | 1253515.88

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98694 | -0.24967 | 0 | 0
1 | 0.98794 | -0.23016 | 0 | 0
2 | 0.98572 | -0.27336 | 0.0029415 | 0.00073721
3 | 0.9747 | -0.48722 | 0.0033173 | 0.00083138
4 | 0.9743 | -0.49516 | 0.0028966 | 0.00072597
5 | 0.97528 | -0.47571 | 0.0028635 | 0.00071766
6 | 0.97428 | -0.49552 | 0.0014793 | 0.00037075
7 | 0.9754 | -0.47346 | 0.00084318 | 0.00021132
8 | 0.97374 | -0.50615 | 0.0013727 | 0.00034403
9 | 0.97631 | -0.45561 | 0 | 0
10 | 0.98948 | -0.20045 | 0 | 0
11 | 0.98788 | -0.23145 | 0.00094406 | 0.0002366
12 | 0.9955 | -0.086524 | 0 | 0
13 | 0.99541 | -0.088172 | 0 | 0
14 | 0.99576 | -0.08153 | 0.0089701 | 0.0022481
15 | 1 | 0 | -0.32068 | -0.081598
16 | 0.99954 | -0.0086314 | 0 | 0
17 | 0.99962 | -0.0072475 | 0.00888 | 0.0022255
18 | 0.99639 | -0.069219 | 0 | 0
19 | 0.99669 | -0.063426 | 0 | 0
20 | 0.97554 | -0.47088 | 0 | 0
21 | 0.97617 | -0.45853 | 0.018332 | 0.0045944
22 | 0.97538 | -0.47418 | 0.010732 | 0.0026896
23 | 0.98041 | -0.37545 | 0 | 0
24 | 0.97873 | -0.40806 | 0.0013438 | 0.00033679
25 | 0.97902 | -0.40265 | 0 | 0
26 | 0.98196 | -0.34522 | 0.0042287 | 0.0010598
27 | 0.97812 | -0.42028 | 0.021106 | 0.0052897
28 | 0.98944 | -0.20114 | 0.00099142 | 0.00024847
29 | 0.98995 | -0.19131 | 0.0030329 | 0.00076013
30 | 0.97354 | -0.51013 | 0.012887 | 0.0032297
31 | 0.97353 | -0.51036 | 0.0010079 | 0.00025261
32 | 0.97729 | -0.43646 | 0 | 0
33 | 0.9947 | -0.10054 | 0.0020181 | 0.00050578
34 | 0.99468 | -0.10105 | 0.0018121 | 0.00045416
35 | 0.99476 | -0.099372 | 0.0018629 | 0.0004669
36 | 0.99466 | -0.10134 | 0.0017611 | 0.00044138
37 | 0.99489 | -0.096879 | 0.0015832 | 0.00039679
38 | 0.99497 | -0.095407 | 0.0019464 | 0.0004878
39 | 0.99653 | -0.065752 | 0.002101 | 0.00052656
40 | 0.99644 | -0.067372 | 0.0018194 | 0.00045599
41 | 0.99667 | -0.063023 | 0 | 0
42 | 0.99632 | -0.069788 | 0.0019029 | 0.00047692
43 | 0.99534 | -0.08827 | 0.0088802 | 0.0022256
44 | 0.99624 | -0.07124 | 0.0020082 | 0.00050329
45 | 0.99511 | -0.092599 | 0 | 0
46 | 0.99866 | -0.025643 | 0.0080502 | 0.0020176
47 | 0.99526 | -0.091087 | 0.0081514 | 0.0020429
48 | 0.99285 | -0.13582 | 0.0023192 | 0.00058124
49 | 0.99275 | -0.1378 | 0.0012031 | 0.00030152
50 | 0.99312 | -0.13059 | 0 | 0
51 | 0.99268 | -0.13902 | 0.0012465 | 0.00031241
52 | 0.99259 | -0.14074 | 0.0040578 | 0.001017
53 | 0.99321 | -0.12882 | 0.0038623 | 0.00096797
54 | 0.99264 | -0.13992 | 0.001372 | 0.00034384
55 | 0.99206 | -0.15083 | 0.0013987 | 0.00035056
56 | 0.99415 | -0.11095 | 0.0029608 | 0.00074204
57 | 0.99244 | -0.14373 | 0.0013876 | 0.00034776
58 | 0.99244 | -0.14373 | 0.0011815 | 0.00029612
59 | 0.99247 | -0.1431 | 0.0012106 | 0.00030339
60 | 0.99241 | -0.14431 | 0.0012078 | 0.00030271
61 | 0.99251 | -0.1424 | 0.0013563 | 0.00033992
62 | 0.99241 | -0.14434 | 0.0012834 | 0.00032166
63 | 0.99622 | -0.071667 | 0.0018309 | 0.00045886
64 | 0.99621 | -0.071985 | 0.0019312 | 0.000484
65 | 0.9924 | -0.14446 | 0.0012545 | 0.0003144
66 | 0.97138 | -0.55267 | 0.0051014 | 0.0012785
67 | 0.97158 | -0.54863 | 0.0060983 | 0.0015284
68 | 0.97191 | -0.54221 | 0 | 0
69 | 0.97526 | -0.4762 | 0 | 0
70 | 0.97546 | -0.47226 | 0 | 0
71 | 0.97371 | -0.50666 | 0 | 0
72 | 0.97286 | -0.52334 | 0.0031893 | 0.00079932
73 | 0.97154 | -0.54942 | 0.0062313 | 0.0015617
74 | 0.97462 | -0.4888 | 0.0020494 | 0.00051364
75 | 0.97339 | -0.51303 | 0 | 0
76 | 0.97316 | -0.51755 | 0.0057604 | 0.0014437
77 | 0.97318 | -0.51712 | 0 | 0
78 | 0.9737 | -0.50694 | 0.0007527 | 0.00018864
79 | 0.98455 | -0.29504 | 0.00056002 | 0.00014035
80 | 0.98404 | -0.30498 | 0.003795 | 0.00095112
81 | 0.98458 | -0.29444 | 0.0019243 | 0.00048227
82 | 0.98337 | -0.31787 | 0.0038749 | 0.00097115
83 | 0.98528 | -0.28097 | 0.00095222 | 0.00023865
84 | 0.98216 | -0.34137 | 0 | 0
85 | 0.98537 | -0.27911 | 0.0014865 | 0.00037255
86 | 0.97294 | -0.52199 | 0.0006971 | 0.00017471
87 | 0.97274 | -0.52581 | 0.0010051 | 0.0002519
88 | 0.97306 | -0.51961 | 0.00081776 | 0.00020495
89 | 0.9727 | -0.52673 | 0.0053455 | 0.0013397
90 | 0.97144 | -0.55154 | 0.0051107 | 0.0012809
91 | 0.97127 | -0.55491 | 0.0035685 | 0.00089435
92 | 0.99857 | -0.027304 | 0.0056212 | 0.0014088
93 | 0.99722 | -0.053345 | 0.0053884 | 0.0013505
94 | 0.99673 | -0.062688 | 0.0091997 | 0.0023057
95 | 0.97797 | -0.42308 | 0 | 0
96 | 0.99203 | -0.15132 | 0.001006 | 0.00025213
97 | 0.9916 | -0.15966 | 0.00093032 | 0.00023316
98 | 0.99052 | -0.18021 | 0 | 0
99 | 0.98976 | -0.19483 | 0.0017665 | 0.00044274
100 | 0.99036 | -0.18329 | 0.00059528 | 0.00014919
101 | 0.97594 | -0.46277 | 0.0078595 | 0.0019698
102 | 0.98853 | -0.21845 | 0.0054544 | 0.001367
103 | 0.98865 | -0.21613 | 0.0008829 | 0.00022128
104 | 0.9887 | -0.21512 | 0.0016638 | 0.00041699
105 | 0.98892 | -0.21088 | 0 | 0
106 | 0.98941 | -0.20179 | 0.0015389 | 0.00038569
107 | 0.98214 | -0.34165 | 0.002237 | 0.00056065
108 | 0.98212 | -0.34222 | 0.0010817 | 0.00027109
109 | 0.98607 | -0.26565 | 0.0028976 | 0.0007262
110 | 0.98691 | -0.24945 | 0 | 0
111 | 0.98917 | -0.206 | 0.0039846 | 0.00099863
112 | 0.99934 | -0.012612 | 0.0094811 | 0.0023762
113 | 0.98787 | -0.23165 | 0.00093783 | 0.00023504
114 | 0.98529 | -0.28189 | 0.0084232 | 0.0021111
115 | 0.98549 | -0.27801 | 0 | 0
116 | 0.98524 | -0.28284 | 0 | 0
117 | 0.98513 | -0.28496 | 0.00227 | 0.00056891
118 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013655 | -0.0034273 | 0.013667 | 0.0034344 | 1.2716e-05 | 7.115e-06 | 0.020589 | 0.020589 | 0.020589 | 0.98694 | -0.24967 | 0.98794 | -0.23016 | 5.6564
1 | 0.013655 | 0.0034273 | -0.013639 | -0.0034186 | 1.5408e-05 | 8.6241e-06 | 0.020589 | 0.02059 | 0.02059 | 0.98694 | -0.24967 | 0.98572 | -0.27336 | 5.6565
2 | -0.015549 | -0.0039055 | 0.015572 | 0.0039182 | 2.208e-05 | 1.2755e-05 | 0.023423 | 0.023423 | 0.023423 | 0.98794 | -0.23016 | 0.98948 | -0.20045 | 6.435
3 | 0.001882 | 0.00047109 | -0.0018819 | -0.0004715 | 1.1571e-07 | -4.1769e-07 | 0.0028344 | 0.0028346 | 0.0028346 | 0.98794 | -0.23016 | 0.98788 | -0.23145 | 0.77874
4 | 0.010698 | 0.0026814 | -0.010695 | -0.0026802 | 2.3696e-06 | 1.2078e-06 | 0.016149 | 0.016149 | 0.016149 | 0.98572 | -0.27336 | 0.98549 | -0.27801 | 4.4366
5 | 0.019661 | 0.0049335 | -0.019654 | -0.004929 | 7.4391e-06 | 4.4867e-06 | 0.030018 | 0.030018 | 0.030018 | 0.9747 | -0.48722 | 0.9743 | -0.49516 | 8.2467
6 | -0.022978 | -0.0057649 | 0.022991 | 0.0057726 | 1.2615e-05 | 7.7327e-06 | 0.035082 | 0.035082 | 0.035082 | 0.9747 | -0.48722 | 0.97528 | -0.47571 | 9.6379
7 | 0.016757 | 0.004203 | -0.016757 | -0.0042029 | 2.8804e-07 | 1.6974e-07 | 0.025594 | 0.025594 | 0.025594 | 0.9743 | -0.49516 | 0.97428 | -0.49552 | 7.0313
8 | -0.025855 | -0.0064903 | 0.025857 | 0.006492 | 2.7723e-06 | 1.715e-06 | 0.039451 | 0.039451 | 0.039451 | 0.97528 | -0.47571 | 0.9754 | -0.47346 | 10.8381
9 | 0.015278 | 0.0038321 | -0.01527 | -0.0038276 | 7.7421e-06 | 4.4831e-06 | 0.023335 | 0.023335 | 0.023335 | 0.97428 | -0.49552 | 0.97374 | -0.50615 | 6.4106
10 | -0.026701 | -0.0067033 | 0.026723 | 0.0067174 | 2.2758e-05 | 1.4108e-05 | 0.040737 | 0.040737 | 0.040737 | 0.9754 | -0.47346 | 0.97631 | -0.45561 | 11.1915
11 | 0.013897 | 0.0034836 | -0.013894 | -0.0034821 | 2.6304e-06 | 1.49e-06 | 0.021237 | 0.021237 | 0.021237 | 0.97374 | -0.50615 | 0.97354 | -0.51013 | 5.8344
12 | 0.0078622 | 0.0019709 | -0.0078595 | -0.0019698 | 2.682e-06 | 1.0939e-06 | 0.011983 | 0.011983 | 0.011983 | 0.97631 | -0.45561 | 0.97594 | -0.46277 | 3.2921
13 | 0.045905 | 0.011565 | -0.045869 | -0.011542 | 3.652e-05 | 2.3124e-05 | 0.069987 | 0.069988 | 0.069988 | 0.97631 | -0.45561 | 0.97546 | -0.47226 | 19.2273
14 | -0.080491 | -0.020254 | 0.080616 | 0.020334 | 0.00012533 | 7.9935e-05 | 0.12271 | 0.12271 | 0.12271 | 0.97631 | -0.45561 | 0.97797 | -0.42308 | 33.7108
15 | 0.0025305 | 0.00063375 | -0.0025304 | -0.00063389 | 8.3073e-08 | -1.4333e-07 | 0.0038053 | 0.0038054 | 0.0038054 | 0.98948 | -0.20045 | 0.98944 | -0.20114 | 1.0454
16 | -0.018102 | -0.004552 | 0.01811 | 0.0045567 | 7.9006e-06 | 4.6912e-06 | 0.027228 | 0.027228 | 0.027228 | 0.98948 | -0.20045 | 0.98995 | -0.19131 | 7.4802
17 | 0.00093784 | 0.0002349 | -0.00093783 | -0.00023504 | 8.5983e-09 | -1.4161e-07 | 0.0014126 | 0.0014127 | 0.0014127 | 0.98788 | -0.23145 | 0.98787 | -0.23165 | 0.38809
18 | 0.0081532 | 0.0020437 | -0.0081526 | -0.0020434 | 6.4035e-07 | 2.6036e-07 | 0.012187 | 0.012187 | 0.012187 | 0.9955 | -0.086524 | 0.99541 | -0.088172 | 3.3481
19 | -0.0081532 | -0.0020437 | 0.0081552 | 0.0020445 | 1.9401e-06 | 7.8868e-07 | 0.012187 | 0.012187 | 0.012187 | 0.9955 | -0.086524 | 0.99576 | -0.08153 | 3.3481
20 | 0.0081526 | 0.0020434 | -0.0081514 | -0.0020429 | 1.132e-06 | 4.6034e-07 | 0.012187 | 0.012187 | 0.012187 | 0.99541 | -0.088172 | 0.99526 | -0.091087 | 3.3481
21 | -0.017125 | -0.0042926 | 0.017135 | 0.0042985 | 1.0051e-05 | 5.8998e-06 | 0.025591 | 0.025591 | 0.025591 | 0.99576 | -0.08153 | 0.99639 | -0.069219 | 7.0306
22 | 0.30066 | 0.076991 | -0.30053 | -0.076911 | 0.00012565 | 8.0068e-05 | 0.44797 | 0.44797 | 0.44797 | 1 | 0 | 0.99954 | -0.0086314 | 30.7669
23 | 0.01837 | 0.0046066 | -0.018364 | -0.0046029 | 6.343e-06 | 3.7627e-06 | 0.027336 | 0.027336 | 0.027336 | 1 | 0 | 0.99962 | -0.0072475 | 7.5098
24 | 0.045491 | 0.011441 | -0.045454 | -0.011418 | 3.6933e-05 | 2.3356e-05 | 0.067737 | 0.067737 | 0.067737 | 0.99954 | -0.0086314 | 0.99866 | -0.025643 | 18.609
25 | 0.25504 | 0.06547 | -0.25437 | -0.065043 | 0.00067136 | 0.00042708 | 0.38023 | 0.38023 | 0.38023 | 0.99954 | -0.0086314 | 0.99667 | -0.063023 | 26.1148
26 | 0.0094835 | 0.0023773 | -0.0094811 | -0.0023762 | 2.4235e-06 | 1.126e-06 | 0.014117 | 0.014117 | 0.014117 | 0.99962 | -0.0072475 | 0.99934 | -0.012612 | 3.8784
27 | -0.017135 | -0.0042985 | 0.01714 | 0.0043013 | 4.7338e-06 | 2.7785e-06 | 0.025591 | 0.025591 | 0.025591 | 0.99639 | -0.069219 | 0.99669 | -0.063426 | 7.0306
28 | -0.01714 | -0.0043013 | 0.017141 | 0.0043016 | 6.0265e-07 | 3.5371e-07 | 0.025591 | 0.025591 | 0.025591 | 0.99669 | -0.063426 | 0.99673 | -0.062688 | 7.0306
29 | -0.010733 | -0.0026905 | 0.01074 | 0.0026937 | 6.318e-06 | 3.2582e-06 | 0.016372 | 0.016371 | 0.016372 | 0.97554 | -0.47088 | 0.97617 | -0.45853 | 4.4977
30 | 0.010733 | 0.0026905 | -0.010732 | -0.0026896 | 1.6872e-06 | 8.7025e-07 | 0.016372 | 0.016372 | 0.016372 | 0.97554 | -0.47088 | 0.97538 | -0.47418 | 4.4978
31 | -0.029071 | -0.0072881 | 0.029102 | 0.0073072 | 3.0604e-05 | 1.9066e-05 | 0.044315 | 0.044315 | 0.044315 | 0.97617 | -0.45853 | 0.97729 | -0.43646 | 12.1746
32 | 0.082146 | 0.020788 | -0.082018 | -0.020707 | 0.00012835 | 8.1035e-05 | 0.12475 | 0.12475 | 0.12475 | 0.98041 | -0.37545 | 0.97873 | -0.40806 | 17.136
33 | 0.050338 | 0.012679 | -0.050273 | -0.012638 | 6.5399e-05 | 4.148e-05 | 0.076424 | 0.076424 | 0.076424 | 0.98041 | -0.37545 | 0.97902 | -0.40265 | 20.9957
34 | -0.13248 | -0.033467 | 0.13268 | 0.033588 | 0.00019228 | 0.0001205 | 0.20117 | 0.20117 | 0.20117 | 0.98041 | -0.37545 | 0.98196 | -0.34522 | 13.8169
35 | 0.080674 | 0.02037 | -0.080616 | -0.020334 | 5.8015e-05 | 3.6613e-05 | 0.12271 | 0.12271 | 0.12271 | 0.97873 | -0.40806 | 0.97797 | -0.42308 | 16.8554
36 | 0.050273 | 0.012638 | -0.050231 | -0.012611 | 4.2273e-05 | 2.6812e-05 | 0.076424 | 0.076424 | 0.076424 | 0.97902 | -0.40265 | 0.97812 | -0.42028 | 20.9957
37 | -0.13691 | -0.034647 | 0.13693 | 0.034663 | 2.5272e-05 | 1.5858e-05 | 0.20758 | 0.20758 | 0.20758 | 0.98196 | -0.34522 | 0.98216 | -0.34137 | 14.2569
38 | 0.029125 | 0.0073212 | -0.029102 | -0.0073072 | 2.2481e-05 | 1.4005e-05 | 0.044315 | 0.044315 | 0.044315 | 0.97812 | -0.42028 | 0.97729 | -0.43646 | 12.1745
39 | 0.001539 | 0.00038542 | -0.0015389 | -0.00038569 | 4.7482e-08 | -2.7321e-07 | 0.0023144 | 0.0023145 | 0.0023145 | 0.98944 | -0.20114 | 0.98941 | -0.20179 | 0.63584
40 | -0.021143 | -0.0053168 | 0.021151 | 0.0053217 | 8.1092e-06 | 4.9146e-06 | 0.031787 | 0.031787 | 0.031787 | 0.98995 | -0.19131 | 0.99036 | -0.18329 | 8.7326
41 | 0.0010079 | 0.00025246 | -0.0010079 | -0.00025261 | 1.1098e-08 | -1.4794e-07 | 0.0015406 | 0.0015406 | 0.0015406 | 0.97354 | -0.51013 | 0.97353 | -0.51036 | 0.42324
42 | 0.0035734 | 0.00089539 | -0.0035733 | -0.00089544 | 8.6145e-08 | -4.9221e-08 | 0.0053455 | 0.0053455 | 0.0053455 | 0.9947 | -0.10054 | 0.99468 | -0.10105 | 1.4685
43 | -0.0055914 | -0.0014012 | 0.0055918 | 0.0014012 | 3.1221e-07 | 4.5334e-08 | 0.0083644 | 0.0083644 | 0.0083644 | 0.9947 | -0.10054 | 0.99476 | -0.099372 | 2.2979
44 | 0.0017612 | 0.00044128 | -0.0017611 | -0.00044138 | 2.4111e-08 | -1.048e-07 | 0.0026346 | 0.0026347 | 0.0026347 | 0.99468 | -0.10105 | 0.99466 | -0.10134 | 0.72381
45 | -0.0074547 | -0.0018681 | 0.0074556 | 0.0018684 | 8.8553e-07 | 3.2016e-07 | 0.011151 | 0.011151 | 0.011151 | 0.99476 | -0.099372 | 0.99489 | -0.096879 | 3.0635
46 | -0.0090388 | -0.0022652 | 0.0090394 | 0.0022655 | 6.3374e-07 | 2.8551e-07 | 0.013519 | 0.013519 | 0.013519 | 0.99489 | -0.096879 | 0.99497 | -0.095407 | 3.714
47 | -0.010986 | -0.0027533 | 0.010987 | 0.0027541 | 1.4697e-06 | 7.52e-07 | 0.01643 | 0.01643 | 0.01643 | 0.99497 | -0.095407 | 0.99511 | -0.092599 | 4.5137
48 | 0.0094947 | 0.0023797 | -0.009494 | -0.0023793 | 7.3278e-07 | 3.4233e-07 | 0.014177 | 0.014178 | 0.014178 | 0.99653 | -0.065752 | 0.99644 | -0.067372 | 3.8949
49 | -0.011596 | -0.0029062 | 0.011597 | 0.002907 | 1.5078e-06 | 7.9024e-07 | 0.017315 | 0.017315 | 0.017315 | 0.99653 | -0.065752 | 0.99667 | -0.063023 | 4.7568
50 | 0.0076745 | 0.0019233 | -0.0076736 | -0.001923 | 8.8326e-07 | 3.3172e-07 | 0.011461 | 0.011461 | 0.011461 | 0.99644 | -0.067372 | 0.99632 | -0.069788 | 3.1485
51 | 0.24277 | 0.062136 | -0.24248 | -0.061948 | 0.0002964 | 0.00018844 | 0.36292 | 0.36292 | 0.36292 | 0.99667 | -0.063023 | 0.99534 | -0.08827 | 24.9257
52 | 0.0057707 | 0.0014461 | -0.0057703 | -0.001446 | 3.9909e-07 | 6.8848e-08 | 0.0086186 | 0.0086186 | 0.0086186 | 0.99632 | -0.069788 | 0.99624 | -0.07124 | 2.3678
53 | 0.2336 | 0.059722 | -0.23355 | -0.059691 | 4.8915e-05 | 3.1084e-05 | 0.34964 | 0.34964 | 0.34964 | 0.99534 | -0.08827 | 0.99511 | -0.092599 | 24.0139
54 | 0.0037622 | 0.00094272 | -0.0037621 | -0.00094275 | 7.654e-08 | -3.5181e-08 | 0.0056192 | 0.0056192 | 0.0056192 | 0.99624 | -0.07124 | 0.99622 | -0.071667 | 1.5437
55 | 0.22256 | 0.056937 | -0.22236 | -0.056811 | 0.00019754 | 0.00012544 | 0.33321 | 0.33321 | 0.33321 | 0.99511 | -0.092599 | 0.99415 | -0.11095 | 22.8855
56 | 0.037404 | 0.0094003 | -0.037401 | -0.0093984 | 2.9659e-06 | 1.8649e-06 | 0.055742 | 0.055742 | 0.055742 | 0.99866 | -0.025643 | 0.99857 | -0.027304 | 15.3137
57 | 0.012707 | 0.0031855 | -0.012706 | -0.0031848 | 1.1991e-06 | 6.5341e-07 | 0.019045 | 0.019045 | 0.019045 | 0.99285 | -0.13582 | 0.99275 | -0.1378 | 5.2322
58 | -0.015026 | -0.0037667 | 0.01503 | 0.0037688 | 3.7458e-06 | 2.1425e-06 | 0.022521 | 0.022521 | 0.022521 | 0.99285 | -0.13582 | 0.99312 | -0.13059 | 6.187
59 | 0.011503 | 0.0028833 | -0.011502 | -0.0028829 | 6.6945e-07 | 3.5081e-07 | 0.017242 | 0.017242 | 0.017242 | 0.99275 | -0.1378 | 0.99268 | -0.13902 | 4.7368
60 | 0.2003 | 0.051201 | -0.2002 | -0.051138 | 9.8297e-05 | 6.2309e-05 | 0.30047 | 0.30048 | 0.30048 | 0.99312 | -0.13059 | 0.99259 | -0.14074 | 20.637
61 | -0.21533 | -0.054969 | 0.21535 | 0.054981 | 1.8406e-05 | 1.1682e-05 | 0.323 | 0.323 | 0.323 | 0.99312 | -0.13059 | 0.99321 | -0.12882 | 22.1838
62 | 0.010256 | 0.0025705 | -0.010255 | -0.0025703 | 4.372e-07 | 2.1604e-07 | 0.015373 | 0.015373 | 0.015373 | 0.99268 | -0.13902 | 0.99264 | -0.13992 | 4.2234
63 | 0.19615 | 0.050121 | -0.19605 | -0.050061 | 9.571e-05 | 6.0646e-05 | 0.29439 | 0.29439 | 0.29439 | 0.99259 | -0.14074 | 0.99206 | -0.15083 | 20.2193
64 | -0.21921 | -0.055949 | 0.2194 | 0.056069 | 0.0001894 | 0.00012025 | 0.32878 | 0.32878 | 0.32878 | 0.99321 | -0.12882 | 0.99415 | -0.11095 | 22.5812
65 | 0.0088834 | 0.0022265 | -0.0088823 | -0.002226 | 1.0529e-06 | 4.692e-07 | 0.013317 | 0.013317 | 0.013317 | 0.99264 | -0.13992 | 0.99251 | -0.1424 | 3.6584
66 | 0.19465 | 0.04971 | -0.19465 | -0.049707 | 4.6193e-06 | 2.9265e-06 | 0.29229 | 0.29229 | 0.29229 | 0.99206 | -0.15083 | 0.99203 | -0.15132 | 20.0752
67 | 0.0049274 | 0.0012348 | -0.0049274 | -0.0012348 | 2.595e-10 | 7.4738e-12 | 0.0073879 | 0.0073879 | 0.0073879 | 0.99244 | -0.14373 | 0.99244 | -0.14373 | 2.0296
68 | -0.006315 | -0.0015825 | 0.0063152 | 0.0015826 | 1.9008e-07 | 4.859e-08 | 0.0094684 | 0.0094683 | 0.0094684 | 0.99244 | -0.14373 | 0.99247 | -0.1431 | 2.6012
69 | 0.0037459 | 0.00093866 | -0.0037458 | -0.00093871 | 1.0385e-07 | -4.6976e-08 | 0.0056163 | 0.0056164 | 0.0056164 | 0.99244 | -0.14373 | 0.99241 | -0.14431 | 1.543
70 | -0.0075257 | -0.001886 | 0.007526 | 0.0018861 | 2.4921e-07 | 9.2038e-08 | 0.011283 | 0.011283 | 0.011283 | 0.99247 | -0.1431 | 0.99251 | -0.1424 | 3.0998
71 | 0.0025379 | 0.00063599 | -0.0025379 | -0.000636 | 3.6362e-09 | -6.3243e-09 | 0.0038053 | 0.0038053 | 0.0038053 | 0.99241 | -0.14431 | 0.99241 | -0.14434 | 1.0454
72 | 0.0012545 | 0.00031434 | -0.0012545 | -0.0003144 | 6.8892e-09 | -6.2682e-08 | 0.001881 | 0.001881 | 0.001881 | 0.99241 | -0.14434 | 0.9924 | -0.14446 | 0.51675
73 | 0.0019312 | 0.0004839 | -0.0019312 | -0.000484 | 2.9253e-08 | -1.0334e-07 | 0.0028845 | 0.0028846 | 0.0028846 | 0.99622 | -0.071667 | 0.99621 | -0.071985 | 0.79247
74 | -0.0051014 | -0.0012785 | 0.0051024 | 0.0012786 | 9.8308e-07 | 9.7644e-08 | 0.0078147 | 0.0078145 | 0.0078147 | 0.97138 | -0.55267 | 0.97158 | -0.54863 | 2.1469
75 | -0.011201 | -0.002807 | 0.011204 | 0.0028088 | 3.4251e-06 | 1.8075e-06 | 0.017154 | 0.017154 | 0.017154 | 0.97158 | -0.54863 | 0.97191 | -0.54221 | 4.7127
76 | -0.026121 | -0.0065488 | 0.026145 | 0.0065634 | 2.3508e-05 | 1.4559e-05 | 0.039993 | 0.039993 | 0.039993 | 0.97191 | -0.54221 | 0.97286 | -0.52334 | 10.9871
77 | 0.014917 | 0.00374 | -0.014912 | -0.003737 | 5.1216e-06 | 2.9535e-06 | 0.022839 | 0.022839 | 0.022839 | 0.97191 | -0.54221 | 0.97154 | -0.54942 | 6.2745
78 | -0.014409 | -0.0036186 | 0.014412 | 0.0036201 | 2.7105e-06 | 1.5481e-06 | 0.021988 | 0.021988 | 0.021988 | 0.97526 | -0.4762 | 0.97546 | -0.47226 | 6.0407
79 | 0.014409 | 0.0036186 | -0.014389 | -0.0036066 | 2.091e-05 | 1.1945e-05 | 0.021988 | 0.021989 | 0.021989 | 0.97526 | -0.4762 | 0.97371 | -0.50666 | 6.0408
80 | 0.031457 | 0.0079221 | -0.031432 | -0.0079065 | 2.4858e-05 | 1.555e-05 | 0.048 | 0.048 | 0.048 | 0.97546 | -0.47226 | 0.97462 | -0.4888 | 13.1867
81 | 0.0078725 | 0.0019739 | -0.0078686 | -0.0019723 | 3.9258e-06 | 1.6134e-06 | 0.012031 | 0.012031 | 0.012031 | 0.97371 | -0.50666 | 0.97318 | -0.51712 | 3.3053
82 | 0.00075271 | 0.00018839 | -0.0007527 | -0.00018864 | 1.0177e-08 | -2.4863e-07 | 0.0011502 | 0.0011503 | 0.0011503 | 0.97371 | -0.50666 | 0.9737 | -0.50694 | 0.31601
83 | 0.0057634 | 0.0014443 | -0.0057616 | -0.0014439 | 1.7492e-06 | 3.7179e-07 | 0.0088075 | 0.0088077 | 0.0088077 | 0.97371 | -0.50666 | 0.97339 | -0.51303 | 2.4197
84 | -0.029334 | -0.0073627 | 0.029382 | 0.0073929 | 4.8411e-05 | 3.0186e-05 | 0.044871 | 0.044871 | 0.044871 | 0.97286 | -0.52334 | 0.97462 | -0.4888 | 12.3272
85 | 0.0086806 | 0.0021753 | -0.0086798 | -0.0021749 | 8.7643e-07 | 3.972e-07 | 0.013295 | 0.013295 | 0.013295 | 0.97154 | -0.54942 | 0.97144 | -0.55154 | 3.6525
86 | 0.0057616 | 0.0014439 | -0.0057604 | -0.0014437 | 1.2416e-06 | 2.6423e-07 | 0.0088077 | 0.0088079 | 0.0088079 | 0.97339 | -0.51303 | 0.97316 | -0.51755 | 2.4198
87 | 0.0078686 | 0.0019723 | -0.0078676 | -0.0019719 | 9.3059e-07 | 3.826e-07 | 0.012031 | 0.012031 | 0.012031 | 0.97318 | -0.51712 | 0.97306 | -0.51961 | 3.3053
88 | 0.14824 | 0.037617 | -0.14817 | -0.037573 | 7.0795e-05 | 4.4545e-05 | 0.22421 | 0.22421 | 0.22421 | 0.98455 | -0.29504 | 0.98404 | -0.30498 | 15.399
89 | -0.1488 | -0.037758 | 0.1488 | 0.03776 | 4.2838e-06 | 2.6957e-06 | 0.22506 | 0.22506 | 0.22506 | 0.98455 | -0.29504 | 0.98458 | -0.29444 | 15.4571
90 | 0.14437 | 0.036622 | -0.14428 | -0.036565 | 8.9436e-05 | 5.6224e-05 | 0.21847 | 0.21847 | 0.21847 | 0.98404 | -0.30498 | 0.98337 | -0.31787 | 15.0049
91 | -0.15073 | -0.038243 | 0.15082 | 0.038304 | 9.7743e-05 | 6.1534e-05 | 0.22796 | 0.22796 | 0.22796 | 0.98458 | -0.29444 | 0.98528 | -0.28097 | 15.6569
92 | 0.14041 | 0.035594 | -0.14025 | -0.035495 | 0.00015839 | 9.9473e-05 | 0.21261 | 0.21261 | 0.21261 | 0.98337 | -0.31787 | 0.98216 | -0.34137 | 14.6022
93 | -0.15178 | -0.038543 | 0.15179 | 0.038551 | 1.3576e-05 | 8.5482e-06 | 0.2294 | 0.2294 | 0.2294 | 0.98528 | -0.28097 | 0.98537 | -0.27911 | 15.7556
94 | 0.0033188 | 0.00083136 | -0.0033187 | -0.00083139 | 4.4427e-08 | -3.0874e-08 | 0.0050279 | 0.0050279 | 0.0050279 | 0.98216 | -0.34137 | 0.98214 | -0.34165 | 1.3813
95 | -0.15328 | -0.038924 | 0.15338 | 0.038986 | 9.9348e-05 | 6.2576e-05 | 0.23165 | 0.23165 | 0.23165 | 0.98537 | -0.27911 | 0.98607 | -0.26565 | 15.9098
96 | 0.006352 | 0.001592 | -0.0063508 | -0.0015916 | 1.1581e-06 | 3.3488e-07 | 0.0097147 | 0.0097149 | 0.0097149 | 0.97294 | -0.52199 | 0.97274 | -0.52581 | 2.6689
97 | -0.0070491 | -0.0017667 | 0.0070499 | 0.001767 | 7.9916e-07 | 2.8373e-07 | 0.010781 | 0.010781 | 0.010781 | 0.97294 | -0.52199 | 0.97306 | -0.51961 | 2.9618
98 | 0.0053457 | 0.0013397 | -0.0053455 | -0.0013397 | 2.3346e-07 | 3.3847e-08 | 0.0081774 | 0.0081774 | 0.0081774 | 0.97274 | -0.52581 | 0.9727 | -0.52673 | 2.2465
99 | 0.0035691 | 0.00089409 | -0.0035685 | -0.00089435 | 5.7424e-07 | -2.6669e-07 | 0.0054669 | 0.0054671 | 0.0054671 | 0.97144 | -0.55154 | 0.97127 | -0.55491 | 1.5019
100 | 0.03178 | 0.0079896 | -0.031741 | -0.007965 | 3.9466e-05 | 2.4645e-05 | 0.047366 | 0.047366 | 0.047366 | 0.99857 | -0.027304 | 0.99722 | -0.053345 | 13.0126
101 | 0.026352 | 0.0066145 | -0.02634 | -0.0066073 | 1.1738e-05 | 7.2485e-06 | 0.039325 | 0.039325 | 0.039325 | 0.99722 | -0.053345 | 0.99673 | -0.062688 | 10.8037
102 | 0.19364 | 0.049455 | -0.19356 | -0.049406 | 7.796e-05 | 4.9386e-05 | 0.29079 | 0.29079 | 0.29079 | 0.99203 | -0.15132 | 0.9916 | -0.15966 | 19.9715
103 | 0.19263 | 0.049172 | -0.19244 | -0.049051 | 0.0001911 | 0.00012105 | 0.28939 | 0.28939 | 0.28939 | 0.9916 | -0.15966 | 0.99052 | -0.18021 | 19.8757
104 | 0.17069 | 0.043579 | -0.17057 | -0.043502 | 0.00012052 | 7.6132e-05 | 0.25671 | 0.25671 | 0.25671 | 0.99052 | -0.18021 | 0.98976 | -0.19483 | 17.6311
105 | 0.021749 | 0.0054728 | -0.021746 | -0.0054709 | 3.1981e-06 | 1.944e-06 | 0.032681 | 0.032681 | 0.032681 | 0.99052 | -0.18021 | 0.99036 | -0.18329 | 8.9783
106 | 0.16881 | 0.04306 | -0.16871 | -0.043002 | 9.0997e-05 | 5.7465e-05 | 0.25405 | 0.25405 | 0.25405 | 0.98976 | -0.19483 | 0.98917 | -0.206 | 17.4488
107 | -0.0054544 | -0.001367 | 0.005455 | 0.0013671 | 6.0186e-07 | 7.9919e-08 | 0.0082104 | 0.0082103 | 0.0082104 | 0.98853 | -0.21845 | 0.98865 | -0.21613 | 2.2556
108 | -0.0063379 | -0.0015884 | 0.0063382 | 0.0015884 | 3.0665e-07 | 8.1012e-08 | 0.0095391 | 0.0095391 | 0.0095391 | 0.98865 | -0.21613 | 0.9887 | -0.21512 | 2.6206
109 | -0.008002 | -0.0020054 | 0.0080036 | 0.0020061 | 1.6151e-06 | 6.5276e-07 | 0.012043 | 0.012043 | 0.012043 | 0.9887 | -0.21512 | 0.98892 | -0.21088 | 3.3086
110 | 0.15669 | 0.039973 | -0.1564 | -0.039789 | 0.00029133 | 0.00018359 | 0.23602 | 0.23602 | 0.23602 | 0.98892 | -0.21088 | 0.98691 | -0.24945 | 16.21
111 | -0.16469 | -0.041979 | 0.16473 | 0.042004 | 3.8814e-05 | 2.4495e-05 | 0.24806 | 0.24806 | 0.24806 | 0.98892 | -0.21088 | 0.98917 | -0.206 | 17.0371
112 | 0.0010817 | 0.00027074 | -0.0010817 | -0.00027109 | 2.9466e-08 | -3.514e-07 | 0.0016387 | 0.0016388 | 0.0016388 | 0.98214 | -0.34165 | 0.98212 | -0.34222 | 0.45023
113 | -0.15627 | -0.039713 | 0.1564 | 0.039789 | 0.00012199 | 7.6879e-05 | 0.23602 | 0.23602 | 0.23602 | 0.98607 | -0.26565 | 0.98691 | -0.24945 | 16.2101
114 | -0.010694 | -0.0026792 | 0.010695 | 0.0026802 | 1.9762e-06 | 1.0073e-06 | 0.016149 | 0.016149 | 0.016149 | 0.98529 | -0.28189 | 0.98549 | -0.27801 | 4.4367
115 | 0.0022703 | 0.00056816 | -0.0022702 | -0.00056839 | 1.0248e-07 | -2.305e-07 | 0.0034284 | 0.0034285 | 0.0034285 | 0.98529 | -0.28189 | 0.98524 | -0.28284 | 0.9419
116 | 0.0022702 | 0.00056839 | -0.00227 | -0.00056891 | 2.2951e-07 | -5.1607e-07 | 0.0034285 | 0.0034287 | 0.0034287 | 0.98524 | -0.28284 | 0.98513 | -0.28496 | 0.94196

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32068 | 0.081598

## res_load
| p_mw | q_mvar
0 | 0.0029415 | 0.00073721
1 | 0.0033173 | 0.00083138
2 | 0.0028966 | 0.00072597
3 | 0.0028635 | 0.00071766
4 | 0.0014793 | 0.00037075
5 | 0.00084318 | 0.00021132
6 | 0.0013727 | 0.00034403
7 | 0.00094406 | 0.0002366
8 | 0.0089701 | 0.0022481
9 | 0.00888 | 0.0022255
10 | 0.018332 | 0.0045944
11 | 0.010732 | 0.0026896
12 | 0.0013438 | 0.00033679
13 | 0.0042287 | 0.0010598
14 | 0.021106 | 0.0052897
15 | 0.00099142 | 0.00024847
16 | 0.0030329 | 0.00076013
17 | 0.012887 | 0.0032297
18 | 0.0010079 | 0.00025261
19 | 0.0020181 | 0.00050578
20 | 0.0018121 | 0.00045416
21 | 0.0018629 | 0.0004669
22 | 0.0017611 | 0.00044138
23 | 0.0015832 | 0.00039679
24 | 0.0019464 | 0.0004878
25 | 0.002101 | 0.00052656
26 | 0.0018194 | 0.00045599
27 | 0.0019029 | 0.00047692
28 | 0.0088802 | 0.0022256
29 | 0.0020082 | 0.00050329
30 | 0.0080502 | 0.0020176
31 | 0.0081514 | 0.0020429
32 | 0.0023192 | 0.00058124
33 | 0.0012031 | 0.00030152
34 | 0.0012465 | 0.00031241
35 | 0.0040578 | 0.001017
36 | 0.0038623 | 0.00096797
37 | 0.001372 | 0.00034384
38 | 0.0013987 | 0.00035056
39 | 0.0029608 | 0.00074204
40 | 0.0013876 | 0.00034776
41 | 0.0011815 | 0.00029612
42 | 0.0012106 | 0.00030339
43 | 0.0012078 | 0.00030271
44 | 0.0013563 | 0.00033992
45 | 0.0012834 | 0.00032166
46 | 0.0018309 | 0.00045886
47 | 0.0019312 | 0.000484
48 | 0.0012545 | 0.0003144
49 | 0.0051014 | 0.0012785
50 | 0.0060983 | 0.0015284
51 | 0.0031893 | 0.00079932
52 | 0.0062313 | 0.0015617
53 | 0.0020494 | 0.00051364
54 | 0.0057604 | 0.0014437
55 | 0.0007527 | 0.00018864
56 | 0.00056002 | 0.00014035
57 | 0.003795 | 0.00095112
58 | 0.0019243 | 0.00048227
59 | 0.0038749 | 0.00097115
60 | 0.00095222 | 0.00023865
61 | 0.0014865 | 0.00037255
62 | 0.0006971 | 0.00017471
63 | 0.0010051 | 0.0002519
64 | 0.00081776 | 0.00020495
65 | 0.0053455 | 0.0013397
66 | 0.0051107 | 0.0012809
67 | 0.0035685 | 0.00089435
68 | 0.0056212 | 0.0014088
69 | 0.0053884 | 0.0013505
70 | 0.0091997 | 0.0023057
71 | 0.001006 | 0.00025213
72 | 0.00093032 | 0.00023316
73 | 0.0017665 | 0.00044274
74 | 0.00059528 | 0.00014919
75 | 0.0078595 | 0.0019698
76 | 0.0054544 | 0.001367
77 | 0.0008829 | 0.00022128
78 | 0.0016638 | 0.00041699
79 | 0.0015389 | 0.00038569
80 | 0.002237 | 0.00056065
81 | 0.0010817 | 0.00027109
82 | 0.0028976 | 0.0007262
83 | 0.0039846 | 0.00099863
84 | 0.0094811 | 0.0023762
85 | 0.00093783 | 0.00023504
86 | 0.0084232 | 0.0021111
87 | 0.00227 | 0.00056891

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1