## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_181-4_1_2_node_47 | 0.4 | n |  | TRUE
1 | bus_LV_181-4_1_2_node_103 | 0.4 | n |  | TRUE
2 | bus_LV_181-4_1_2_node_250 | 0.4 | n |  | TRUE
3 | bus_LV_181-4_1_2_node_48 | 0.4 | n |  | TRUE
4 | bus_LV_181-4_1_2_node_251 | 0.4 | n |  | TRUE
5 | bus_LV_181-4_1_2_node_57 | 0.4 | n |  | TRUE
6 | bus_LV_181-4_1_2_node_58 | 0.4 | n |  | TRUE
7 | bus_LV_181-4_1_2_node_246 | 0.4 | n |  | TRUE
8 | bus_LV_181-4_1_2_node_59 | 0.4 | n |  | TRUE
9 | bus_LV_181-4_1_2_node_255 | 0.4 | n |  | TRUE
10 | bus_LV_181-4_1_2_node_60 | 0.4 | n |  | TRUE
11 | bus_LV_181-4_1_2_node_61 | 0.4 | n |  | TRUE
12 | bus_LV_181-4_1_2_node_245 | 0.4 | n |  | TRUE
13 | bus_LV_181-4_1_2_node_62 | 0.4 | n |  | TRUE
14 | bus_LV_181-4_1_2_node_63 | 0.4 | n |  | TRUE
15 | bus_LV_181-4_1_2_node_64 | 0.4 | n |  | TRUE
16 | bus_LV_181-4_1_2_node_65 | 0.4 | n |  | TRUE
17 | bus_LV_181-4_1_2_node_66 | 0.4 | n |  | TRUE
18 | bus_LV_181-4_1_2_node_67 | 0.4 | n |  | TRUE
19 | bus_LV_181-4_1_2_node_70 | 0.4 | n |  | TRUE
20 | bus_LV_181-4_1_2_node_68 | 0.4 | n |  | TRUE
21 | bus_LV_181-4_1_2_node_98 | 0.4 | n |  | TRUE
22 | bus_LV_181-4_1_2_node_69 | 0.4 | n |  | TRUE
23 | bus_LV_181-4_1_2_node_71 | 0.4 | n |  | TRUE
24 | bus_LV_181-4_1_2_node_252 | 0.4 | n |  | TRUE
25 | bus_LV_181-4_1_2_node_104 | 0.4 | n |  | TRUE
26 | bus_LV_181-4_1_2_node_106 | 0.4 | n |  | TRUE
27 | bus_LV_181-4_1_2_node_99 | 0.4 | n |  | TRUE
28 | bus_LV_181-4_1_2_node_100 | 0.4 | n |  | TRUE
29 | bus_LV_181-4_1_2_node_101 | 0.4 | n |  | TRUE
30 | bus_LV_181-4_1_2_node_102 | 0.4 | n |  | TRUE
31 | bus_LV_181-4_1_2_node_105 | 0.4 | n |  | TRUE
32 | bus_LV_181-4_1_2_node_249 | 0.4 | n |  | TRUE
33 | bus_LV_181-4_1_2_node_253 | 0.4 | n |  | TRUE
34 | bus_LV_181-4_1_2_node_247 | 0.4 | n |  | TRUE
35 | bus_LV_181-4_1_2_node_248 | 0.4 | n |  | TRUE
36 | bus_MV_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_181-4_1_2_load_250 | 2 | 0.00044305 | 0.00011104 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_181-4_1_2_load_251 | 4 | 0.00044314 | 0.00011106 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_181-4_1_2_load_57 | 5 | 0.00094373 | 0.00023652 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_181-4_1_2_load_59 | 8 | 0.00065339 | 0.00016376 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_181-4_1_2_load_255 | 9 | 0.0058619 | 0.0014691 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_181-4_1_2_load_245 | 12 | 0.00046225 | 0.00011585 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_181-4_1_2_load_62 | 13 | 0.006585 | 0.0016504 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_181-4_1_2_load_64 | 15 | 0.0010087 | 0.0002528 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_181-4_1_2_load_65 | 16 | 0.0032569 | 0.00081626 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_181-4_1_2_load_68 | 20 | 0.0058964 | 0.0014778 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_181-4_1_2_load_98 | 21 | 0.0018111 | 0.00045392 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_181-4_1_2_load_252 | 24 | 0.0030512 | 0.0007647 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_181-4_1_2_load_106 | 26 | 0.0004692 | 0.00011759 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_181-4_1_2_load_99 | 27 | 0.00078458 | 0.00019663 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_181-4_1_2_load_102 | 30 | 0.0002978 | 7.4635e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_181-4_1_2_load_105 | 31 | 0.00084875 | 0.00021272 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_181-4_1_2_load_249 | 32 | 0.00044316 | 0.00011107 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_181-4_1_2_load_253 | 33 | 0.00068841 | 0.00017253 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_181-4_1_2_load_247 | 34 | 0.0013637 | 0.00034177 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_181-4_1_2_load_248 | 35 | 0.00044419 | 0.00011132 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_181-4_1_2_line_0 |  | 0 | 1 | 0.025174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_181-4_1_2_line_1 |  | 0 | 2 | 0.013922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_181-4_1_2_line_2 |  | 1 | 32 | 0.013051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_181-4_1_2_line_3 |  | 1 | 28 | 0.089566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_181-4_1_2_line_4 |  | 2 | 3 | 0.01284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_181-4_1_2_line_5 |  | 3 | 4 | 0.011043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_181-4_1_2_line_6 |  | 4 | 10 | 0.21328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_181-4_1_2_line_7 |  | 5 | 6 | 0.019561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_181-4_1_2_line_8 |  | 5 | 7 | 0.21539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_181-4_1_2_line_9 |  | 6 | 8 | 0.01247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_181-4_1_2_line_10 |  | 7 | 34 | 0.16337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_181-4_1_2_line_11 |  | 7 | 12 | 0.091681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_181-4_1_2_line_12 |  | 8 | 9 | 0.068834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_181-4_1_2_line_13 |  | 10 | 11 | 0.13386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_181-4_1_2_line_14 |  | 11 | 12 | 0.12828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_181-4_1_2_line_15 |  | 13 | 14 | 0.020382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_181-4_1_2_line_16 |  | 13 | 15 | 0.010564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_181-4_1_2_line_17 |  | 14 | 16 | 0.031216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_181-4_1_2_line_18 |  | 14 | 17 | 0.027205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_181-4_1_2_line_19 |  | 14 | 18 | 0.050786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_181-4_1_2_line_20 |  | 17 | 19 | 0.027635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_181-4_1_2_line_21 |  | 17 | 20 | 0.14711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_181-4_1_2_line_22 |  | 18 | 21 | 0.11035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_181-4_1_2_line_23 |  | 19 | 24 | 0.014967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_181-4_1_2_line_24 |  | 20 | 22 | 0.13015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_181-4_1_2_line_25 |  | 22 | 23 | 0.019193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_181-4_1_2_line_26 |  | 23 | 25 | 0.063229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_181-4_1_2_line_27 |  | 23 | 26 | 0.051398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_181-4_1_2_line_28 |  | 25 | 33 | 0.012649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_181-4_1_2_line_29 |  | 26 | 29 | 0.0095313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_181-4_1_2_line_30 |  | 27 | 28 | 0.012938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_181-4_1_2_line_31 |  | 27 | 29 | 0.00012874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_181-4_1_2_line_32 |  | 28 | 30 | 0.012347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_181-4_1_2_line_33 |  | 29 | 31 | 0.038127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_181-4_1_2_line_34 |  | 32 | 35 | 0.012225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_181-4_1_2_trafo_68 | 0.63 MVA 20/0.4 kV | 36 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2706062.6376 | 1252389.1093 | 2706050.213 | 1252381.5363 | 2706040.4162 | 1252377.2798
1 | 2706062.6376 | 1252389.1093 | 2706064.595 | 1252385.1856 | 2706066.7243 | 1252380.9314 | 2706068.8485 | 1252376.6499
2 | 2706040.4162 | 1252377.2798 | 2706042.1573 | 1252373.2076 | 2706044.1638 | 1252368.2284 | 2706045.2943 | 1252365.1768
3 | 2705997.9779 | 1252321.7532 | 2705993.434 | 1252352.9416 | 2705992.173 | 1252355.9215 | 2705991.5426 | 1252357.4003 | 2706013.9749 | 1252365.4748 | 2706020.9076 | 1252370.7587 | 2706024.3245 | 1252371.3203 | 2706032.7089 | 1252373.9391 | 2706040.4162 | 1252377.2798
4 | 2706074.5553 | 1252365.1477 | 2706068.8485 | 1252376.6499
5 | 2706074.5553 | 1252365.1477 | 2706079.4782 | 1252355.2624
6 | 2706079.4782 | 1252355.2624 | 2706188.2127 | 1252171.7822
7 | 2705877.0713 | 1252035.8932 | 2705896.5542 | 1252034.1503
8 | 2705896.5542 | 1252034.1503 | 2706110.6884 | 1252010.963
9 | 2705877.0713 | 1252035.8932 | 2705878.7683 | 1252023.539
10 | 2706147.5123 | 1251904.781 | 2706136.7718 | 1251900.4851 | 2706125.6651 | 1251893.0357 | 2706119.7026 | 1251890.8716 | 2706116.1763 | 1251890.5082 | 2706111.1409 | 1251891.7857 | 2706106.3963 | 1251894.5363 | 2706103.3141 | 1251898.8735 | 2706102.3931 | 1251903.9278 | 2706103.1844 | 1251916.2186 | 2706108.2525 | 1251948.9136 | 2706110.4564 | 1251994.8458 | 2706110.6884 | 1252010.963
11 | 2706110.6884 | 1252010.963 | 2706111.5664 | 1252023.0441 | 2706118.4073 | 1252050.7446 | 2706122.8953 | 1252066.093 | 2706129.5205 | 1252076.3422 | 2706146.0992 | 1252086.7587 | 2706149.0952 | 1252088.0463
12 | 2705878.7683 | 1252023.539 | 2705882.047 | 1251954.7831
13 | 2706188.2127 | 1252171.7822 | 2706219.4177 | 1252184.007 | 2706251.963 | 1252189.684 | 2706261.4847 | 1252189.0876 | 2706272.0107 | 1252181.7482 | 2706268.0448 | 1252175.6054 | 2706264.5772 | 1252165.6685 | 2706264.9076 | 1252155.2549 | 2706266.956 | 1252138.7004
14 | 2706266.956 | 1252138.7004 | 2706149.0952 | 1252088.0463
15 | 2705660.3699 | 1252261.0517 | 2705655.3794 | 1252262.3749 | 2705642.6913 | 1252270.7802
16 | 2705633.8843 | 1252276.6143 | 2705642.6913 | 1252270.7802
17 | 2705660.3699 | 1252261.0517 | 2705662.2835 | 1252272.2505 | 2705672.7536 | 1252289.1398
18 | 2705660.3699 | 1252261.0517 | 2705671.5871 | 1252258.0716 | 2705668.3051 | 1252251.6412 | 2705666.7537 | 1252243.4069
19 | 2705660.3699 | 1252261.0517 | 2705671.5871 | 1252258.0716 | 2705677.4176 | 1252263.8136 | 2705684.9707 | 1252268.6188 | 2705695.5782 | 1252271.8885 | 2705706.3869 | 1252273.6049
20 | 2705644.5326 | 1252233.1801 | 2705657.9065 | 1252238.3561 | 2705666.6015 | 1252238.8227 | 2705666.7537 | 1252243.4069
21 | 2705666.7537 | 1252243.4069 | 2705722.0626 | 1252244.5611 | 2705754.8701 | 1252244.4353 | 2705769.915 | 1252244.3816 | 2705777.4111 | 1252244.3487 | 2705781.5572 | 1252250.5722 | 2705790.4632 | 1252258.66 | 2705796.9057 | 1252258.8752 | 2705805.4681 | 1252252.8287
22 | 2705706.3869 | 1252273.6049 | 2705698.6852 | 1252302.4909 | 2705697.8662 | 1252309.4708 | 2705698.1273 | 1252316.4033 | 2705699.1004 | 1252323.6265 | 2705702.1741 | 1252334.9572 | 2705706.3019 | 1252344.7388 | 2705711.0142 | 1252352.2289 | 2705714.4575 | 1252356.8052 | 2705716.6686 | 1252358.9464 | 2705729.3421 | 1252371.2046 | 2705730.3909 | 1252372.3623
23 | 2705644.5326 | 1252233.1801 | 2705637.8098 | 1252246.56
24 | 2705925.2508 | 1252280.3746 | 2705917.173 | 1252281.2753 | 2705885.1666 | 1252273.7639 | 2705872.1948 | 1252270.5962 | 2705855.2239 | 1252271.5604 | 2705839.6344 | 1252273.7948 | 2705827.7669 | 1252271.3475 | 2705818.2054 | 1252265.3052 | 2705807.1344 | 1252251.652 | 2705805.4681 | 1252252.8287
25 | 2705925.2508 | 1252280.3746 | 2705927.4304 | 1252293.5575 | 2705928.4296 | 1252299.3023
26 | 2705928.4296 | 1252299.3023 | 2705932.6364 | 1252336.7189 | 2705956.8869 | 1252344.848
27 | 2705928.4296 | 1252299.3023 | 2705941.6737 | 1252305.811 | 2705956.4759 | 1252314.2492 | 2705975.1446 | 1252318.3642 | 2705975.6248 | 1252318.4358
28 | 2705958.8315 | 1252332.3505 | 2705956.8869 | 1252344.848
29 | 2705985.0517 | 1252319.8426 | 2705975.6248 | 1252318.4358
30 | 2705997.9779 | 1252321.7532 | 2705985.1791 | 1252319.8614
31 | 2705985.1791 | 1252319.8614 | 2705985.0517 | 1252319.8426
32 | 2706010.2264 | 1252323.5738 | 2705997.9779 | 1252321.7532
33 | 2705985.0517 | 1252319.8426 | 2705989.275 | 1252295.1759 | 2706002.1641 | 1252297.5255
34 | 2706049.5415 | 1252353.7129 | 2706045.2943 | 1252365.1768

## bus_geodata
| x | y | coords
0 | 2706062.6376 | 1252389.1093
1 | 2706040.4162 | 1252377.2798
2 | 2706068.8485 | 1252376.6499
3 | 2706074.5553 | 1252365.1477
4 | 2706079.4782 | 1252355.2624
5 | 2705896.5542 | 1252034.1503
6 | 2705877.0713 | 1252035.8932
7 | 2706110.6884 | 1252010.963
8 | 2705878.7683 | 1252023.539
9 | 2705882.047 | 1251954.7831
10 | 2706188.2127 | 1252171.7822
11 | 2706266.956 | 1252138.7004
12 | 2706149.0952 | 1252088.0463
13 | 2705642.6913 | 1252270.7802
14 | 2705660.3699 | 1252261.0517
15 | 2705633.8843 | 1252276.6143
16 | 2705672.7536 | 1252289.1398
17 | 2705666.7537 | 1252243.4069
18 | 2705706.3869 | 1252273.6049
19 | 2705644.5326 | 1252233.1801
20 | 2705805.4681 | 1252252.8287
21 | 2705730.3909 | 1252372.3623
22 | 2705925.2508 | 1252280.3746
23 | 2705928.4296 | 1252299.3023
24 | 2705637.8098 | 1252246.56
25 | 2705956.8869 | 1252344.848
26 | 2705975.6248 | 1252318.4358
27 | 2705985.1791 | 1252319.8614
28 | 2705997.9779 | 1252321.7532
29 | 2705985.0517 | 1252319.8426
30 | 2706010.2264 | 1252323.5738
31 | 2706002.1641 | 1252297.5255
32 | 2706045.2943 | 1252365.1768
33 | 2705958.8315 | 1252332.3505
34 | 2706147.5123 | 1251904.781
35 | 2706049.5415 | 1252353.7129
36 | 2705805.4681 | 1252252.8287

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99605 | -0.075916 | 0 | 0
1 | 0.99628 | -0.071403 | 0 | 0
2 | 0.99592 | -0.078413 | 0.00044305 | 0.00011104
3 | 0.9958 | -0.080616 | 0 | 0
4 | 0.9957 | -0.082511 | 0.00044314 | 0.00011106
5 | 0.98945 | -0.20362 | 0.00094373 | 0.00023652
6 | 0.98933 | -0.20589 | 0 | 0
7 | 0.99092 | -0.17503 | 0 | 0
8 | 0.98925 | -0.20733 | 0.00065339 | 0.00016376
9 | 0.98888 | -0.21452 | 0.0058619 | 0.0014691
10 | 0.99389 | -0.11751 | 0 | 0
11 | 0.99275 | -0.13952 | 0 | 0
12 | 0.99166 | -0.16066 | 0.00046225 | 0.00011585
13 | 0.99745 | -0.04915 | 0.006585 | 0.0016504
14 | 0.99759 | -0.046439 | 0 | 0
15 | 0.99744 | -0.049337 | 0.0010087 | 0.0002528
16 | 0.99749 | -0.04822 | 0.0032569 | 0.00081626
17 | 0.9979 | -0.040404 | 0 | 0
18 | 0.9975 | -0.048054 | 0 | 0
19 | 0.99782 | -0.041881 | 0 | 0
20 | 1 | 0 | -0.031651 | -0.0075478
21 | 0.99732 | -0.051559 | 0.0018111 | 0.00045392
22 | 0.99832 | -0.03226 | 0 | 0
23 | 0.99807 | -0.037026 | 0 | 0
24 | 0.99778 | -0.04268 | 0.0030512 | 0.0007647
25 | 0.99803 | -0.037789 | 0 | 0
26 | 0.99744 | -0.049176 | 0.0004692 | 0.00011759
27 | 0.99732 | -0.05138 | 0.00078458 | 0.00019663
28 | 0.99719 | -0.053965 | 0 | 0
29 | 0.99732 | -0.051353 | 0 | 0
30 | 0.99718 | -0.054029 | 0.0002978 | 7.4635e-05
31 | 0.99729 | -0.05192 | 0.00084875 | 0.00021272
32 | 0.99627 | -0.071606 | 0.00044316 | 0.00011107
33 | 0.99802 | -0.037941 | 0.00068841 | 0.00017253
34 | 0.99071 | -0.17899 | 0.0013637 | 0.00034177
35 | 0.99627 | -0.071701 | 0.00044419 | 0.00011132
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010229 | -0.0025719 | 0.010231 | 0.002573 | 2.2052e-06 | 1.0836e-06 | 0.015284 | 0.015284 | 0.015284 | 0.99605 | -0.075916 | 0.99628 | -0.071403 | 4.1988
1 | 0.010229 | 0.0025719 | -0.010227 | -0.0025713 | 1.2195e-06 | 5.993e-07 | 0.015284 | 0.015284 | 0.015284 | 0.99605 | -0.075916 | 0.99592 | -0.078413 | 4.1988
2 | 0.00088736 | 0.00022207 | -0.00088735 | -0.00022223 | 8.5958e-09 | -1.6445e-07 | 0.0013252 | 0.0013253 | 0.0013253 | 0.99628 | -0.071403 | 0.99627 | -0.071606 | 0.36409
3 | -0.011118 | -0.0027951 | 0.011127 | 0.0027998 | 9.2649e-06 | 4.7622e-06 | 0.016609 | 0.016608 | 0.016609 | 0.99628 | -0.071403 | 0.99719 | -0.053965 | 4.5629
4 | 0.0097844 | 0.0024603 | -0.0097833 | -0.0024598 | 1.0295e-06 | 4.9179e-07 | 0.014622 | 0.014622 | 0.014622 | 0.99592 | -0.078413 | 0.9958 | -0.080616 | 4.017
5 | 0.0097833 | 0.0024598 | -0.0097824 | -0.0024594 | 8.854e-07 | 4.23e-07 | 0.014622 | 0.014622 | 0.014622 | 0.9958 | -0.080616 | 0.9957 | -0.082511 | 4.017
6 | 0.0093393 | 0.0023483 | -0.0093237 | -0.0023411 | 1.5587e-05 | 7.2067e-06 | 0.01396 | 0.013961 | 0.013961 | 0.9957 | -0.082511 | 0.99389 | -0.11751 | 3.8354
7 | 0.0065184 | 0.0016336 | -0.0065177 | -0.0016334 | 7.0491e-07 | 1.9994e-07 | 0.009803 | 0.0098031 | 0.0098031 | 0.98945 | -0.20362 | 0.98933 | -0.20589 | 2.6931
8 | -0.0074622 | -0.0018701 | 0.0074723 | 0.0018739 | 1.0171e-05 | 3.739e-06 | 0.011222 | 0.011221 | 0.011222 | 0.98945 | -0.20362 | 0.99092 | -0.17503 | 3.083
9 | 0.0065177 | 0.0016334 | -0.0065173 | -0.0016333 | 4.494e-07 | 1.275e-07 | 0.0098031 | 0.0098031 | 0.0098031 | 0.98933 | -0.20589 | 0.98925 | -0.20733 | 2.6932
10 | 0.0013639 | 0.00033983 | -0.0013637 | -0.00034177 | 2.569e-07 | -1.9396e-06 | 0.0020474 | 0.0020482 | 0.0020482 | 0.99092 | -0.17503 | 0.99071 | -0.17899 | 0.56269
11 | -0.0088363 | -0.0022137 | 0.0088423 | 0.0022164 | 6.0528e-06 | 2.6918e-06 | 0.013269 | 0.013268 | 0.013269 | 0.99092 | -0.17503 | 0.99166 | -0.16066 | 3.6452
12 | 0.0058639 | 0.0014695 | -0.0058619 | -0.0014691 | 2.0082e-06 | 4.0185e-07 | 0.0088203 | 0.0088206 | 0.0088206 | 0.98925 | -0.20733 | 0.98888 | -0.21452 | 2.4232
13 | 0.0093237 | 0.0023411 | -0.0093139 | -0.0023366 | 9.7839e-06 | 4.5289e-06 | 0.013961 | 0.013961 | 0.013961 | 0.99389 | -0.11751 | 0.99275 | -0.13952 | 3.8355
14 | 0.0093139 | 0.0023366 | -0.0093046 | -0.0023322 | 9.3773e-06 | 4.3446e-06 | 0.013961 | 0.013962 | 0.013962 | 0.99275 | -0.13952 | 0.99166 | -0.16066 | 3.8357
15 | -0.0075937 | -0.001903 | 0.0075947 | 0.0019034 | 9.809e-07 | 3.617e-07 | 0.011328 | 0.011328 | 0.011328 | 0.99745 | -0.04915 | 0.99759 | -0.046439 | 3.1122
16 | 0.0010087 | 0.00025266 | -0.0010087 | -0.0002528 | 8.9699e-09 | -1.3214e-07 | 0.0015047 | 0.0015048 | 0.0015048 | 0.99745 | -0.04915 | 0.99744 | -0.049337 | 0.4134
17 | 0.0032572 | 0.00081603 | -0.0032569 | -0.00081626 | 2.7631e-07 | -2.3068e-07 | 0.0048584 | 0.0048585 | 0.0048585 | 0.99759 | -0.046439 | 0.99749 | -0.04822 | 1.3348
18 | -0.012663 | -0.0031715 | 0.012667 | 0.0031735 | 3.6397e-06 | 1.9741e-06 | 0.018888 | 0.018888 | 0.018888 | 0.99759 | -0.046439 | 0.9979 | -0.040404 | 5.1891
19 | 0.0018116 | 0.00045209 | -0.0018114 | -0.00045267 | 1.39e-07 | -5.7404e-07 | 0.0027015 | 0.0027017 | 0.0027017 | 0.99759 | -0.046439 | 0.9975 | -0.048054 | 0.74224
20 | 0.0030515 | 0.00076436 | -0.0030513 | -0.00076458 | 2.1456e-07 | -2.2368e-07 | 0.0045501 | 0.0045503 | 0.0045503 | 0.9979 | -0.040404 | 0.99782 | -0.041881 | 1.2501
21 | -0.015719 | -0.0039378 | 0.015749 | 0.0039553 | 3.0304e-05 | 1.7469e-05 | 0.023438 | 0.023438 | 0.023438 | 0.9979 | -0.040404 | 1 | 0 | 6.4391
22 | 0.0018114 | 0.00045267 | -0.0018111 | -0.00045392 | 3.0213e-07 | -1.2469e-06 | 0.0027017 | 0.0027023 | 0.0027023 | 0.9975 | -0.048054 | 0.99732 | -0.051559 | 0.74238
23 | 0.0030513 | 0.00076458 | -0.0030512 | -0.0007647 | 1.1621e-07 | -1.2112e-07 | 0.0045503 | 0.0045503 | 0.0045503 | 0.99782 | -0.041881 | 0.99778 | -0.04268 | 1.2501
24 | 0.014252 | 0.0035924 | -0.01423 | -0.00358 | 2.1966e-05 | 1.2354e-05 | 0.021215 | 0.021215 | 0.021215 | 1 | 0 | 0.99832 | -0.03226 | 5.8283
25 | 0.01423 | 0.00358 | -0.014227 | -0.0035782 | 3.2394e-06 | 1.8223e-06 | 0.021215 | 0.021215 | 0.021215 | 0.99832 | -0.03226 | 0.99807 | -0.037026 | 5.8284
26 | 0.00068844 | 0.00017156 | -0.00068842 | -0.00017237 | 2.497e-08 | -8.1031e-07 | 0.0010261 | 0.0010263 | 0.0010263 | 0.99807 | -0.037026 | 0.99803 | -0.037789 | 0.28196
27 | 0.013538 | 0.0034066 | -0.013531 | -0.0034023 | 7.8563e-06 | 4.3567e-06 | 0.020189 | 0.020189 | 0.020189 | 0.99807 | -0.037026 | 0.99744 | -0.049176 | 5.5465
28 | 0.00068842 | 0.00017237 | -0.00068841 | -0.00017253 | 4.9969e-09 | -1.6209e-07 | 0.0010263 | 0.0010264 | 0.0010264 | 0.99803 | -0.037789 | 0.99802 | -0.037941 | 0.28198
29 | 0.013061 | 0.0032847 | -0.01306 | -0.0032839 | 1.3576e-06 | 7.445e-07 | 0.019489 | 0.019489 | 0.019489 | 0.99744 | -0.049176 | 0.99732 | -0.051353 | 5.3543
30 | 0.011427 | 0.0028751 | -0.011425 | -0.0028743 | 1.4109e-06 | 7.3414e-07 | 0.017053 | 0.017053 | 0.017053 | 0.99732 | -0.05138 | 0.99719 | -0.053965 | 4.6848
31 | -0.012211 | -0.0030717 | 0.012211 | 0.0030717 | 1.6032e-08 | 8.5805e-09 | 0.018223 | 0.018223 | 0.018223 | 0.99732 | -0.05138 | 0.99732 | -0.051353 | 5.0064
32 | 0.0002978 | 7.4475e-05 | -0.0002978 | -7.4635e-05 | 9.142e-10 | -1.6049e-07 | 0.00044432 | 0.00044438 | 0.00044438 | 0.99719 | -0.053965 | 0.99718 | -0.054029 | 0.12208
33 | 0.00084877 | 0.00021223 | -0.00084875 | -0.00021272 | 2.2926e-08 | -4.8284e-07 | 0.0012662 | 0.0012664 | 0.0012664 | 0.99732 | -0.051353 | 0.99729 | -0.05192 | 0.34791
34 | 0.00044419 | 0.00011117 | -0.00044419 | -0.00011132 | 2.0177e-09 | -1.579e-07 | 0.00066339 | 0.00066344 | 0.00066344 | 0.99627 | -0.071606 | 0.99627 | -0.071701 | 0.18226

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.037547 | 0.0090256

## res_load
| p_mw | q_mvar
0 | 0.00044305 | 0.00011104
1 | 0.00044314 | 0.00011106
2 | 0.00094373 | 0.00023652
3 | 0.00065339 | 0.00016376
4 | 0.0058619 | 0.0014691
5 | 0.00046225 | 0.00011585
6 | 0.006585 | 0.0016504
7 | 0.0010087 | 0.0002528
8 | 0.0032569 | 0.00081626
9 | 0.0058964 | 0.0014778
10 | 0.0018111 | 0.00045392
11 | 0.0030512 | 0.0007647
12 | 0.0004692 | 0.00011759
13 | 0.00078458 | 0.00019663
14 | 0.0002978 | 7.4635e-05
15 | 0.00084875 | 0.00021272
16 | 0.00044316 | 0.00011107
17 | 0.00068841 | 0.00017253
18 | 0.0013637 | 0.00034177
19 | 0.00044419 | 0.00011132

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1