## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2124-5_1_6_node_129 | 0.4 | n |  | TRUE
1 | bus_LV_2124-5_1_6_node_104 | 0.4 | n |  | TRUE
2 | bus_LV_2124-5_1_6_node_127 | 0.4 | n |  | TRUE
3 | bus_LV_2124-5_1_6_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_2124-5_1_6_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_2124-5_1_6_node_17 | 0.4 | n |  | TRUE
6 | bus_LV_2124-5_1_6_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_2124-5_1_6_node_34 | 0.4 | n |  | TRUE
8 | bus_LV_2124-5_1_6_node_133 | 0.4 | n |  | TRUE
9 | bus_LV_2124-5_1_6_node_37 | 0.4 | n |  | TRUE
10 | bus_LV_2124-5_1_6_node_52 | 0.4 | n |  | TRUE
11 | bus_LV_2124-5_1_6_node_35 | 0.4 | n |  | TRUE
12 | bus_LV_2124-5_1_6_node_132 | 0.4 | n |  | TRUE
13 | bus_LV_2124-5_1_6_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_2124-5_1_6_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_2124-5_1_6_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_2124-5_1_6_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_2124-5_1_6_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_2124-5_1_6_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_2124-5_1_6_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_2124-5_1_6_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_2124-5_1_6_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_2124-5_1_6_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_2124-5_1_6_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_2124-5_1_6_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_2124-5_1_6_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_2124-5_1_6_node_79 | 0.4 | n |  | TRUE
27 | bus_LV_2124-5_1_6_node_77 | 0.4 | n |  | TRUE
28 | bus_LV_2124-5_1_6_node_87 | 0.4 | n |  | TRUE
29 | bus_LV_2124-5_1_6_node_83 | 0.4 | n |  | TRUE
30 | bus_LV_2124-5_1_6_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_2124-5_1_6_node_108 | 0.4 | n |  | TRUE
32 | bus_LV_2124-5_1_6_node_110 | 0.4 | n |  | TRUE
33 | bus_LV_2124-5_1_6_node_107 | 0.4 | n |  | TRUE
34 | bus_LV_2124-5_1_6_node_49 | 0.4 | n |  | TRUE
35 | bus_LV_2124-5_1_6_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_2124-5_1_6_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_2124-5_1_6_node_40 | 0.4 | n |  | TRUE
38 | bus_LV_2124-5_1_6_node_41 | 0.4 | n |  | TRUE
39 | bus_LV_2124-5_1_6_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_2124-5_1_6_node_103 | 0.4 | n |  | TRUE
41 | bus_LV_2124-5_1_6_node_134 | 0.4 | n |  | TRUE
42 | bus_LV_2124-5_1_6_node_118 | 0.4 | n |  | TRUE
43 | bus_LV_2124-5_1_6_node_126 | 0.4 | n |  | TRUE
44 | bus_LV_2124-5_1_6_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_2124-5_1_6_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_2124-5_1_6_node_45 | 0.4 | n |  | TRUE
47 | bus_LV_2124-5_1_6_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_2124-5_1_6_node_47 | 0.4 | n |  | TRUE
49 | bus_LV_2124-5_1_6_node_61 | 0.4 | n |  | TRUE
50 | bus_LV_2124-5_1_6_node_80 | 0.4 | n |  | TRUE
51 | bus_LV_2124-5_1_6_node_59 | 0.4 | n |  | TRUE
52 | bus_LV_2124-5_1_6_node_90 | 0.4 | n |  | TRUE
53 | bus_LV_2124-5_1_6_node_78 | 0.4 | n |  | TRUE
54 | bus_LV_2124-5_1_6_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_2124-5_1_6_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_2124-5_1_6_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_2124-5_1_6_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_2124-5_1_6_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_2124-5_1_6_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_2124-5_1_6_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_2124-5_1_6_node_138 | 0.4 | n |  | TRUE
62 | bus_LV_2124-5_1_6_node_75 | 0.4 | n |  | TRUE
63 | bus_LV_2124-5_1_6_node_105 | 0.4 | n |  | TRUE
64 | bus_LV_2124-5_1_6_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_2124-5_1_6_node_136 | 0.4 | n |  | TRUE
66 | bus_LV_2124-5_1_6_node_74 | 0.4 | n |  | TRUE
67 | bus_LV_2124-5_1_6_node_106 | 0.4 | n |  | TRUE
68 | bus_LV_2124-5_1_6_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_2124-5_1_6_node_60 | 0.4 | n |  | TRUE
70 | bus_LV_2124-5_1_6_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_2124-5_1_6_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_2124-5_1_6_node_144 | 0.4 | n |  | TRUE
73 | bus_LV_2124-5_1_6_node_94 | 0.4 | n |  | TRUE
74 | bus_LV_2124-5_1_6_node_92 | 0.4 | n |  | TRUE
75 | bus_LV_2124-5_1_6_node_64 | 0.4 | n |  | TRUE
76 | bus_LV_2124-5_1_6_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_2124-5_1_6_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_2124-5_1_6_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_2124-5_1_6_node_68 | 0.4 | n |  | TRUE
80 | bus_LV_2124-5_1_6_node_101 | 0.4 | n |  | TRUE
81 | bus_LV_2124-5_1_6_node_93 | 0.4 | n |  | TRUE
82 | bus_LV_2124-5_1_6_node_102 | 0.4 | n |  | TRUE
83 | bus_LV_2124-5_1_6_node_91 | 0.4 | n |  | TRUE
84 | bus_LV_2124-5_1_6_node_69 | 0.4 | n |  | TRUE
85 | bus_LV_2124-5_1_6_node_70 | 0.4 | n |  | TRUE
86 | bus_LV_2124-5_1_6_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_2124-5_1_6_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_2124-5_1_6_node_85 | 0.4 | n |  | TRUE
89 | bus_LV_2124-5_1_6_node_73 | 0.4 | n |  | TRUE
90 | bus_LV_2124-5_1_6_node_125 | 0.4 | n |  | TRUE
91 | bus_LV_2124-5_1_6_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_2124-5_1_6_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_2124-5_1_6_node_112 | 0.4 | n |  | TRUE
94 | bus_LV_2124-5_1_6_node_124 | 0.4 | n |  | TRUE
95 | bus_LV_2124-5_1_6_node_81 | 0.4 | n |  | TRUE
96 | bus_LV_2124-5_1_6_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_2124-5_1_6_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_2124-5_1_6_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_2124-5_1_6_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_2124-5_1_6_node_123 | 0.4 | n |  | TRUE
101 | bus_LV_2124-5_1_6_node_95 | 0.4 | n |  | TRUE
102 | bus_LV_2124-5_1_6_node_96 | 0.4 | n |  | TRUE
103 | bus_LV_2124-5_1_6_node_97 | 0.4 | n |  | TRUE
104 | bus_LV_2124-5_1_6_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_2124-5_1_6_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_2124-5_1_6_node_120 | 0.4 | n |  | TRUE
107 | bus_LV_2124-5_1_6_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_2124-5_1_6_node_141 | 0.4 | n |  | TRUE
109 | bus_LV_2124-5_1_6_node_116 | 0.4 | n |  | TRUE
110 | bus_LV_2124-5_1_6_node_130 | 0.4 | n |  | TRUE
111 | bus_LV_2124-5_1_6_node_131 | 0.4 | n |  | TRUE
112 | bus_LV_2124-5_1_6_node_114 | 0.4 | n |  | TRUE
113 | bus_LV_2124-5_1_6_node_128 | 0.4 | n |  | TRUE
114 | bus_LV_2124-5_1_6_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_2124-5_1_6_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_2124-5_1_6_node_117 | 0.4 | n |  | TRUE
117 | bus_LV_2124-5_1_6_node_109 | 0.4 | n |  | TRUE
118 | bus_LV_2124-5_1_6_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_2124-5_1_6_node_122 | 0.4 | n |  | TRUE
120 | bus_LV_2124-5_1_6_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_2124-5_1_6_node_119 | 0.4 | n |  | TRUE
122 | bus_LV_2124-5_1_6_node_139 | 0.4 | n |  | TRUE
123 | bus_LV_2124-5_1_6_node_140 | 0.4 | n |  | TRUE
124 | bus_LV_2124-5_1_6_node_135 | 0.4 | n |  | TRUE
125 | bus_LV_2124-5_1_6_node_137 | 0.4 | n |  | TRUE
126 | bus_MV_28_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2124-5_1_6_load_104 | 1 | 0.0056363 | 0.0014126 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2124-5_1_6_load_127 | 2 | 0.0027821 | 0.00069726 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2124-5_1_6_load_12 | 3 | 0.0018171 | 0.00045541 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2124-5_1_6_load_18 | 6 | 0.0018012 | 0.00045142 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2124-5_1_6_load_34 | 7 | 0.0024388 | 0.00061122 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2124-5_1_6_load_133 | 8 | 0.002508 | 0.00062856 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2124-5_1_6_load_37 | 9 | 0.0016712 | 0.00041885 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2124-5_1_6_load_52 | 10 | 0.0010525 | 0.00026379 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2124-5_1_6_load_35 | 11 | 0.0021359 | 0.00053532 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2124-5_1_6_load_132 | 12 | 0.0034992 | 0.00087697 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2124-5_1_6_load_19 | 13 | 0.0014145 | 0.00035451 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2124-5_1_6_load_20 | 14 | 0.0025526 | 0.00063974 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2124-5_1_6_load_23 | 16 | 0.00097162 | 0.00024351 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2124-5_1_6_load_24 | 17 | 0.0010895 | 0.00027305 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2124-5_1_6_load_30 | 19 | 0.0020782 | 0.00052086 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2124-5_1_6_load_26 | 21 | 0.0011957 | 0.00029967 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2124-5_1_6_load_27 | 22 | 0.0033229 | 0.00083281 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2124-5_1_6_load_29 | 23 | 0.0081919 | 0.0020531 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2124-5_1_6_load_31 | 24 | 0.002955 | 0.00074058 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2124-5_1_6_load_33 | 25 | 0.0021663 | 0.00054292 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2124-5_1_6_load_79 | 26 | 0.0031023 | 0.00077752 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2124-5_1_6_load_77 | 27 | 0.0030005 | 0.00075199 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2124-5_1_6_load_87 | 28 | 0.0043144 | 0.0010813 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2124-5_1_6_load_36 | 30 | 0.0009237 | 0.0002315 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2124-5_1_6_load_110 | 32 | 0.00059983 | 0.00015033 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2124-5_1_6_load_107 | 33 | 0.00062525 | 0.0001567 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2124-5_1_6_load_38 | 35 | 0.0032332 | 0.00081031 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2124-5_1_6_load_39 | 36 | 0.0020322 | 0.00050931 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2124-5_1_6_load_40 | 37 | 0.0011721 | 0.00029376 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2124-5_1_6_load_42 | 39 | 0.0088135 | 0.0022089 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2124-5_1_6_load_103 | 40 | 0.002988 | 0.00074886 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2124-5_1_6_load_134 | 41 | 0.0021919 | 0.00054934 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2124-5_1_6_load_118 | 42 | 0.00080539 | 0.00020185 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2124-5_1_6_load_126 | 43 | 0.0022191 | 0.00055616 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2124-5_1_6_load_43 | 44 | 0.0035823 | 0.00089782 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2124-5_1_6_load_44 | 45 | 0.0013794 | 0.00034571 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2124-5_1_6_load_45 | 46 | 0.0022039 | 0.00055236 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2124-5_1_6_load_47 | 48 | 0.00203 | 0.00050877 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2124-5_1_6_load_61 | 49 | 0.0018657 | 0.00046759 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2124-5_1_6_load_59 | 51 | 0.0016023 | 0.00040156 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2124-5_1_6_load_90 | 52 | 0.0037348 | 0.00093603 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2124-5_1_6_load_78 | 53 | 0.0020387 | 0.00051094 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2124-5_1_6_load_48 | 54 | 0.0033101 | 0.00082959 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2124-5_1_6_load_51 | 56 | 0.0014394 | 0.00036076 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2124-5_1_6_load_53 | 57 | 0.0013783 | 0.00034544 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2124-5_1_6_load_54 | 58 | 0.0048094 | 0.0012053 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2124-5_1_6_load_55 | 59 | 0.0027497 | 0.00068914 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2124-5_1_6_load_56 | 60 | 0.0040483 | 0.0010146 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2124-5_1_6_load_138 | 61 | 0.0013525 | 0.00033896 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2124-5_1_6_load_75 | 62 | 0.0027599 | 0.0006917 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2124-5_1_6_load_105 | 63 | 0.0023022 | 0.00057699 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2124-5_1_6_load_57 | 64 | 0.0030459 | 0.00076336 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2124-5_1_6_load_136 | 65 | 0.0012281 | 0.00030778 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2124-5_1_6_load_74 | 66 | 0.0025645 | 0.00064273 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2124-5_1_6_load_106 | 67 | 0.0010345 | 0.00025927 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2124-5_1_6_load_58 | 68 | 0.0028572 | 0.00071608 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2124-5_1_6_load_144 | 72 | 0.0064418 | 0.0016145 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2124-5_1_6_load_94 | 73 | 0.0015701 | 0.0003935 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2124-5_1_6_load_92 | 74 | 0.00090778 | 0.00022751 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2124-5_1_6_load_64 | 75 | 0.0011634 | 0.00029158 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2124-5_1_6_load_65 | 76 | 0.003393 | 0.00085036 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2124-5_1_6_load_66 | 77 | 0.0018086 | 0.00045328 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2124-5_1_6_load_67 | 78 | 0.00067081 | 0.00016812 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2124-5_1_6_load_68 | 79 | 0.0023326 | 0.0005846 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2124-5_1_6_load_101 | 80 | 0.0031167 | 0.00078113 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2124-5_1_6_load_91 | 83 | 0.0019671 | 0.000493 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2124-5_1_6_load_69 | 84 | 0.0047503 | 0.0011905 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2124-5_1_6_load_70 | 85 | 0.0038434 | 0.00096325 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2124-5_1_6_load_71 | 86 | 0.0023989 | 0.00060121 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2124-5_1_6_load_85 | 88 | 0.0023764 | 0.00059559 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2124-5_1_6_load_76 | 91 | 0.001502 | 0.00037644 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2124-5_1_6_load_112 | 93 | 0.0032382 | 0.00081157 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2124-5_1_6_load_81 | 95 | 0.0023199 | 0.00058142 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2124-5_1_6_load_84 | 96 | 0.0205 | 0.0051379 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2124-5_1_6_load_86 | 97 | 0.0084619 | 0.0021207 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2124-5_1_6_load_88 | 98 | 0.0047561 | 0.001192 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2124-5_1_6_load_89 | 99 | 0.0087898 | 0.0022029 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2124-5_1_6_load_123 | 100 | 0.0032533 | 0.00081535 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2124-5_1_6_load_95 | 101 | 0.0061725 | 0.001547 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2124-5_1_6_load_96 | 102 | 0.0086601 | 0.0021704 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2124-5_1_6_load_99 | 105 | 0.0064124 | 0.0016071 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2124-5_1_6_load_120 | 106 | 0.0064033 | 0.0016048 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2124-5_1_6_load_141 | 108 | 0.0040923 | 0.0010256 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2124-5_1_6_load_116 | 109 | 0.0074838 | 0.0018756 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2124-5_1_6_load_131 | 111 | 0.0054049 | 0.0013546 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2124-5_1_6_load_114 | 112 | 0.0054047 | 0.0013545 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2124-5_1_6_load_128 | 113 | 0.0024392 | 0.00061133 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2124-5_1_6_load_113 | 114 | 0.0010681 | 0.00026769 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2124-5_1_6_load_121 | 115 | 0.0042561 | 0.0010667 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2124-5_1_6_load_117 | 116 | 0.0004561 | 0.00011431 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2124-5_1_6_load_109 | 117 | 0.0015536 | 0.00038936 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2124-5_1_6_load_111 | 118 | 0.00035499 | 8.8968e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2124-5_1_6_load_122 | 119 | 0.0006945 | 0.00017406 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2124-5_1_6_load_115 | 120 | 0.0054033 | 0.0013542 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2124-5_1_6_load_119 | 121 | 0.000896 | 0.00022456 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2124-5_1_6_load_139 | 122 | 0.0019671 | 0.000493 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2124-5_1_6_load_140 | 123 | 0.00064794 | 0.00016239 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2124-5_1_6_load_135 | 124 | 0.00123 | 0.00030826 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2124-5_1_6_load_137 | 125 | 0.0013403 | 0.0003359 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 84 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2124-5_1_6_line_0 |  | 0 | 1 | 0.026523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
1 | LV_2124-5_1_6_line_1 |  | 0 | 2 | 0.01939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
2 | LV_2124-5_1_6_line_2 |  | 1 | 38 | 0.032857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_2124-5_1_6_line_3 |  | 2 | 113 | 0.054658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_2124-5_1_6_line_4 |  | 3 | 4 | 0.033289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2124-5_1_6_line_5 |  | 4 | 5 | 0.044325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2124-5_1_6_line_6 |  | 4 | 6 | 0.006692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2124-5_1_6_line_7 |  | 5 | 7 | 0.024724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2124-5_1_6_line_8 |  | 6 | 8 | 0.014207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2124-5_1_6_line_9 |  | 7 | 11 | 0.026252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2124-5_1_6_line_10 |  | 8 | 12 | 0.016164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2124-5_1_6_line_11 |  | 9 | 10 | 0.023107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2124-5_1_6_line_12 |  | 10 | 34 | 0.025876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2124-5_1_6_line_13 |  | 11 | 30 | 0.044688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2124-5_1_6_line_14 |  | 12 | 119 | 0.014957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2124-5_1_6_line_15 |  | 13 | 14 | 0.011533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2124-5_1_6_line_16 |  | 13 | 15 | 0.0066311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2124-5_1_6_line_17 |  | 15 | 16 | 0.0044012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2124-5_1_6_line_18 |  | 16 | 17 | 0.025143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2124-5_1_6_line_19 |  | 17 | 18 | 0.03512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2124-5_1_6_line_20 |  | 18 | 19 | 0.0046242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2124-5_1_6_line_21 |  | 19 | 20 | 0.029342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2124-5_1_6_line_22 |  | 20 | 24 | 0.012233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2124-5_1_6_line_23 |  | 20 | 21 | 0.014001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2124-5_1_6_line_24 |  | 21 | 22 | 0.032037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2124-5_1_6_line_25 |  | 22 | 23 | 0.00022141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2124-5_1_6_line_26 |  | 23 | 25 | 0.050761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2124-5_1_6_line_27 |  | 24 | 26 | 0.012099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2124-5_1_6_line_28 |  | 26 | 27 | 0.060461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2124-5_1_6_line_29 |  | 27 | 53 | 0.023892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2124-5_1_6_line_30 |  | 28 | 29 | 0.040424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2124-5_1_6_line_31 |  | 29 | 97 | 0.035147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2124-5_1_6_line_32 |  | 29 | 95 | 0.0081997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2124-5_1_6_line_33 |  | 31 | 32 | 0.025034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2124-5_1_6_line_34 |  | 31 | 33 | 0.025636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2124-5_1_6_line_35 |  | 32 | 118 | 0.021775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2124-5_1_6_line_36 |  | 33 | 117 | 0.010598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2124-5_1_6_line_37 |  | 34 | 56 | 0.01486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2124-5_1_6_line_38 |  | 34 | 57 | 0.034764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2124-5_1_6_line_39 |  | 34 | 54 | 0.036763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2124-5_1_6_line_40 |  | 35 | 36 | 0.026129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_2124-5_1_6_line_41 |  | 35 | 37 | 0.010663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_2124-5_1_6_line_42 |  | 36 | 38 | 0.03125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_2124-5_1_6_line_43 |  | 37 | 39 | 0.038721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_2124-5_1_6_line_44 |  | 38 | 40 | 0.0257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2124-5_1_6_line_45 |  | 39 | 41 | 0.0039667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_2124-5_1_6_line_46 |  | 40 | 42 | 0.0046544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2124-5_1_6_line_47 |  | 41 | 43 | 0.047444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_2124-5_1_6_line_48 |  | 42 | 116 | 0.0027981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2124-5_1_6_line_49 |  | 43 | 122 | 0.019858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2124-5_1_6_line_50 |  | 43 | 90 | 0.01168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_2124-5_1_6_line_51 |  | 44 | 45 | 0.011685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_2124-5_1_6_line_52 |  | 44 | 46 | 0.0064576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_2124-5_1_6_line_53 |  | 45 | 47 | 0.010877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_2124-5_1_6_line_54 |  | 46 | 48 | 0.0034548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_2124-5_1_6_line_55 |  | 47 | 49 | 0.0022588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_2124-5_1_6_line_56 |  | 48 | 50 | 0.010612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_2124-5_1_6_line_57 |  | 49 | 51 | 0.017778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_2124-5_1_6_line_58 |  | 50 | 52 | 0.045925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_2124-5_1_6_line_59 |  | 50 | 53 | 0.0113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2124-5_1_6_line_60 |  | 51 | 68 | 0.026197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_2124-5_1_6_line_61 |  | 52 | 94 | 0.01536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_2124-5_1_6_line_62 |  | 54 | 55 | 0.037365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2124-5_1_6_line_63 |  | 55 | 58 | 0.013715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_2124-5_1_6_line_64 |  | 55 | 59 | 0.041666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_2124-5_1_6_line_65 |  | 56 | 60 | 0.0016291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2124-5_1_6_line_66 |  | 57 | 61 | 0.012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2124-5_1_6_line_67 |  | 58 | 62 | 0.0052735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_2124-5_1_6_line_68 |  | 59 | 63 | 0.0023412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_2124-5_1_6_line_69 |  | 60 | 64 | 0.037618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2124-5_1_6_line_70 |  | 61 | 65 | 0.0020906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2124-5_1_6_line_71 |  | 62 | 66 | 0.027186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_2124-5_1_6_line_72 |  | 63 | 67 | 0.026778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_2124-5_1_6_line_73 |  | 65 | 124 | 0.019139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2124-5_1_6_line_74 |  | 66 | 91 | 0.0067686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_2124-5_1_6_line_75 |  | 67 | 71 | 0.025243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_2124-5_1_6_line_76 |  | 68 | 69 | 0.0082099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_2124-5_1_6_line_77 |  | 69 | 70 | 0.054955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2124-5_1_6_line_78 |  | 69 | 71 | 0.009482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_2124-5_1_6_line_79 |  | 70 | 72 | 0.01954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2124-5_1_6_line_80 |  | 71 | 73 | 0.013395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2124-5_1_6_line_81 |  | 73 | 74 | 0.016843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2124-5_1_6_line_82 |  | 74 | 83 | 0.0078688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2124-5_1_6_line_83 |  | 75 | 76 | 0.015562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2124-5_1_6_line_84 |  | 75 | 77 | 0.006133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2124-5_1_6_line_85 |  | 76 | 78 | 0.010651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2124-5_1_6_line_86 |  | 77 | 79 | 0.01865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2124-5_1_6_line_87 |  | 78 | 80 | 0.006671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2124-5_1_6_line_88 |  | 79 | 81 | 0.027041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2124-5_1_6_line_89 |  | 80 | 82 | 0.012405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2124-5_1_6_line_90 |  | 81 | 83 | 0.0062907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2124-5_1_6_line_91 |  | 82 | 114 | 0.0052954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2124-5_1_6_line_92 |  | 84 | 85 | 0.031826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_2124-5_1_6_line_93 |  | 84 | 86 | 0.033218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2124-5_1_6_line_94 |  | 85 | 87 | 0.043224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_2124-5_1_6_line_95 |  | 87 | 88 | 0.0021353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_2124-5_1_6_line_96 |  | 88 | 92 | 0.03634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_2124-5_1_6_line_97 |  | 89 | 90 | 0.032458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_2124-5_1_6_line_98 |  | 89 | 91 | 0.027115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_2124-5_1_6_line_99 |  | 90 | 93 | 0.010907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2124-5_1_6_line_100 |  | 92 | 96 | 0.014455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_2124-5_1_6_line_101 |  | 92 | 95 | 0.018755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2124-5_1_6_line_102 |  | 93 | 118 | 0.022138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2124-5_1_6_line_103 |  | 94 | 100 | 0.0064418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2124-5_1_6_line_104 |  | 94 | 99 | 0.031363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_2124-5_1_6_line_105 |  | 96 | 98 | 0.0083001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_2124-5_1_6_line_106 |  | 98 | 99 | 0.039683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_2124-5_1_6_line_107 |  | 101 | 102 | 0.01595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_2124-5_1_6_line_108 |  | 101 | 103 | 0.013867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2124-5_1_6_line_109 |  | 102 | 104 | 0.016655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_2124-5_1_6_line_110 |  | 103 | 105 | 0.072721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2124-5_1_6_line_111 |  | 104 | 106 | 0.0098412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2124-5_1_6_line_112 |  | 104 | 107 | 0.051486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_2124-5_1_6_line_113 |  | 105 | 108 | 0.040794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2124-5_1_6_line_114 |  | 106 | 111 | 0.014492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2124-5_1_6_line_115 |  | 107 | 109 | 0.025044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2124-5_1_6_line_116 |  | 107 | 110 | 0.067114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_2124-5_1_6_line_117 |  | 109 | 112 | 0.02353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2124-5_1_6_line_118 |  | 110 | 113 | 0.010841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
119 | LV_2124-5_1_6_line_119 |  | 112 | 120 | 0.013985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2124-5_1_6_line_120 |  | 114 | 115 | 0.021142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2124-5_1_6_line_121 |  | 115 | 119 | 0.013138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2124-5_1_6_line_122 |  | 116 | 121 | 0.022287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2124-5_1_6_line_123 |  | 122 | 123 | 0.0058684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2124-5_1_6_line_124 |  | 124 | 125 | 0.0044298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2124-5_1_6_trafo_69 | 0.63 MVA 20/0.4 kV | 126 | 84 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2574232.2202 | 1160904.521 | 2574258.3176 | 1160909.2523
1 | 2574232.2202 | 1160904.521 | 2574230.1156 | 1160910.4664 | 2574220.9299 | 1160919.7819
2 | 2574284.2426 | 1160922.5956 | 2574283.4119 | 1160916.4961 | 2574279.4203 | 1160913.0781 | 2574258.3176 | 1160909.2523
3 | 2574220.9299 | 1160919.7819 | 2574182.5527 | 1160958.7015
4 | 2574521.9503 | 1160990.848 | 2574528.5582 | 1160971.6881 | 2574535.1615 | 1160960.4655
5 | 2574521.9503 | 1160990.848 | 2574485.2934 | 1160965.7803
6 | 2574521.9503 | 1160990.848 | 2574523.0504 | 1160997.4489
7 | 2574485.2934 | 1160965.7803 | 2574473.7497 | 1160957.6587 | 2574464.8504 | 1160951.8821
8 | 2574523.0504 | 1160997.4489 | 2574523.8925 | 1161002.5012 | 2574524.8738 | 1161011.5328
9 | 2574442.8307 | 1160937.589 | 2574464.8504 | 1160951.8821
10 | 2574526.6198 | 1161027.6022 | 2574524.8738 | 1161011.5328
11 | 2574447.7695 | 1161003.4301 | 2574431.4578 | 1161019.7965
12 | 2574413.1916 | 1161038.124 | 2574431.4578 | 1161019.7965
13 | 2574442.8307 | 1160937.589 | 2574438.3427 | 1160934.6758 | 2574404.9904 | 1160913.8187 | 2574404.9904 | 1160913.8187
14 | 2574530.5768 | 1161042.0259 | 2574526.6198 | 1161027.6022 | 2574526.6198 | 1161027.6022
15 | 2574265.6004 | 1161348.9275 | 2574276.2415 | 1161353.3745
16 | 2574259.4821 | 1161346.3706 | 2574265.6004 | 1161348.9275
17 | 2574259.4821 | 1161346.3706 | 2574255.4213 | 1161344.6732
18 | 2574255.4213 | 1161344.6732 | 2574252.5585 | 1161343.4766 | 2574232.8805 | 1161333.5495
19 | 2574204.1093 | 1161314.526 | 2574210.2795 | 1161322.1477 | 2574232.8805 | 1161333.5495
20 | 2574204.1093 | 1161314.526 | 2574208.6782 | 1161313.8131
21 | 2574237.6697 | 1161309.2901 | 2574208.6782 | 1161313.8131
22 | 2574237.6697 | 1161309.2901 | 2574237.8785 | 1161302.608 | 2574240.8542 | 1161297.9262
23 | 2574237.6697 | 1161309.2901 | 2574251.534 | 1161307.3362
24 | 2574251.534 | 1161307.3362 | 2574254.1868 | 1161306.9624 | 2574283.2589 | 1161302.8745
25 | 2574283.2589 | 1161302.8745 | 2574283.4782 | 1161302.8437
26 | 2574283.4782 | 1161302.8437 | 2574333.7447 | 1161295.7756
27 | 2574240.8542 | 1161297.9262 | 2574249.8006 | 1161289.7802
28 | 2574297.3022 | 1161252.3781 | 2574250.3487 | 1161289.2811 | 2574249.8006 | 1161289.7802
29 | 2574297.3022 | 1161252.3781 | 2574316.0871 | 1161237.6141
30 | 2574190.8757 | 1161225.3269 | 2574174.6765 | 1161248.1193 | 2574166.2703 | 1161257.3187
31 | 2574190.8757 | 1161225.3269 | 2574216.0294 | 1161249.9422
32 | 2574190.8757 | 1161225.3269 | 2574195.6297 | 1161218.646
33 | 2574365.3291 | 1160947.9165 | 2574347.1103 | 1160965.0851
34 | 2574365.3291 | 1160947.9165 | 2574368.4728 | 1160953.7727 | 2574383.2873 | 1160965.6531
35 | 2574331.2633 | 1160980.0185 | 2574347.1103 | 1160965.0851
36 | 2574391.5549 | 1160972.2833 | 2574383.2873 | 1160965.6531
37 | 2574413.1916 | 1161038.124 | 2574401.94 | 1161028.4176
38 | 2574413.1916 | 1161038.124 | 2574439.2196 | 1161061.169
39 | 2574413.1916 | 1161038.124 | 2574387.8111 | 1161064.7198
40 | 2574237.1544 | 1160946.788 | 2574241.0884 | 1160937.1882 | 2574256.4432 | 1160933.6607
41 | 2574237.1544 | 1160946.788 | 2574233.1111 | 1160956.6545 | 2574233.1111 | 1160956.6545
42 | 2574284.2426 | 1160922.5956 | 2574280.0448 | 1160928.2386 | 2574256.4432 | 1160933.6607
43 | 2574254.3611 | 1160989.0215 | 2574242.8974 | 1160971.1975 | 2574233.1111 | 1160956.6545
44 | 2574284.2426 | 1160922.5956 | 2574308.3162 | 1160913.5975
45 | 2574254.3611 | 1160989.0215 | 2574256.5068 | 1160992.3577
46 | 2574312.676 | 1160911.968 | 2574308.3162 | 1160913.5975
47 | 2574303.9421 | 1160991.4692 | 2574256.5068 | 1160992.3577
48 | 2574312.676 | 1160911.968 | 2574315.297 | 1160910.9883
49 | 2574303.9421 | 1160991.4692 | 2574301.9721 | 1160984.7174 | 2574301.6483 | 1160978.9048 | 2574303.5914 | 1160972.1768
50 | 2574307.2137 | 1161002.6818 | 2574303.9421 | 1160991.4692
51 | 2574340.8625 | 1161217.6423 | 2574349.9096 | 1161210.2473
52 | 2574340.8625 | 1161217.6423 | 2574335.8627 | 1161221.7291
53 | 2574358.3309 | 1161203.3638 | 2574349.9096 | 1161210.2473
54 | 2574333.1878 | 1161223.9155 | 2574335.8627 | 1161221.7291
55 | 2574358.3309 | 1161203.3638 | 2574360.0799 | 1161201.9344
56 | 2574324.9715 | 1161230.6314 | 2574333.1878 | 1161223.9155
57 | 2574360.0799 | 1161201.9344 | 2574373.8455 | 1161190.6841
58 | 2574324.9715 | 1161230.6314 | 2574305.7384 | 1161216.0954 | 2574288.9915 | 1161202.1123
59 | 2574324.9715 | 1161230.6314 | 2574316.0871 | 1161237.6141
60 | 2574394.1299 | 1161174.1061 | 2574373.8455 | 1161190.6841
61 | 2574276.9806 | 1161192.5403 | 2574286.6908 | 1161200.1913 | 2574288.9915 | 1161202.1123
62 | 2574362.1445 | 1161091.8581 | 2574366.8791 | 1161086.3128 | 2574380.5961 | 1161072.2804 | 2574387.8111 | 1161064.7198
63 | 2574362.1445 | 1161091.8581 | 2574360.9475 | 1161089.6732 | 2574353.1866 | 1161081.5647
64 | 2574362.1445 | 1161091.8581 | 2574361.2148 | 1161094.8413 | 2574355.3203 | 1161101.5032 | 2574354.025 | 1161108.579 | 2574358.0895 | 1161114.7425 | 2574369.2348 | 1161124.885
65 | 2574401.94 | 1161028.4176 | 2574400.7064 | 1161027.3534
66 | 2574430.1874 | 1161069.0698 | 2574439.2196 | 1161061.169 | 2574439.2196 | 1161061.169
67 | 2574349.5403 | 1161077.755 | 2574353.1866 | 1161081.5647
68 | 2574369.2348 | 1161124.885 | 2574370.9663 | 1161126.4608
69 | 2574372.2226 | 1161002.7813 | 2574400.7064 | 1161027.3534
70 | 2574428.6139 | 1161070.4463 | 2574430.1874 | 1161069.0698
71 | 2574349.5403 | 1161077.755 | 2574330.7423 | 1161058.115
72 | 2574390.7714 | 1161144.484 | 2574370.9663 | 1161126.4608
73 | 2574414.2081 | 1161083.0476 | 2574428.6139 | 1161070.4463
74 | 2574325.8104 | 1161053.4819 | 2574330.0371 | 1161057.3781 | 2574330.7423 | 1161058.115
75 | 2574407.8399 | 1161162.8985 | 2574401.8968 | 1161154.6086 | 2574390.7714 | 1161144.484
76 | 2574400.4868 | 1161168.9107 | 2574394.1299 | 1161174.1061
77 | 2574400.4868 | 1161168.9107 | 2574441.8689 | 1161200.8057 | 2574444.0677 | 1161202.5416
78 | 2574407.8399 | 1161162.8985 | 2574400.4868 | 1161168.9107
79 | 2574444.0677 | 1161202.5416 | 2574455.2628 | 1161186.5081
80 | 2574407.8399 | 1161162.8985 | 2574418.4741 | 1161154.7531
81 | 2574431.8452 | 1161144.5113 | 2574418.4741 | 1161154.7531
82 | 2574438.092 | 1161139.7265 | 2574431.8452 | 1161144.5113
83 | 2574484.2302 | 1161104.391 | 2574496.5855 | 1161094.9287
84 | 2574484.2302 | 1161104.391 | 2574479.3611 | 1161108.12
85 | 2574505.0412 | 1161088.4529 | 2574496.5855 | 1161094.9287
86 | 2574479.3611 | 1161108.12 | 2574464.5543 | 1161119.4598
87 | 2574505.0412 | 1161088.4529 | 2574510.3375 | 1161084.3967
88 | 2574443.0861 | 1161135.9012 | 2574464.5543 | 1161119.4598
89 | 2574520.1859 | 1161076.8543 | 2574510.3375 | 1161084.3967
90 | 2574443.0861 | 1161135.9012 | 2574438.092 | 1161139.7265
91 | 2574520.1859 | 1161076.8543 | 2574523.5906 | 1161072.7986
92 | 2574272.5768 | 1161119.6498 | 2574272.0139 | 1161120.8144 | 2574253.9424 | 1161137.7672 | 2574249.1553 | 1161140.9602
93 | 2574272.5768 | 1161119.6498 | 2574287.0324 | 1161089.7421
94 | 2574213.1963 | 1161164.9449 | 2574249.1553 | 1161140.9602
95 | 2574213.1963 | 1161164.9449 | 2574211.992 | 1161166.7083
96 | 2574202.5418 | 1161201.4091 | 2574204.7706 | 1161185.1691 | 2574209.7698 | 1161169.9622 | 2574211.992 | 1161166.7083
97 | 2574305.8739 | 1161035.1038 | 2574307.2137 | 1161002.6818
98 | 2574305.8739 | 1161035.1038 | 2574325.8104 | 1161053.4819
99 | 2574307.2137 | 1161002.6818 | 2574315.1517 | 1160995.2013
100 | 2574202.5418 | 1161201.4091 | 2574212.9257 | 1161211.4648
101 | 2574202.5418 | 1161201.4091 | 2574198.4613 | 1161214.6667 | 2574195.6297 | 1161218.646
102 | 2574331.2633 | 1160980.0185 | 2574315.1517 | 1160995.2013
103 | 2574276.9806 | 1161192.5403 | 2574271.5765 | 1161189.0342
104 | 2574276.9806 | 1161192.5403 | 2574253.1739 | 1161212.9583
105 | 2574212.9257 | 1161211.4648 | 2574218.8882 | 1161217.2389
106 | 2574253.1739 | 1161212.9583 | 2574240.0622 | 1161224.2037 | 2574228.342 | 1161221.3415 | 2574219.3077 | 1161217.6451 | 2574218.8882 | 1161217.2389
107 | 2574171.0955 | 1161108.2328 | 2574179.6309 | 1161094.7591
108 | 2574160.8406 | 1161108.253 | 2574168.3073 | 1161112.6341 | 2574171.0955 | 1161108.2328
109 | 2574186.5481 | 1161079.8835 | 2574185.3398 | 1161085.7472 | 2574179.6309 | 1161094.7591
110 | 2574160.8406 | 1161108.253 | 2574153.9332 | 1161119.8331 | 2574144.299 | 1161135.2046 | 2574134.546 | 1161162.0824 | 2574130.6337 | 1161173.9578
111 | 2574186.5481 | 1161079.8835 | 2574192.2771 | 1161079.2919 | 2574195.6308 | 1161076.9652
112 | 2574182.2654 | 1161032.0001 | 2574182.0845 | 1161062.9275 | 2574179.5119 | 1161074.0553 | 2574186.5481 | 1161079.8835
113 | 2574109.1031 | 1161208.4944 | 2574118.8662 | 1161195.1334 | 2574130.288 | 1161175.0073 | 2574130.6337 | 1161173.9578
114 | 2574203.2816 | 1161064.6568 | 2574195.6308 | 1161076.9652
115 | 2574182.2654 | 1161032.0001 | 2574206.7855 | 1161026.9044
116 | 2574174.9409 | 1160966.4209 | 2574172.4737 | 1160970.0111 | 2574182.2654 | 1161032.0001
117 | 2574206.7855 | 1161026.9044 | 2574214.1663 | 1161025.3705 | 2574219.7646 | 1161026.4803 | 2574222.9962 | 1161029.5791 | 2574223.1161 | 1161034.3032 | 2574222.5267 | 1161035.2102
118 | 2574174.9409 | 1160966.4209 | 2574182.5527 | 1160958.7015
119 | 2574222.5267 | 1161035.2102 | 2574214.9059 | 1161046.9368
120 | 2574523.5906 | 1161072.7986 | 2574529.3268 | 1161065.9656 | 2574534.0526 | 1161054.6954 | 2574534.0526 | 1161054.6954
121 | 2574530.5768 | 1161042.0259 | 2574534.0526 | 1161054.6954
122 | 2574336.1731 | 1160903.1854 | 2574315.297 | 1160910.9883
123 | 2574305.2197 | 1160966.5388 | 2574303.5914 | 1160972.1768
124 | 2574414.2081 | 1161083.0476 | 2574410.8739 | 1161085.9642

## bus_geodata
| x | y | coords
0 | 2574232.2202 | 1160904.521
1 | 2574258.3176 | 1160909.2523
2 | 2574220.9299 | 1160919.7819
3 | 2574535.1615 | 1160960.4655
4 | 2574521.9503 | 1160990.848
5 | 2574485.2934 | 1160965.7803
6 | 2574523.0504 | 1160997.4489
7 | 2574464.8504 | 1160951.8821
8 | 2574524.8738 | 1161011.5328
9 | 2574447.7695 | 1161003.4301
10 | 2574431.4578 | 1161019.7965
11 | 2574442.8307 | 1160937.589
12 | 2574526.6198 | 1161027.6022
13 | 2574265.6004 | 1161348.9275
14 | 2574276.2415 | 1161353.3745
15 | 2574259.4821 | 1161346.3706
16 | 2574255.4213 | 1161344.6732
17 | 2574232.8805 | 1161333.5495
18 | 2574204.1093 | 1161314.526
19 | 2574208.6782 | 1161313.8131
20 | 2574237.6697 | 1161309.2901
21 | 2574251.534 | 1161307.3362
22 | 2574283.2589 | 1161302.8745
23 | 2574283.4782 | 1161302.8437
24 | 2574240.8542 | 1161297.9262
25 | 2574333.7447 | 1161295.7756
26 | 2574249.8006 | 1161289.7802
27 | 2574297.3022 | 1161252.3781
28 | 2574166.2703 | 1161257.3187
29 | 2574190.8757 | 1161225.3269
30 | 2574404.9904 | 1160913.8187
31 | 2574365.3291 | 1160947.9165
32 | 2574347.1103 | 1160965.0851
33 | 2574383.2873 | 1160965.6531
34 | 2574413.1916 | 1161038.124
35 | 2574237.1544 | 1160946.788
36 | 2574256.4432 | 1160933.6607
37 | 2574233.1111 | 1160956.6545
38 | 2574284.2426 | 1160922.5956
39 | 2574254.3611 | 1160989.0215
40 | 2574308.3162 | 1160913.5975
41 | 2574256.5068 | 1160992.3577
42 | 2574312.676 | 1160911.968
43 | 2574303.9421 | 1160991.4692
44 | 2574340.8625 | 1161217.6423
45 | 2574349.9096 | 1161210.2473
46 | 2574335.8627 | 1161221.7291
47 | 2574358.3309 | 1161203.3638
48 | 2574333.1878 | 1161223.9155
49 | 2574360.0799 | 1161201.9344
50 | 2574324.9715 | 1161230.6314
51 | 2574373.8455 | 1161190.6841
52 | 2574288.9915 | 1161202.1123
53 | 2574316.0871 | 1161237.6141
54 | 2574387.8111 | 1161064.7198
55 | 2574362.1445 | 1161091.8581
56 | 2574401.94 | 1161028.4176
57 | 2574439.2196 | 1161061.169
58 | 2574353.1866 | 1161081.5647
59 | 2574369.2348 | 1161124.885
60 | 2574400.7064 | 1161027.3534
61 | 2574430.1874 | 1161069.0698
62 | 2574349.5403 | 1161077.755
63 | 2574370.9663 | 1161126.4608
64 | 2574372.2226 | 1161002.7813
65 | 2574428.6139 | 1161070.4463
66 | 2574330.7423 | 1161058.115
67 | 2574390.7714 | 1161144.484
68 | 2574394.1299 | 1161174.1061
69 | 2574400.4868 | 1161168.9107
70 | 2574444.0677 | 1161202.5416
71 | 2574407.8399 | 1161162.8985
72 | 2574455.2627 | 1161186.5081
73 | 2574418.4741 | 1161154.7531
74 | 2574431.8452 | 1161144.5113
75 | 2574484.2302 | 1161104.391
76 | 2574496.5855 | 1161094.9287
77 | 2574479.3611 | 1161108.12
78 | 2574505.0412 | 1161088.4529
79 | 2574464.5543 | 1161119.4598
80 | 2574510.3375 | 1161084.3967
81 | 2574443.0861 | 1161135.9012
82 | 2574520.1859 | 1161076.8543
83 | 2574438.092 | 1161139.7265
84 | 2574272.5768 | 1161119.6498
85 | 2574249.1553 | 1161140.9602
86 | 2574287.0324 | 1161089.7421
87 | 2574213.1963 | 1161164.9449
88 | 2574211.992 | 1161166.7083
89 | 2574305.8739 | 1161035.1038
90 | 2574307.2137 | 1161002.6818
91 | 2574325.8104 | 1161053.4819
92 | 2574202.5418 | 1161201.4091
93 | 2574315.1517 | 1160995.2013
94 | 2574276.9806 | 1161192.5403
95 | 2574195.6297 | 1161218.646
96 | 2574212.9257 | 1161211.4648
97 | 2574216.0294 | 1161249.9422
98 | 2574218.8882 | 1161217.2389
99 | 2574253.1739 | 1161212.9583
100 | 2574271.5765 | 1161189.0342
101 | 2574171.0955 | 1161108.2328
102 | 2574179.6309 | 1161094.7591
103 | 2574160.8406 | 1161108.253
104 | 2574186.5481 | 1161079.8835
105 | 2574130.6337 | 1161173.9578
106 | 2574195.6308 | 1161076.9652
107 | 2574182.2654 | 1161032.0001
108 | 2574109.1031 | 1161208.4944
109 | 2574206.7855 | 1161026.9044
110 | 2574174.9409 | 1160966.4209
111 | 2574203.2816 | 1161064.6568
112 | 2574222.5267 | 1161035.2102
113 | 2574182.5527 | 1160958.7015
114 | 2574523.5906 | 1161072.7986
115 | 2574534.0526 | 1161054.6954
116 | 2574315.297 | 1160910.9883
117 | 2574391.5549 | 1160972.2833
118 | 2574331.2633 | 1160980.0185
119 | 2574530.5768 | 1161042.0259
120 | 2574214.9059 | 1161046.9368
121 | 2574336.1731 | 1160903.1854
122 | 2574303.5914 | 1160972.1768
123 | 2574305.2197 | 1160966.5388
124 | 2574414.2081 | 1161083.0476
125 | 2574410.8739 | 1161085.9642
126 | 2574213.1963 | 1161164.9449

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97529 | -0.47635 | 0 | 0
1 | 0.97559 | -0.47045 | 0.0056363 | 0.0014126
2 | 0.97507 | -0.48066 | 0.0027821 | 0.00069726
3 | 0.97772 | -0.42885 | 0.0018171 | 0.00045541
4 | 0.97778 | -0.42775 | 0 | 0
5 | 0.97755 | -0.43219 | 0 | 0
6 | 0.97782 | -0.42685 | 0.0018012 | 0.00045142
7 | 0.97743 | -0.43467 | 0.0024388 | 0.00061122
8 | 0.97794 | -0.42449 | 0.002508 | 0.00062856
9 | 0.97925 | -0.3987 | 0.0016712 | 0.00041885
10 | 0.97929 | -0.398 | 0.0010525 | 0.00026379
11 | 0.97735 | -0.43614 | 0.0021359 | 0.00053532
12 | 0.97812 | -0.42106 | 0.0034992 | 0.00087697
13 | 0.98304 | -0.32528 | 0.0014145 | 0.00035451
14 | 0.98301 | -0.32581 | 0.0025526 | 0.00063974
15 | 0.98306 | -0.32481 | 0 | 0
16 | 0.98308 | -0.32449 | 0.00097162 | 0.00024351
17 | 0.98319 | -0.32225 | 0.0010895 | 0.00027305
18 | 0.98339 | -0.31843 | 0 | 0
19 | 0.98341 | -0.31793 | 0.0020782 | 0.00052086
20 | 0.98363 | -0.31364 | 0 | 0
21 | 0.98344 | -0.3174 | 0.0011957 | 0.00029967
22 | 0.98303 | -0.3253 | 0.0033229 | 0.00083281
23 | 0.98303 | -0.32534 | 0.0081919 | 0.0020531
24 | 0.98389 | -0.30858 | 0.002955 | 0.00074058
25 | 0.98293 | -0.32733 | 0.0021663 | 0.00054292
26 | 0.98418 | -0.30293 | 0.0031023 | 0.00077752
27 | 0.9858 | -0.27138 | 0.0030005 | 0.00075199
28 | 0.99336 | -0.12622 | 0.0043144 | 0.0010813
29 | 0.99351 | -0.12314 | 0 | 0
30 | 0.97731 | -0.43689 | 0.0009237 | 0.0002315
31 | 0.9783 | -0.41726 | 0 | 0
32 | 0.97835 | -0.41627 | 0.00059983 | 0.00015033
33 | 0.97825 | -0.41828 | 0.00062525 | 0.0001567
34 | 0.97935 | -0.39672 | 0 | 0
35 | 0.97677 | -0.44727 | 0.0032332 | 0.00081031
36 | 0.97641 | -0.45429 | 0.0020322 | 0.00050931
37 | 0.97692 | -0.44428 | 0.0011721 | 0.00029376
38 | 0.97599 | -0.46247 | 0 | 0
39 | 0.97748 | -0.43326 | 0.0088135 | 0.0022089
40 | 0.97587 | -0.46489 | 0.002988 | 0.00074886
41 | 0.97754 | -0.43201 | 0.0021919 | 0.00054934
42 | 0.97586 | -0.46507 | 0.00080539 | 0.00020185
43 | 0.97833 | -0.41662 | 0.0022191 | 0.00055616
44 | 0.98611 | -0.26527 | 0.0035823 | 0.00089782
45 | 0.98569 | -0.27329 | 0.0013794 | 0.00034571
46 | 0.98634 | -0.26076 | 0.0022039 | 0.00055236
47 | 0.98531 | -0.2807 | 0 | 0
48 | 0.98647 | -0.25832 | 0.00203 | 0.00050877
49 | 0.98523 | -0.28224 | 0.0018657 | 0.00046759
50 | 0.98686 | -0.25075 | 0 | 0
51 | 0.98461 | -0.29425 | 0.0016023 | 0.00040156
52 | 0.98884 | -0.2125 | 0.0037348 | 0.00093603
53 | 0.9865 | -0.25765 | 0.0020387 | 0.00051094
54 | 0.97996 | -0.38484 | 0.0033101 | 0.00082959
55 | 0.98069 | -0.37054 | 0 | 0
56 | 0.97924 | -0.39903 | 0.0014394 | 0.00036076
57 | 0.97914 | -0.40085 | 0.0013783 | 0.00034544
58 | 0.9804 | -0.3761 | 0.0048094 | 0.0012053
59 | 0.98172 | -0.35048 | 0.0027497 | 0.00068914
60 | 0.97922 | -0.39924 | 0.0040483 | 0.0010146
61 | 0.97909 | -0.40197 | 0.0013525 | 0.00033896
62 | 0.9803 | -0.37815 | 0.0027599 | 0.0006917
63 | 0.98178 | -0.34934 | 0.0023022 | 0.00057699
64 | 0.97912 | -0.40132 | 0.0030459 | 0.00076336
65 | 0.97908 | -0.40212 | 0.0012281 | 0.00030778
66 | 0.97977 | -0.38843 | 0.0025645 | 0.00064273
67 | 0.98246 | -0.33598 | 0.0010345 | 0.00025927
68 | 0.9837 | -0.31183 | 0.0028572 | 0.00071608
69 | 0.98342 | -0.31726 | 0 | 0
70 | 0.9831 | -0.32364 | 0 | 0
71 | 0.98311 | -0.32331 | 0 | 0
72 | 0.98298 | -0.32591 | 0.0064418 | 0.0016145
73 | 0.98264 | -0.33252 | 0.0015701 | 0.0003935
74 | 0.98207 | -0.34363 | 0.00090778 | 0.00022751
75 | 0.98006 | -0.38285 | 0.0011634 | 0.00029158
76 | 0.97966 | -0.39086 | 0.003393 | 0.00085036
77 | 0.98023 | -0.37957 | 0.0018086 | 0.00045328
78 | 0.97941 | -0.39568 | 0.00067081 | 0.00016812
79 | 0.98077 | -0.36899 | 0.0023326 | 0.0005846
80 | 0.97926 | -0.39862 | 0.0031167 | 0.00078113
81 | 0.98162 | -0.35252 | 0 | 0
82 | 0.97902 | -0.40339 | 0 | 0
83 | 0.98181 | -0.34869 | 0.0019671 | 0.000493
84 | 1 | 0 | -0.30451 | -0.0778
85 | 0.99826 | -0.032851 | 0.0038434 | 0.00096325
86 | 0.99993 | -0.0013893 | 0.0023989 | 0.00060121
87 | 0.99593 | -0.077065 | 0 | 0
88 | 0.99581 | -0.079255 | 0.0023764 | 0.00059559
89 | 0.97914 | -0.40081 | 0 | 0
90 | 0.97853 | -0.41264 | 0 | 0
91 | 0.97964 | -0.39093 | 0.001502 | 0.00037644
92 | 0.99387 | -0.11629 | 0 | 0
93 | 0.97847 | -0.4139 | 0.0032382 | 0.00081157
94 | 0.98952 | -0.19953 | 0 | 0
95 | 0.99361 | -0.12129 | 0.0023199 | 0.00058142
96 | 0.99314 | -0.13029 | 0.0205 | 0.0051379
97 | 0.99324 | -0.12839 | 0.0084619 | 0.0021207
98 | 0.99275 | -0.13774 | 0.0047561 | 0.001192
99 | 0.99091 | -0.17275 | 0.0087898 | 0.0022029
100 | 0.9895 | -0.19991 | 0.0032533 | 0.00081535
101 | 0.97311 | -0.5192 | 0.0061725 | 0.001547
102 | 0.97324 | -0.51675 | 0.0086601 | 0.0021704
103 | 0.97298 | -0.52188 | 0 | 0
104 | 0.97332 | -0.51519 | 0 | 0
105 | 0.97227 | -0.53596 | 0.0064124 | 0.0016071
106 | 0.97321 | -0.51733 | 0.0064033 | 0.0016048
107 | 0.97367 | -0.50816 | 0 | 0
108 | 0.97211 | -0.53904 | 0.0040923 | 0.0010256
109 | 0.97325 | -0.51658 | 0.0074838 | 0.0018756
110 | 0.97437 | -0.49448 | 0 | 0
111 | 0.97314 | -0.51877 | 0.0054049 | 0.0013546
112 | 0.97301 | -0.52127 | 0.0054047 | 0.0013545
113 | 0.97448 | -0.49227 | 0.0024392 | 0.00061133
114 | 0.97891 | -0.40543 | 0.0010681 | 0.00026769
115 | 0.97852 | -0.41316 | 0.0042561 | 0.0010667
116 | 0.97586 | -0.46514 | 0.0004561 | 0.00011431
117 | 0.97823 | -0.41858 | 0.0015536 | 0.00038936
118 | 0.9784 | -0.41517 | 0.00035499 | 8.8968e-05
119 | 0.97833 | -0.41694 | 0.0006945 | 0.00017406
120 | 0.97294 | -0.52266 | 0.0054033 | 0.0013542
121 | 0.97584 | -0.46551 | 0.000896 | 0.00022456
122 | 0.97828 | -0.41757 | 0.0019671 | 0.000493
123 | 0.97828 | -0.41764 | 0.00064794 | 0.00016239
124 | 0.97903 | -0.40301 | 0.00123 | 0.00030826
125 | 0.97903 | -0.40312 | 0.0013403 | 0.0003359
126 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.060782 | -0.015265 | 0.060799 | 0.015274 | 1.7111e-05 | 9.2959e-06 | 0.092748 | 0.092747 | 0.092748 | 0.97529 | -0.47635 | 0.97559 | -0.47045 | 5.096
1 | 0.060782 | 0.015265 | -0.06077 | -0.015258 | 1.2509e-05 | 6.7965e-06 | 0.092748 | 0.092748 | 0.092748 | 0.97529 | -0.47635 | 0.97507 | -0.48066 | 5.0961
2 | -0.066436 | -0.016687 | 0.066461 | 0.016701 | 2.531e-05 | 1.4146e-05 | 0.10134 | 0.10134 | 0.10134 | 0.97559 | -0.47045 | 0.97599 | -0.46247 | 5.5683
3 | 0.057988 | 0.014561 | -0.057955 | -0.014544 | 3.211e-05 | 1.7143e-05 | 0.088503 | 0.088504 | 0.088504 | 0.97507 | -0.48066 | 0.97448 | -0.49227 | 4.8628
4 | -0.0018171 | -0.00045541 | 0.0018172 | 0.00045505 | 9.5465e-08 | -3.5641e-07 | 0.0027655 | 0.0027653 | 0.0027655 | 0.97772 | -0.42885 | 0.97778 | -0.42775 | 0.75975
5 | 0.0055005 | 0.0013776 | -0.0054993 | -0.0013774 | 1.1646e-06 | 1.8955e-07 | 0.0083705 | 0.0083707 | 0.0083707 | 0.97778 | -0.42775 | 0.97755 | -0.43219 | 2.2996
6 | -0.0073177 | -0.0018327 | 0.007318 | 0.0018328 | 3.1119e-07 | 1.1522e-07 | 0.011136 | 0.011136 | 0.011136 | 0.97778 | -0.42775 | 0.97782 | -0.42685 | 3.0593
7 | 0.0054993 | 0.0013774 | -0.0054987 | -0.0013773 | 6.4966e-07 | 1.0586e-07 | 0.0083707 | 0.0083708 | 0.0083708 | 0.97755 | -0.43219 | 0.97743 | -0.43467 | 2.2997
8 | -0.0091192 | -0.0022842 | 0.0091202 | 0.0022847 | 1.0259e-06 | 4.7834e-07 | 0.013877 | 0.013877 | 0.013877 | 0.97782 | -0.42685 | 0.97794 | -0.42449 | 3.8123
9 | 0.0030599 | 0.00076609 | -0.0030597 | -0.00076628 | 2.136e-07 | -1.923e-07 | 0.004658 | 0.0046582 | 0.0046582 | 0.97743 | -0.43467 | 0.97735 | -0.43614 | 1.2797
10 | -0.011628 | -0.0029132 | 0.01163 | 0.0029142 | 1.8974e-06 | 1.0115e-06 | 0.017693 | 0.017693 | 0.017693 | 0.97794 | -0.42449 | 0.97812 | -0.42106 | 4.8607
11 | -0.0016712 | -0.00041885 | 0.0016713 | 0.0004186 | 5.5881e-08 | -2.5494e-07 | 0.0025395 | 0.0025394 | 0.0025395 | 0.97925 | -0.3987 | 0.97929 | -0.398 | 0.69767
12 | -0.0027238 | -0.00068239 | 0.002724 | 0.00068217 | 1.6621e-07 | -2.192e-07 | 0.0041388 | 0.0041386 | 0.0041388 | 0.97929 | -0.398 | 0.97935 | -0.39672 | 1.137
13 | 0.00092373 | 0.00023096 | -0.0009237 | -0.0002315 | 3.3141e-08 | -5.3878e-07 | 0.0014062 | 0.0014064 | 0.0014064 | 0.97735 | -0.43614 | 0.97731 | -0.43689 | 0.38637
14 | -0.015129 | -0.0037912 | 0.015132 | 0.0037929 | 2.9711e-06 | 1.7138e-06 | 0.023016 | 0.023016 | 0.023016 | 0.97812 | -0.42106 | 0.97833 | -0.41694 | 6.3231
15 | 0.0025527 | 0.00063964 | -0.0025526 | -0.00063974 | 6.4571e-08 | -1.0489e-07 | 0.0038639 | 0.003864 | 0.003864 | 0.98304 | -0.32528 | 0.98301 | -0.32581 | 1.0615
16 | -0.0039672 | -0.00099415 | 0.0039673 | 0.00099413 | 8.9671e-08 | -2.6681e-08 | 0.0060051 | 0.0060051 | 0.0060051 | 0.98304 | -0.32528 | 0.98306 | -0.32481 | 1.6497
17 | -0.0039673 | -0.00099413 | 0.0039674 | 0.00099411 | 5.9516e-08 | -1.7712e-08 | 0.0060051 | 0.006005 | 0.0060051 | 0.98306 | -0.32481 | 0.98308 | -0.32449 | 1.6497
18 | -0.004939 | -0.0012376 | 0.0049395 | 0.0012376 | 5.2693e-07 | 1.8406e-08 | 0.0074757 | 0.0074756 | 0.0074757 | 0.98308 | -0.32449 | 0.98319 | -0.32225 | 2.0538
19 | -0.006029 | -0.0015107 | 0.0060301 | 0.0015109 | 1.0965e-06 | 2.5626e-07 | 0.0091245 | 0.0091243 | 0.0091245 | 0.98319 | -0.32225 | 0.98339 | -0.31843 | 2.5067
20 | -0.0060301 | -0.0015109 | 0.0060302 | 0.001511 | 1.4437e-07 | 3.3727e-08 | 0.0091243 | 0.0091243 | 0.0091243 | 0.98339 | -0.31843 | 0.98341 | -0.31793 | 2.5067
21 | -0.0081085 | -0.0020318 | 0.0081101 | 0.0020325 | 1.6563e-06 | 6.8765e-07 | 0.012269 | 0.012269 | 0.012269 | 0.98341 | -0.31793 | 0.98363 | -0.31364 | 3.3706
22 | -0.022995 | -0.0057649 | 0.023001 | 0.0057683 | 5.5512e-06 | 3.3975e-06 | 0.034787 | 0.034787 | 0.034787 | 0.98363 | -0.31364 | 0.98389 | -0.30858 | 9.5569
23 | 0.014885 | 0.0037324 | -0.014882 | -0.0037309 | 2.6624e-06 | 1.5262e-06 | 0.022518 | 0.022518 | 0.022518 | 0.98363 | -0.31364 | 0.98344 | -0.3174 | 6.1863
24 | 0.013687 | 0.0034312 | -0.013681 | -0.0034283 | 5.1524e-06 | 2.8912e-06 | 0.020709 | 0.020709 | 0.020709 | 0.98344 | -0.3174 | 0.98303 | -0.3253 | 5.6893
25 | 0.010358 | 0.0025955 | -0.010358 | -0.0025955 | 2.0412e-08 | 1.0256e-08 | 0.015679 | 0.015679 | 0.015679 | 0.98303 | -0.3253 | 0.98303 | -0.32534 | 4.3075
26 | 0.0021665 | 0.00054241 | -0.0021663 | -0.00054292 | 2.0471e-07 | -5.1246e-07 | 0.0032792 | 0.0032795 | 0.0032795 | 0.98303 | -0.32534 | 0.98293 | -0.32733 | 0.90095
27 | -0.025956 | -0.0065089 | 0.025963 | 0.0065132 | 6.9921e-06 | 4.3212e-06 | 0.039256 | 0.039256 | 0.039256 | 0.98389 | -0.30858 | 0.98418 | -0.30293 | 10.7846
28 | -0.029065 | -0.0072907 | 0.029109 | 0.007318 | 4.3788e-05 | 2.7255e-05 | 0.043946 | 0.043946 | 0.043946 | 0.98418 | -0.30293 | 0.9858 | -0.27138 | 12.0732
29 | -0.032109 | -0.00807 | 0.03213 | 0.0080832 | 2.1054e-05 | 1.317e-05 | 0.048475 | 0.048475 | 0.048475 | 0.9858 | -0.27138 | 0.9865 | -0.25765 | 13.3174
30 | -0.0043144 | -0.0010813 | 0.004315 | 0.0010812 | 6.3315e-07 | -1.1818e-07 | 0.0064628 | 0.0064626 | 0.0064628 | 0.99336 | -0.12622 | 0.99351 | -0.12314 | 1.7755
31 | 0.008464 | 0.0021216 | -0.0084619 | -0.0021207 | 2.1181e-06 | 9.0058e-07 | 0.012677 | 0.012677 | 0.012677 | 0.99351 | -0.12314 | 0.99324 | -0.12839 | 3.4827
32 | -0.012779 | -0.0032028 | 0.01278 | 0.0032034 | 1.1264e-06 | 6.147e-07 | 0.01914 | 0.01914 | 0.01914 | 0.99351 | -0.12314 | 0.99361 | -0.12129 | 5.2581
33 | -0.002179 | -0.00054569 | 0.0021791 | 0.00054545 | 1.031e-07 | -2.4835e-07 | 0.0033141 | 0.003314 | 0.0033141 | 0.9783 | -0.41726 | 0.97835 | -0.41627 | 0.91047
34 | 0.002179 | 0.00054569 | -0.0021789 | -0.00054595 | 1.0559e-07 | -2.543e-07 | 0.0033141 | 0.0033142 | 0.0033142 | 0.9783 | -0.41726 | 0.97825 | -0.41828 | 0.9105
35 | -0.0027789 | -0.00069578 | 0.002779 | 0.0006956 | 1.4585e-07 | -1.8011e-07 | 0.0042263 | 0.0042262 | 0.0042263 | 0.97835 | -0.41627 | 0.9784 | -0.41517 | 1.1611
36 | 0.0015536 | 0.00038924 | -0.0015536 | -0.00038936 | 2.2194e-08 | -1.1885e-07 | 0.0023631 | 0.0023632 | 0.0023632 | 0.97825 | -0.41828 | 0.97823 | -0.41858 | 0.64923
37 | 0.0085349 | 0.0021389 | -0.008534 | -0.0021385 | 9.3708e-07 | 4.1277e-07 | 0.012968 | 0.012968 | 0.012968 | 0.97935 | -0.39672 | 0.97924 | -0.39903 | 3.5626
38 | 0.0065308 | 0.0016365 | -0.0065295 | -0.0016361 | 1.2836e-06 | 3.8416e-07 | 0.0099227 | 0.0099229 | 0.0099229 | 0.97935 | -0.39672 | 0.97914 | -0.40085 | 2.7261
39 | -0.01779 | -0.0044576 | 0.0178 | 0.0044636 | 1.0072e-05 | 5.983e-06 | 0.027029 | 0.027029 | 0.027029 | 0.97935 | -0.39672 | 0.97996 | -0.38484 | 7.4256
40 | 0.073692 | 0.01853 | -0.073667 | -0.018515 | 2.4708e-05 | 1.4178e-05 | 0.11228 | 0.11229 | 0.11229 | 0.97677 | -0.44727 | 0.97641 | -0.45429 | 6.1695
41 | -0.076925 | -0.01934 | 0.076936 | 0.019346 | 1.0987e-05 | 6.364e-06 | 0.11721 | 0.11721 | 0.11721 | 0.97677 | -0.44727 | 0.97692 | -0.44428 | 6.4401
42 | 0.071635 | 0.018006 | -0.071607 | -0.01799 | 2.7942e-05 | 1.593e-05 | 0.10919 | 0.10919 | 0.10919 | 0.97641 | -0.45429 | 0.97599 | -0.46247 | 5.9994
43 | -0.078108 | -0.01964 | 0.078149 | 0.019664 | 4.1121e-05 | 2.3892e-05 | 0.119 | 0.11899 | 0.119 | 0.97692 | -0.44428 | 0.97748 | -0.43326 | 6.5382
44 | 0.0051461 | 0.0012893 | -0.0051455 | -0.0012892 | 5.9325e-07 | 5.8546e-08 | 0.0078457 | 0.0078458 | 0.0078458 | 0.97599 | -0.46247 | 0.97587 | -0.46489 | 2.1554
45 | -0.086963 | -0.021873 | 0.086968 | 0.021876 | 5.216e-06 | 3.0896e-06 | 0.13241 | 0.13241 | 0.13241 | 0.97748 | -0.43326 | 0.97754 | -0.43201 | 7.2753
46 | 0.0021575 | 0.00054037 | -0.0021575 | -0.00054042 | 1.8889e-08 | -4.6061e-08 | 0.0032897 | 0.0032897 | 0.0032897 | 0.97587 | -0.46489 | 0.97586 | -0.46507 | 0.90377
47 | -0.08916 | -0.022425 | 0.089225 | 0.022464 | 6.5569e-05 | 3.8988e-05 | 0.13575 | 0.13575 | 0.13575 | 0.97754 | -0.43201 | 0.97833 | -0.41662 | 7.4586
48 | 0.0013521 | 0.00033857 | -0.0013521 | -0.0003386 | 4.4599e-09 | -3.2104e-08 | 0.0020616 | 0.0020616 | 0.0020616 | 0.97586 | -0.46507 | 0.97586 | -0.46514 | 0.56639
49 | 0.0026152 | 0.00065515 | -0.0026151 | -0.00065532 | 1.1781e-07 | -1.7394e-07 | 0.0039775 | 0.0039776 | 0.0039776 | 0.97833 | -0.41662 | 0.97828 | -0.41757 | 1.0927
50 | -0.09406 | -0.023675 | 0.094078 | 0.023686 | 1.7938e-05 | 1.0747e-05 | 0.1431 | 0.1431 | 0.1431 | 0.97833 | -0.41662 | 0.97853 | -0.41264 | 7.8626
51 | 0.1927 | 0.048848 | -0.19263 | -0.048801 | 7.4203e-05 | 4.6745e-05 | 0.29098 | 0.29098 | 0.29098 | 0.98611 | -0.26527 | 0.98569 | -0.27329 | 15.9881
52 | -0.19629 | -0.049746 | 0.19633 | 0.049773 | 4.2545e-05 | 2.6817e-05 | 0.29639 | 0.29639 | 0.29639 | 0.98611 | -0.26527 | 0.98634 | -0.26076 | 16.2851
53 | 0.19125 | 0.048456 | -0.19118 | -0.048413 | 6.8085e-05 | 4.2881e-05 | 0.2889 | 0.2889 | 0.2889 | 0.98569 | -0.27329 | 0.98531 | -0.2807 | 15.8737
54 | -0.19853 | -0.050325 | 0.19856 | 0.05034 | 2.3275e-05 | 1.4676e-05 | 0.29971 | 0.29971 | 0.29971 | 0.98634 | -0.26076 | 0.98647 | -0.25832 | 16.4677
55 | 0.19118 | 0.048413 | -0.19117 | -0.048404 | 1.4139e-05 | 8.9053e-06 | 0.2889 | 0.2889 | 0.2889 | 0.98531 | -0.2807 | 0.98523 | -0.28224 | 15.8737
56 | -0.20059 | -0.050849 | 0.20066 | 0.050895 | 7.2961e-05 | 4.6017e-05 | 0.30277 | 0.30277 | 0.30277 | 0.98647 | -0.25832 | 0.98686 | -0.25075 | 16.636
57 | 0.1893 | 0.047936 | -0.18919 | -0.047868 | 0.00010913 | 6.871e-05 | 0.28608 | 0.28608 | 0.28608 | 0.98523 | -0.28224 | 0.98461 | -0.29425 | 15.7189
58 | -0.23484 | -0.059496 | 0.23527 | 0.05977 | 0.00043243 | 0.00027382 | 0.35432 | 0.35432 | 0.35432 | 0.98686 | -0.25075 | 0.98884 | -0.2125 | 19.4684
59 | 0.03418 | 0.0086012 | -0.034169 | -0.0085941 | 1.1261e-05 | 7.0626e-06 | 0.05155 | 0.05155 | 0.05155 | 0.98686 | -0.25075 | 0.9865 | -0.25765 | 14.1622
60 | 0.18759 | 0.047466 | -0.18743 | -0.047367 | 0.00015809 | 9.9516e-05 | 0.28366 | 0.28366 | 0.28366 | 0.98461 | -0.29425 | 0.9837 | -0.31183 | 15.5858
61 | -0.23901 | -0.060706 | 0.23915 | 0.0608 | 0.00014925 | 9.4533e-05 | 0.35994 | 0.35994 | 0.35994 | 0.98884 | -0.2125 | 0.98952 | -0.19953 | 19.7771
62 | -0.02111 | -0.0052931 | 0.021124 | 0.0053019 | 1.4398e-05 | 8.7435e-06 | 0.032055 | 0.032055 | 0.032055 | 0.97996 | -0.38484 | 0.98069 | -0.37054 | 8.8064
63 | 0.11229 | 0.028325 | -0.11226 | -0.028307 | 2.9886e-05 | 1.8262e-05 | 0.17045 | 0.17045 | 0.17045 | 0.98069 | -0.37054 | 0.9804 | -0.3761 | 9.3655
64 | -0.13342 | -0.033627 | 0.13355 | 0.033706 | 0.00012815 | 7.9385e-05 | 0.20251 | 0.20251 | 0.20251 | 0.98069 | -0.37054 | 0.98172 | -0.35048 | 11.1267
65 | 0.0070945 | 0.0017777 | -0.0070944 | -0.0017777 | 7.1001e-08 | 2.4946e-08 | 0.01078 | 0.01078 | 0.01078 | 0.97924 | -0.39903 | 0.97922 | -0.39924 | 2.9617
66 | 0.0051512 | 0.0012907 | -0.0051509 | -0.0012907 | 2.7577e-07 | 2.5566e-08 | 0.0078282 | 0.0078283 | 0.0078283 | 0.97914 | -0.40085 | 0.97909 | -0.40197 | 2.1506
67 | 0.10746 | 0.027101 | -0.10744 | -0.027095 | 1.0528e-05 | 6.4055e-06 | 0.16315 | 0.16315 | 0.16315 | 0.9804 | -0.3761 | 0.9803 | -0.37815 | 8.9644
68 | -0.1363 | -0.034395 | 0.1363 | 0.0344 | 7.5001e-06 | 4.6521e-06 | 0.20667 | 0.20667 | 0.20667 | 0.98172 | -0.35048 | 0.98178 | -0.34934 | 11.3557
69 | 0.0030462 | 0.00076308 | -0.0030459 | -0.00076336 | 3.0226e-07 | -2.7973e-07 | 0.0046288 | 0.0046289 | 0.0046289 | 0.97922 | -0.39924 | 0.97912 | -0.40132 | 1.2717
70 | 0.0037984 | 0.00095171 | -0.0037984 | -0.00095172 | 2.6126e-08 | -9.5712e-09 | 0.0057728 | 0.0057728 | 0.0057728 | 0.97909 | -0.40197 | 0.97908 | -0.40212 | 1.5859
71 | 0.10468 | 0.026403 | -0.10463 | -0.026372 | 5.1524e-05 | 3.1262e-05 | 0.15896 | 0.15896 | 0.15896 | 0.9803 | -0.37815 | 0.97977 | -0.38843 | 8.7343
72 | -0.13861 | -0.034977 | 0.1387 | 0.035032 | 8.8706e-05 | 5.5078e-05 | 0.21016 | 0.21016 | 0.21016 | 0.98178 | -0.34934 | 0.98246 | -0.33598 | 11.5474
73 | 0.0025704 | 0.00064394 | -0.0025702 | -0.00064411 | 1.0953e-07 | -1.7059e-07 | 0.0039064 | 0.0039065 | 0.0039065 | 0.97908 | -0.40212 | 0.97903 | -0.40301 | 1.0732
74 | 0.10207 | 0.025729 | -0.10206 | -0.025722 | 1.2207e-05 | 7.3863e-06 | 0.15507 | 0.15507 | 0.15507 | 0.97977 | -0.38843 | 0.97964 | -0.39093 | 8.5203
75 | -0.13973 | -0.035291 | 0.13981 | 0.035344 | 8.4871e-05 | 5.2718e-05 | 0.21173 | 0.21173 | 0.21173 | 0.98246 | -0.33598 | 0.98311 | -0.32331 | 11.6335
76 | 0.18457 | 0.046651 | -0.18453 | -0.04662 | 4.8047e-05 | 3.0229e-05 | 0.27934 | 0.27934 | 0.27934 | 0.9837 | -0.31183 | 0.98342 | -0.31726 | 15.3484
77 | 0.0064445 | 0.0016152 | -0.0064425 | -0.0016147 | 1.9596e-06 | 5.571e-07 | 0.0097512 | 0.0097514 | 0.0097514 | 0.98342 | -0.31726 | 0.9831 | -0.32364 | 2.679
78 | 0.17808 | 0.045005 | -0.17803 | -0.044973 | 5.1685e-05 | 3.2477e-05 | 0.26959 | 0.26959 | 0.26959 | 0.98342 | -0.31726 | 0.98311 | -0.32331 | 14.8126
79 | 0.0064425 | 0.0016147 | -0.0064418 | -0.0016145 | 6.9678e-07 | 1.9821e-07 | 0.0097514 | 0.0097515 | 0.0097515 | 0.9831 | -0.32364 | 0.98298 | -0.32591 | 2.679
80 | 0.038216 | 0.0096286 | -0.038199 | -0.009618 | 1.6817e-05 | 1.0593e-05 | 0.057861 | 0.057861 | 0.057861 | 0.98311 | -0.32331 | 0.98264 | -0.33252 | 15.8959
81 | 0.036629 | 0.0092245 | -0.03661 | -0.0092123 | 1.9444e-05 | 1.2231e-05 | 0.055484 | 0.055484 | 0.055484 | 0.98264 | -0.33252 | 0.98207 | -0.34363 | 15.2428
82 | 0.035702 | 0.0089848 | -0.035693 | -0.0089794 | 8.6391e-06 | 5.4295e-06 | 0.054108 | 0.054108 | 0.054108 | 0.98207 | -0.34363 | 0.98181 | -0.34869 | 14.8649
83 | 0.028368 | 0.0071236 | -0.028358 | -0.0071169 | 1.0829e-05 | 6.7345e-06 | 0.043076 | 0.043076 | 0.043076 | 0.98006 | -0.38285 | 0.97966 | -0.39086 | 11.8342
84 | -0.029532 | -0.0074152 | 0.029537 | 0.0074181 | 4.6248e-06 | 2.8826e-06 | 0.044843 | 0.044843 | 0.044843 | 0.98006 | -0.38285 | 0.98023 | -0.37957 | 12.3194
85 | 0.024965 | 0.0062665 | -0.024959 | -0.006263 | 5.7439e-06 | 3.542e-06 | 0.037923 | 0.037923 | 0.037923 | 0.97966 | -0.39086 | 0.97941 | -0.39568 | 10.4184
86 | -0.031345 | -0.0078714 | 0.031361 | 0.0078813 | 1.5839e-05 | 9.9014e-06 | 0.047588 | 0.047588 | 0.047588 | 0.98023 | -0.37957 | 0.98077 | -0.36899 | 13.0737
87 | 0.024288 | 0.0060949 | -0.024285 | -0.0060928 | 3.4069e-06 | 2.0965e-06 | 0.036904 | 0.036904 | 0.036904 | 0.97941 | -0.39568 | 0.97926 | -0.39862 | 10.1384
88 | -0.033694 | -0.0084659 | 0.03372 | 0.0084825 | 2.6507e-05 | 1.6623e-05 | 0.051127 | 0.051127 | 0.051127 | 0.98077 | -0.36899 | 0.98162 | -0.35252 | 14.0459
89 | 0.021168 | 0.0053116 | -0.021163 | -0.0053087 | 4.8135e-06 | 2.9246e-06 | 0.032168 | 0.032168 | 0.032168 | 0.97926 | -0.39862 | 0.97902 | -0.40339 | 8.8373
90 | -0.03372 | -0.0084825 | 0.033726 | 0.0084864 | 6.1664e-06 | 3.867e-06 | 0.051127 | 0.051127 | 0.051127 | 0.98162 | -0.35252 | 0.98181 | -0.34869 | 14.0459
91 | 0.021163 | 0.0053087 | -0.021161 | -0.0053075 | 2.0548e-06 | 1.2485e-06 | 0.032168 | 0.032168 | 0.032168 | 0.97902 | -0.40339 | 0.97891 | -0.40543 | 8.8373
92 | 0.30046 | 0.077199 | -0.29999 | -0.076895 | 0.00047858 | 0.00030421 | 0.44777 | 0.44777 | 0.44777 | 1 | 0 | 0.99826 | -0.032851 | 24.6027
93 | 0.002399 | 0.00060088 | -0.0023989 | -0.00060121 | 1.5874e-07 | -3.3417e-07 | 0.0035697 | 0.0035698 | 0.0035698 | 1 | 0 | 0.99993 | -0.0013893 | 0.98072
94 | 0.29614 | 0.075932 | -0.29551 | -0.075529 | 0.00063345 | 0.00040259 | 0.44204 | 0.44204 | 0.44204 | 0.99826 | -0.032851 | 0.99593 | -0.077065 | 24.288
95 | 0.29551 | 0.075529 | -0.29548 | -0.07551 | 3.1293e-05 | 1.9889e-05 | 0.44204 | 0.44204 | 0.44204 | 0.99593 | -0.077065 | 0.99581 | -0.079255 | 24.288
96 | 0.2931 | 0.074914 | -0.29258 | -0.074581 | 0.00052404 | 0.00033303 | 0.43849 | 0.43849 | 0.43849 | 0.99581 | -0.079255 | 0.99387 | -0.11629 | 24.0929
97 | 0.10051 | 0.025317 | -0.10045 | -0.025282 | 5.6828e-05 | 3.433e-05 | 0.15279 | 0.15279 | 0.15279 | 0.97914 | -0.40081 | 0.97853 | -0.41264 | 8.395
98 | -0.10051 | -0.025317 | 0.10055 | 0.025345 | 4.7473e-05 | 2.8677e-05 | 0.15279 | 0.15279 | 0.15279 | 0.97914 | -0.40081 | 0.97964 | -0.39093 | 8.395
99 | 0.0063728 | 0.0015961 | -0.0063724 | -0.001596 | 3.8409e-07 | 1.0881e-07 | 0.0096904 | 0.0096905 | 0.0096905 | 0.97853 | -0.41264 | 0.97847 | -0.4139 | 2.6622
100 | 0.27747 | 0.070794 | -0.27729 | -0.070675 | 0.0001875 | 0.00011907 | 0.41588 | 0.41588 | 0.41588 | 0.99387 | -0.11629 | 0.99314 | -0.13029 | 22.8504
101 | 0.015104 | 0.0037869 | -0.0151 | -0.0037849 | 3.5967e-06 | 2.0589e-06 | 0.022614 | 0.022614 | 0.022614 | 0.99387 | -0.11629 | 0.99361 | -0.12129 | 6.2126
102 | 0.0031342 | 0.00078441 | -0.003134 | -0.00078456 | 1.8858e-07 | -1.5736e-07 | 0.004766 | 0.0047661 | 0.0047661 | 0.97847 | -0.4139 | 0.9784 | -0.41517 | 1.3094
103 | 0.0032534 | 0.00081531 | -0.0032533 | -0.00081535 | 5.7819e-08 | -4.5744e-08 | 0.0048923 | 0.0048923 | 0.0048923 | 0.98952 | -0.19953 | 0.9895 | -0.19991 | 1.344
104 | -0.24241 | -0.061616 | 0.24272 | 0.061814 | 0.0003131 | 0.00019836 | 0.36484 | 0.36484 | 0.36484 | 0.98952 | -0.19953 | 0.99091 | -0.17275 | 20.0459
105 | 0.25678 | 0.065537 | -0.25669 | -0.065478 | 9.2349e-05 | 5.8566e-05 | 0.38516 | 0.38516 | 0.38516 | 0.99314 | -0.13029 | 0.99275 | -0.13774 | 21.1628
106 | 0.25194 | 0.064286 | -0.25151 | -0.064017 | 0.00042533 | 0.00026965 | 0.37803 | 0.37803 | 0.37803 | 0.99275 | -0.13774 | 0.99091 | -0.17275 | 20.7711
107 | -0.016686 | -0.0041839 | 0.016688 | 0.0041847 | 1.947e-06 | 8.4975e-07 | 0.025516 | 0.025516 | 0.025516 | 0.97311 | -0.5192 | 0.97324 | -0.51675 | 3.5049
108 | 0.010514 | 0.0026369 | -0.010512 | -0.0026362 | 1.3442e-06 | 6.8802e-07 | 0.016077 | 0.016077 | 0.016077 | 0.97311 | -0.5192 | 0.97298 | -0.52188 | 4.4169
109 | -0.025348 | -0.0063551 | 0.02535 | 0.0063553 | 1.8762e-06 | 1.659e-07 | 0.038757 | 0.038756 | 0.038757 | 0.97324 | -0.51675 | 0.97332 | -0.51519 | 2.1295
110 | 0.010512 | 0.0026362 | -0.010505 | -0.0026326 | 7.0491e-06 | 3.6089e-06 | 0.016077 | 0.016078 | 0.016078 | 0.97298 | -0.52188 | 0.97227 | -0.53596 | 4.417
111 | 0.01181 | 0.0029601 | -0.011808 | -0.0029594 | 1.203e-06 | 6.4763e-07 | 0.018055 | 0.018055 | 0.018055 | 0.97332 | -0.51519 | 0.97321 | -0.51733 | 4.9601
112 | -0.03716 | -0.0093154 | 0.037172 | 0.0093202 | 1.2463e-05 | 4.7754e-06 | 0.056811 | 0.05681 | 0.056811 | 0.97332 | -0.51519 | 0.97367 | -0.50816 | 3.1215
113 | 0.0040929 | 0.0010255 | -0.0040923 | -0.0010256 | 6.0025e-07 | -1.2167e-07 | 0.0062639 | 0.0062641 | 0.0062641 | 0.97227 | -0.53596 | 0.97211 | -0.53904 | 1.7209
114 | 0.0054052 | 0.0013546 | -0.0054049 | -0.0013546 | 3.712e-07 | 5.7501e-08 | 0.0082645 | 0.0082645 | 0.0082645 | 0.97321 | -0.51733 | 0.97314 | -0.51877 | 2.2705
115 | 0.018302 | 0.00459 | -0.018295 | -0.0045857 | 7.3477e-06 | 4.3912e-06 | 0.027971 | 0.027971 | 0.027971 | 0.97367 | -0.50816 | 0.97325 | -0.51658 | 7.6844
116 | -0.055474 | -0.01391 | 0.05551 | 0.013929 | 3.6179e-05 | 1.8978e-05 | 0.084781 | 0.084779 | 0.084781 | 0.97367 | -0.50816 | 0.97437 | -0.49448 | 4.6583
117 | 0.010811 | 0.00271 | -0.010808 | -0.0027088 | 2.4108e-06 | 1.2506e-06 | 0.016529 | 0.016529 | 0.016529 | 0.97325 | -0.51658 | 0.97301 | -0.52127 | 4.541
118 | -0.05551 | -0.013929 | 0.055516 | 0.013932 | 5.844e-06 | 3.0649e-06 | 0.084779 | 0.084779 | 0.084779 | 0.97437 | -0.49448 | 0.97448 | -0.49227 | 4.6582
119 | 0.0054037 | 0.0013543 | -0.0054033 | -0.0013542 | 3.5815e-07 | 5.5522e-08 | 0.0082638 | 0.0082638 | 0.0082638 | 0.97301 | -0.52127 | 0.97294 | -0.52266 | 2.2703
120 | 0.020093 | 0.0050398 | -0.020086 | -0.0050353 | 7.3968e-06 | 4.4683e-06 | 0.030544 | 0.030544 | 0.030544 | 0.97891 | -0.40543 | 0.97852 | -0.41316 | 8.3913
121 | 0.01583 | 0.0039686 | -0.015827 | -0.003967 | 2.8548e-06 | 1.6621e-06 | 0.024072 | 0.024072 | 0.024072 | 0.97852 | -0.41316 | 0.97833 | -0.41694 | 6.6133
122 | 0.00089602 | 0.00022429 | -0.000896 | -0.00022456 | 1.56e-08 | -2.6845e-07 | 0.0013662 | 0.0013663 | 0.0013663 | 0.97586 | -0.46514 | 0.97584 | -0.46551 | 0.37535
123 | 0.00064795 | 0.00016232 | -0.00064794 | -0.00016239 | 2.1375e-09 | -7.2314e-08 | 0.00098553 | 0.00098556 | 0.00098556 | 0.97828 | -0.41757 | 0.97828 | -0.41764 | 0.27076
124 | 0.0013403 | 0.00033585 | -0.0013403 | -0.0003359 | 6.8932e-09 | -5.1293e-08 | 0.002037 | 0.0020371 | 0.0020371 | 0.97903 | -0.40301 | 0.97903 | -0.40312 | 0.55963

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30926 | 0.078991

## res_load
| p_mw | q_mvar
0 | 0.0056363 | 0.0014126
1 | 0.0027821 | 0.00069726
2 | 0.0018171 | 0.00045541
3 | 0.0018012 | 0.00045142
4 | 0.0024388 | 0.00061122
5 | 0.002508 | 0.00062856
6 | 0.0016712 | 0.00041885
7 | 0.0010525 | 0.00026379
8 | 0.0021359 | 0.00053532
9 | 0.0034992 | 0.00087697
10 | 0.0014145 | 0.00035451
11 | 0.0025526 | 0.00063974
12 | 0.00097162 | 0.00024351
13 | 0.0010895 | 0.00027305
14 | 0.0020782 | 0.00052086
15 | 0.0011957 | 0.00029967
16 | 0.0033229 | 0.00083281
17 | 0.0081919 | 0.0020531
18 | 0.002955 | 0.00074058
19 | 0.0021663 | 0.00054292
20 | 0.0031023 | 0.00077752
21 | 0.0030005 | 0.00075199
22 | 0.0043144 | 0.0010813
23 | 0.0009237 | 0.0002315
24 | 0.00059983 | 0.00015033
25 | 0.00062525 | 0.0001567
26 | 0.0032332 | 0.00081031
27 | 0.0020322 | 0.00050931
28 | 0.0011721 | 0.00029376
29 | 0.0088135 | 0.0022089
30 | 0.002988 | 0.00074886
31 | 0.0021919 | 0.00054934
32 | 0.00080539 | 0.00020185
33 | 0.0022191 | 0.00055616
34 | 0.0035823 | 0.00089782
35 | 0.0013794 | 0.00034571
36 | 0.0022039 | 0.00055236
37 | 0.00203 | 0.00050877
38 | 0.0018657 | 0.00046759
39 | 0.0016023 | 0.00040156
40 | 0.0037348 | 0.00093603
41 | 0.0020387 | 0.00051094
42 | 0.0033101 | 0.00082959
43 | 0.0014394 | 0.00036076
44 | 0.0013783 | 0.00034544
45 | 0.0048094 | 0.0012053
46 | 0.0027497 | 0.00068914
47 | 0.0040483 | 0.0010146
48 | 0.0013525 | 0.00033896
49 | 0.0027599 | 0.0006917
50 | 0.0023022 | 0.00057699
51 | 0.0030459 | 0.00076336
52 | 0.0012281 | 0.00030778
53 | 0.0025645 | 0.00064273
54 | 0.0010345 | 0.00025927
55 | 0.0028572 | 0.00071608
56 | 0.0064418 | 0.0016145
57 | 0.0015701 | 0.0003935
58 | 0.00090778 | 0.00022751
59 | 0.0011634 | 0.00029158
60 | 0.003393 | 0.00085036
61 | 0.0018086 | 0.00045328
62 | 0.00067081 | 0.00016812
63 | 0.0023326 | 0.0005846
64 | 0.0031167 | 0.00078113
65 | 0.0019671 | 0.000493
66 | 0.0047503 | 0.0011905
67 | 0.0038434 | 0.00096325
68 | 0.0023989 | 0.00060121
69 | 0.0023764 | 0.00059559
70 | 0.001502 | 0.00037644
71 | 0.0032382 | 0.00081157
72 | 0.0023199 | 0.00058142
73 | 0.0205 | 0.0051379
74 | 0.0084619 | 0.0021207
75 | 0.0047561 | 0.001192
76 | 0.0087898 | 0.0022029
77 | 0.0032533 | 0.00081535
78 | 0.0061725 | 0.001547
79 | 0.0086601 | 0.0021704
80 | 0.0064124 | 0.0016071
81 | 0.0064033 | 0.0016048
82 | 0.0040923 | 0.0010256
83 | 0.0074838 | 0.0018756
84 | 0.0054049 | 0.0013546
85 | 0.0054047 | 0.0013545
86 | 0.0024392 | 0.00061133
87 | 0.0010681 | 0.00026769
88 | 0.0042561 | 0.0010667
89 | 0.0004561 | 0.00011431
90 | 0.0015536 | 0.00038936
91 | 0.00035499 | 8.8968e-05
92 | 0.0006945 | 0.00017406
93 | 0.0054033 | 0.0013542
94 | 0.000896 | 0.00022456
95 | 0.0019671 | 0.000493
96 | 0.00064794 | 0.00016239
97 | 0.00123 | 0.00030826
98 | 0.0013403 | 0.0003359

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1