## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2134-2_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2134-2_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2134-2_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2134-2_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2134-2_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2134-2_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2134-2_0_6_node_159 | 0.4 | n |  | TRUE
7 | bus_LV_2134-2_0_6_node_101 | 0.4 | n |  | TRUE
8 | bus_LV_2134-2_0_6_node_113 | 0.4 | n |  | TRUE
9 | bus_LV_2134-2_0_6_node_203 | 0.4 | n |  | TRUE
10 | bus_LV_2134-2_0_6_node_215 | 0.4 | n |  | TRUE
11 | bus_LV_2134-2_0_6_node_189 | 0.4 | n |  | TRUE
12 | bus_LV_2134-2_0_6_node_99 | 0.4 | n |  | TRUE
13 | bus_LV_2134-2_0_6_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_2134-2_0_6_node_54 | 0.4 | n |  | TRUE
15 | bus_LV_2134-2_0_6_node_188 | 0.4 | n |  | TRUE
16 | bus_LV_2134-2_0_6_node_214 | 0.4 | n |  | TRUE
17 | bus_LV_2134-2_0_6_node_6 | 0.4 | n |  | TRUE
18 | bus_LV_2134-2_0_6_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_2134-2_0_6_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_2134-2_0_6_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_2134-2_0_6_node_124 | 0.4 | n |  | TRUE
22 | bus_LV_2134-2_0_6_node_78 | 0.4 | n |  | TRUE
23 | bus_LV_2134-2_0_6_node_84 | 0.4 | n |  | TRUE
24 | bus_LV_2134-2_0_6_node_80 | 0.4 | n |  | TRUE
25 | bus_LV_2134-2_0_6_node_77 | 0.4 | n |  | TRUE
26 | bus_LV_2134-2_0_6_node_10 | 0.4 | n |  | TRUE
27 | bus_LV_2134-2_0_6_node_11 | 0.4 | n |  | TRUE
28 | bus_LV_2134-2_0_6_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_2134-2_0_6_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_2134-2_0_6_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_2134-2_0_6_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_2134-2_0_6_node_107 | 0.4 | n |  | TRUE
33 | bus_LV_2134-2_0_6_node_109 | 0.4 | n |  | TRUE
34 | bus_LV_2134-2_0_6_node_83 | 0.4 | n |  | TRUE
35 | bus_LV_2134-2_0_6_node_274 | 0.4 | n |  | TRUE
36 | bus_LV_2134-2_0_6_node_111 | 0.4 | n |  | TRUE
37 | bus_LV_2134-2_0_6_node_108 | 0.4 | n |  | TRUE
38 | bus_LV_2134-2_0_6_node_82 | 0.4 | n |  | TRUE
39 | bus_LV_2134-2_0_6_node_269 | 0.4 | n |  | TRUE
40 | bus_LV_2134-2_0_6_node_16 | 0.4 | n |  | TRUE
41 | bus_LV_2134-2_0_6_node_17 | 0.4 | n |  | TRUE
42 | bus_LV_2134-2_0_6_node_18 | 0.4 | n |  | TRUE
43 | bus_LV_2134-2_0_6_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_2134-2_0_6_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_2134-2_0_6_node_21 | 0.4 | n |  | TRUE
46 | bus_LV_2134-2_0_6_node_58 | 0.4 | n |  | TRUE
47 | bus_LV_2134-2_0_6_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_2134-2_0_6_node_22 | 0.4 | n |  | TRUE
49 | bus_LV_2134-2_0_6_node_102 | 0.4 | n |  | TRUE
50 | bus_LV_2134-2_0_6_node_53 | 0.4 | n |  | TRUE
51 | bus_LV_2134-2_0_6_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_2134-2_0_6_node_23 | 0.4 | n |  | TRUE
53 | bus_LV_2134-2_0_6_node_25 | 0.4 | n |  | TRUE
54 | bus_LV_2134-2_0_6_node_26 | 0.4 | n |  | TRUE
55 | bus_LV_2134-2_0_6_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_2134-2_0_6_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_2134-2_0_6_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_2134-2_0_6_node_118 | 0.4 | n |  | TRUE
59 | bus_LV_2134-2_0_6_node_119 | 0.4 | n |  | TRUE
60 | bus_LV_2134-2_0_6_node_30 | 0.4 | n |  | TRUE
61 | bus_LV_2134-2_0_6_node_33 | 0.4 | n |  | TRUE
62 | bus_LV_2134-2_0_6_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_2134-2_0_6_node_35 | 0.4 | n |  | TRUE
64 | bus_LV_2134-2_0_6_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_2134-2_0_6_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_2134-2_0_6_node_38 | 0.4 | n |  | TRUE
67 | bus_LV_2134-2_0_6_node_122 | 0.4 | n |  | TRUE
68 | bus_LV_2134-2_0_6_node_86 | 0.4 | n |  | TRUE
69 | bus_LV_2134-2_0_6_node_241 | 0.4 | n |  | TRUE
70 | bus_LV_2134-2_0_6_node_123 | 0.4 | n |  | TRUE
71 | bus_LV_2134-2_0_6_node_87 | 0.4 | n |  | TRUE
72 | bus_LV_2134-2_0_6_node_217 | 0.4 | n |  | TRUE
73 | bus_LV_2134-2_0_6_node_39 | 0.4 | n |  | TRUE
74 | bus_LV_2134-2_0_6_node_40 | 0.4 | n |  | TRUE
75 | bus_LV_2134-2_0_6_node_41 | 0.4 | n |  | TRUE
76 | bus_LV_2134-2_0_6_node_42 | 0.4 | n |  | TRUE
77 | bus_LV_2134-2_0_6_node_43 | 0.4 | n |  | TRUE
78 | bus_LV_2134-2_0_6_node_44 | 0.4 | n |  | TRUE
79 | bus_LV_2134-2_0_6_node_68 | 0.4 | n |  | TRUE
80 | bus_LV_2134-2_0_6_node_120 | 0.4 | n |  | TRUE
81 | bus_LV_2134-2_0_6_node_45 | 0.4 | n |  | TRUE
82 | bus_LV_2134-2_0_6_node_165 | 0.4 | n |  | TRUE
83 | bus_LV_2134-2_0_6_node_162 | 0.4 | n |  | TRUE
84 | bus_LV_2134-2_0_6_node_121 | 0.4 | n |  | TRUE
85 | bus_LV_2134-2_0_6_node_245 | 0.4 | n |  | TRUE
86 | bus_LV_2134-2_0_6_node_67 | 0.4 | n |  | TRUE
87 | bus_LV_2134-2_0_6_node_46 | 0.4 | n |  | TRUE
88 | bus_LV_2134-2_0_6_node_163 | 0.4 | n |  | TRUE
89 | bus_LV_2134-2_0_6_node_65 | 0.4 | n |  | TRUE
90 | bus_LV_2134-2_0_6_node_62 | 0.4 | n |  | TRUE
91 | bus_LV_2134-2_0_6_node_104 | 0.4 | n |  | TRUE
92 | bus_LV_2134-2_0_6_node_63 | 0.4 | n |  | TRUE
93 | bus_LV_2134-2_0_6_node_47 | 0.4 | n |  | TRUE
94 | bus_LV_2134-2_0_6_node_48 | 0.4 | n |  | TRUE
95 | bus_LV_2134-2_0_6_node_49 | 0.4 | n |  | TRUE
96 | bus_LV_2134-2_0_6_node_50 | 0.4 | n |  | TRUE
97 | bus_LV_2134-2_0_6_node_51 | 0.4 | n |  | TRUE
98 | bus_LV_2134-2_0_6_node_52 | 0.4 | n |  | TRUE
99 | bus_LV_2134-2_0_6_node_66 | 0.4 | n |  | TRUE
100 | bus_LV_2134-2_0_6_node_75 | 0.4 | n |  | TRUE
101 | bus_LV_2134-2_0_6_node_276 | 0.4 | n |  | TRUE
102 | bus_LV_2134-2_0_6_node_64 | 0.4 | n |  | TRUE
103 | bus_LV_2134-2_0_6_node_73 | 0.4 | n |  | TRUE
104 | bus_LV_2134-2_0_6_node_267 | 0.4 | n |  | TRUE
105 | bus_LV_2134-2_0_6_node_55 | 0.4 | n |  | TRUE
106 | bus_LV_2134-2_0_6_node_56 | 0.4 | n |  | TRUE
107 | bus_LV_2134-2_0_6_node_57 | 0.4 | n |  | TRUE
108 | bus_LV_2134-2_0_6_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_2134-2_0_6_node_95 | 0.4 | n |  | TRUE
110 | bus_LV_2134-2_0_6_node_96 | 0.4 | n |  | TRUE
111 | bus_LV_2134-2_0_6_node_59 | 0.4 | n |  | TRUE
112 | bus_LV_2134-2_0_6_node_60 | 0.4 | n |  | TRUE
113 | bus_LV_2134-2_0_6_node_61 | 0.4 | n |  | TRUE
114 | bus_LV_2134-2_0_6_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_2134-2_0_6_node_117 | 0.4 | n |  | TRUE
116 | bus_LV_2134-2_0_6_node_114 | 0.4 | n |  | TRUE
117 | bus_LV_2134-2_0_6_node_255 | 0.4 | n |  | TRUE
118 | bus_LV_2134-2_0_6_node_254 | 0.4 | n |  | TRUE
119 | bus_LV_2134-2_0_6_node_228 | 0.4 | n |  | TRUE
120 | bus_LV_2134-2_0_6_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_2134-2_0_6_node_139 | 0.4 | n |  | TRUE
122 | bus_LV_2134-2_0_6_node_229 | 0.4 | n |  | TRUE
123 | bus_LV_2134-2_0_6_node_137 | 0.4 | n |  | TRUE
124 | bus_LV_2134-2_0_6_node_105 | 0.4 | n |  | TRUE
125 | bus_LV_2134-2_0_6_node_69 | 0.4 | n |  | TRUE
126 | bus_LV_2134-2_0_6_node_70 | 0.4 | n |  | TRUE
127 | bus_LV_2134-2_0_6_node_161 | 0.4 | n |  | TRUE
128 | bus_LV_2134-2_0_6_node_152 | 0.4 | n |  | TRUE
129 | bus_LV_2134-2_0_6_node_71 | 0.4 | n |  | TRUE
130 | bus_LV_2134-2_0_6_node_72 | 0.4 | n |  | TRUE
131 | bus_LV_2134-2_0_6_node_74 | 0.4 | n |  | TRUE
132 | bus_LV_2134-2_0_6_node_76 | 0.4 | n |  | TRUE
133 | bus_LV_2134-2_0_6_node_153 | 0.4 | n |  | TRUE
134 | bus_LV_2134-2_0_6_node_154 | 0.4 | n |  | TRUE
135 | bus_LV_2134-2_0_6_node_88 | 0.4 | n |  | TRUE
136 | bus_LV_2134-2_0_6_node_89 | 0.4 | n |  | TRUE
137 | bus_LV_2134-2_0_6_node_90 | 0.4 | n |  | TRUE
138 | bus_LV_2134-2_0_6_node_91 | 0.4 | n |  | TRUE
139 | bus_LV_2134-2_0_6_node_92 | 0.4 | n |  | TRUE
140 | bus_LV_2134-2_0_6_node_93 | 0.4 | n |  | TRUE
141 | bus_LV_2134-2_0_6_node_201 | 0.4 | n |  | TRUE
142 | bus_LV_2134-2_0_6_node_221 | 0.4 | n |  | TRUE
143 | bus_LV_2134-2_0_6_node_204 | 0.4 | n |  | TRUE
144 | bus_LV_2134-2_0_6_node_192 | 0.4 | n |  | TRUE
145 | bus_LV_2134-2_0_6_node_240 | 0.4 | n |  | TRUE
146 | bus_LV_2134-2_0_6_node_236 | 0.4 | n |  | TRUE
147 | bus_LV_2134-2_0_6_node_239 | 0.4 | n |  | TRUE
148 | bus_LV_2134-2_0_6_node_248 | 0.4 | n |  | TRUE
149 | bus_LV_2134-2_0_6_node_270 | 0.4 | n |  | TRUE
150 | bus_LV_2134-2_0_6_node_264 | 0.4 | n |  | TRUE
151 | bus_LV_2134-2_0_6_node_237 | 0.4 | n |  | TRUE
152 | bus_LV_2134-2_0_6_node_97 | 0.4 | n |  | TRUE
153 | bus_LV_2134-2_0_6_node_98 | 0.4 | n |  | TRUE
154 | bus_LV_2134-2_0_6_node_100 | 0.4 | n |  | TRUE
155 | bus_LV_2134-2_0_6_node_193 | 0.4 | n |  | TRUE
156 | bus_LV_2134-2_0_6_node_222 | 0.4 | n |  | TRUE
157 | bus_LV_2134-2_0_6_node_198 | 0.4 | n |  | TRUE
158 | bus_LV_2134-2_0_6_node_284 | 0.4 | n |  | TRUE
159 | bus_LV_2134-2_0_6_node_282 | 0.4 | n |  | TRUE
160 | bus_LV_2134-2_0_6_node_106 | 0.4 | n |  | TRUE
161 | bus_LV_2134-2_0_6_node_134 | 0.4 | n |  | TRUE
162 | bus_LV_2134-2_0_6_node_133 | 0.4 | n |  | TRUE
163 | bus_LV_2134-2_0_6_node_110 | 0.4 | n |  | TRUE
164 | bus_LV_2134-2_0_6_node_112 | 0.4 | n |  | TRUE
165 | bus_LV_2134-2_0_6_node_116 | 0.4 | n |  | TRUE
166 | bus_LV_2134-2_0_6_node_235 | 0.4 | n |  | TRUE
167 | bus_LV_2134-2_0_6_node_232 | 0.4 | n |  | TRUE
168 | bus_LV_2134-2_0_6_node_242 | 0.4 | n |  | TRUE
169 | bus_LV_2134-2_0_6_node_233 | 0.4 | n |  | TRUE
170 | bus_LV_2134-2_0_6_node_226 | 0.4 | n |  | TRUE
171 | bus_LV_2134-2_0_6_node_243 | 0.4 | n |  | TRUE
172 | bus_LV_2134-2_0_6_node_244 | 0.4 | n |  | TRUE
173 | bus_LV_2134-2_0_6_node_230 | 0.4 | n |  | TRUE
174 | bus_LV_2134-2_0_6_node_145 | 0.4 | n |  | TRUE
175 | bus_LV_2134-2_0_6_node_127 | 0.4 | n |  | TRUE
176 | bus_LV_2134-2_0_6_node_128 | 0.4 | n |  | TRUE
177 | bus_LV_2134-2_0_6_node_129 | 0.4 | n |  | TRUE
178 | bus_LV_2134-2_0_6_node_130 | 0.4 | n |  | TRUE
179 | bus_LV_2134-2_0_6_node_131 | 0.4 | n |  | TRUE
180 | bus_LV_2134-2_0_6_node_151 | 0.4 | n |  | TRUE
181 | bus_LV_2134-2_0_6_node_144 | 0.4 | n |  | TRUE
182 | bus_LV_2134-2_0_6_node_141 | 0.4 | n |  | TRUE
183 | bus_LV_2134-2_0_6_node_149 | 0.4 | n |  | TRUE
184 | bus_LV_2134-2_0_6_node_160 | 0.4 | n |  | TRUE
185 | bus_LV_2134-2_0_6_node_262 | 0.4 | n |  | TRUE
186 | bus_LV_2134-2_0_6_node_142 | 0.4 | n |  | TRUE
187 | bus_LV_2134-2_0_6_node_146 | 0.4 | n |  | TRUE
188 | bus_LV_2134-2_0_6_node_280 | 0.4 | n |  | TRUE
189 | bus_LV_2134-2_0_6_node_135 | 0.4 | n |  | TRUE
190 | bus_LV_2134-2_0_6_node_136 | 0.4 | n |  | TRUE
191 | bus_LV_2134-2_0_6_node_140 | 0.4 | n |  | TRUE
192 | bus_LV_2134-2_0_6_node_138 | 0.4 | n |  | TRUE
193 | bus_LV_2134-2_0_6_node_227 | 0.4 | n |  | TRUE
194 | bus_LV_2134-2_0_6_node_231 | 0.4 | n |  | TRUE
195 | bus_LV_2134-2_0_6_node_143 | 0.4 | n |  | TRUE
196 | bus_LV_2134-2_0_6_node_157 | 0.4 | n |  | TRUE
197 | bus_LV_2134-2_0_6_node_150 | 0.4 | n |  | TRUE
198 | bus_LV_2134-2_0_6_node_260 | 0.4 | n |  | TRUE
199 | bus_LV_2134-2_0_6_node_278 | 0.4 | n |  | TRUE
200 | bus_LV_2134-2_0_6_node_147 | 0.4 | n |  | TRUE
201 | bus_LV_2134-2_0_6_node_148 | 0.4 | n |  | TRUE
202 | bus_LV_2134-2_0_6_node_155 | 0.4 | n |  | TRUE
203 | bus_LV_2134-2_0_6_node_156 | 0.4 | n |  | TRUE
204 | bus_LV_2134-2_0_6_node_158 | 0.4 | n |  | TRUE
205 | bus_LV_2134-2_0_6_node_263 | 0.4 | n |  | TRUE
206 | bus_LV_2134-2_0_6_node_275 | 0.4 | n |  | TRUE
207 | bus_LV_2134-2_0_6_node_190 | 0.4 | n |  | TRUE
208 | bus_LV_2134-2_0_6_node_164 | 0.4 | n |  | TRUE
209 | bus_LV_2134-2_0_6_node_234 | 0.4 | n |  | TRUE
210 | bus_LV_2134-2_0_6_node_247 | 0.4 | n |  | TRUE
211 | bus_LV_2134-2_0_6_node_166 | 0.4 | n |  | TRUE
212 | bus_LV_2134-2_0_6_node_167 | 0.4 | n |  | TRUE
213 | bus_LV_2134-2_0_6_node_168 | 0.4 | n |  | TRUE
214 | bus_LV_2134-2_0_6_node_169 | 0.4 | n |  | TRUE
215 | bus_LV_2134-2_0_6_node_170 | 0.4 | n |  | TRUE
216 | bus_LV_2134-2_0_6_node_171 | 0.4 | n |  | TRUE
217 | bus_LV_2134-2_0_6_node_172 | 0.4 | n |  | TRUE
218 | bus_LV_2134-2_0_6_node_177 | 0.4 | n |  | TRUE
219 | bus_LV_2134-2_0_6_node_223 | 0.4 | n |  | TRUE
220 | bus_LV_2134-2_0_6_node_173 | 0.4 | n |  | TRUE
221 | bus_LV_2134-2_0_6_node_210 | 0.4 | n |  | TRUE
222 | bus_LV_2134-2_0_6_node_174 | 0.4 | n |  | TRUE
223 | bus_LV_2134-2_0_6_node_176 | 0.4 | n |  | TRUE
224 | bus_LV_2134-2_0_6_node_178 | 0.4 | n |  | TRUE
225 | bus_LV_2134-2_0_6_node_179 | 0.4 | n |  | TRUE
226 | bus_LV_2134-2_0_6_node_199 | 0.4 | n |  | TRUE
227 | bus_LV_2134-2_0_6_node_200 | 0.4 | n |  | TRUE
228 | bus_LV_2134-2_0_6_node_181 | 0.4 | n |  | TRUE
229 | bus_LV_2134-2_0_6_node_182 | 0.4 | n |  | TRUE
230 | bus_LV_2134-2_0_6_node_183 | 0.4 | n |  | TRUE
231 | bus_LV_2134-2_0_6_node_184 | 0.4 | n |  | TRUE
232 | bus_LV_2134-2_0_6_node_202 | 0.4 | n |  | TRUE
233 | bus_LV_2134-2_0_6_node_258 | 0.4 | n |  | TRUE
234 | bus_LV_2134-2_0_6_node_257 | 0.4 | n |  | TRUE
235 | bus_LV_2134-2_0_6_node_185 | 0.4 | n |  | TRUE
236 | bus_LV_2134-2_0_6_node_186 | 0.4 | n |  | TRUE
237 | bus_LV_2134-2_0_6_node_187 | 0.4 | n |  | TRUE
238 | bus_LV_2134-2_0_6_node_191 | 0.4 | n |  | TRUE
239 | bus_LV_2134-2_0_6_node_205 | 0.4 | n |  | TRUE
240 | bus_LV_2134-2_0_6_node_196 | 0.4 | n |  | TRUE
241 | bus_LV_2134-2_0_6_node_219 | 0.4 | n |  | TRUE
242 | bus_LV_2134-2_0_6_node_194 | 0.4 | n |  | TRUE
243 | bus_LV_2134-2_0_6_node_224 | 0.4 | n |  | TRUE
244 | bus_LV_2134-2_0_6_node_195 | 0.4 | n |  | TRUE
245 | bus_LV_2134-2_0_6_node_197 | 0.4 | n |  | TRUE
246 | bus_LV_2134-2_0_6_node_209 | 0.4 | n |  | TRUE
247 | bus_LV_2134-2_0_6_node_207 | 0.4 | n |  | TRUE
248 | bus_LV_2134-2_0_6_node_220 | 0.4 | n |  | TRUE
249 | bus_LV_2134-2_0_6_node_206 | 0.4 | n |  | TRUE
250 | bus_LV_2134-2_0_6_node_208 | 0.4 | n |  | TRUE
251 | bus_LV_2134-2_0_6_node_211 | 0.4 | n |  | TRUE
252 | bus_LV_2134-2_0_6_node_212 | 0.4 | n |  | TRUE
253 | bus_LV_2134-2_0_6_node_213 | 0.4 | n |  | TRUE
254 | bus_LV_2134-2_0_6_node_273 | 0.4 | n |  | TRUE
255 | bus_LV_2134-2_0_6_node_218 | 0.4 | n |  | TRUE
256 | bus_LV_2134-2_0_6_node_256 | 0.4 | n |  | TRUE
257 | bus_LV_2134-2_0_6_node_272 | 0.4 | n |  | TRUE
258 | bus_LV_2134-2_0_6_node_252 | 0.4 | n |  | TRUE
259 | bus_LV_2134-2_0_6_node_225 | 0.4 | n |  | TRUE
260 | bus_LV_2134-2_0_6_node_249 | 0.4 | n |  | TRUE
261 | bus_LV_2134-2_0_6_node_246 | 0.4 | n |  | TRUE
262 | bus_LV_2134-2_0_6_node_238 | 0.4 | n |  | TRUE
263 | bus_LV_2134-2_0_6_node_250 | 0.4 | n |  | TRUE
264 | bus_LV_2134-2_0_6_node_251 | 0.4 | n |  | TRUE
265 | bus_LV_2134-2_0_6_node_271 | 0.4 | n |  | TRUE
266 | bus_LV_2134-2_0_6_node_253 | 0.4 | n |  | TRUE
267 | bus_LV_2134-2_0_6_node_259 | 0.4 | n |  | TRUE
268 | bus_LV_2134-2_0_6_node_265 | 0.4 | n |  | TRUE
269 | bus_LV_2134-2_0_6_node_266 | 0.4 | n |  | TRUE
270 | bus_LV_2134-2_0_6_node_268 | 0.4 | n |  | TRUE
271 | bus_LV_2134-2_0_6_node_279 | 0.4 | n |  | TRUE
272 | bus_LV_2134-2_0_6_node_281 | 0.4 | n |  | TRUE
273 | bus_MV_30_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2134-2_0_6_load_0 | 0 | 0.0024365 | 0.00061065 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2134-2_0_6_load_1 | 1 | 0.0013513 | 0.00033866 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2134-2_0_6_load_4 | 4 | 0.0032672 | 0.00081885 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2134-2_0_6_load_159 | 6 | 0.0037565 | 0.00094146 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2134-2_0_6_load_101 | 7 | 0.00076155 | 0.00019086 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2134-2_0_6_load_203 | 9 | 0.0041595 | 0.0010425 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2134-2_0_6_load_189 | 11 | 0.0030536 | 0.00076531 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2134-2_0_6_load_99 | 12 | 0.0050211 | 0.0012584 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2134-2_0_6_load_24 | 13 | 0.0019677 | 0.00049315 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2134-2_0_6_load_54 | 14 | 0.0018721 | 0.00046919 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2134-2_0_6_load_188 | 15 | 0.0019695 | 0.0004936 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2134-2_0_6_load_214 | 16 | 0.0014839 | 0.00037191 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2134-2_0_6_load_6 | 17 | 0.0053276 | 0.0013352 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2134-2_0_6_load_124 | 21 | 0.0023142 | 0.00058 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2134-2_0_6_load_84 | 23 | 0.0037738 | 0.0009458 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2134-2_0_6_load_80 | 24 | 0.00046926 | 0.00011761 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2134-2_0_6_load_77 | 25 | 0.00078536 | 0.00019683 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2134-2_0_6_load_10 | 26 | 0.0040561 | 0.0010166 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2134-2_0_6_load_11 | 27 | 0.0020956 | 0.00052521 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2134-2_0_6_load_13 | 29 | 0.0027072 | 0.00067849 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2134-2_0_6_load_14 | 30 | 0.0018758 | 0.00047013 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2134-2_0_6_load_107 | 32 | 0.0025176 | 0.00063097 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2134-2_0_6_load_83 | 34 | 0.0024954 | 0.00062541 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2134-2_0_6_load_274 | 35 | 0.0051623 | 0.0012938 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2134-2_0_6_load_111 | 36 | 0.005542 | 0.001389 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2134-2_0_6_load_108 | 37 | 0.0043214 | 0.001083 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2134-2_0_6_load_82 | 38 | 0.0016713 | 0.00041886 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2134-2_0_6_load_16 | 40 | 0.0013108 | 0.00032851 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2134-2_0_6_load_17 | 41 | 0.0018458 | 0.00046261 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2134-2_0_6_load_18 | 42 | 0.0013793 | 0.00034568 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2134-2_0_6_load_19 | 43 | 0.0016862 | 0.0004226 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2134-2_0_6_load_21 | 45 | 0.0012709 | 0.00031853 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2134-2_0_6_load_102 | 49 | 0.001713 | 0.00042931 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2134-2_0_6_load_53 | 50 | 0.0027784 | 0.00069634 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2134-2_0_6_load_31 | 51 | 0.0025114 | 0.00062942 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2134-2_0_6_load_23 | 52 | 0.0016538 | 0.00041449 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2134-2_0_6_load_25 | 53 | 0.0026305 | 0.00065926 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2134-2_0_6_load_26 | 54 | 0.0025472 | 0.00063838 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2134-2_0_6_load_27 | 55 | 0.0022229 | 0.00055711 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2134-2_0_6_load_28 | 56 | 0.0010769 | 0.00026989 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2134-2_0_6_load_29 | 57 | 0.0077713 | 0.0019477 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2134-2_0_6_load_118 | 58 | 0.0025128 | 0.00062976 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2134-2_0_6_load_30 | 60 | 0.002207 | 0.00055313 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2134-2_0_6_load_33 | 61 | 0.0016827 | 0.00042172 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2134-2_0_6_load_34 | 62 | 0.0022245 | 0.00055751 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2134-2_0_6_load_36 | 64 | 0.0015646 | 0.00039213 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2134-2_0_6_load_37 | 65 | 0.002157 | 0.0005406 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2134-2_0_6_load_38 | 66 | 0.0029616 | 0.00074224 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2134-2_0_6_load_86 | 68 | 0.008736 | 0.0021894 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2134-2_0_6_load_241 | 69 | 0.0020346 | 0.00050993 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2134-2_0_6_load_123 | 70 | 0.001857 | 0.0004654 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2134-2_0_6_load_87 | 71 | 0.0011355 | 0.00028458 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2134-2_0_6_load_39 | 73 | 0.0028505 | 0.00071441 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2134-2_0_6_load_40 | 74 | 0.00083545 | 0.00020938 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2134-2_0_6_load_43 | 77 | 0.0031921 | 0.00080002 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2134-2_0_6_load_68 | 79 | 0.00057497 | 0.0001441 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2134-2_0_6_load_120 | 80 | 0.0084184 | 0.0021099 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2134-2_0_6_load_45 | 81 | 0.0045863 | 0.0011494 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2134-2_0_6_load_165 | 82 | 0.0014711 | 0.00036869 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2134-2_0_6_load_162 | 83 | 0.0022082 | 0.00055344 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2134-2_0_6_load_121 | 84 | 0.003084 | 0.00077292 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2134-2_0_6_load_245 | 85 | 0.0032297 | 0.00080945 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2134-2_0_6_load_67 | 86 | 0.001667 | 0.00041778 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2134-2_0_6_load_163 | 88 | 0.0016372 | 0.00041032 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2134-2_0_6_load_65 | 89 | 0.0057652 | 0.0014449 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2134-2_0_6_load_62 | 90 | 0.0010846 | 0.00027184 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2134-2_0_6_load_104 | 91 | 0.0023329 | 0.00058468 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2134-2_0_6_load_63 | 92 | 0.0030084 | 0.00075398 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2134-2_0_6_load_47 | 93 | 0.00284 | 0.00071176 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2134-2_0_6_load_50 | 96 | 0.002702 | 0.00067718 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2134-2_0_6_load_51 | 97 | 0.0014538 | 0.00036435 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2134-2_0_6_load_75 | 100 | 0.0013323 | 0.00033391 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2134-2_0_6_load_276 | 101 | 0.0063792 | 0.0015988 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2134-2_0_6_load_64 | 102 | 0.0028142 | 0.0007053 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2134-2_0_6_load_267 | 104 | 0.0037713 | 0.00094518 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2134-2_0_6_load_55 | 105 | 0.0038669 | 0.00096913 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2134-2_0_6_load_56 | 106 | 0.00072395 | 0.00018144 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2134-2_0_6_load_57 | 107 | 0.0014273 | 0.00035771 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2134-2_0_6_load_96 | 110 | 0.00037754 | 9.4622e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2134-2_0_6_load_61 | 113 | 0.0011898 | 0.00029818 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2134-2_0_6_load_103 | 114 | 0.0025264 | 0.00063317 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2134-2_0_6_load_117 | 115 | 0.0049901 | 0.0012506 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2134-2_0_6_load_114 | 116 | 0.0026937 | 0.0006751 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2134-2_0_6_load_255 | 117 | 0.0026445 | 0.00066278 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2134-2_0_6_load_254 | 118 | 0.0044846 | 0.001124 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2134-2_0_6_load_228 | 119 | 0.004002 | 0.001003 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2134-2_0_6_load_115 | 120 | 0.0048464 | 0.0012146 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2134-2_0_6_load_139 | 121 | 0.0034983 | 0.00087675 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2134-2_0_6_load_229 | 122 | 0.0055542 | 0.001392 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2134-2_0_6_load_137 | 123 | 0.0043178 | 0.0010821 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2134-2_0_6_load_105 | 124 | 0.00097146 | 0.00024347 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2134-2_0_6_load_69 | 125 | 0.0035266 | 0.00088386 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2134-2_0_6_load_70 | 126 | 0.0045489 | 0.0011401 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2134-2_0_6_load_161 | 127 | 0.0013487 | 0.00033802 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2134-2_0_6_load_71 | 129 | 0.0019547 | 0.0004899 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2134-2_0_6_load_72 | 130 | 0.0012805 | 0.00032094 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2134-2_0_6_load_74 | 131 | 0.0012205 | 0.0003059 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2134-2_0_6_load_76 | 132 | 0.0014894 | 0.00037328 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2134-2_0_6_load_153 | 133 | 0.00035558 | 8.9118e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2134-2_0_6_load_88 | 135 | 0.002493 | 0.0006248 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2134-2_0_6_load_89 | 136 | 0.0033812 | 0.0008474 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2134-2_0_6_load_91 | 138 | 0.0029957 | 0.00075079 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2134-2_0_6_load_92 | 139 | 0.0034832 | 0.00087298 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2134-2_0_6_load_93 | 140 | 0.0047517 | 0.0011909 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2134-2_0_6_load_221 | 142 | 0.0038167 | 0.00095657 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2134-2_0_6_load_204 | 143 | 0.0021339 | 0.00053481 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2134-2_0_6_load_240 | 145 | 0.00098418 | 0.00024666 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2134-2_0_6_load_236 | 146 | 0.0029141 | 0.00073035 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2134-2_0_6_load_270 | 149 | 0.0010149 | 0.00025435 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2134-2_0_6_load_264 | 150 | 0.002839 | 0.00071151 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2134-2_0_6_load_237 | 151 | 0.0024442 | 0.00061259 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2134-2_0_6_load_97 | 152 | 0.0021339 | 0.00053481 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2134-2_0_6_load_98 | 153 | 0.0048591 | 0.0012178 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2134-2_0_6_load_193 | 155 | 0.010604 | 0.0026577 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2134-2_0_6_load_222 | 156 | 0.0035127 | 0.00088037 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2134-2_0_6_load_198 | 157 | 0.0067999 | 0.0017042 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2134-2_0_6_load_282 | 159 | 0.0013757 | 0.00034479 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2134-2_0_6_load_106 | 160 | 0.0043628 | 0.0010934 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2134-2_0_6_load_134 | 161 | 0.00086222 | 0.00021609 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2134-2_0_6_load_133 | 162 | 0.0029829 | 0.00074758 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2134-2_0_6_load_112 | 164 | 0.0052943 | 0.0013269 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2134-2_0_6_load_235 | 166 | 0.005812 | 0.0014566 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2134-2_0_6_load_232 | 167 | 0.0045083 | 0.0011299 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2134-2_0_6_load_242 | 168 | 0.0059006 | 0.0014788 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2134-2_0_6_load_233 | 169 | 0.0043132 | 0.001081 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2134-2_0_6_load_226 | 170 | 0.0056076 | 0.0014054 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2134-2_0_6_load_243 | 171 | 0.0066674 | 0.001671 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2134-2_0_6_load_244 | 172 | 0.003663 | 0.00091804 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2134-2_0_6_load_230 | 173 | 0.0050882 | 0.0012752 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2134-2_0_6_load_127 | 175 | 0.00057536 | 0.0001442 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2134-2_0_6_load_128 | 176 | 0.0028199 | 0.00070673 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2134-2_0_6_load_130 | 178 | 0.0011097 | 0.00027811 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2134-2_0_6_load_141 | 182 | 0.0013099 | 0.00032829 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2134-2_0_6_load_149 | 183 | 0.0030455 | 0.00076326 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2134-2_0_6_load_262 | 185 | 0.0023998 | 0.00060144 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2134-2_0_6_load_142 | 186 | 0.0037451 | 0.00093862 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2134-2_0_6_load_280 | 188 | 0.0022169 | 0.00055562 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2134-2_0_6_load_135 | 189 | 0.0045905 | 0.0011505 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_2134-2_0_6_load_136 | 190 | 0.00061057 | 0.00015302 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_2134-2_0_6_load_138 | 192 | 0.0013714 | 0.00034371 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_2134-2_0_6_load_227 | 193 | 0.0049913 | 0.001251 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_2134-2_0_6_load_231 | 194 | 0.022148 | 0.0055509 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_2134-2_0_6_load_143 | 195 | 0.0010795 | 0.00027054 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_2134-2_0_6_load_157 | 196 | 0.0017894 | 0.00044846 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_2134-2_0_6_load_150 | 197 | 0.0011611 | 0.000291 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_2134-2_0_6_load_260 | 198 | 0.00076643 | 0.00019208 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_2134-2_0_6_load_278 | 199 | 0.00053978 | 0.00013528 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_2134-2_0_6_load_147 | 200 | 0.00075997 | 0.00019047 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_2134-2_0_6_load_148 | 201 | 0.0012934 | 0.00032416 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_2134-2_0_6_load_155 | 202 | 0.0016205 | 0.00040615 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_2134-2_0_6_load_156 | 203 | 0.0018261 | 0.00045766 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_2134-2_0_6_load_158 | 204 | 0.0011745 | 0.00029436 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_2134-2_0_6_load_275 | 206 | 0.0013221 | 0.00033135 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_2134-2_0_6_load_190 | 207 | 0.0019888 | 0.00049843 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_2134-2_0_6_load_164 | 208 | 0.00060905 | 0.00015264 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_2134-2_0_6_load_234 | 209 | 0.0057748 | 0.0014473 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_2134-2_0_6_load_247 | 210 | 0.0025011 | 0.00062684 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_2134-2_0_6_load_166 | 211 | 0.001499 | 0.00037569 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_2134-2_0_6_load_169 | 214 | 0.0022595 | 0.00056628 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_2134-2_0_6_load_170 | 215 | 0.0022133 | 0.00055471 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_2134-2_0_6_load_172 | 217 | 0.0035148 | 0.0008809 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_2134-2_0_6_load_177 | 218 | 0.0018423 | 0.00046173 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_2134-2_0_6_load_223 | 219 | 0.0025717 | 0.00064452 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_2134-2_0_6_load_173 | 220 | 0.0028739 | 0.00072027 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_2134-2_0_6_load_210 | 221 | 0.00075676 | 0.00018966 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_2134-2_0_6_load_176 | 223 | 0.0028827 | 0.00072247 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_2134-2_0_6_load_178 | 224 | 0.001437 | 0.00036014 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_2134-2_0_6_load_179 | 225 | 0.0015254 | 0.0003823 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_2134-2_0_6_load_199 | 226 | 0.0093073 | 0.0023326 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_2134-2_0_6_load_181 | 228 | 0.0054128 | 0.0013566 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_2134-2_0_6_load_183 | 230 | 0.00064004 | 0.00016041 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_2134-2_0_6_load_184 | 231 | 0.0011237 | 0.00028163 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_2134-2_0_6_load_202 | 232 | 0.0015382 | 0.00038552 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_2134-2_0_6_load_258 | 233 | 0.001758 | 0.00044059 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_2134-2_0_6_load_257 | 234 | 0.00042254 | 0.0001059 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_2134-2_0_6_load_185 | 235 | 0.0017013 | 0.0004264 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_2134-2_0_6_load_186 | 236 | 0.0015957 | 0.00039993 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_2134-2_0_6_load_187 | 237 | 0.00092988 | 0.00023305 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_2134-2_0_6_load_205 | 239 | 0.0016939 | 0.00042453 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_2134-2_0_6_load_196 | 240 | 0.0029869 | 0.00074859 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_2134-2_0_6_load_219 | 241 | 0.0016857 | 0.00042248 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_2134-2_0_6_load_194 | 242 | 0.0026816 | 0.00067208 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_2134-2_0_6_load_224 | 243 | 0.0062169 | 0.0015581 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_2134-2_0_6_load_195 | 244 | 0.0018586 | 0.00046581 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_2134-2_0_6_load_197 | 245 | 0.0032486 | 0.00081418 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_2134-2_0_6_load_209 | 246 | 0.0035324 | 0.0008853 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_2134-2_0_6_load_207 | 247 | 0.0031609 | 0.0007922 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_2134-2_0_6_load_220 | 248 | 0.00089933 | 0.00022539 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_2134-2_0_6_load_206 | 249 | 0.0010766 | 0.00026983 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_2134-2_0_6_load_208 | 250 | 0.0018281 | 0.00045816 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_2134-2_0_6_load_211 | 251 | 0.00074725 | 0.00018728 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_2134-2_0_6_load_212 | 252 | 0.0016975 | 0.00042542 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_2134-2_0_6_load_273 | 254 | 0.0045724 | 0.0011459 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_2134-2_0_6_load_256 | 256 | 0.0023321 | 0.00058447 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_2134-2_0_6_load_272 | 257 | 0.0014065 | 0.00035249 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_2134-2_0_6_load_252 | 258 | 0.01806 | 0.0045261 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_2134-2_0_6_load_225 | 259 | 0.0021851 | 0.00054765 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_2134-2_0_6_load_238 | 262 | 0.0031929 | 0.00080021 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_2134-2_0_6_load_250 | 263 | 0.0080308 | 0.0020127 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_2134-2_0_6_load_271 | 265 | 0.0029011 | 0.00072708 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_2134-2_0_6_load_253 | 266 | 0.0016639 | 0.000417 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_2134-2_0_6_load_259 | 267 | 0.0028315 | 0.00070965 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_2134-2_0_6_load_265 | 268 | 0.002625 | 0.0006579 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_2134-2_0_6_load_266 | 269 | 0.0060492 | 0.0015161 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_2134-2_0_6_load_268 | 270 | 0.0035971 | 0.00090151 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_2134-2_0_6_load_279 | 271 | 0.00044187 | 0.00011074 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_2134-2_0_6_load_281 | 272 | 0.0014585 | 0.00036554 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 194 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2134-2_0_6_line_0 |  | 0 | 1 | 0.011873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2134-2_0_6_line_1 |  | 0 | 2 | 0.02708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2134-2_0_6_line_2 |  | 1 | 3 | 0.0072413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2134-2_0_6_line_3 |  | 2 | 4 | 0.033639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2134-2_0_6_line_4 |  | 2 | 5 | 0.044114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2134-2_0_6_line_5 |  | 3 | 6 | 0.029075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2134-2_0_6_line_6 |  | 3 | 7 | 0.017456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2134-2_0_6_line_7 |  | 5 | 8 | 0.054627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2134-2_0_6_line_8 |  | 5 | 9 | 0.02439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2134-2_0_6_line_9 |  | 5 | 10 | 0.025273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2134-2_0_6_line_10 |  | 6 | 11 | 0.02386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2134-2_0_6_line_11 |  | 7 | 12 | 0.020174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2134-2_0_6_line_12 |  | 8 | 13 | 0.00443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2134-2_0_6_line_13 |  | 8 | 14 | 0.018455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2134-2_0_6_line_14 |  | 9 | 15 | 0.024753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2134-2_0_6_line_15 |  | 10 | 16 | 0.027473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2134-2_0_6_line_16 |  | 11 | 207 | 0.035872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2134-2_0_6_line_17 |  | 12 | 152 | 0.024767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2134-2_0_6_line_18 |  | 13 | 48 | 0.018385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2134-2_0_6_line_19 |  | 14 | 56 | 0.011549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2134-2_0_6_line_20 |  | 15 | 237 | 0.0042981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2134-2_0_6_line_21 |  | 16 | 253 | 0.013635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2134-2_0_6_line_22 |  | 17 | 18 | 0.00154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2134-2_0_6_line_23 |  | 18 | 19 | 0.026331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2134-2_0_6_line_24 |  | 19 | 20 | 0.040819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2134-2_0_6_line_25 |  | 19 | 21 | 0.016848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2134-2_0_6_line_26 |  | 20 | 22 | 0.030009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2134-2_0_6_line_27 |  | 20 | 23 | 0.054313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2134-2_0_6_line_28 |  | 22 | 24 | 0.032816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2134-2_0_6_line_29 |  | 22 | 25 | 0.01137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2134-2_0_6_line_30 |  | 24 | 38 | 0.032083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2134-2_0_6_line_31 |  | 26 | 27 | 0.036562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2134-2_0_6_line_32 |  | 26 | 28 | 0.013037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2134-2_0_6_line_33 |  | 27 | 29 | 0.026882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2134-2_0_6_line_34 |  | 28 | 30 | 0.020313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2134-2_0_6_line_35 |  | 28 | 31 | 0.031741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2134-2_0_6_line_36 |  | 29 | 32 | 0.024171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2134-2_0_6_line_37 |  | 30 | 33 | 0.011795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2134-2_0_6_line_38 |  | 31 | 34 | 0.014259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2134-2_0_6_line_39 |  | 31 | 35 | 0.034436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2134-2_0_6_line_40 |  | 33 | 36 | 0.019677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2134-2_0_6_line_41 |  | 33 | 37 | 0.02139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2134-2_0_6_line_42 |  | 34 | 38 | 0.020086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2134-2_0_6_line_43 |  | 35 | 39 | 0.0015107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2134-2_0_6_line_44 |  | 37 | 163 | 0.0038674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2134-2_0_6_line_45 |  | 39 | 104 | 0.018306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2134-2_0_6_line_46 |  | 39 | 98 | 0.040909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2134-2_0_6_line_47 |  | 40 | 41 | 0.025565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2134-2_0_6_line_48 |  | 40 | 42 | 0.0044322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2134-2_0_6_line_49 |  | 41 | 43 | 0.00014383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2134-2_0_6_line_50 |  | 42 | 44 | 0.01506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2134-2_0_6_line_51 |  | 43 | 45 | 0.0040959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2134-2_0_6_line_52 |  | 44 | 46 | 0.014926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2134-2_0_6_line_53 |  | 44 | 47 | 0.038026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2134-2_0_6_line_54 |  | 45 | 48 | 0.02936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2134-2_0_6_line_55 |  | 46 | 49 | 0.016156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2134-2_0_6_line_56 |  | 47 | 50 | 0.019247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2134-2_0_6_line_57 |  | 47 | 51 | 0.014949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2134-2_0_6_line_58 |  | 48 | 52 | 0.015606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2134-2_0_6_line_59 |  | 49 | 114 | 0.0045125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2134-2_0_6_line_60 |  | 51 | 60 | 0.0021173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2134-2_0_6_line_61 |  | 53 | 54 | 0.028903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2134-2_0_6_line_62 |  | 53 | 55 | 0.005327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2134-2_0_6_line_63 |  | 54 | 56 | 0.016709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2134-2_0_6_line_64 |  | 57 | 58 | 0.0084124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2134-2_0_6_line_65 |  | 58 | 59 | 0.015535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2134-2_0_6_line_66 |  | 59 | 157 | 0.021329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2134-2_0_6_line_67 |  | 59 | 67 | 0.008957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2134-2_0_6_line_68 |  | 61 | 62 | 0.018522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_2134-2_0_6_line_69 |  | 61 | 63 | 0.011802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_2134-2_0_6_line_70 |  | 62 | 64 | 0.0051771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_2134-2_0_6_line_71 |  | 63 | 65 | 0.023564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2134-2_0_6_line_72 |  | 63 | 66 | 0.0078054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_2134-2_0_6_line_73 |  | 64 | 67 | 0.022411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_2134-2_0_6_line_74 |  | 65 | 68 | 0.01136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2134-2_0_6_line_75 |  | 66 | 69 | 0.0087597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2134-2_0_6_line_76 |  | 67 | 70 | 0.010038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2134-2_0_6_line_77 |  | 68 | 71 | 0.0020412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2134-2_0_6_line_78 |  | 69 | 72 | 0.013098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_2134-2_0_6_line_79 |  | 72 | 254 | 0.014499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2134-2_0_6_line_80 |  | 73 | 74 | 0.010699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_2134-2_0_6_line_81 |  | 73 | 75 | 0.0039842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_2134-2_0_6_line_82 |  | 74 | 76 | 0.0096213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_2134-2_0_6_line_83 |  | 75 | 77 | 0.016656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_2134-2_0_6_line_84 |  | 75 | 78 | 0.037862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2134-2_0_6_line_85 |  | 76 | 79 | 0.019611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2134-2_0_6_line_86 |  | 76 | 80 | 0.037014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2134-2_0_6_line_87 |  | 77 | 81 | 0.012114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_2134-2_0_6_line_88 |  | 78 | 82 | 0.03878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2134-2_0_6_line_89 |  | 78 | 83 | 0.0038131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2134-2_0_6_line_90 |  | 79 | 86 | 0.011852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2134-2_0_6_line_91 |  | 81 | 87 | 0.03418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_2134-2_0_6_line_92 |  | 83 | 88 | 0.016704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2134-2_0_6_line_93 |  | 84 | 85 | 0.043838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2134-2_0_6_line_94 |  | 85 | 171 | 0.035068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2134-2_0_6_line_95 |  | 86 | 125 | 0.014645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2134-2_0_6_line_96 |  | 87 | 89 | 0.013816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_2134-2_0_6_line_97 |  | 87 | 90 | 0.0030359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_2134-2_0_6_line_98 |  | 88 | 208 | 0.00027813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2134-2_0_6_line_99 |  | 89 | 91 | 0.0043755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_2134-2_0_6_line_100 |  | 90 | 92 | 0.011844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_2134-2_0_6_line_101 |  | 91 | 124 | 0.0048049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_2134-2_0_6_line_102 |  | 92 | 102 | 0.013924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2134-2_0_6_line_103 |  | 93 | 94 | 0.030058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2134-2_0_6_line_104 |  | 93 | 95 | 0.042894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2134-2_0_6_line_105 |  | 94 | 96 | 0.025293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2134-2_0_6_line_106 |  | 95 | 97 | 0.044941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2134-2_0_6_line_107 |  | 95 | 98 | 0.026107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2134-2_0_6_line_108 |  | 96 | 99 | 0.033258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2134-2_0_6_line_109 |  | 97 | 100 | 0.024099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2134-2_0_6_line_110 |  | 98 | 101 | 0.037745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2134-2_0_6_line_111 |  | 99 | 102 | 0.010177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2134-2_0_6_line_112 |  | 100 | 103 | 0.024844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2134-2_0_6_line_113 |  | 103 | 132 | 0.019204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2134-2_0_6_line_114 |  | 103 | 129 | 0.0080709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2134-2_0_6_line_115 |  | 104 | 268 | 0.022915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2134-2_0_6_line_116 |  | 105 | 106 | 0.03463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2134-2_0_6_line_117 |  | 106 | 107 | 0.02191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2134-2_0_6_line_118 |  | 107 | 111 | 0.01635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2134-2_0_6_line_119 |  | 108 | 109 | 0.015268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2134-2_0_6_line_120 |  | 108 | 110 | 0.0079003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2134-2_0_6_line_121 |  | 109 | 145 | 0.010257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2134-2_0_6_line_122 |  | 109 | 146 | 0.012289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2134-2_0_6_line_123 |  | 110 | 117 | 0.017286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2134-2_0_6_line_124 |  | 111 | 112 | 0.02909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2134-2_0_6_line_125 |  | 111 | 113 | 0.022664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2134-2_0_6_line_126 |  | 112 | 115 | 0.015273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2134-2_0_6_line_127 |  | 112 | 116 | 0.0045603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2134-2_0_6_line_128 |  | 114 | 158 | 0.066491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2134-2_0_6_line_129 |  | 115 | 119 | 0.010088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2134-2_0_6_line_130 |  | 116 | 120 | 0.03386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2134-2_0_6_line_131 |  | 117 | 118 | 0.0036748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2134-2_0_6_line_132 |  | 118 | 260 | 0.02198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2134-2_0_6_line_133 |  | 119 | 170 | 0.020603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2134-2_0_6_line_134 |  | 120 | 165 | 0.019494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2134-2_0_6_line_135 |  | 121 | 122 | 0.028747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2134-2_0_6_line_136 |  | 121 | 123 | 0.0051527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2134-2_0_6_line_137 |  | 122 | 193 | 0.017005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2134-2_0_6_line_138 |  | 123 | 192 | 0.030709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
139 | LV_2134-2_0_6_line_139 |  | 124 | 160 | 0.0081285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
140 | LV_2134-2_0_6_line_140 |  | 125 | 126 | 0.028224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2134-2_0_6_line_141 |  | 126 | 127 | 0.019218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2134-2_0_6_line_142 |  | 127 | 128 | 0.012499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2134-2_0_6_line_143 |  | 128 | 196 | 0.032574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2134-2_0_6_line_144 |  | 128 | 195 | 0.011907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2134-2_0_6_line_145 |  | 129 | 130 | 0.0039816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2134-2_0_6_line_146 |  | 130 | 131 | 0.01316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2134-2_0_6_line_147 |  | 133 | 134 | 0.0085316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2134-2_0_6_line_148 |  | 134 | 180 | 0.003607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2134-2_0_6_line_149 |  | 134 | 187 | 0.02372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2134-2_0_6_line_150 |  | 135 | 136 | 0.032479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_2134-2_0_6_line_151 |  | 135 | 137 | 0.015289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2134-2_0_6_line_152 |  | 136 | 138 | 0.027681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2134-2_0_6_line_153 |  | 137 | 139 | 0.032946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_2134-2_0_6_line_154 |  | 137 | 140 | 0.0053137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_2134-2_0_6_line_155 |  | 139 | 141 | 0.018965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_2134-2_0_6_line_156 |  | 140 | 142 | 0.0089553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_2134-2_0_6_line_157 |  | 141 | 143 | 0.032202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_2134-2_0_6_line_158 |  | 142 | 144 | 0.015982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_2134-2_0_6_line_159 |  | 144 | 156 | 0.036364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_2134-2_0_6_line_160 |  | 144 | 154 | 0.006962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_2134-2_0_6_line_161 |  | 145 | 150 | 0.021925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_2134-2_0_6_line_162 |  | 146 | 151 | 0.046414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_2134-2_0_6_line_163 |  | 147 | 148 | 0.025218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
164 | LV_2134-2_0_6_line_164 |  | 147 | 149 | 0.0062449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
165 | LV_2134-2_0_6_line_165 |  | 148 | 260 | 0.016774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_2134-2_0_6_line_166 |  | 148 | 194 | 0.017826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
167 | LV_2134-2_0_6_line_167 |  | 149 | 265 | 0.022777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
168 | LV_2134-2_0_6_line_168 |  | 150 | 255 | 0.012191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_2134-2_0_6_line_169 |  | 151 | 262 | 0.0063694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_2134-2_0_6_line_170 |  | 152 | 153 | 0.0068859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
171 | LV_2134-2_0_6_line_171 |  | 153 | 154 | 0.01729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
172 | LV_2134-2_0_6_line_172 |  | 154 | 155 | 0.036602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
173 | LV_2134-2_0_6_line_173 |  | 155 | 157 | 0.015909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
174 | LV_2134-2_0_6_line_174 |  | 156 | 243 | 0.013073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_2134-2_0_6_line_175 |  | 158 | 159 | 0.011338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_2134-2_0_6_line_176 |  | 160 | 161 | 0.0075094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
177 | LV_2134-2_0_6_line_177 |  | 161 | 162 | 0.0088619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
178 | LV_2134-2_0_6_line_178 |  | 162 | 189 | 0.013979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
179 | LV_2134-2_0_6_line_179 |  | 163 | 164 | 0.018533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_2134-2_0_6_line_180 |  | 165 | 166 | 0.015919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_2134-2_0_6_line_181 |  | 165 | 167 | 0.0040967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_2134-2_0_6_line_182 |  | 166 | 168 | 0.031875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_2134-2_0_6_line_183 |  | 167 | 169 | 0.018215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_2134-2_0_6_line_184 |  | 169 | 209 | 0.013257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_2134-2_0_6_line_185 |  | 170 | 193 | 0.016176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_2134-2_0_6_line_186 |  | 171 | 172 | 0.025527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_2134-2_0_6_line_187 |  | 172 | 261 | 0.014161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_2134-2_0_6_line_188 |  | 173 | 174 | 0.014091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_2134-2_0_6_line_189 |  | 174 | 194 | 0.027504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
190 | LV_2134-2_0_6_line_190 |  | 174 | 191 | 0.015433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
191 | LV_2134-2_0_6_line_191 |  | 175 | 176 | 0.004737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_2134-2_0_6_line_192 |  | 175 | 177 | 0.015687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_2134-2_0_6_line_193 |  | 176 | 178 | 0.0094292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_2134-2_0_6_line_194 |  | 177 | 179 | 0.024278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_2134-2_0_6_line_195 |  | 178 | 180 | 0.0065253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_2134-2_0_6_line_196 |  | 179 | 181 | 0.006701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_2134-2_0_6_line_197 |  | 179 | 182 | 0.010735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_2134-2_0_6_line_198 |  | 180 | 183 | 0.0088328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_2134-2_0_6_line_199 |  | 181 | 184 | 0.025081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_2134-2_0_6_line_200 |  | 181 | 185 | 0.034164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_2134-2_0_6_line_201 |  | 182 | 186 | 6.9959e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_2134-2_0_6_line_202 |  | 183 | 200 | 0.031532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_2134-2_0_6_line_203 |  | 184 | 197 | 0.030825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_2134-2_0_6_line_204 |  | 185 | 198 | 0.029811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_2134-2_0_6_line_205 |  | 186 | 195 | 0.026809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_2134-2_0_6_line_206 |  | 187 | 188 | 0.0034833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_2134-2_0_6_line_207 |  | 188 | 199 | 0.014504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_2134-2_0_6_line_208 |  | 189 | 190 | 0.0035236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
209 | LV_2134-2_0_6_line_209 |  | 190 | 191 | 0.023518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
210 | LV_2134-2_0_6_line_210 |  | 191 | 192 | 0.01362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
211 | LV_2134-2_0_6_line_211 |  | 196 | 202 | 0.0011038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_2134-2_0_6_line_212 |  | 197 | 201 | 0.012473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_2134-2_0_6_line_213 |  | 198 | 267 | 0.027892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_2134-2_0_6_line_214 |  | 199 | 271 | 0.0028813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_2134-2_0_6_line_215 |  | 202 | 203 | 0.013671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_2134-2_0_6_line_216 |  | 203 | 204 | 0.038446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_2134-2_0_6_line_217 |  | 204 | 205 | 0.018182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_2134-2_0_6_line_218 |  | 205 | 206 | 0.020867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_2134-2_0_6_line_219 |  | 207 | 238 | 0.012149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_2134-2_0_6_line_220 |  | 209 | 210 | 0.02495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_2134-2_0_6_line_221 |  | 210 | 261 | 0.00056051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_2134-2_0_6_line_222 |  | 211 | 212 | 0.028475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_2134-2_0_6_line_223 |  | 211 | 213 | 0.014241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_2134-2_0_6_line_224 |  | 212 | 214 | 0.016786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_2134-2_0_6_line_225 |  | 212 | 215 | 0.02328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
226 | LV_2134-2_0_6_line_226 |  | 213 | 216 | 0.015654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_2134-2_0_6_line_227 |  | 213 | 217 | 0.012071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_2134-2_0_6_line_228 |  | 214 | 218 | 0.016585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_2134-2_0_6_line_229 |  | 215 | 219 | 0.027482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_2134-2_0_6_line_230 |  | 216 | 220 | 0.016129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_2134-2_0_6_line_231 |  | 219 | 221 | 0.013354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_2134-2_0_6_line_232 |  | 220 | 222 | 0.019861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_2134-2_0_6_line_233 |  | 221 | 250 | 0.0058022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_2134-2_0_6_line_234 |  | 222 | 223 | 0.0040262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
235 | LV_2134-2_0_6_line_235 |  | 224 | 225 | 0.020068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_2134-2_0_6_line_236 |  | 225 | 226 | 0.042073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_2134-2_0_6_line_237 |  | 226 | 227 | 0.033758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_2134-2_0_6_line_238 |  | 227 | 232 | 0.024779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_2134-2_0_6_line_239 |  | 228 | 229 | 0.029343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_2134-2_0_6_line_240 |  | 229 | 230 | 0.035444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_2134-2_0_6_line_241 |  | 229 | 231 | 0.022584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_2134-2_0_6_line_242 |  | 230 | 232 | 0.017681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_2134-2_0_6_line_243 |  | 231 | 233 | 0.023713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_2134-2_0_6_line_244 |  | 233 | 234 | 0.015212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_2134-2_0_6_line_245 |  | 234 | 266 | 0.014924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
246 | LV_2134-2_0_6_line_246 |  | 235 | 236 | 0.059085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
247 | LV_2134-2_0_6_line_247 |  | 236 | 237 | 0.034447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
248 | LV_2134-2_0_6_line_248 |  | 238 | 239 | 0.017564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
249 | LV_2134-2_0_6_line_249 |  | 238 | 240 | 0.013709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
250 | LV_2134-2_0_6_line_250 |  | 239 | 241 | 0.013374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_2134-2_0_6_line_251 |  | 240 | 242 | 0.0026936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
252 | LV_2134-2_0_6_line_252 |  | 241 | 248 | 0.0068495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_2134-2_0_6_line_253 |  | 242 | 244 | 0.019073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_2134-2_0_6_line_254 |  | 244 | 245 | 0.0024411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
255 | LV_2134-2_0_6_line_255 |  | 245 | 246 | 0.019618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_2134-2_0_6_line_256 |  | 246 | 247 | 0.00244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_2134-2_0_6_line_257 |  | 247 | 249 | 0.0047774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_2134-2_0_6_line_258 |  | 248 | 259 | 0.01837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
259 | LV_2134-2_0_6_line_259 |  | 249 | 250 | 0.038063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
260 | LV_2134-2_0_6_line_260 |  | 251 | 252 | 0.004015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
261 | LV_2134-2_0_6_line_261 |  | 252 | 253 | 0.05025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_2134-2_0_6_line_262 |  | 254 | 257 | 0.0013739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
263 | LV_2134-2_0_6_line_263 |  | 255 | 256 | 0.027768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
264 | LV_2134-2_0_6_line_264 |  | 256 | 258 | 0.015506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
265 | LV_2134-2_0_6_line_265 |  | 257 | 265 | 0.019662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
266 | LV_2134-2_0_6_line_266 |  | 262 | 263 | 0.034717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
267 | LV_2134-2_0_6_line_267 |  | 263 | 264 | 0.0066751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
268 | LV_2134-2_0_6_line_268 |  | 264 | 266 | 0.019339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
269 | LV_2134-2_0_6_line_269 |  | 268 | 269 | 0.012537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
270 | LV_2134-2_0_6_line_270 |  | 269 | 270 | 0.01878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
271 | LV_2134-2_0_6_line_271 |  | 271 | 272 | 0.012588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2134-2_0_6_trafo_231 | 0.63 MVA 20/0.4 kV | 273 | 194 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2572770.427 | 1154466.3389 | 2572781.7794 | 1154469.8161
1 | 2572744.5345 | 1154458.4082 | 2572770.427 | 1154466.3389
2 | 2572788.7032 | 1154471.9368 | 2572781.7794 | 1154469.8161
3 | 2572744.5345 | 1154458.4082 | 2572729.8909 | 1154488.6924
4 | 2572703.2182 | 1154442.9883 | 2572717.0774 | 1154447.6054 | 2572744.5345 | 1154458.4082
5 | 2572788.7032 | 1154471.9368 | 2572778.9726 | 1154499.3348
6 | 2572788.7032 | 1154471.9368 | 2572805.6953 | 1154475.9325
7 | 2572703.2182 | 1154442.9883 | 2572717.0774 | 1154447.6054 | 2572736.9404 | 1154412.8644
8 | 2572703.2182 | 1154442.9883 | 2572698.2512 | 1154452.2377 | 2572690.3977 | 1154463.6957
9 | 2572679.384 | 1154434.3924 | 2572682.6415 | 1154435.5004 | 2572700.4981 | 1154441.9779 | 2572703.2182 | 1154442.9883
10 | 2572778.9726 | 1154499.3348 | 2572770.9872 | 1154521.8191
11 | 2572805.6953 | 1154475.9325 | 2572825.3336 | 1154480.5505
12 | 2572736.9404 | 1154412.8644 | 2572739.1468 | 1154409.0229
13 | 2572736.9404 | 1154412.8644 | 2572754.4262 | 1154418.7652
14 | 2572690.3977 | 1154463.6957 | 2572676.4032 | 1154484.1131
15 | 2572679.384 | 1154434.3924 | 2572655.6547 | 1154448.2377
16 | 2572758.9818 | 1154555.6224 | 2572770.9872 | 1154521.8191
17 | 2572825.3336 | 1154480.5505 | 2572842.1798 | 1154484.5119 | 2572849.5603 | 1154485.6059
18 | 2572748.3032 | 1154393.0806 | 2572739.1468 | 1154409.0229
19 | 2572765.3688 | 1154422.458 | 2572754.4262 | 1154418.7652
20 | 2572673.9732 | 1154487.6584 | 2572676.4032 | 1154484.1131
21 | 2572643.878 | 1154455.109 | 2572655.6547 | 1154448.2377
22 | 2572962.5661 | 1153844.7705 | 2572961.0708 | 1153845.1388
23 | 2572962.5661 | 1153844.7705 | 2572962.949 | 1153849.7268 | 2572963.6577 | 1153853.7701 | 2572970.8017 | 1153869.4791
24 | 2572970.8017 | 1153869.4791 | 2572991.1825 | 1153860.3717 | 2572998.7306 | 1153877.2573
25 | 2572970.8017 | 1153869.4791 | 2572955.7597 | 1153877.0683
26 | 2573010.1124 | 1153903.9083 | 2573006.4921 | 1153900.6341 | 2573003.595 | 1153896.1337 | 2573001.4113 | 1153891.6302 | 2572999.2057 | 1153885.6594 | 2572998.7306 | 1153877.2573
27 | 2572998.7306 | 1153877.2573 | 2573005.0092 | 1153859.22 | 2573009.9511 | 1153847.592 | 2573018.2493 | 1153835.104 | 2573023.3019 | 1153829.4458
28 | 2573010.1124 | 1153903.9083 | 2573003.8773 | 1153916.2425 | 2572998.6411 | 1153925.5374 | 2572993.754 | 1153932.2796
29 | 2573010.1124 | 1153903.9083 | 2573015.3286 | 1153905.5079 | 2573021.2005 | 1153906.2152
30 | 2572993.754 | 1153932.2796 | 2572990.2011 | 1153937.1812 | 2572973.98 | 1153956.8196 | 2572973.6157 | 1153957.2426
31 | 2572923.6783 | 1153942.9746 | 2572909.1162 | 1153909.4381
32 | 2572928.8709 | 1153954.9331 | 2572923.6783 | 1153942.9746
33 | 2572898.4096 | 1153884.7807 | 2572909.1162 | 1153909.4381
34 | 2572928.8709 | 1153954.9331 | 2572912.0719 | 1153966.3529
35 | 2572928.8709 | 1153954.9331 | 2572948.5304 | 1153979.8902
36 | 2572898.4096 | 1153884.7807 | 2572888.7826 | 1153862.6098
37 | 2572902.317 | 1153972.9842 | 2572912.0719 | 1153966.3529
38 | 2572948.5304 | 1153979.8902 | 2572958.633 | 1153974.6421 | 2572960.5089 | 1153972.4636
39 | 2572948.5304 | 1153979.8902 | 2572948.6529 | 1153998.5546 | 2572956.0945 | 1154012.4601
40 | 2572912.1751 | 1153990.026 | 2572902.317 | 1153972.9842
41 | 2572902.317 | 1153972.9842 | 2572884.6286 | 1153985.0111
42 | 2572960.5089 | 1153972.4636 | 2572973.6157 | 1153957.2426
43 | 2572956.8073 | 1154013.7921 | 2572956.0945 | 1154012.4601
44 | 2572881.4305 | 1153987.1856 | 2572884.6286 | 1153985.0111
45 | 2572956.8073 | 1154013.7921 | 2572940.2854 | 1154021.675
46 | 2572955.9388 | 1154049.1804 | 2572964.3668 | 1154040.0379 | 2572965.5186 | 1154030.0721 | 2572956.8073 | 1154013.7921
47 | 2572777.7628 | 1154341.7724 | 2572765.0334 | 1154363.9425
48 | 2572779.9697 | 1154337.9287 | 2572777.7628 | 1154341.7724
49 | 2572765.0334 | 1154363.9425 | 2572764.9618 | 1154364.0672
50 | 2572787.4683 | 1154324.8688 | 2572779.9697 | 1154337.9287
51 | 2572764.9618 | 1154364.0672 | 2572762.9223 | 1154367.6193
52 | 2572787.4683 | 1154324.8688 | 2572794.6273 | 1154311.7631
53 | 2572822.0072 | 1154340.987 | 2572787.4683 | 1154324.8688
54 | 2572748.3032 | 1154393.0806 | 2572762.9223 | 1154367.6193
55 | 2572794.6273 | 1154311.7631 | 2572780.6612 | 1154303.6408
56 | 2572822.0072 | 1154340.987 | 2572817.0366 | 1154359.5815
57 | 2572822.0072 | 1154340.987 | 2572825.8695 | 1154326.5458
58 | 2572748.3032 | 1154393.0806 | 2572734.5529 | 1154385.699
59 | 2572776.7604 | 1154301.3722 | 2572780.6612 | 1154303.6408
60 | 2572825.8695 | 1154326.5458 | 2572826.4165 | 1154324.5005
61 | 2572781.2002 | 1154427.8005 | 2572807.0524 | 1154436.5248 | 2572808.6694 | 1154436.4684
62 | 2572813.9932 | 1154436.2828 | 2572808.6694 | 1154436.4684
63 | 2572765.3688 | 1154422.458 | 2572781.2002 | 1154427.8005
64 | 2572881.9858 | 1154423.1423 | 2572879.4987 | 1154423.546 | 2572873.6422 | 1154424.1993
65 | 2572897.3205 | 1154420.6529 | 2572881.9858 | 1154423.1423
66 | 2572897.3205 | 1154420.6529 | 2572893.1263 | 1154441.5651
67 | 2572901.7882 | 1154412.8844 | 2572897.3205 | 1154420.6529
68 | 2572910.0717 | 1154386.5966 | 2572912.6742 | 1154379.1295 | 2572917.7938 | 1154369.8312
69 | 2572923.4859 | 1154359.4931 | 2572917.7938 | 1154369.8312
70 | 2572910.0717 | 1154386.5966 | 2572908.3679 | 1154391.4853
71 | 2572923.4859 | 1154359.4931 | 2572922.4706 | 1154335.9505
72 | 2572923.4859 | 1154359.4931 | 2572929.1736 | 1154364.8387
73 | 2572901.7882 | 1154412.8844 | 2572903.9352 | 1154404.2037 | 2572908.3679 | 1154391.4853
74 | 2572921.9811 | 1154324.6014 | 2572922.4706 | 1154335.9505
75 | 2572929.1736 | 1154364.8387 | 2572931.6672 | 1154367.1822 | 2572935.9614 | 1154370.3526
76 | 2572901.7882 | 1154412.8844 | 2572909.8409 | 1154406.8913
77 | 2572921.9811 | 1154324.6014 | 2572921.8931 | 1154322.5621
78 | 2572946.4985 | 1154378.1319 | 2572935.9614 | 1154370.3526
79 | 2572946.4985 | 1154378.1319 | 2572959.9921 | 1154372.8256
80 | 2573020.4527 | 1154109.8747 | 2573012.8504 | 1154117.4024
81 | 2573010.0193 | 1154120.2058 | 2573012.8504 | 1154117.4024
82 | 2573026.1247 | 1154102.1799 | 2573022.8423 | 1154107.5085 | 2573020.4527 | 1154109.8747
83 | 2573010.0193 | 1154120.2058 | 2572998.0521 | 1154131.7903
84 | 2573038.4163 | 1154145.3352 | 2573010.0193 | 1154120.2058
85 | 2573026.1247 | 1154102.1799 | 2573034.2033 | 1154084.3106
86 | 2573026.1247 | 1154102.1799 | 2573011.7824 | 1154090.9165 | 2573004.98 | 1154087.9679 | 2573000.6639 | 1154088.5987 | 2572994.0897 | 1154091.0088
87 | 2572998.0521 | 1154131.7903 | 2572989.348 | 1154140.216
88 | 2573010.6073 | 1154172.4404 | 2573038.4163 | 1154145.3352
89 | 2573038.4163 | 1154145.3352 | 2573041.2718 | 1154147.8621
90 | 2573039.0857 | 1154073.5109 | 2573034.2033 | 1154084.3106
91 | 2572966.2046 | 1154165.2589 | 2572974.541 | 1154154.5493 | 2572989.348 | 1154140.216
92 | 2573053.7811 | 1154158.9322 | 2573041.2718 | 1154147.8621
93 | 2573068.6653 | 1154135.3721 | 2573112.4855 | 1154134.1083
94 | 2573112.4855 | 1154134.1083 | 2573120.1687 | 1154145.3462 | 2573136.4253 | 1154159.3475
95 | 2573046.6947 | 1154061.1978 | 2573042.6075 | 1154065.721 | 2573039.0857 | 1154073.5109
96 | 2572966.2046 | 1154165.2589 | 2572973.3949 | 1154177.0567
97 | 2572966.2046 | 1154165.2589 | 2572963.3322 | 1154166.2415
98 | 2573053.7811 | 1154158.9322 | 2573053.9894 | 1154159.1166
99 | 2572975.6721 | 1154180.793 | 2572973.3949 | 1154177.0567
100 | 2572963.3322 | 1154166.2415 | 2572956.1938 | 1154168.6835 | 2572953.0491 | 1154171.6161
101 | 2572978.1727 | 1154184.896 | 2572975.6721 | 1154180.793
102 | 2572953.0491 | 1154171.6161 | 2572942.8659 | 1154181.1126
103 | 2572933.5482 | 1154129.5326 | 2572947.4879 | 1154102.902
104 | 2572972.7067 | 1154069.226 | 2572959.3697 | 1154080.2027 | 2572947.4879 | 1154102.902
105 | 2572933.5482 | 1154129.5326 | 2572934.3581 | 1154154.8127
106 | 2572972.7067 | 1154069.226 | 2573013.2312 | 1154049.7985
107 | 2572972.7067 | 1154069.226 | 2572955.9388 | 1154049.1804
108 | 2572935.4232 | 1154188.0535 | 2572934.3581 | 1154154.8127
109 | 2573013.2312 | 1154049.7985 | 2573021.1388 | 1154046.0076 | 2573034.1345 | 1154037.8767
110 | 2572955.9388 | 1154049.1804 | 2572926.6257 | 1154072.9583
111 | 2572935.4232 | 1154188.0535 | 2572942.8659 | 1154181.1126
112 | 2573055.196 | 1154024.6995 | 2573034.1345 | 1154037.8767
113 | 2573055.196 | 1154024.6995 | 2573044.7973 | 1154008.5549
114 | 2573055.196 | 1154024.6995 | 2573062.0364 | 1154020.4159
115 | 2572919.6039 | 1154031.5426 | 2572940.2854 | 1154021.675
116 | 2573148.7741 | 1154373.1927 | 2573126.1014 | 1154347.0164
117 | 2573126.1014 | 1154347.0164 | 2573111.7565 | 1154330.4548
118 | 2573101.0519 | 1154318.096 | 2573111.7565 | 1154330.4548
119 | 2573018.8813 | 1154361.0309 | 2573006.7417 | 1154370.3345
120 | 2573018.8813 | 1154361.0309 | 2573016.7074 | 1154353.4356
121 | 2573006.7417 | 1154370.3345 | 2572998.1063 | 1154375.87
122 | 2573006.7417 | 1154370.3345 | 2573014.3945 | 1154379.9494 | 2573014.3945 | 1154379.9494
123 | 2573016.7074 | 1154353.4356 | 2573011.9509 | 1154336.8169
124 | 2573113.9143 | 1154291.992 | 2573101.0519 | 1154318.096
125 | 2573101.0519 | 1154318.096 | 2573087.1682 | 1154336.0096
126 | 2573113.9143 | 1154291.992 | 2573109.0837 | 1154289.0566 | 2573102.7555 | 1154281.81
127 | 2573113.9143 | 1154291.992 | 2573115.9297 | 1154287.9012
128 | 2572776.7604 | 1154301.3722 | 2572710.3453 | 1154298.1945
129 | 2573102.7555 | 1154281.81 | 2573096.1202 | 1154274.2118
130 | 2573130.8944 | 1154257.5275 | 2573115.9297 | 1154287.9012
131 | 2573010.9397 | 1154333.2839 | 2573011.9509 | 1154336.8169
132 | 2573002.6709 | 1154312.9464 | 2573009.9266 | 1154329.7444 | 2573010.9397 | 1154333.2839
133 | 2573082.5682 | 1154258.6931 | 2573096.1202 | 1154274.2118
134 | 2573139.51 | 1154240.0403 | 2573130.8944 | 1154257.5275
135 | 2573032.7442 | 1154240.2192 | 2573060.7427 | 1154233.7001
136 | 2573032.7442 | 1154240.2192 | 2573027.6651 | 1154241.0872
137 | 2573071.928 | 1154246.5087 | 2573060.7427 | 1154233.7001
138 | 2573027.6651 | 1154241.0872 | 2572997.3954 | 1154246.2598
139 | 2572978.1727 | 1154184.896 | 2572982.4029 | 1154191.837
140 | 2573046.6947 | 1154061.1978 | 2573050.1722 | 1154057.3495 | 2573069.9341 | 1154045.5104 | 2573069.9341 | 1154045.5104
141 | 2573069.9341 | 1154045.5104 | 2573075.4105 | 1154040.1609 | 2573082.9539 | 1154031.3985
142 | 2573091.1087 | 1154021.9258 | 2573082.9539 | 1154031.3985
143 | 2573091.1087 | 1154021.9258 | 2573102.0198 | 1154032.7156 | 2573109.4282 | 1154037.3625 | 2573114.3301 | 1154037.3406 | 2573117.8755 | 1154036.8295
144 | 2573091.1087 | 1154021.9258 | 2573098.8758 | 1154012.9003
145 | 2573062.0364 | 1154020.4159 | 2573065.4109 | 1154018.3026
146 | 2573074.681 | 1154009.0527 | 2573067.2293 | 1154017.1639 | 2573065.4109 | 1154018.3026
147 | 2573099.1446 | 1153925.3082 | 2573095.1664 | 1153917.7608
148 | 2573100.8237 | 1153928.5022 | 2573099.1446 | 1153925.3082
149 | 2573079.5172 | 1153934.7342 | 2573083.4153 | 1153928.1245 | 2573092.2951 | 1153927.2732 | 2573099.1446 | 1153925.3082
150 | 2572907.9097 | 1154532.3303 | 2572915.8972 | 1154515.2942 | 2572916.0426 | 1154501.6311
151 | 2572910.3022 | 1154487.4611 | 2572916.0426 | 1154501.6311
152 | 2572896.1587 | 1154557.3932 | 2572907.9097 | 1154532.3303
153 | 2572910.3022 | 1154487.4611 | 2572934.6358 | 1154477.6686 | 2572940.4197 | 1154474.2558
154 | 2572910.3022 | 1154487.4611 | 2572905.0657 | 1154488.3637
155 | 2572956.7533 | 1154464.6179 | 2572940.4197 | 1154474.2558
156 | 2572896.2405 | 1154489.8848 | 2572905.0657 | 1154488.3637
157 | 2572956.7533 | 1154464.6179 | 2572945.5601 | 1154434.4238
158 | 2572880.4126 | 1154489.9306 | 2572889.8371 | 1154490.9886 | 2572896.2405 | 1154489.8848
159 | 2572880.4126 | 1154489.9306 | 2572876.783 | 1154499.8186 | 2572868.8393 | 1154510.7156 | 2572860.8156 | 1154520.0982
160 | 2572880.4126 | 1154489.9306 | 2572873.4746 | 1154489.1505
161 | 2572998.1063 | 1154375.87 | 2572979.6484 | 1154387.702
162 | 2573014.3945 | 1154379.9494 | 2573017.9325 | 1154426.2284
163 | 2572989.1887 | 1154306.8929 | 2572985.397 | 1154313.2131 | 2572984.4665 | 1154321.2102 | 2572984.2881 | 1154331.0048
164 | 2572984.2881 | 1154331.0048 | 2572981.5425 | 1154336.6137
165 | 2573002.6709 | 1154312.9464 | 2572999.508 | 1154307.2911 | 2572989.1887 | 1154306.8929
166 | 2572989.1887 | 1154306.8929 | 2572984.2224 | 1154289.7728
167 | 2572981.5425 | 1154336.6137 | 2572972.6661 | 1154354.7468 | 2572971.864 | 1154357.2073
168 | 2572969.3847 | 1154394.2813 | 2572979.6484 | 1154387.702
169 | 2573017.9325 | 1154426.2284 | 2573018.418 | 1154432.5792
170 | 2572849.5603 | 1154485.6059 | 2572856.3717 | 1154486.6155
171 | 2572873.4746 | 1154489.1505 | 2572856.3717 | 1154486.6155
172 | 2572873.4746 | 1154489.1505 | 2572883.3364 | 1154476.6441 | 2572888.6709 | 1154463.7802 | 2572889.998 | 1154457.1631
173 | 2572893.1263 | 1154441.5651 | 2572889.998 | 1154457.1631
174 | 2572852.3195 | 1154530.0333 | 2572860.8156 | 1154520.0982
175 | 2572710.3453 | 1154298.1945 | 2572704.3309 | 1154307.806
176 | 2572984.0007 | 1154199.0239 | 2572983.4543 | 1154193.562 | 2572982.4029 | 1154191.837
177 | 2572984.8829 | 1154207.8418 | 2572984.0007 | 1154199.0239
178 | 2572986.2744 | 1154221.7515 | 2572984.8829 | 1154207.8418
179 | 2572890.3261 | 1154003.4536 | 2572881.4305 | 1153987.1856
180 | 2573139.51 | 1154240.0403 | 2573128.4374 | 1154228.6032
181 | 2573139.51 | 1154240.0403 | 2573141.3202 | 1154236.3652
182 | 2573128.4374 | 1154228.6032 | 2573106.266 | 1154205.7023
183 | 2573141.3202 | 1154236.3652 | 2573149.3683 | 1154220.025
184 | 2573155.2257 | 1154208.1326 | 2573149.3683 | 1154220.025
185 | 2573082.5682 | 1154258.6931 | 2573071.928 | 1154246.5087
186 | 2573136.4253 | 1154159.3475 | 2573155.7672 | 1154176.0061
187 | 2573166.4974 | 1154185.2477 | 2573155.7672 | 1154176.0061
188 | 2572978.7188 | 1154262.8624 | 2572969.9318 | 1154258.6555 | 2572965.6148 | 1154258.1321
189 | 2572978.7188 | 1154262.8624 | 2572980.5893 | 1154271.0915 | 2572982.6122 | 1154284.2223 | 2572984.2224 | 1154289.7728
190 | 2572983.9704 | 1154248.5539 | 2572983.1747 | 1154254.1269 | 2572978.7188 | 1154262.8624
191 | 2573103.7779 | 1153948.9818 | 2573103.1016 | 1153944.2933
192 | 2573106.0176 | 1153964.5081 | 2573103.7779 | 1153948.9818
193 | 2573103.1016 | 1153944.2933 | 2573101.7553 | 1153934.9607
194 | 2573106.0176 | 1153964.5081 | 2573121.7199 | 1153983.0581
195 | 2573100.8237 | 1153928.5022 | 2573101.7553 | 1153934.9607
196 | 2573124.8078 | 1153977.108 | 2573121.7199 | 1153983.0581
197 | 2573121.7199 | 1153983.0581 | 2573115.4565 | 1153991.777
198 | 2573100.8237 | 1153928.5022 | 2573103.9237 | 1153920.2313
199 | 2573124.8078 | 1153977.108 | 2573136.361 | 1153954.834
200 | 2573124.8078 | 1153977.108 | 2573142.8047 | 1153983.8752 | 2573157.5267 | 1153986.4005
201 | 2573115.4157 | 1153991.8338 | 2573115.4565 | 1153991.777
202 | 2573113.6416 | 1153890.2577 | 2573108.4197 | 1153908.2358 | 2573103.9237 | 1153920.2313
203 | 2573136.361 | 1153954.834 | 2573134.544 | 1153944.8149 | 2573137.0885 | 1153933.9981 | 2573139.0015 | 1153926.0522 | 2573138.7847 | 1153924.7125
204 | 2573179.9794 | 1154003.8112 | 2573175.5767 | 1153995.8124 | 2573162.5738 | 1153987.2663 | 2573157.5267 | 1153986.4005
205 | 2573115.4157 | 1153991.8338 | 2573107.387 | 1154003.0101 | 2573098.8758 | 1154012.9003
206 | 2573079.5172 | 1153934.7342 | 2573077.6091 | 1153937.6484
207 | 2573069.6641 | 1153949.7825 | 2573077.6091 | 1153937.6484
208 | 2572986.2744 | 1154221.7515 | 2572986.6252 | 1154225.2577
209 | 2572983.9704 | 1154248.5539 | 2572986.9003 | 1154228.0082 | 2572986.6252 | 1154225.2577
210 | 2572983.9704 | 1154248.5539 | 2572997.3954 | 1154246.2598
211 | 2573117.8755 | 1154036.8295 | 2573118.968 | 1154036.672
212 | 2573138.7847 | 1153924.7125 | 2573136.7923 | 1153912.3997
213 | 2573194.0734 | 1154027.8672 | 2573187.1008 | 1154016.7492 | 2573179.9794 | 1154003.8112
214 | 2573069.6641 | 1153949.7825 | 2573068.0858 | 1153952.1931
215 | 2573131.8497 | 1154039.8787 | 2573131.7242 | 1154039.7528 | 2573127.2177 | 1154037.2828 | 2573121.4139 | 1154036.3194 | 2573118.968 | 1154036.672
216 | 2573131.8497 | 1154039.8787 | 2573144.7705 | 1154052.8454 | 2573151.5841 | 1154056.5945 | 2573161.9963 | 1154063.261
217 | 2573176.4705 | 1154073.8808 | 2573172.2356 | 1154072.0766 | 2573165.8092 | 1154065.7021 | 2573161.9963 | 1154063.261
218 | 2573176.4705 | 1154073.8808 | 2573177.8277 | 1154082.3011 | 2573181.6932 | 1154094.0182
219 | 2572754.9158 | 1154567.071 | 2572758.9818 | 1154555.6224
220 | 2573155.2257 | 1154208.1326 | 2573166.2497 | 1154185.7505
221 | 2573166.2497 | 1154185.7505 | 2573166.4974 | 1154185.2477
222 | 2572895.3282 | 1154662.1717 | 2572871.9418 | 1154678.4176
223 | 2572860.2459 | 1154686.5424 | 2572871.9418 | 1154678.4176
224 | 2572895.3282 | 1154662.1717 | 2572908.934 | 1154652.3401
225 | 2572895.3282 | 1154662.1717 | 2572881.6757 | 1154643.3155
226 | 2572860.2459 | 1154686.5424 | 2572867.6796 | 1154700.3268
227 | 2572860.2459 | 1154686.5424 | 2572852.3164 | 1154692.0477 | 2572850.3311 | 1154693.4271
228 | 2572908.934 | 1154652.3401 | 2572922.3768 | 1154642.6264
229 | 2572881.6757 | 1154643.3155 | 2572871.6855 | 1154629.5177 | 2572862.4729 | 1154624.5909
230 | 2572867.6796 | 1154700.3268 | 2572881.1287 | 1154691.4228
231 | 2572862.4729 | 1154624.5909 | 2572850.6971 | 1154618.2934
232 | 2572897.689 | 1154680.459 | 2572881.1287 | 1154691.4228
233 | 2572850.6971 | 1154618.2934 | 2572845.5807 | 1154615.5572
234 | 2572897.689 | 1154680.459 | 2572901.0453 | 1154678.2352
235 | 2572953.8249 | 1154578.2957 | 2572946.5825 | 1154597.0115
236 | 2572953.8249 | 1154578.2957 | 2572961.1236 | 1154559.4345 | 2572970.9139 | 1154539.9019
237 | 2572990.3987 | 1154512.557 | 2572975.6213 | 1154530.5103 | 2572970.9139 | 1154539.9019
238 | 2572990.3987 | 1154512.557 | 2573005.8763 | 1154531.9079
239 | 2573045.8854 | 1154566.3789 | 2573063.7614 | 1154589.6482
240 | 2573045.8854 | 1154566.3789 | 2573017.6071 | 1154545.0099
241 | 2573045.8854 | 1154566.3789 | 2573040.9249 | 1154544.3461
242 | 2573017.6071 | 1154545.0099 | 2573014.4437 | 1154542.6194 | 2573005.8763 | 1154531.9079
243 | 2573040.9249 | 1154544.3461 | 2573035.8043 | 1154521.6018 | 2573035.6887 | 1154521.2199
244 | 2573031.2832 | 1154506.66 | 2573035.6887 | 1154521.2199
245 | 2573026.961 | 1154492.3751 | 2573031.2832 | 1154506.66
246 | 2572666.5911 | 1154552.5961 | 2572651.0093 | 1154545.3884 | 2572647.8574 | 1154545.5584 | 2572641.975 | 1154544.1178 | 2572640.1314 | 1154541.8584 | 2572641.4254 | 1154536.2942 | 2572654.7907 | 1154516.2696
247 | 2572673.9732 | 1154487.6584 | 2572670.689 | 1154492.45 | 2572654.7907 | 1154516.2696
248 | 2572754.9158 | 1154567.071 | 2572737.3902 | 1154565.9036
249 | 2572754.9158 | 1154567.071 | 2572767.0049 | 1154573.5361
250 | 2572737.3902 | 1154565.9036 | 2572724.0459 | 1154565.0148
251 | 2572767.0049 | 1154573.5361 | 2572769.3802 | 1154574.8064
252 | 2572717.2116 | 1154564.5595 | 2572724.0459 | 1154565.0148
253 | 2572786.1992 | 1154583.8009 | 2572769.3802 | 1154574.8064
254 | 2572786.1992 | 1154583.8009 | 2572788.3518 | 1154584.9521
255 | 2572788.3518 | 1154584.9521 | 2572805.6513 | 1154594.2036
256 | 2572807.8029 | 1154595.3543 | 2572805.6513 | 1154594.2036
257 | 2572812.0157 | 1154597.6072 | 2572807.8029 | 1154595.3543
258 | 2572699.4876 | 1154560.2614 | 2572711.1718 | 1154564.1572 | 2572717.2116 | 1154564.5595
259 | 2572812.0157 | 1154597.6072 | 2572845.5807 | 1154615.5572
260 | 2572616.9339 | 1154502.1355 | 2572617.5126 | 1154500.3408 | 2572618.5326 | 1154498.4717
261 | 2572643.878 | 1154455.109 | 2572631.0991 | 1154475.4441 | 2572618.5326 | 1154498.4717
262 | 2572961.2707 | 1154372.3228 | 2572959.9921 | 1154372.8256
263 | 2572969.3847 | 1154394.2813 | 2572979.5474 | 1154420.1224
264 | 2572985.2224 | 1154434.5524 | 2572985.2224 | 1154434.5524 | 2572979.5474 | 1154420.1224
265 | 2572971.864 | 1154357.2073 | 2572969.1856 | 1154365.4234 | 2572965.887 | 1154370.5074 | 2572961.2707 | 1154372.3228
266 | 2573020.9693 | 1154467.2014 | 2573020.6541 | 1154461.8289 | 2573018.418 | 1154432.5792
267 | 2573021.3603 | 1154473.865 | 2573020.9693 | 1154467.2014
268 | 2573021.3603 | 1154473.865 | 2573026.961 | 1154492.3751
269 | 2572919.6039 | 1154031.5426 | 2572908.2884 | 1154036.9414
270 | 2572908.2884 | 1154036.9414 | 2572892.5214 | 1154044.4642 | 2572891.4122 | 1154045.161
271 | 2573061.1902 | 1153962.7244 | 2573068.0858 | 1153952.1931

## bus_geodata
| x | y | coords
0 | 2572770.427 | 1154466.3389
1 | 2572781.7794 | 1154469.8161
2 | 2572744.5345 | 1154458.4082
3 | 2572788.7032 | 1154471.9368
4 | 2572729.8909 | 1154488.6924
5 | 2572703.2182 | 1154442.9883
6 | 2572778.9726 | 1154499.3348
7 | 2572805.6953 | 1154475.9325
8 | 2572736.9404 | 1154412.8644
9 | 2572690.3977 | 1154463.6957
10 | 2572679.384 | 1154434.3925
11 | 2572770.9872 | 1154521.8191
12 | 2572825.3336 | 1154480.5505
13 | 2572739.1468 | 1154409.0229
14 | 2572754.4262 | 1154418.7652
15 | 2572676.4032 | 1154484.1131
16 | 2572655.6547 | 1154448.2377
17 | 2572961.0708 | 1153845.1388
18 | 2572962.5661 | 1153844.7705
19 | 2572970.8017 | 1153869.4791
20 | 2572998.7306 | 1153877.2573
21 | 2572955.7597 | 1153877.0683
22 | 2573010.1124 | 1153903.9083
23 | 2573023.3019 | 1153829.4458
24 | 2572993.754 | 1153932.2796
25 | 2573021.2005 | 1153906.2152
26 | 2572923.6783 | 1153942.9746
27 | 2572909.1162 | 1153909.4381
28 | 2572928.8709 | 1153954.9331
29 | 2572898.4096 | 1153884.7807
30 | 2572912.0719 | 1153966.3529
31 | 2572948.5304 | 1153979.8902
32 | 2572888.7826 | 1153862.6098
33 | 2572902.317 | 1153972.9842
34 | 2572960.5089 | 1153972.4636
35 | 2572956.0945 | 1154012.4601
36 | 2572912.1751 | 1153990.026
37 | 2572884.6286 | 1153985.0111
38 | 2572973.6157 | 1153957.2426
39 | 2572956.8073 | 1154013.7921
40 | 2572777.7628 | 1154341.7724
41 | 2572765.0334 | 1154363.9425
42 | 2572779.9697 | 1154337.9287
43 | 2572764.9618 | 1154364.0672
44 | 2572787.4683 | 1154324.8688
45 | 2572762.9223 | 1154367.6193
46 | 2572794.6273 | 1154311.7631
47 | 2572822.0072 | 1154340.987
48 | 2572748.3032 | 1154393.0806
49 | 2572780.6612 | 1154303.6408
50 | 2572817.0366 | 1154359.5815
51 | 2572825.8695 | 1154326.5458
52 | 2572734.5529 | 1154385.699
53 | 2572808.6694 | 1154436.4684
54 | 2572781.2002 | 1154427.8005
55 | 2572813.9932 | 1154436.2828
56 | 2572765.3688 | 1154422.458
57 | 2572873.6422 | 1154424.1993
58 | 2572881.9858 | 1154423.1423
59 | 2572897.3205 | 1154420.6529
60 | 2572826.4165 | 1154324.5005
61 | 2572917.7938 | 1154369.8312
62 | 2572910.0717 | 1154386.5966
63 | 2572923.4859 | 1154359.4931
64 | 2572908.3679 | 1154391.4853
65 | 2572922.4706 | 1154335.9505
66 | 2572929.1736 | 1154364.8387
67 | 2572901.7882 | 1154412.8844
68 | 2572921.9811 | 1154324.6014
69 | 2572935.9614 | 1154370.3526
70 | 2572909.8409 | 1154406.8913
71 | 2572921.8931 | 1154322.5621
72 | 2572946.4985 | 1154378.1319
73 | 2573012.8504 | 1154117.4024
74 | 2573020.4527 | 1154109.8747
75 | 2573010.0193 | 1154120.2058
76 | 2573026.1247 | 1154102.1799
77 | 2572998.0521 | 1154131.7903
78 | 2573038.4163 | 1154145.3352
79 | 2573034.2033 | 1154084.3106
80 | 2572994.0897 | 1154091.0088
81 | 2572989.348 | 1154140.216
82 | 2573010.6073 | 1154172.4404
83 | 2573041.2718 | 1154147.8621
84 | 2573068.6653 | 1154135.3721
85 | 2573112.4855 | 1154134.1083
86 | 2573039.0857 | 1154073.5109
87 | 2572966.2046 | 1154165.2589
88 | 2573053.7811 | 1154158.9322
89 | 2572973.3949 | 1154177.0567
90 | 2572963.3322 | 1154166.2415
91 | 2572975.6721 | 1154180.793
92 | 2572953.0491 | 1154171.6161
93 | 2572947.4879 | 1154102.902
94 | 2572933.5482 | 1154129.5326
95 | 2572972.7067 | 1154069.226
96 | 2572934.3581 | 1154154.8127
97 | 2573013.2312 | 1154049.7985
98 | 2572955.9388 | 1154049.1804
99 | 2572935.4232 | 1154188.0535
100 | 2573034.1345 | 1154037.8767
101 | 2572926.6257 | 1154072.9583
102 | 2572942.8659 | 1154181.1126
103 | 2573055.196 | 1154024.6995
104 | 2572940.2854 | 1154021.675
105 | 2573148.7741 | 1154373.1927
106 | 2573126.1014 | 1154347.0164
107 | 2573111.7565 | 1154330.4548
108 | 2573018.8813 | 1154361.0309
109 | 2573006.7417 | 1154370.3345
110 | 2573016.7074 | 1154353.4356
111 | 2573101.0519 | 1154318.096
112 | 2573113.9143 | 1154291.992
113 | 2573087.1682 | 1154336.0096
114 | 2572776.7604 | 1154301.3722
115 | 2573102.7555 | 1154281.81
116 | 2573115.9297 | 1154287.9012
117 | 2573011.9509 | 1154336.8169
118 | 2573010.9397 | 1154333.2839
119 | 2573096.1202 | 1154274.2118
120 | 2573130.8944 | 1154257.5275
121 | 2573032.7442 | 1154240.2192
122 | 2573060.7427 | 1154233.7001
123 | 2573027.6651 | 1154241.0872
124 | 2572978.1727 | 1154184.896
125 | 2573046.6947 | 1154061.1978
126 | 2573069.9341 | 1154045.5104
127 | 2573082.9539 | 1154031.3985
128 | 2573091.1087 | 1154021.9258
129 | 2573062.0364 | 1154020.4159
130 | 2573065.4109 | 1154018.3026
131 | 2573074.681 | 1154009.0527
132 | 2573044.7973 | 1154008.5549
133 | 2573095.1664 | 1153917.7608
134 | 2573099.1446 | 1153925.3082
135 | 2572916.0426 | 1154501.6311
136 | 2572907.9097 | 1154532.3303
137 | 2572910.3022 | 1154487.4611
138 | 2572896.1587 | 1154557.3932
139 | 2572940.4197 | 1154474.2558
140 | 2572905.0657 | 1154488.3637
141 | 2572956.7533 | 1154464.6179
142 | 2572896.2405 | 1154489.8848
143 | 2572945.5601 | 1154434.4238
144 | 2572880.4126 | 1154489.9306
145 | 2572998.1063 | 1154375.87
146 | 2573014.3945 | 1154379.9494
147 | 2572984.2881 | 1154331.0048
148 | 2572989.1887 | 1154306.8929
149 | 2572981.5425 | 1154336.6137
150 | 2572979.6484 | 1154387.702
151 | 2573017.9325 | 1154426.2284
152 | 2572849.5603 | 1154485.6059
153 | 2572856.3717 | 1154486.6155
154 | 2572873.4746 | 1154489.1505
155 | 2572889.998 | 1154457.1631
156 | 2572860.8156 | 1154520.0982
157 | 2572893.1263 | 1154441.5651
158 | 2572710.3453 | 1154298.1945
159 | 2572704.3309 | 1154307.806
160 | 2572982.4029 | 1154191.837
161 | 2572984.0007 | 1154199.0239
162 | 2572984.8828 | 1154207.8418
163 | 2572881.4305 | 1153987.1856
164 | 2572890.3261 | 1154003.4536
165 | 2573139.51 | 1154240.0403
166 | 2573128.4374 | 1154228.6032
167 | 2573141.3202 | 1154236.3652
168 | 2573106.266 | 1154205.7024
169 | 2573149.3683 | 1154220.025
170 | 2573082.5682 | 1154258.6931
171 | 2573136.4253 | 1154159.3475
172 | 2573155.7672 | 1154176.0061
173 | 2572965.6148 | 1154258.1321
174 | 2572978.7188 | 1154262.8624
175 | 2573103.7779 | 1153948.9818
176 | 2573103.1016 | 1153944.2933
177 | 2573106.0176 | 1153964.5081
178 | 2573101.7553 | 1153934.9607
179 | 2573121.7199 | 1153983.0581
180 | 2573100.8237 | 1153928.5022
181 | 2573124.8078 | 1153977.108
182 | 2573115.4565 | 1153991.777
183 | 2573103.9237 | 1153920.2313
184 | 2573136.361 | 1153954.834
185 | 2573157.5267 | 1153986.4005
186 | 2573115.4157 | 1153991.8338
187 | 2573079.5172 | 1153934.7342
188 | 2573077.6091 | 1153937.6484
189 | 2572986.2744 | 1154221.7515
190 | 2572986.6252 | 1154225.2577
191 | 2572983.9704 | 1154248.5539
192 | 2572997.3954 | 1154246.2598
193 | 2573071.928 | 1154246.5087
194 | 2572984.2224 | 1154289.7728
195 | 2573098.8758 | 1154012.9003
196 | 2573117.8755 | 1154036.8295
197 | 2573138.7847 | 1153924.7125
198 | 2573179.9794 | 1154003.8112
199 | 2573069.6641 | 1153949.7825
200 | 2573113.6416 | 1153890.2577
201 | 2573136.7923 | 1153912.3997
202 | 2573118.968 | 1154036.672
203 | 2573131.8497 | 1154039.8787
204 | 2573161.9963 | 1154063.261
205 | 2573176.4705 | 1154073.8808
206 | 2573181.6932 | 1154094.0182
207 | 2572758.9818 | 1154555.6224
208 | 2573053.9894 | 1154159.1166
209 | 2573155.2257 | 1154208.1326
210 | 2573166.2497 | 1154185.7505
211 | 2572871.9418 | 1154678.4176
212 | 2572895.3282 | 1154662.1717
213 | 2572860.2459 | 1154686.5424
214 | 2572908.934 | 1154652.3401
215 | 2572881.6757 | 1154643.3155
216 | 2572867.6796 | 1154700.3268
217 | 2572850.3311 | 1154693.4271
218 | 2572922.3768 | 1154642.6264
219 | 2572862.4729 | 1154624.5909
220 | 2572881.1287 | 1154691.4228
221 | 2572850.6971 | 1154618.2934
222 | 2572897.689 | 1154680.459
223 | 2572901.0453 | 1154678.2352
224 | 2572946.5825 | 1154597.0115
225 | 2572953.8249 | 1154578.2957
226 | 2572970.9139 | 1154539.9019
227 | 2572990.3987 | 1154512.557
228 | 2573063.7614 | 1154589.6482
229 | 2573045.8854 | 1154566.3789
230 | 2573017.6071 | 1154545.0099
231 | 2573040.9249 | 1154544.3461
232 | 2573005.8763 | 1154531.9079
233 | 2573035.6887 | 1154521.2199
234 | 2573031.2832 | 1154506.66
235 | 2572666.5911 | 1154552.5961
236 | 2572654.7907 | 1154516.2696
237 | 2572673.9732 | 1154487.6584
238 | 2572754.9158 | 1154567.071
239 | 2572737.3902 | 1154565.9036
240 | 2572767.0049 | 1154573.5361
241 | 2572724.0459 | 1154565.0148
242 | 2572769.3802 | 1154574.8064
243 | 2572852.3195 | 1154530.0333
244 | 2572786.1992 | 1154583.8009
245 | 2572788.3518 | 1154584.9521
246 | 2572805.6513 | 1154594.2036
247 | 2572807.8029 | 1154595.3543
248 | 2572717.2116 | 1154564.5595
249 | 2572812.0157 | 1154597.6072
250 | 2572845.5807 | 1154615.5572
251 | 2572616.9339 | 1154502.1355
252 | 2572618.5326 | 1154498.4717
253 | 2572643.878 | 1154455.109
254 | 2572959.9921 | 1154372.8256
255 | 2572969.3847 | 1154394.2813
256 | 2572979.5474 | 1154420.1224
257 | 2572961.2707 | 1154372.3228
258 | 2572985.2224 | 1154434.5524
259 | 2572699.4876 | 1154560.2614
260 | 2573002.6709 | 1154312.9464
261 | 2573166.4974 | 1154185.2477
262 | 2573018.418 | 1154432.5792
263 | 2573020.9693 | 1154467.2014
264 | 2573021.3603 | 1154473.865
265 | 2572971.864 | 1154357.2073
266 | 2573026.961 | 1154492.3751
267 | 2573194.0734 | 1154027.8672
268 | 2572919.6039 | 1154031.5426
269 | 2572908.2884 | 1154036.9414
270 | 2572891.4122 | 1154045.161
271 | 2573068.0858 | 1153952.1931
272 | 2573061.1902 | 1153962.7244
273 | 2572989.1887 | 1154306.8929

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97801 | -0.42212 | 0.0024365 | 0.00061065
1 | 0.97861 | -0.41032 | 0.0013513 | 0.00033866
2 | 0.97669 | -0.44789 | 0 | 0
3 | 0.97899 | -0.40295 | 0 | 0
4 | 0.97659 | -0.4499 | 0.0032672 | 0.00081885
5 | 0.97468 | -0.48737 | 0 | 0
6 | 0.97823 | -0.41778 | 0.0037565 | 0.00094146
7 | 0.9799 | -0.38519 | 0.00076155 | 0.00019086
8 | 0.97292 | -0.5221 | 0 | 0
9 | 0.97445 | -0.49201 | 0.0041595 | 0.0010425
10 | 0.97459 | -0.4892 | 0 | 0
11 | 0.97765 | -0.42916 | 0.0030536 | 0.00076531
12 | 0.98096 | -0.36456 | 0.0050211 | 0.0012584
13 | 0.97282 | -0.52408 | 0.0019677 | 0.00049315
14 | 0.97274 | -0.52562 | 0.0018721 | 0.00046919
15 | 0.97431 | -0.49483 | 0.0019695 | 0.0004936
16 | 0.97449 | -0.49118 | 0.0014839 | 0.00037191
17 | 0.97051 | -0.56933 | 0.0053276 | 0.0013352
18 | 0.97052 | -0.56918 | 0 | 0
19 | 0.97065 | -0.56658 | 0 | 0
20 | 0.97094 | -0.56081 | 0 | 0
21 | 0.97062 | -0.5673 | 0.0023142 | 0.00058
22 | 0.97126 | -0.55448 | 0 | 0
23 | 0.97075 | -0.5646 | 0.0037738 | 0.0009458
24 | 0.97164 | -0.54708 | 0.00046926 | 0.00011761
25 | 0.97125 | -0.55464 | 0.00078536 | 0.00019683
26 | 0.97153 | -0.5492 | 0.0040561 | 0.0010166
27 | 0.97128 | -0.55415 | 0.0020956 | 0.00052521
28 | 0.97167 | -0.54647 | 0 | 0
29 | 0.97115 | -0.55675 | 0.0027072 | 0.00067849
30 | 0.97135 | -0.55286 | 0.0018758 | 0.00047013
31 | 0.97251 | -0.52983 | 0 | 0
32 | 0.97109 | -0.55787 | 0.0025176 | 0.00063097
33 | 0.97118 | -0.55616 | 0 | 0
34 | 0.97229 | -0.53426 | 0.0024954 | 0.00062541
35 | 0.97396 | -0.50115 | 0.0051623 | 0.0012938
36 | 0.97108 | -0.55818 | 0.005542 | 0.001389
37 | 0.97099 | -0.55996 | 0.0043214 | 0.001083
38 | 0.97202 | -0.53957 | 0.0016713 | 0.00041886
39 | 0.97404 | -0.49975 | 0 | 0
40 | 0.97142 | -0.55175 | 0.0013108 | 0.00032851
41 | 0.9718 | -0.54429 | 0.0018458 | 0.00046261
42 | 0.97136 | -0.55294 | 0.0013793 | 0.00034568
43 | 0.9718 | -0.54424 | 0.0016862 | 0.0004226
44 | 0.97118 | -0.55659 | 0 | 0
45 | 0.97187 | -0.54278 | 0.0012709 | 0.00031853
46 | 0.9711 | -0.55814 | 0 | 0
47 | 0.97091 | -0.56186 | 0 | 0
48 | 0.97244 | -0.53162 | 0 | 0
49 | 0.97101 | -0.55982 | 0.001713 | 0.00042931
50 | 0.97086 | -0.56285 | 0.0027784 | 0.00069634
51 | 0.97084 | -0.56317 | 0.0025114 | 0.00062942
52 | 0.97241 | -0.5321 | 0.0016538 | 0.00041449
53 | 0.97241 | -0.53229 | 0.0026305 | 0.00065926
54 | 0.97254 | -0.5297 | 0.0025472 | 0.00063838
55 | 0.97239 | -0.53251 | 0.0022229 | 0.00055711
56 | 0.97265 | -0.52742 | 0.0010769 | 0.00026989
57 | 0.98636 | -0.26007 | 0.0077713 | 0.0019477
58 | 0.98642 | -0.2589 | 0.0025128 | 0.00062976
59 | 0.98656 | -0.25604 | 0 | 0
60 | 0.97084 | -0.56325 | 0.002207 | 0.00055313
61 | 0.98977 | -0.19436 | 0.0016827 | 0.00042172
62 | 0.98868 | -0.21536 | 0.0022245 | 0.00055751
63 | 0.99047 | -0.18089 | 0 | 0
64 | 0.98837 | -0.22116 | 0.0015646 | 0.00039213
65 | 0.99021 | -0.18593 | 0.002157 | 0.0005406
66 | 0.99097 | -0.17143 | 0.0029616 | 0.00074224
67 | 0.98708 | -0.24614 | 0 | 0
68 | 0.99011 | -0.18792 | 0.008736 | 0.0021894
69 | 0.99153 | -0.16068 | 0.0020346 | 0.00050993
70 | 0.98706 | -0.24647 | 0.001857 | 0.0004654
71 | 0.99011 | -0.18796 | 0.0011355 | 0.00028458
72 | 0.99238 | -0.14447 | 0 | 0
73 | 0.98984 | -0.19377 | 0.0028505 | 0.00071441
74 | 0.98965 | -0.19736 | 0.00083545 | 0.00020938
75 | 0.98991 | -0.19237 | 0 | 0
76 | 0.9894 | -0.20213 | 0 | 0
77 | 0.99024 | -0.18591 | 0.0031921 | 0.00080002
78 | 0.9897 | -0.19636 | 0 | 0
79 | 0.98855 | -0.21867 | 0.00057497 | 0.0001441
80 | 0.98912 | -0.20768 | 0.0084184 | 0.0021099
81 | 0.9905 | -0.18099 | 0.0045863 | 0.0011494
82 | 0.98965 | -0.19737 | 0.0014711 | 0.00036869
83 | 0.98969 | -0.19666 | 0.0022082 | 0.00055344
84 | 0.98184 | -0.34973 | 0.003084 | 0.00077292
85 | 0.98197 | -0.34728 | 0.0032297 | 0.00080945
86 | 0.98804 | -0.22856 | 0.001667 | 0.00041778
87 | 0.99126 | -0.1662 | 0 | 0
88 | 0.98965 | -0.19733 | 0.0016372 | 0.00041032
89 | 0.99198 | -0.15255 | 0.0057652 | 0.0014449
90 | 0.99117 | -0.16789 | 0.0010846 | 0.00027184
91 | 0.99221 | -0.14808 | 0.0023329 | 0.00058468
92 | 0.99066 | -0.17766 | 0.0030084 | 0.00075398
93 | 0.98161 | -0.35171 | 0.00284 | 0.00071176
94 | 0.98397 | -0.30591 | 0 | 0
95 | 0.97835 | -0.41522 | 0 | 0
96 | 0.98597 | -0.26754 | 0.002702 | 0.00067718
97 | 0.97798 | -0.42237 | 0.0014538 | 0.00036435
98 | 0.97657 | -0.44992 | 0 | 0
99 | 0.98867 | -0.21573 | 0 | 0
100 | 0.97782 | -0.42557 | 0.0013323 | 0.00033391
101 | 0.97635 | -0.45432 | 0.0063792 | 0.0015988
102 | 0.98949 | -0.19993 | 0.0028142 | 0.0007053
103 | 0.97768 | -0.42827 | 0 | 0
104 | 0.97376 | -0.50514 | 0.0037713 | 0.00094518
105 | 0.98618 | -0.26511 | 0.0038669 | 0.00096913
106 | 0.9863 | -0.26271 | 0.00072395 | 0.00018144
107 | 0.98639 | -0.26091 | 0.0014273 | 0.00035771
108 | 0.99404 | -0.11373 | 0 | 0
109 | 0.99313 | -0.13142 | 0 | 0
110 | 0.99452 | -0.10459 | 0.00037754 | 9.4622e-05
111 | 0.98649 | -0.25914 | 0 | 0
112 | 0.98668 | -0.25539 | 0 | 0
113 | 0.98646 | -0.25963 | 0.0011898 | 0.00029818
114 | 0.971 | -0.56014 | 0.0025264 | 0.00063317
115 | 0.98753 | -0.23894 | 0.0049901 | 0.0012506
116 | 0.98646 | -0.25972 | 0.0026937 | 0.0006751
117 | 0.99556 | -0.084497 | 0.0026445 | 0.00066278
118 | 0.9958 | -0.080061 | 0.0044846 | 0.001124
119 | 0.98813 | -0.22719 | 0.004002 | 0.001003
120 | 0.98488 | -0.29028 | 0.0048464 | 0.0012146
121 | 0.99407 | -0.11279 | 0.0034983 | 0.00087675
122 | 0.99181 | -0.15617 | 0.0055542 | 0.001392
123 | 0.99449 | -0.10471 | 0.0043178 | 0.0010821
124 | 0.99247 | -0.14311 | 0.00097146 | 0.00024347
125 | 0.98743 | -0.24036 | 0.0035266 | 0.00088386
126 | 0.98635 | -0.26135 | 0.0045489 | 0.0011401
127 | 0.9857 | -0.2741 | 0.0013487 | 0.00033802
128 | 0.98529 | -0.2821 | 0 | 0
129 | 0.97765 | -0.42892 | 0.0019547 | 0.0004899
130 | 0.97764 | -0.4291 | 0.0012805 | 0.00032094
131 | 0.97763 | -0.4294 | 0.0012205 | 0.0003059
132 | 0.97766 | -0.42879 | 0.0014894 | 0.00037328
133 | 0.98339 | -0.31903 | 0.00035558 | 8.9118e-05
134 | 0.9834 | -0.31897 | 0 | 0
135 | 0.98189 | -0.34673 | 0.002493 | 0.0006248
136 | 0.9817 | -0.35048 | 0.0033812 | 0.0008474
137 | 0.98201 | -0.34428 | 0 | 0
138 | 0.98162 | -0.35198 | 0.0029957 | 0.00075079
139 | 0.98184 | -0.34763 | 0.0034832 | 0.00087298
140 | 0.98208 | -0.34289 | 0.0047517 | 0.0011909
141 | 0.9818 | -0.34836 | 0 | 0
142 | 0.98224 | -0.33978 | 0.0038167 | 0.00095657
143 | 0.98174 | -0.3496 | 0.0021339 | 0.00053481
144 | 0.98258 | -0.33312 | 0 | 0
145 | 0.9929 | -0.13582 | 0.00098418 | 0.00024666
146 | 0.99266 | -0.14042 | 0.0029141 | 0.00073035
147 | 0.99668 | -0.062688 | 0 | 0
148 | 0.99839 | -0.030362 | 0 | 0
149 | 0.99626 | -0.07071 | 0.0010149 | 0.00025435
150 | 0.99243 | -0.14482 | 0.002839 | 0.00071151
151 | 0.99102 | -0.17209 | 0.0024442 | 0.00061259
152 | 0.98187 | -0.34696 | 0.0021339 | 0.00053481
153 | 0.98212 | -0.34199 | 0.0048591 | 0.0012178
154 | 0.98279 | -0.329 | 0 | 0
155 | 0.98458 | -0.29437 | 0.010604 | 0.0026577
156 | 0.98226 | -0.33951 | 0.0035127 | 0.00088037
157 | 0.98541 | -0.27835 | 0.0067999 | 0.0017042
158 | 0.97091 | -0.56184 | 0 | 0
159 | 0.9709 | -0.56212 | 0.0013757 | 0.00034479
160 | 0.99291 | -0.13467 | 0.0043628 | 0.0010934
161 | 0.99333 | -0.12668 | 0.00086222 | 0.00021609
162 | 0.99383 | -0.11721 | 0.0029829 | 0.00074758
163 | 0.97097 | -0.56034 | 0 | 0
164 | 0.97088 | -0.56215 | 0.0052943 | 0.0013269
165 | 0.98407 | -0.30621 | 0 | 0
166 | 0.9839 | -0.30957 | 0.005812 | 0.0014566
167 | 0.98394 | -0.3087 | 0.0045083 | 0.0011299
168 | 0.98372 | -0.31296 | 0.0059006 | 0.0014788
169 | 0.98345 | -0.3183 | 0.0043132 | 0.001081
170 | 0.98945 | -0.20177 | 0.0056076 | 0.0014054
171 | 0.98217 | -0.34328 | 0.0066674 | 0.001671
172 | 0.98248 | -0.3373 | 0.003663 | 0.00091804
173 | 0.99749 | -0.047602 | 0.0050882 | 0.0012752
174 | 0.99755 | -0.046346 | 0 | 0
175 | 0.98361 | -0.31483 | 0.00057536 | 0.0001442
176 | 0.98355 | -0.31592 | 0.0028199 | 0.00070673
177 | 0.9838 | -0.31107 | 0 | 0
178 | 0.98347 | -0.31761 | 0.0011097 | 0.00027811
179 | 0.9841 | -0.30524 | 0 | 0
180 | 0.98341 | -0.31865 | 0 | 0
181 | 0.98405 | -0.30626 | 0 | 0
182 | 0.98432 | -0.30103 | 0.0013099 | 0.00032829
183 | 0.98338 | -0.31925 | 0.0030455 | 0.00076326
184 | 0.98399 | -0.30737 | 0 | 0
185 | 0.98386 | -0.30995 | 0.0023998 | 0.00060144
186 | 0.98432 | -0.301 | 0.0037451 | 0.00093862
187 | 0.9833 | -0.32096 | 0 | 0
188 | 0.98328 | -0.32126 | 0.0022169 | 0.00055562
189 | 0.99462 | -0.10205 | 0.0045905 | 0.0011505
190 | 0.99483 | -0.098143 | 0.00061057 | 0.00015302
191 | 0.9962 | -0.071992 | 0 | 0
192 | 0.99581 | -0.079534 | 0.0013714 | 0.00034371
193 | 0.99056 | -0.18025 | 0.0049913 | 0.001251
194 | 1 | 0 | -0.59285 | -0.15174
195 | 0.98498 | -0.28807 | 0.0010795 | 0.00027054
196 | 0.98505 | -0.28662 | 0.0017894 | 0.00044846
197 | 0.98392 | -0.30873 | 0.0011611 | 0.000291
198 | 0.98376 | -0.31188 | 0.00076643 | 0.00019208
199 | 0.98325 | -0.32189 | 0.00053978 | 0.00013528
200 | 0.98336 | -0.31968 | 0.00075997 | 0.00019047
201 | 0.98391 | -0.30902 | 0.0012934 | 0.00032416
202 | 0.98505 | -0.28674 | 0.0016205 | 0.00040615
203 | 0.98499 | -0.2878 | 0.0018261 | 0.00045766
204 | 0.98491 | -0.28953 | 0.0011745 | 0.00029436
205 | 0.98488 | -0.28996 | 0 | 0
206 | 0.98486 | -0.29046 | 0.0013221 | 0.00033135
207 | 0.976 | -0.46143 | 0.0019888 | 0.00049843
208 | 0.98965 | -0.19733 | 0.00060905 | 0.00015264
209 | 0.98314 | -0.32425 | 0.0057748 | 0.0014473
210 | 0.9827 | -0.33287 | 0.0025011 | 0.00062684
211 | 0.97125 | -0.55524 | 0.001499 | 0.00037569
212 | 0.97153 | -0.54958 | 0 | 0
213 | 0.97112 | -0.55768 | 0 | 0
214 | 0.97147 | -0.55085 | 0.0022595 | 0.00056628
215 | 0.97186 | -0.54318 | 0.0022133 | 0.00055471
216 | 0.97104 | -0.55935 | 0 | 0
217 | 0.97108 | -0.55847 | 0.0035148 | 0.0008809
218 | 0.97144 | -0.55141 | 0.0018423 | 0.00046173
219 | 0.97229 | -0.53452 | 0.0025717 | 0.00064452
220 | 0.97095 | -0.56107 | 0.0028739 | 0.00072027
221 | 0.97254 | -0.52968 | 0.00075676 | 0.00018966
222 | 0.9709 | -0.56213 | 0 | 0
223 | 0.97089 | -0.56234 | 0.0028827 | 0.00072247
224 | 0.98617 | -0.26632 | 0.001437 | 0.00036014
225 | 0.98619 | -0.26581 | 0.0015254 | 0.0003823
226 | 0.98631 | -0.26357 | 0.0093073 | 0.0023326
227 | 0.98669 | -0.25615 | 0 | 0
228 | 0.98752 | -0.24002 | 0.0054128 | 0.0013566
229 | 0.98766 | -0.23718 | 0 | 0
230 | 0.98719 | -0.24634 | 0.00064004 | 0.00016041
231 | 0.98808 | -0.22917 | 0.0011237 | 0.00028163
232 | 0.98697 | -0.25071 | 0.0015382 | 0.00038552
233 | 0.98853 | -0.22029 | 0.001758 | 0.00044059
234 | 0.98885 | -0.21412 | 0.00042254 | 0.0001059
235 | 0.97409 | -0.4991 | 0.0017013 | 0.0004264
236 | 0.97418 | -0.49725 | 0.0015957 | 0.00039993
237 | 0.97429 | -0.49516 | 0.00092988 | 0.00023305
238 | 0.97547 | -0.47194 | 0 | 0
239 | 0.97536 | -0.47402 | 0.0016939 | 0.00042453
240 | 0.97495 | -0.48219 | 0.0029869 | 0.00074859
241 | 0.9753 | -0.47519 | 0.0016857 | 0.00042248
242 | 0.97485 | -0.48406 | 0.0026816 | 0.00067208
243 | 0.98218 | -0.34098 | 0.0062169 | 0.0015581
244 | 0.97423 | -0.49635 | 0.0018586 | 0.00046581
245 | 0.97415 | -0.49785 | 0.0032486 | 0.00081418
246 | 0.9736 | -0.50867 | 0.0035324 | 0.0008853
247 | 0.97354 | -0.50986 | 0.0031609 | 0.0007922
248 | 0.97529 | -0.47558 | 0.00089933 | 0.00022539
249 | 0.97344 | -0.51191 | 0.0010766 | 0.00026983
250 | 0.97265 | -0.5275 | 0.0018281 | 0.00045816
251 | 0.97434 | -0.4941 | 0.00074725 | 0.00018728
252 | 0.97435 | -0.49405 | 0.0016975 | 0.00042542
253 | 0.97446 | -0.49179 | 0 | 0
254 | 0.99332 | -0.12655 | 0.0045724 | 0.0011459
255 | 0.99221 | -0.14923 | 0 | 0
256 | 0.99169 | -0.15926 | 0.0023321 | 0.00058447
257 | 0.99341 | -0.12482 | 0.0014065 | 0.00035249
258 | 0.99143 | -0.16422 | 0.01806 | 0.0045261
259 | 0.97525 | -0.47631 | 0.0021851 | 0.00054765
260 | 0.99727 | -0.051842 | 0 | 0
261 | 0.98269 | -0.33304 | 0 | 0
262 | 0.99081 | -0.17617 | 0.0031929 | 0.00080021
263 | 0.98976 | -0.19645 | 0.0080308 | 0.0020127
264 | 0.98961 | -0.1994 | 0 | 0
265 | 0.99472 | -0.099891 | 0.0029011 | 0.00072708
266 | 0.98917 | -0.20795 | 0.0016639 | 0.000417
267 | 0.98369 | -0.31331 | 0.0028315 | 0.00070965
268 | 0.9735 | -0.51032 | 0.002625 | 0.0006579
269 | 0.97339 | -0.51254 | 0.0060492 | 0.0015161
270 | 0.97332 | -0.51378 | 0.0035971 | 0.00090151
271 | 0.98324 | -0.32199 | 0.00044187 | 0.00011074
272 | 0.98323 | -0.32232 | 0.0014585 | 0.00036554
273 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.054822 | -0.01383 | 0.054853 | 0.01385 | 3.1001e-05 | 1.9692e-05 | 0.083443 | 0.083443 | 0.083443 | 0.97801 | -0.42212 | 0.97861 | -0.41032 | 22.924
1 | 0.052386 | 0.01322 | -0.052321 | -0.013179 | 6.4564e-05 | 4.0982e-05 | 0.079736 | 0.079737 | 0.079737 | 0.97801 | -0.42212 | 0.97669 | -0.44789 | 21.9056
2 | -0.056205 | -0.014189 | 0.056225 | 0.014201 | 1.985e-05 | 1.2613e-05 | 0.085498 | 0.085498 | 0.085498 | 0.97861 | -0.41032 | 0.97899 | -0.40295 | 23.4885
3 | 0.0032676 | 0.00081863 | -0.0032672 | -0.00081885 | 3.1262e-07 | -2.2087e-07 | 0.0049781 | 0.0049782 | 0.0049782 | 0.97669 | -0.44789 | 0.97659 | -0.4499 | 1.3676
4 | 0.049054 | 0.01236 | -0.048961 | -0.012301 | 9.2455e-05 | 5.862e-05 | 0.074758 | 0.074759 | 0.074759 | 0.97669 | -0.44789 | 0.97468 | -0.48737 | 20.5381
5 | 0.056326 | 0.014218 | -0.056286 | -0.014193 | 3.9992e-05 | 2.4864e-05 | 0.08565 | 0.08565 | 0.08565 | 0.97899 | -0.40295 | 0.97823 | -0.41778 | 11.7651
6 | -0.11255 | -0.028419 | 0.11265 | 0.02848 | 9.5869e-05 | 6.0917e-05 | 0.17115 | 0.17115 | 0.17115 | 0.97899 | -0.40295 | 0.9799 | -0.38519 | 23.5093
7 | 0.034672 | 0.0087216 | -0.034615 | -0.0086855 | 5.7421e-05 | 3.607e-05 | 0.052944 | 0.052944 | 0.052944 | 0.97468 | -0.48737 | 0.97292 | -0.5221 | 14.5452
8 | 0.01036 | 0.002596 | -0.010357 | -0.0025948 | 2.2877e-06 | 1.1602e-06 | 0.015815 | 0.015816 | 0.015816 | 0.97468 | -0.48737 | 0.97445 | -0.49201 | 4.3449
9 | 0.0039297 | 0.00098378 | -0.0039293 | -0.00098387 | 3.4107e-07 | -9.6674e-08 | 0.0059989 | 0.005999 | 0.005999 | 0.97468 | -0.48737 | 0.97459 | -0.4892 | 1.6481
10 | 0.05253 | 0.013251 | -0.052501 | -0.013234 | 2.8586e-05 | 1.7697e-05 | 0.079936 | 0.079936 | 0.079936 | 0.97823 | -0.41778 | 0.97765 | -0.42916 | 10.9802
11 | -0.11341 | -0.028671 | 0.11352 | 0.028742 | 0.0001123 | 7.1364e-05 | 0.1723 | 0.1723 | 0.1723 | 0.9799 | -0.38519 | 0.98096 | -0.36456 | 23.6681
12 | 0.024261 | 0.0060902 | -0.024259 | -0.0060888 | 2.2877e-06 | 1.4091e-06 | 0.037109 | 0.037109 | 0.037109 | 0.97292 | -0.5221 | 0.97282 | -0.52408 | 10.1949
13 | 0.010353 | 0.0025953 | -0.010352 | -0.0025944 | 1.7353e-06 | 8.8146e-07 | 0.015835 | 0.015835 | 0.015835 | 0.97292 | -0.5221 | 0.97274 | -0.52562 | 4.3503
14 | 0.0061978 | 0.0015523 | -0.006197 | -0.0015521 | 8.3139e-07 | 2.2378e-07 | 0.0094639 | 0.009464 | 0.009464 | 0.97445 | -0.49201 | 0.97431 | -0.49483 | 2.6
15 | 0.0039293 | 0.00098387 | -0.003929 | -0.00098398 | 3.7078e-07 | -1.0501e-07 | 0.005999 | 0.0059992 | 0.0059992 | 0.97459 | -0.4892 | 0.97449 | -0.49118 | 1.6481
16 | 0.049448 | 0.012468 | -0.049372 | -0.01242 | 7.625e-05 | 4.8351e-05 | 0.075288 | 0.075288 | 0.075288 | 0.97765 | -0.42916 | 0.976 | -0.46143 | 20.6836
17 | -0.11854 | -0.03 | 0.11864 | 0.030063 | 0.00010022 | 6.32e-05 | 0.17992 | 0.17992 | 0.17992 | 0.98096 | -0.36456 | 0.98187 | -0.34696 | 16.4762
18 | 0.022291 | 0.0055957 | -0.022283 | -0.0055908 | 8.0166e-06 | 4.9024e-06 | 0.0341 | 0.0341 | 0.0341 | 0.97282 | -0.52408 | 0.97244 | -0.53162 | 9.3681
19 | 0.0084796 | 0.0021252 | -0.0084789 | -0.0021249 | 7.2869e-07 | 3.2301e-07 | 0.012971 | 0.012971 | 0.012971 | 0.97274 | -0.52562 | 0.97265 | -0.52742 | 3.5636
20 | 0.0042275 | 0.0010585 | -0.0042274 | -0.0010585 | 6.7181e-08 | -1.053e-08 | 0.0064561 | 0.0064561 | 0.0064561 | 0.97431 | -0.49483 | 0.97429 | -0.49516 | 1.7737
21 | 0.002445 | 0.00061207 | -0.002445 | -0.0006122 | 7.1262e-08 | -1.2426e-07 | 0.0037332 | 0.0037333 | 0.0037333 | 0.97449 | -0.49118 | 0.97446 | -0.49179 | 1.0256
22 | -0.0053276 | -0.0013352 | 0.0053276 | 0.0013352 | 3.8533e-08 | 5.631e-09 | 0.0081684 | 0.0081684 | 0.0081684 | 0.97051 | -0.56933 | 0.97052 | -0.56918 | 2.2441
23 | -0.0053276 | -0.0013352 | 0.0053283 | 0.0013353 | 6.5882e-07 | 9.6223e-08 | 0.0081684 | 0.0081683 | 0.0081684 | 0.97052 | -0.56918 | 0.97065 | -0.56658 | 2.2441
24 | -0.0076426 | -0.0019152 | 0.0076447 | 0.001916 | 2.1011e-06 | 8.4002e-07 | 0.011716 | 0.011716 | 0.011716 | 0.97065 | -0.56658 | 0.97094 | -0.56081 | 3.2187
25 | 0.0023143 | 0.00057984 | -0.0023142 | -0.00058 | 7.9525e-08 | -1.5735e-07 | 0.0035478 | 0.0035479 | 0.0035479 | 0.97065 | -0.56658 | 0.97062 | -0.5673 | 0.97468
26 | -0.011419 | -0.0028616 | 0.011423 | 0.0028634 | 3.4464e-06 | 1.8344e-06 | 0.0175 | 0.0175 | 0.0175 | 0.97094 | -0.56081 | 0.97126 | -0.55448 | 4.8078
27 | 0.0037745 | 0.00094557 | -0.0037738 | -0.0009458 | 6.8151e-07 | -2.3544e-07 | 0.0057844 | 0.0057847 | 0.0057847 | 0.97094 | -0.56081 | 0.97075 | -0.5646 | 1.5892
28 | -0.012208 | -0.0030601 | 0.012212 | 0.0030625 | 4.3048e-06 | 2.3488e-06 | 0.018703 | 0.018703 | 0.018703 | 0.97126 | -0.55448 | 0.97164 | -0.54708 | 5.1383
29 | 0.00078537 | 0.00019669 | -0.00078536 | -0.00019683 | 6.1727e-09 | -1.3677e-07 | 0.0012032 | 0.0012032 | 0.0012032 | 0.97126 | -0.55448 | 0.97125 | -0.55464 | 0.33056
30 | -0.012682 | -0.0031801 | 0.012686 | 0.0031826 | 4.5383e-06 | 2.507e-06 | 0.019422 | 0.019422 | 0.019422 | 0.97164 | -0.54708 | 0.97202 | -0.53957 | 5.3357
31 | 0.0073229 | 0.0018352 | -0.0073212 | -0.0018345 | 1.7248e-06 | 6.5123e-07 | 0.011216 | 0.011216 | 0.011216 | 0.97153 | -0.5492 | 0.97128 | -0.55415 | 3.0813
32 | -0.011379 | -0.0028517 | 0.011381 | 0.0028525 | 1.485e-06 | 7.8894e-07 | 0.017428 | 0.017428 | 0.017428 | 0.97153 | -0.5492 | 0.97167 | -0.54647 | 4.788
33 | 0.0052256 | 0.0013093 | -0.005225 | -0.0013092 | 6.4607e-07 | 8.0828e-08 | 0.0080056 | 0.0080057 | 0.0080057 | 0.97128 | -0.55415 | 0.97115 | -0.55675 | 2.1994
34 | 0.017044 | 0.0042745 | -0.017039 | -0.0042714 | 5.1899e-06 | 3.07e-06 | 0.026102 | 0.026102 | 0.026102 | 0.97167 | -0.54647 | 0.97135 | -0.55286 | 7.1709
35 | -0.028424 | -0.007127 | 0.028447 | 0.007141 | 2.2555e-05 | 1.4041e-05 | 0.04353 | 0.04353 | 0.04353 | 0.97167 | -0.54647 | 0.97251 | -0.52983 | 11.9589
36 | 0.0025177 | 0.00063076 | -0.0025176 | -0.00063097 | 1.3489e-07 | -2.1272e-07 | 0.0038576 | 0.0038578 | 0.0038578 | 0.97115 | -0.55675 | 0.97109 | -0.55787 | 1.0598
37 | 0.015163 | 0.0038013 | -0.01516 | -0.0037999 | 2.3867e-06 | 1.3815e-06 | 0.023229 | 0.023229 | 0.023229 | 0.97135 | -0.55286 | 0.97118 | -0.55616 | 6.3815
38 | 0.01686 | 0.004231 | -0.016856 | -0.0042289 | 3.5591e-06 | 2.1009e-06 | 0.025799 | 0.025799 | 0.025799 | 0.97251 | -0.52983 | 0.97229 | -0.53426 | 7.0877
39 | -0.045307 | -0.011372 | 0.045369 | 0.011411 | 6.207e-05 | 3.9297e-05 | 0.069329 | 0.069329 | 0.069329 | 0.97251 | -0.52983 | 0.97396 | -0.50115 | 19.0465
40 | 0.0055426 | 0.0013891 | -0.005542 | -0.001389 | 5.3215e-07 | 9.7119e-08 | 0.0084922 | 0.0084923 | 0.0084923 | 0.97118 | -0.55616 | 0.97108 | -0.55818 | 2.333
41 | 0.0096179 | 0.0024108 | -0.0096162 | -0.00241 | 1.7419e-06 | 8.5021e-07 | 0.014736 | 0.014737 | 0.014737 | 0.97118 | -0.55616 | 0.97099 | -0.55996 | 4.0485
42 | 0.014361 | 0.0036035 | -0.014357 | -0.0036014 | 3.6391e-06 | 2.08e-06 | 0.02198 | 0.02198 | 0.02198 | 0.97229 | -0.53426 | 0.97202 | -0.53957 | 6.0385
43 | -0.050531 | -0.012705 | 0.050535 | 0.012707 | 3.3778e-06 | 2.143e-06 | 0.077216 | 0.077216 | 0.077216 | 0.97396 | -0.50115 | 0.97404 | -0.49975 | 21.2132
44 | 0.0052948 | 0.0013269 | -0.0052947 | -0.0013269 | 9.5487e-08 | 1.3276e-08 | 0.0081142 | 0.0081142 | 0.0081142 | 0.97099 | -0.55996 | 0.97097 | -0.56034 | 2.2292
45 | 0.016051 | 0.0040251 | -0.016047 | -0.0040227 | 4.1279e-06 | 2.4141e-06 | 0.024522 | 0.024522 | 0.024522 | 0.97404 | -0.49975 | 0.97376 | -0.50514 | 6.7368
46 | -0.066586 | -0.016732 | 0.066744 | 0.016834 | 0.00015879 | 0.00010111 | 0.10174 | 0.10174 | 0.10174 | 0.97404 | -0.49975 | 0.97657 | -0.44992 | 27.9499
47 | -0.015808 | -0.0039619 | 0.015814 | 0.0039652 | 5.6214e-06 | 3.2811e-06 | 0.024215 | 0.024215 | 0.024215 | 0.97142 | -0.55175 | 0.9718 | -0.54429 | 6.6525
48 | 0.014498 | 0.0036334 | -0.014497 | -0.0036329 | 8.1969e-07 | 4.6973e-07 | 0.022207 | 0.022207 | 0.022207 | 0.97142 | -0.55175 | 0.97136 | -0.55294 | 6.1009
49 | -0.01766 | -0.0044278 | 0.01766 | 0.0044278 | 3.9439e-08 | 2.3459e-08 | 0.027041 | 0.027041 | 0.027041 | 0.9718 | -0.54429 | 0.9718 | -0.54424 | 7.429
50 | 0.013118 | 0.0032873 | -0.013115 | -0.003286 | 2.2804e-06 | 1.273e-06 | 0.020095 | 0.020095 | 0.020095 | 0.97136 | -0.55294 | 0.97118 | -0.55659 | 5.5205
51 | -0.019346 | -0.0048504 | 0.019347 | 0.0048513 | 1.3479e-06 | 8.119e-07 | 0.029623 | 0.029623 | 0.029623 | 0.9718 | -0.54424 | 0.97187 | -0.54278 | 8.1383
52 | 0.0056161 | 0.0014065 | -0.0056157 | -0.0014065 | 4.1441e-07 | 8.0547e-08 | 0.0086045 | 0.0086046 | 0.0086046 | 0.97118 | -0.55659 | 0.9711 | -0.55814 | 2.3639
53 | 0.0074992 | 0.0018794 | -0.0074973 | -0.0018787 | 1.8826e-06 | 7.3447e-07 | 0.01149 | 0.01149 | 0.01149 | 0.97118 | -0.55659 | 0.97091 | -0.56186 | 3.1567
54 | -0.020618 | -0.0051698 | 0.020629 | 0.0051764 | 1.0973e-05 | 6.6585e-06 | 0.031569 | 0.031569 | 0.031569 | 0.97187 | -0.54278 | 0.97244 | -0.53162 | 8.6729
55 | 0.0056157 | 0.0014065 | -0.0056153 | -0.0014064 | 4.4858e-07 | 8.7224e-08 | 0.0086046 | 0.0086047 | 0.0086047 | 0.9711 | -0.55814 | 0.97101 | -0.55982 | 2.3639
56 | 0.0027785 | 0.00069618 | -0.0027784 | -0.00069634 | 1.3089e-07 | -1.5426e-07 | 0.0042583 | 0.0042584 | 0.0042584 | 0.97091 | -0.56186 | 0.97086 | -0.56285 | 1.1699
57 | 0.0047187 | 0.0011825 | -0.0047184 | -0.0011825 | 2.9319e-07 | 2.7788e-09 | 0.0072319 | 0.007232 | 0.007232 | 0.97091 | -0.56186 | 0.97084 | -0.56317 | 1.9868
58 | 0.0016539 | 0.00041432 | -0.0016538 | -0.00041449 | 3.7482e-08 | -1.6962e-07 | 0.0025307 | 0.0025307 | 0.0025307 | 0.97244 | -0.53162 | 0.97241 | -0.5321 | 0.69526
59 | 0.0039023 | 0.00097706 | -0.0039022 | -0.00097708 | 6.0507e-08 | -1.7093e-08 | 0.0059797 | 0.0059797 | 0.0059797 | 0.97101 | -0.55982 | 0.971 | -0.56014 | 1.6428
60 | 0.002207 | 0.00055311 | -0.002207 | -0.00055313 | 9.0852e-09 | -2.0366e-08 | 0.0033827 | 0.0033827 | 0.0033827 | 0.97084 | -0.56317 | 0.97084 | -0.56325 | 0.92931
61 | -0.0048534 | -0.0012163 | 0.004854 | 0.0012163 | 5.9782e-07 | 2.4012e-08 | 0.0074268 | 0.0074267 | 0.0074268 | 0.97241 | -0.53229 | 0.97254 | -0.5297 | 2.0403
62 | 0.0022229 | 0.00055706 | -0.0022229 | -0.00055711 | 2.3114e-08 | -5.1289e-08 | 0.0034016 | 0.0034016 | 0.0034016 | 0.97241 | -0.53229 | 0.97239 | -0.53251 | 0.93451
63 | -0.0074012 | -0.0018547 | 0.007402 | 0.001855 | 8.0346e-07 | 3.0686e-07 | 0.011324 | 0.011324 | 0.011324 | 0.97254 | -0.5297 | 0.97265 | -0.52742 | 3.111
64 | -0.0077713 | -0.0019477 | 0.0077717 | 0.0019478 | 4.336e-07 | 1.7012e-07 | 0.011724 | 0.011724 | 0.011724 | 0.98636 | -0.26007 | 0.98642 | -0.2589 | 3.2208
65 | -0.010284 | -0.0025776 | 0.010286 | 0.0025783 | 1.4022e-06 | 6.9907e-07 | 0.015514 | 0.015514 | 0.015514 | 0.98642 | -0.2589 | 0.98656 | -0.25604 | 4.2622
66 | 0.17654 | 0.044846 | -0.17635 | -0.044726 | 0.00018933 | 0.00012036 | 0.26649 | 0.26649 | 0.26649 | 0.98656 | -0.25604 | 0.98541 | -0.27835 | 24.4036
67 | -0.18683 | -0.047424 | 0.18691 | 0.047481 | 8.9038e-05 | 5.6641e-05 | 0.282 | 0.282 | 0.282 | 0.98656 | -0.25604 | 0.98708 | -0.24614 | 25.8243
68 | 0.19304 | 0.049199 | -0.19284 | -0.049074 | 0.00019539 | 0.00012434 | 0.2905 | 0.2905 | 0.2905 | 0.98977 | -0.19436 | 0.98868 | -0.21536 | 26.6029
69 | -0.19472 | -0.04962 | 0.19485 | 0.049701 | 0.00012667 | 8.0615e-05 | 0.29303 | 0.29303 | 0.29303 | 0.98977 | -0.19436 | 0.99047 | -0.18089 | 26.8345
70 | 0.19062 | 0.048517 | -0.19056 | -0.048483 | 5.3362e-05 | 3.3953e-05 | 0.28716 | 0.28716 | 0.28716 | 0.98868 | -0.21536 | 0.98837 | -0.22116 | 26.2963
71 | 0.012032 | 0.0030166 | -0.012029 | -0.0030151 | 2.8876e-06 | 1.5449e-06 | 0.018077 | 0.018077 | 0.018077 | 0.99047 | -0.18089 | 0.99021 | -0.18593 | 4.9662
72 | -0.20688 | -0.052718 | 0.20697 | 0.052778 | 9.4435e-05 | 6.0137e-05 | 0.31111 | 0.31111 | 0.31111 | 0.99047 | -0.18089 | 0.99097 | -0.17143 | 28.4899
73 | 0.189 | 0.048091 | -0.18877 | -0.047946 | 0.00022722 | 0.00014456 | 0.2848 | 0.2848 | 0.2848 | 0.98837 | -0.22116 | 0.98708 | -0.24614 | 26.0806
74 | 0.0098724 | 0.0024745 | -0.0098715 | -0.002474 | 9.3758e-07 | 4.5394e-07 | 0.014836 | 0.014836 | 0.014836 | 0.99021 | -0.18593 | 0.99011 | -0.18792 | 4.0757
75 | -0.20993 | -0.05352 | 0.21004 | 0.053589 | 0.00010903 | 6.9442e-05 | 0.31556 | 0.31556 | 0.31556 | 0.99097 | -0.17143 | 0.99153 | -0.16068 | 28.8971
76 | 0.001857 | 0.00046529 | -0.001857 | -0.0004654 | 2.9499e-08 | -1.0943e-07 | 0.0027994 | 0.0027994 | 0.0027994 | 0.98708 | -0.24614 | 0.98706 | -0.24647 | 0.76907
77 | 0.0011355 | 0.00028456 | -0.0011355 | -0.00028458 | 2.229e-09 | -2.4825e-08 | 0.0017065 | 0.0017065 | 0.0017065 | 0.99011 | -0.18792 | 0.99011 | -0.18796 | 0.46882
78 | -0.21208 | -0.054099 | 0.21224 | 0.054205 | 0.0001662 | 0.00010586 | 0.31861 | 0.31861 | 0.31861 | 0.99153 | -0.16068 | 0.99238 | -0.14447 | 29.1767
79 | -0.21224 | -0.054205 | 0.21243 | 0.054322 | 0.00018398 | 0.00011719 | 0.31861 | 0.31861 | 0.31861 | 0.99238 | -0.14447 | 0.99332 | -0.12655 | 29.1767
80 | 0.056792 | 0.014314 | -0.056783 | -0.014308 | 9.7544e-06 | 5.8303e-06 | 0.085404 | 0.085405 | 0.085405 | 0.98984 | -0.19377 | 0.98965 | -0.19736 | 7.8209
81 | -0.059643 | -0.015029 | 0.059647 | 0.015031 | 4.0062e-06 | 2.4103e-06 | 0.08969 | 0.08969 | 0.08969 | 0.98984 | -0.19377 | 0.98991 | -0.19237 | 8.2133
82 | 0.055947 | 0.014099 | -0.055934 | -0.014091 | 1.2774e-05 | 7.9282e-06 | 0.084148 | 0.084149 | 0.084149 | 0.98965 | -0.19736 | 0.9894 | -0.20213 | 11.5589
83 | -0.065574 | -0.016516 | 0.065594 | 0.016528 | 2.024e-05 | 1.2311e-05 | 0.098599 | 0.098598 | 0.098599 | 0.98991 | -0.19237 | 0.99024 | -0.18591 | 9.0292
84 | 0.0059269 | 0.0014847 | -0.0059258 | -0.0014845 | 1.1269e-06 | 2.346e-07 | 0.008909 | 0.0089092 | 0.0089092 | 0.98991 | -0.19237 | 0.9897 | -0.19636 | 2.4476
85 | 0.047514 | 0.01198 | -0.047476 | -0.011956 | 3.7579e-05 | 2.3799e-05 | 0.071484 | 0.071484 | 0.071484 | 0.9894 | -0.20213 | 0.98855 | -0.21867 | 19.6385
86 | 0.0084207 | 0.0021108 | -0.0084184 | -0.0021099 | 2.2263e-06 | 9.4958e-07 | 0.012664 | 0.012665 | 0.012665 | 0.9894 | -0.20213 | 0.98912 | -0.20768 | 3.4793
87 | -0.068786 | -0.017328 | 0.068803 | 0.017338 | 1.6188e-05 | 9.8929e-06 | 0.1034 | 0.10339 | 0.1034 | 0.99024 | -0.18591 | 0.9905 | -0.18099 | 9.4684
88 | 0.0014712 | 0.00036824 | -0.0014711 | -0.00036869 | 7.1144e-08 | -4.5278e-07 | 0.0022117 | 0.0022119 | 0.0022119 | 0.9897 | -0.19636 | 0.98965 | -0.19737 | 0.60767
89 | 0.0044546 | 0.0011162 | -0.0044546 | -0.0011162 | 6.414e-08 | -7.9496e-09 | 0.0066975 | 0.0066975 | 0.0066975 | 0.9897 | -0.19636 | 0.98969 | -0.19666 | 1.84
90 | 0.046901 | 0.011812 | -0.046879 | -0.011798 | 2.2165e-05 | 1.4034e-05 | 0.070619 | 0.070619 | 0.070619 | 0.98855 | -0.21867 | 0.98804 | -0.22856 | 19.4008
91 | -0.073389 | -0.018487 | 0.073441 | 0.018519 | 5.1965e-05 | 3.1937e-05 | 0.11028 | 0.11028 | 0.11028 | 0.9905 | -0.18099 | 0.99126 | -0.1662 | 10.0993
92 | 0.0022463 | 0.00056279 | -0.0022463 | -0.00056296 | 7.1452e-08 | -1.6891e-07 | 0.0033773 | 0.0033774 | 0.0033774 | 0.98969 | -0.19666 | 0.98965 | -0.19733 | 0.92786
93 | -0.003084 | -0.00077292 | 0.0030843 | 0.0007726 | 3.5911e-07 | -3.2467e-07 | 0.0046739 | 0.0046737 | 0.0046739 | 0.98184 | -0.34973 | 0.98197 | -0.34728 | 1.284
94 | -0.0063141 | -0.001582 | 0.0063153 | 0.0015824 | 1.2038e-06 | 3.2674e-07 | 0.0095679 | 0.0095677 | 0.0095679 | 0.98197 | -0.34728 | 0.98217 | -0.34328 | 2.6285
95 | 0.045212 | 0.01138 | -0.045187 | -0.011364 | 2.5476e-05 | 1.6117e-05 | 0.068108 | 0.068108 | 0.068108 | 0.98804 | -0.22856 | 0.98743 | -0.24036 | 18.7111
96 | -0.16891 | -0.043 | 0.16902 | 0.04307 | 0.00011124 | 7.0658e-05 | 0.25379 | 0.25379 | 0.25379 | 0.99126 | -0.1662 | 0.99198 | -0.15255 | 23.241
97 | 0.095468 | 0.024481 | -0.09546 | -0.024476 | 7.8153e-06 | 4.8844e-06 | 0.14351 | 0.14351 | 0.14351 | 0.99126 | -0.1662 | 0.99117 | -0.16789 | 13.1418
98 | 0.00060905 | 0.00015264 | -0.00060905 | -0.00015264 | 8.7306e-11 | -3.5174e-09 | 0.00091574 | 0.00091574 | 0.00091574 | 0.98965 | -0.19733 | 0.98965 | -0.19733 | 0.25158
99 | -0.17479 | -0.044515 | 0.17482 | 0.044539 | 3.7671e-05 | 2.394e-05 | 0.26244 | 0.26244 | 0.26244 | 0.99198 | -0.15255 | 0.99221 | -0.14808 | 24.0329
100 | 0.094375 | 0.024204 | -0.094331 | -0.024175 | 4.4705e-05 | 2.8306e-05 | 0.14188 | 0.14188 | 0.14188 | 0.99117 | -0.16789 | 0.99066 | -0.17766 | 19.489
101 | -0.17716 | -0.045124 | 0.1772 | 0.045151 | 4.2477e-05 | 2.6999e-05 | 0.26594 | 0.26594 | 0.26594 | 0.99221 | -0.14808 | 0.99247 | -0.14311 | 24.3533
102 | 0.091322 | 0.023421 | -0.091224 | -0.023359 | 9.8521e-05 | 6.2874e-05 | 0.13736 | 0.13736 | 0.13736 | 0.99066 | -0.17766 | 0.98949 | -0.19993 | 37.7366
103 | -0.085073 | -0.021571 | 0.085261 | 0.021691 | 0.00018773 | 0.00011976 | 0.12905 | 0.12905 | 0.12905 | 0.98161 | -0.35171 | 0.98397 | -0.30591 | 35.4539
104 | 0.082233 | 0.02086 | -0.081983 | -0.0207 | 0.00025032 | 0.00015966 | 0.12475 | 0.12475 | 0.12475 | 0.98161 | -0.35171 | 0.97835 | -0.41522 | 34.2712
105 | -0.085261 | -0.021691 | 0.085419 | 0.021792 | 0.00015796 | 0.00010078 | 0.12905 | 0.12905 | 0.12905 | 0.98397 | -0.30591 | 0.98597 | -0.26754 | 35.4538
106 | 0.0087364 | 0.0021898 | -0.0087334 | -0.0021884 | 2.9756e-06 | 1.3403e-06 | 0.013288 | 0.013288 | 0.013288 | 0.97835 | -0.41522 | 0.97798 | -0.42237 | 3.6505
107 | 0.073247 | 0.01851 | -0.073125 | -0.018433 | 0.00012163 | 7.7513e-05 | 0.11146 | 0.11146 | 0.11146 | 0.97835 | -0.41522 | 0.97657 | -0.44992 | 30.6208
108 | -0.088121 | -0.022469 | 0.088342 | 0.02261 | 0.00022104 | 0.00014104 | 0.13313 | 0.13313 | 0.13313 | 0.98597 | -0.26754 | 0.98867 | -0.21573 | 36.5741
109 | 0.0072796 | 0.0018241 | -0.0072785 | -0.0018237 | 1.1086e-06 | 4.0719e-07 | 0.011076 | 0.011076 | 0.011076 | 0.97798 | -0.42237 | 0.97782 | -0.42557 | 3.0429
110 | 0.0063806 | 0.0015992 | -0.0063792 | -0.0015988 | 1.3379e-06 | 3.841e-07 | 0.0097222 | 0.0097223 | 0.0097223 | 0.97657 | -0.44992 | 0.97635 | -0.45432 | 2.671
111 | -0.088342 | -0.02261 | 0.08841 | 0.022653 | 6.7639e-05 | 4.3158e-05 | 0.13313 | 0.13313 | 0.13313 | 0.98867 | -0.21573 | 0.98949 | -0.19993 | 36.574
112 | 0.0059462 | 0.0014898 | -0.0059454 | -0.0014896 | 7.6281e-07 | 1.7661e-07 | 0.0090486 | 0.0090487 | 0.0090487 | 0.97782 | -0.42557 | 0.97768 | -0.42827 | 2.4859
113 | 0.0014894 | 0.00037306 | -0.0014894 | -0.00037328 | 3.7006e-08 | -2.1713e-07 | 0.0022668 | 0.0022669 | 0.0022669 | 0.97768 | -0.42827 | 0.97766 | -0.42879 | 0.62278
114 | 0.004456 | 0.0011165 | -0.0044558 | -0.0011165 | 1.392e-07 | -1.2117e-08 | 0.0067818 | 0.0067819 | 0.0067819 | 0.97768 | -0.42827 | 0.97765 | -0.42892 | 1.8632
115 | 0.012276 | 0.0030775 | -0.012273 | -0.0030759 | 3.0239e-06 | 1.6503e-06 | 0.018759 | 0.018759 | 0.018759 | 0.97376 | -0.50514 | 0.9735 | -0.51032 | 5.1536
116 | -0.0038669 | -0.00096913 | 0.0038673 | 0.00096897 | 4.4207e-07 | -1.5898e-07 | 0.0058346 | 0.0058344 | 0.0058346 | 0.98618 | -0.26511 | 0.9863 | -0.26271 | 1.6029
117 | -0.0045913 | -0.0011504 | 0.0045916 | 0.0011504 | 3.942e-07 | -2.7364e-08 | 0.0069266 | 0.0069265 | 0.0069266 | 0.9863 | -0.26271 | 0.98639 | -0.26091 | 1.9029
118 | -0.0060189 | -0.0015081 | 0.0060194 | 0.0015082 | 5.0546e-07 | 1.1477e-07 | 0.0090797 | 0.0090796 | 0.0090797 | 0.98639 | -0.26091 | 0.98649 | -0.25914 | 2.4944
119 | 0.065892 | 0.016611 | -0.065836 | -0.016576 | 5.5742e-05 | 3.5477e-05 | 0.09867 | 0.09867 | 0.09867 | 0.99404 | -0.11373 | 0.99313 | -0.13142 | 27.1071
120 | -0.065892 | -0.016611 | 0.06592 | 0.016629 | 2.8843e-05 | 1.8357e-05 | 0.09867 | 0.09867 | 0.09867 | 0.99404 | -0.11373 | 0.99452 | -0.10459 | 27.107
121 | 0.024248 | 0.006089 | -0.024243 | -0.0060859 | 5.0784e-06 | 3.1175e-06 | 0.036336 | 0.036336 | 0.036336 | 0.99313 | -0.13142 | 0.9929 | -0.13582 | 9.9823
122 | 0.041588 | 0.010487 | -0.04157 | -0.010475 | 1.7906e-05 | 1.1301e-05 | 0.062334 | 0.062334 | 0.062334 | 0.99313 | -0.13142 | 0.99266 | -0.14042 | 17.1248
123 | -0.066298 | -0.016724 | 0.066362 | 0.016765 | 6.3834e-05 | 4.0629e-05 | 0.099235 | 0.099234 | 0.099235 | 0.99452 | -0.10459 | 0.99556 | -0.084497 | 27.2622
124 | -0.0072092 | -0.0018061 | 0.0072105 | 0.0018066 | 1.2899e-06 | 4.5408e-07 | 0.010874 | 0.010874 | 0.010874 | 0.98649 | -0.25914 | 0.98668 | -0.25539 | 2.9874
125 | 0.0011898 | 0.00029791 | -0.0011898 | -0.00029818 | 2.7372e-08 | -2.7183e-07 | 0.0017946 | 0.0017947 | 0.0017947 | 0.98649 | -0.25914 | 0.98646 | -0.25963 | 0.49304
126 | -0.060368 | -0.015189 | 0.060415 | 0.015219 | 4.7494e-05 | 3.0201e-05 | 0.091062 | 0.091062 | 0.091062 | 0.98668 | -0.25539 | 0.98753 | -0.23894 | 25.0171
127 | 0.053157 | 0.013382 | -0.053146 | -0.013375 | 1.0996e-05 | 6.9794e-06 | 0.080188 | 0.080188 | 0.080188 | 0.98668 | -0.25539 | 0.98646 | -0.25972 | 22.0297
128 | 0.0013759 | 0.00034391 | -0.0013757 | -0.00034466 | 1.1083e-07 | -7.5145e-07 | 0.0021081 | 0.0021084 | 0.0021084 | 0.971 | -0.56014 | 0.97091 | -0.56184 | 0.57924
129 | -0.065405 | -0.01647 | 0.065442 | 0.016493 | 3.6763e-05 | 2.3399e-05 | 0.098581 | 0.098581 | 0.098581 | 0.98753 | -0.23894 | 0.98813 | -0.22719 | 27.0828
130 | 0.050453 | 0.0127 | -0.050379 | -0.012654 | 7.3582e-05 | 4.6661e-05 | 0.076125 | 0.076125 | 0.076125 | 0.98646 | -0.25972 | 0.98488 | -0.29028 | 20.9135
131 | -0.069006 | -0.017427 | 0.069021 | 0.017437 | 1.4673e-05 | 9.3429e-06 | 0.10319 | 0.10319 | 0.10319 | 0.99556 | -0.084497 | 0.9958 | -0.080061 | 28.3481
132 | -0.073506 | -0.018561 | 0.073605 | 0.018624 | 9.9531e-05 | 6.3413e-05 | 0.10989 | 0.10989 | 0.10989 | 0.9958 | -0.080061 | 0.99727 | -0.051842 | 30.1891
133 | -0.069444 | -0.017496 | 0.069529 | 0.01755 | 8.4545e-05 | 5.3845e-05 | 0.10461 | 0.10461 | 0.10461 | 0.98813 | -0.22719 | 0.98945 | -0.20177 | 28.7384
134 | 0.045533 | 0.011439 | -0.045498 | -0.011417 | 3.4606e-05 | 2.19e-05 | 0.068803 | 0.068803 | 0.068803 | 0.98488 | -0.29028 | 0.98407 | -0.30621 | 18.9019
135 | 0.086031 | 0.021821 | -0.085852 | -0.021707 | 0.00017904 | 0.00011421 | 0.12887 | 0.12887 | 0.12887 | 0.99407 | -0.11279 | 0.99181 | -0.15617 | 35.4043
136 | -0.089529 | -0.022698 | 0.089564 | 0.02272 | 3.4752e-05 | 2.2174e-05 | 0.13411 | 0.13411 | 0.13411 | 0.99407 | -0.11279 | 0.99449 | -0.10471 | 36.8429
137 | 0.080298 | 0.020315 | -0.080205 | -0.020256 | 9.2654e-05 | 5.9079e-05 | 0.12054 | 0.12054 | 0.12054 | 0.99181 | -0.15617 | 0.99056 | -0.18025 | 33.1151
138 | -0.093882 | -0.023802 | 0.093996 | 0.023874 | 0.00011377 | 7.2016e-05 | 0.14057 | 0.14057 | 0.14057 | 0.99449 | -0.10471 | 0.99581 | -0.079534 | 19.3089
139 | -0.17817 | -0.045394 | 0.17824 | 0.045441 | 7.2648e-05 | 4.618e-05 | 0.26739 | 0.26739 | 0.26739 | 0.99247 | -0.14311 | 0.99291 | -0.13467 | 24.4867
140 | 0.04166 | 0.01048 | -0.041618 | -0.010454 | 4.1733e-05 | 2.6349e-05 | 0.062794 | 0.062794 | 0.062794 | 0.98743 | -0.24036 | 0.98635 | -0.26135 | 17.2511
141 | 0.037069 | 0.0093141 | -0.037047 | -0.0092999 | 2.2545e-05 | 1.4184e-05 | 0.055932 | 0.055932 | 0.055932 | 0.98635 | -0.26135 | 0.9857 | -0.2741 | 15.3658
142 | 0.035698 | 0.0089619 | -0.035685 | -0.0089533 | 1.3615e-05 | 8.5545e-06 | 0.053896 | 0.053896 | 0.053896 | 0.9857 | -0.2741 | 0.98529 | -0.2821 | 14.8065
143 | 0.0077348 | 0.0019378 | -0.0077331 | -0.0019371 | 1.6668e-06 | 6.5198e-07 | 0.011681 | 0.011681 | 0.011681 | 0.98529 | -0.2821 | 0.98505 | -0.28662 | 3.2091
144 | 0.02795 | 0.0070155 | -0.027942 | -0.0070106 | 7.9575e-06 | 4.9412e-06 | 0.042215 | 0.042215 | 0.042215 | 0.98529 | -0.2821 | 0.98498 | -0.28807 | 11.5974
145 | 0.0025011 | 0.00062664 | -0.0025011 | -0.00062668 | 2.1637e-08 | -3.6079e-08 | 0.0038067 | 0.0038068 | 0.0038068 | 0.97765 | -0.42892 | 0.97764 | -0.4291 | 1.0458
146 | 0.0012206 | 0.00030574 | -0.0012205 | -0.0003059 | 1.7032e-08 | -1.5411e-07 | 0.0018577 | 0.0018578 | 0.0018578 | 0.97764 | -0.4291 | 0.97763 | -0.4294 | 0.51037
147 | -0.00035558 | -8.9118e-05 | 0.00035558 | 8.901e-05 | 9.2614e-10 | -1.0765e-07 | 0.00053805 | 0.00053801 | 0.00053805 | 0.98339 | -0.31903 | 0.9834 | -0.31897 | 0.14782
148 | -0.0050133 | -0.0012559 | 0.0050134 | 0.0012559 | 7.7833e-08 | 4.049e-09 | 0.0075856 | 0.0075856 | 0.0075856 | 0.9834 | -0.31897 | 0.98341 | -0.31865 | 2.084
149 | 0.0046577 | 0.0011669 | -0.0046573 | -0.0011669 | 4.4181e-07 | -1.815e-08 | 0.0070476 | 0.0070477 | 0.0070477 | 0.9834 | -0.31897 | 0.9833 | -0.32096 | 1.9362
150 | 0.0063782 | 0.0015983 | -0.0063771 | -0.001598 | 1.138e-06 | 3.1757e-07 | 0.0096659 | 0.009666 | 0.009666 | 0.98189 | -0.34673 | 0.9817 | -0.35048 | 2.6555
151 | -0.0088712 | -0.0022231 | 0.0088722 | 0.0022236 | 1.0362e-06 | 4.6978e-07 | 0.013444 | 0.013444 | 0.013444 | 0.98189 | -0.34673 | 0.98201 | -0.34428 | 3.6934
152 | 0.0029959 | 0.00075058 | -0.0029957 | -0.00075079 | 2.1405e-07 | -2.1296e-07 | 0.004541 | 0.0045411 | 0.0045411 | 0.9817 | -0.35048 | 0.98162 | -0.35198 | 1.2476
153 | 0.0056182 | 0.0014074 | -0.0056173 | -0.0014073 | 8.9535e-07 | 1.5628e-07 | 0.0085129 | 0.0085131 | 0.0085131 | 0.98201 | -0.34428 | 0.98184 | -0.34763 | 2.3388
154 | -0.01449 | -0.003631 | 0.014491 | 0.0036315 | 9.6065e-07 | 5.4758e-07 | 0.021957 | 0.021957 | 0.021957 | 0.98201 | -0.34428 | 0.98208 | -0.34289 | 6.0321
155 | 0.0021341 | 0.00053429 | -0.002134 | -0.00053448 | 7.4389e-08 | -1.9224e-07 | 0.0032341 | 0.0032342 | 0.0032342 | 0.98184 | -0.34763 | 0.9818 | -0.34836 | 0.88852
156 | -0.019243 | -0.0048224 | 0.019246 | 0.0048241 | 2.8548e-06 | 1.7137e-06 | 0.029156 | 0.029156 | 0.029156 | 0.98208 | -0.34289 | 0.98224 | -0.33978 | 8.01
157 | 0.002134 | 0.00053448 | -0.0021339 | -0.00053481 | 1.2632e-07 | -3.2636e-07 | 0.0032342 | 0.0032343 | 0.0032343 | 0.9818 | -0.34836 | 0.98174 | -0.3496 | 0.88856
158 | -0.023063 | -0.0057807 | 0.02307 | 0.0057852 | 7.3157e-06 | 4.4797e-06 | 0.034938 | 0.034938 | 0.034938 | 0.98224 | -0.33978 | 0.98258 | -0.33312 | 9.5984
159 | 0.009733 | 0.00244 | -0.00973 | -0.0024386 | 2.9627e-06 | 1.4357e-06 | 0.01474 | 0.01474 | 0.01474 | 0.98258 | -0.33312 | 0.98226 | -0.33951 | 4.0495
160 | -0.032803 | -0.0082252 | 0.032809 | 0.0082292 | 6.4431e-06 | 4.0354e-06 | 0.049678 | 0.049678 | 0.049678 | 0.98258 | -0.33312 | 0.98279 | -0.329 | 13.6478
161 | 0.023259 | 0.0058392 | -0.023249 | -0.0058331 | 9.9916e-06 | 6.1112e-06 | 0.034861 | 0.034861 | 0.034861 | 0.9929 | -0.13582 | 0.99243 | -0.14482 | 9.5771
162 | 0.038656 | 0.0097449 | -0.038597 | -0.009708 | 5.8483e-05 | 3.683e-05 | 0.057966 | 0.057966 | 0.057966 | 0.99266 | -0.14042 | 0.99102 | -0.17209 | 15.9247
163 | -0.22301 | -0.057237 | 0.22336 | 0.05746 | 0.00035043 | 0.00022329 | 0.33342 | 0.33342 | 0.33342 | 0.99668 | -0.062688 | 0.99839 | -0.030362 | 30.533
164 | 0.22301 | 0.057237 | -0.22292 | -0.057182 | 8.678e-05 | 5.5295e-05 | 0.33342 | 0.33342 | 0.33342 | 0.99668 | -0.062688 | 0.99626 | -0.07071 | 30.533
165 | 0.073681 | 0.018673 | -0.073605 | -0.018624 | 7.5957e-05 | 4.8394e-05 | 0.10989 | 0.10989 | 0.10989 | 0.99839 | -0.030362 | 0.99727 | -0.051842 | 30.1891
166 | -0.29704 | -0.076133 | 0.29748 | 0.076412 | 0.0004379 | 0.00027955 | 0.44331 | 0.44331 | 0.44331 | 0.99839 | -0.030362 | 1 | 0 | 40.5959
167 | 0.2219 | 0.056927 | -0.22159 | -0.056727 | 0.00031364 | 0.00019984 | 0.3319 | 0.3319 | 0.3319 | 0.99626 | -0.07071 | 0.99472 | -0.099891 | 30.3942
168 | 0.02041 | 0.0051216 | -0.020406 | -0.005119 | 4.282e-06 | 2.583e-06 | 0.030604 | 0.030604 | 0.030604 | 0.99243 | -0.14482 | 0.99221 | -0.14923 | 8.4077
169 | 0.036153 | 0.0090955 | -0.036146 | -0.009091 | 7.0415e-06 | 4.4245e-06 | 0.054296 | 0.054296 | 0.054296 | 0.99102 | -0.17209 | 0.99081 | -0.17617 | 14.9165
170 | -0.12078 | -0.030598 | 0.1208 | 0.030617 | 2.8874e-05 | 1.8218e-05 | 0.18315 | 0.18315 | 0.18315 | 0.98187 | -0.34696 | 0.98212 | -0.34199 | 16.7723
171 | -0.12566 | -0.031834 | 0.12574 | 0.031884 | 7.8444e-05 | 4.9547e-05 | 0.19052 | 0.19052 | 0.19052 | 0.98212 | -0.34199 | 0.98279 | -0.329 | 17.4465
172 | -0.15855 | -0.040113 | 0.15882 | 0.040281 | 0.00026396 | 0.00016754 | 0.24019 | 0.24019 | 0.24019 | 0.98279 | -0.329 | 0.98458 | -0.29437 | 21.9958
173 | -0.16942 | -0.042938 | 0.16955 | 0.043021 | 0.00013055 | 8.2943e-05 | 0.25622 | 0.25622 | 0.25622 | 0.98458 | -0.29437 | 0.98541 | -0.27835 | 23.4633
174 | 0.0062173 | 0.0015582 | -0.0062169 | -0.0015581 | 4.3487e-07 | 1.1286e-07 | 0.0094186 | 0.0094186 | 0.0094186 | 0.98226 | -0.33951 | 0.98218 | -0.34098 | 2.5875
175 | 0.0013757 | 0.00034466 | -0.0013757 | -0.00034479 | 1.8902e-08 | -1.2812e-07 | 0.0021084 | 0.0021085 | 0.0021085 | 0.97091 | -0.56184 | 0.9709 | -0.56212 | 0.57925
176 | -0.1826 | -0.046534 | 0.18268 | 0.046579 | 7.0437e-05 | 4.4788e-05 | 0.27393 | 0.27393 | 0.27393 | 0.99291 | -0.13467 | 0.99333 | -0.12668 | 25.0854
177 | -0.18354 | -0.046795 | 0.18362 | 0.046848 | 8.391e-05 | 5.3358e-05 | 0.27522 | 0.27522 | 0.27522 | 0.99333 | -0.12668 | 0.99383 | -0.11721 | 25.2037
178 | -0.1866 | -0.047596 | 0.18674 | 0.047683 | 0.00013669 | 8.6939e-05 | 0.27969 | 0.27969 | 0.27969 | 0.99383 | -0.11721 | 0.99462 | -0.10205 | 25.6127
179 | 0.0052947 | 0.0013269 | -0.0052943 | -0.0013269 | 4.5759e-07 | 6.365e-08 | 0.0081142 | 0.0081143 | 0.0081143 | 0.97097 | -0.56034 | 0.97088 | -0.56215 | 2.2292
180 | 0.011715 | 0.0029367 | -0.011714 | -0.0029357 | 1.8734e-06 | 9.9678e-07 | 0.017715 | 0.017715 | 0.017715 | 0.98407 | -0.30621 | 0.9839 | -0.30957 | 4.8668
181 | 0.033783 | 0.0084804 | -0.033779 | -0.0084779 | 4.0096e-06 | 2.5141e-06 | 0.051088 | 0.051088 | 0.051088 | 0.98407 | -0.30621 | 0.98394 | -0.3087 | 14.0351
182 | 0.0059016 | 0.001479 | -0.0059006 | -0.0014788 | 9.5223e-07 | 2.0468e-07 | 0.0089254 | 0.0089255 | 0.0089255 | 0.9839 | -0.30957 | 0.98372 | -0.31296 | 2.4521
183 | 0.02927 | 0.007348 | -0.029257 | -0.0073397 | 1.3387e-05 | 8.3362e-06 | 0.04427 | 0.04427 | 0.04427 | 0.98394 | -0.3087 | 0.98345 | -0.3183 | 12.1621
184 | 0.024944 | 0.0062587 | -0.024937 | -0.0062544 | 7.082e-06 | 4.3643e-06 | 0.037744 | 0.037744 | 0.037744 | 0.98345 | -0.3183 | 0.98314 | -0.32425 | 10.3692
185 | -0.075136 | -0.018955 | 0.075214 | 0.019005 | 7.7514e-05 | 4.9401e-05 | 0.11304 | 0.11304 | 0.11304 | 0.98945 | -0.20177 | 0.99056 | -0.18025 | 31.0552
186 | -0.012983 | -0.0032534 | 0.012986 | 0.0032554 | 3.7033e-06 | 2.0469e-06 | 0.019669 | 0.019669 | 0.019669 | 0.98217 | -0.34328 | 0.98248 | -0.3373 | 5.4036
187 | -0.016649 | -0.0041735 | 0.016653 | 0.0041754 | 3.3769e-06 | 1.9818e-06 | 0.025217 | 0.025217 | 0.025217 | 0.98248 | -0.3373 | 0.98269 | -0.33304 | 6.9277
188 | -0.0050882 | -0.0012752 | 0.0050885 | 0.0012752 | 3.0443e-07 | 1.0893e-08 | 0.0075904 | 0.0075903 | 0.0075904 | 0.99749 | -0.047602 | 0.99755 | -0.046346 | 2.0853
189 | -0.29307 | -0.074906 | 0.29373 | 0.075327 | 0.00065859 | 0.00042042 | 0.43768 | 0.43768 | 0.43768 | 0.99755 | -0.046346 | 1 | 0 | 40.0804
190 | 0.28798 | 0.073631 | -0.28762 | -0.073403 | 0.00035684 | 0.00022777 | 0.43009 | 0.43009 | 0.43009 | 0.99755 | -0.046346 | 0.9962 | -0.071992 | 39.3853
191 | 0.01275 | 0.0031949 | -0.01275 | -0.0031946 | 6.6091e-07 | 3.6286e-07 | 0.019289 | 0.019289 | 0.019289 | 0.98361 | -0.31483 | 0.98355 | -0.31592 | 5.2991
192 | -0.013326 | -0.0033391 | 0.013328 | 0.0033405 | 2.3906e-06 | 1.3309e-06 | 0.020159 | 0.020159 | 0.020159 | 0.98361 | -0.31483 | 0.9838 | -0.31107 | 5.5382
193 | 0.0099299 | 0.0024879 | -0.0099291 | -0.0024875 | 7.9799e-07 | 3.9105e-07 | 0.015023 | 0.015023 | 0.015023 | 0.98355 | -0.31592 | 0.98347 | -0.31761 | 4.1271
194 | -0.013328 | -0.0033405 | 0.013332 | 0.0033425 | 3.6998e-06 | 2.0595e-06 | 0.020159 | 0.020159 | 0.020159 | 0.9838 | -0.31107 | 0.9841 | -0.30524 | 5.5382
195 | 0.0088194 | 0.0022094 | -0.008819 | -0.0022092 | 4.3569e-07 | 1.9605e-07 | 0.013344 | 0.013344 | 0.013344 | 0.98347 | -0.31761 | 0.98341 | -0.31865 | 3.6659
196 | 0.0084545 | 0.0021177 | -0.0084541 | -0.0021175 | 4.1064e-07 | 1.7767e-07 | 0.012783 | 0.012783 | 0.012783 | 0.9841 | -0.30524 | 0.98405 | -0.30626 | 3.5119
197 | -0.021786 | -0.0054602 | 0.021791 | 0.0054629 | 4.3687e-06 | 2.6596e-06 | 0.032942 | 0.032942 | 0.032942 | 0.9841 | -0.30524 | 0.98432 | -0.30103 | 9.0501
198 | 0.0038056 | 0.0009533 | -0.0038054 | -0.00095334 | 1.0982e-07 | -4.1779e-08 | 0.0057581 | 0.0057581 | 0.0057581 | 0.98341 | -0.31865 | 0.98338 | -0.31925 | 1.5819
199 | 0.0024549 | 0.0006145 | -0.0024547 | -0.00061473 | 1.2959e-07 | -2.3568e-07 | 0.0037118 | 0.0037119 | 0.0037119 | 0.98405 | -0.30626 | 0.98399 | -0.30737 | 1.0198
200 | 0.0059993 | 0.001503 | -0.0059982 | -0.0015028 | 1.0543e-06 | 2.4082e-07 | 0.0090715 | 0.0090717 | 0.0090717 | 0.98405 | -0.30626 | 0.98386 | -0.30995 | 2.4922
201 | -0.023101 | -0.0057912 | 0.023101 | 0.0057912 | 3.1998e-08 | 1.9589e-08 | 0.034922 | 0.034922 | 0.034922 | 0.98432 | -0.30103 | 0.98432 | -0.301 | 9.5941
202 | 0.00075999 | 0.00019008 | -0.00075997 | -0.00019047 | 1.5635e-08 | -3.9002e-07 | 0.0011498 | 0.00115 | 0.00115 | 0.98338 | -0.31925 | 0.98336 | -0.31968 | 0.31593
203 | 0.0024547 | 0.00061473 | -0.0024546 | -0.00061502 | 1.5927e-07 | -2.8959e-07 | 0.0037119 | 0.0037121 | 0.0037121 | 0.98399 | -0.30737 | 0.98392 | -0.30873 | 1.0198
204 | 0.0035985 | 0.00090133 | -0.0035981 | -0.0009015 | 3.3111e-07 | -1.6663e-07 | 0.0054422 | 0.0054424 | 0.0054424 | 0.98386 | -0.30995 | 0.98376 | -0.31188 | 1.4952
205 | -0.026846 | -0.0067298 | 0.026862 | 0.0067401 | 1.6559e-05 | 1.0257e-05 | 0.040584 | 0.040584 | 0.040584 | 0.98432 | -0.301 | 0.98498 | -0.28807 | 11.1495
206 | 0.0046573 | 0.0011669 | -0.0046572 | -0.0011669 | 6.4882e-08 | -2.6594e-09 | 0.0070477 | 0.0070478 | 0.0070478 | 0.9833 | -0.32096 | 0.98328 | -0.32126 | 1.9362
207 | 0.0024403 | 0.00061126 | -0.0024402 | -0.00061139 | 7.4171e-08 | -1.3649e-07 | 0.0036928 | 0.0036929 | 0.0036929 | 0.98328 | -0.32126 | 0.98325 | -0.32189 | 1.0145
208 | -0.19133 | -0.048833 | 0.19137 | 0.048856 | 3.6168e-05 | 2.301e-05 | 0.28656 | 0.28656 | 0.28656 | 0.99462 | -0.10205 | 0.99483 | -0.098143 | 26.2415
209 | -0.19198 | -0.049009 | 0.19222 | 0.049164 | 0.00024294 | 0.00015456 | 0.28747 | 0.28747 | 0.28747 | 0.99483 | -0.098143 | 0.9962 | -0.071992 | 26.3252
210 | 0.095402 | 0.024239 | -0.095367 | -0.024218 | 3.4627e-05 | 2.163e-05 | 0.14262 | 0.14262 | 0.14262 | 0.9962 | -0.071992 | 0.99581 | -0.079534 | 13.0602
211 | 0.0059438 | 0.0014887 | -0.0059437 | -0.0014887 | 3.3368e-08 | 7.3034e-09 | 0.0089783 | 0.0089783 | 0.0089783 | 0.98505 | -0.28662 | 0.98505 | -0.28674 | 2.4666
212 | 0.0012934 | 0.00032402 | -0.0012934 | -0.00032416 | 1.7897e-08 | -1.4696e-07 | 0.0019561 | 0.0019561 | 0.0019561 | 0.98392 | -0.30873 | 0.98391 | -0.30902 | 0.5374
213 | 0.0028317 | 0.00070941 | -0.0028315 | -0.00070965 | 1.9188e-07 | -2.313e-07 | 0.0042831 | 0.0042832 | 0.0042832 | 0.98376 | -0.31188 | 0.98369 | -0.31331 | 1.1767
214 | 0.0019004 | 0.00047611 | -0.0019004 | -0.00047614 | 8.9372e-09 | -3.0825e-08 | 0.002876 | 0.002876 | 0.002876 | 0.98325 | -0.32189 | 0.98324 | -0.32199 | 0.79011
215 | 0.0043232 | 0.0010825 | -0.004323 | -0.0010826 | 2.1863e-07 | -3.4101e-08 | 0.0065303 | 0.0065304 | 0.0065304 | 0.98505 | -0.28674 | 0.98499 | -0.2878 | 1.7941
216 | 0.0024969 | 0.0006249 | -0.0024967 | -0.00062526 | 2.051e-07 | -3.5805e-07 | 0.0037717 | 0.0037719 | 0.0037719 | 0.98499 | -0.2878 | 0.98491 | -0.28953 | 1.0362
217 | 0.0013222 | 0.0003309 | -0.0013222 | -0.00033111 | 2.7204e-08 | -2.1398e-07 | 0.0019974 | 0.0019975 | 0.0019975 | 0.98491 | -0.28953 | 0.98488 | -0.28996 | 0.54876
218 | 0.0013222 | 0.00033111 | -0.0013221 | -0.00033135 | 3.1224e-08 | -2.4556e-07 | 0.0019975 | 0.0019976 | 0.0019976 | 0.98488 | -0.28996 | 0.98486 | -0.29046 | 0.54879
219 | 0.047383 | 0.011921 | -0.047359 | -0.011906 | 2.3787e-05 | 1.5072e-05 | 0.072256 | 0.072256 | 0.072256 | 0.976 | -0.46143 | 0.97547 | -0.47194 | 19.8507
220 | 0.019162 | 0.0048071 | -0.019154 | -0.0048024 | 7.8705e-06 | 4.7209e-06 | 0.029004 | 0.029004 | 0.029004 | 0.98314 | -0.32425 | 0.9827 | -0.33287 | 7.9681
221 | 0.016653 | 0.0041755 | -0.016653 | -0.0041754 | 1.3366e-07 | 7.8439e-08 | 0.025217 | 0.025217 | 0.025217 | 0.9827 | -0.33287 | 0.98269 | -0.33304 | 6.9276
222 | -0.010773 | -0.0026998 | 0.010776 | 0.0027013 | 2.9087e-06 | 1.5091e-06 | 0.016505 | 0.016504 | 0.016505 | 0.97125 | -0.55524 | 0.97153 | -0.54958 | 4.5342
223 | 0.0092737 | 0.0023241 | -0.0092726 | -0.0023236 | 1.078e-06 | 5.1373e-07 | 0.014208 | 0.014208 | 0.014208 | 0.97125 | -0.55524 | 0.97112 | -0.55768 | 3.9033
224 | 0.0041021 | 0.0010278 | -0.0041019 | -0.0010278 | 2.4848e-07 | -4.8824e-08 | 0.0062827 | 0.0062828 | 0.0062828 | 0.97153 | -0.54958 | 0.97147 | -0.55085 | 1.726
225 | -0.014878 | -0.0037291 | 0.014882 | 0.0037317 | 4.533e-06 | 2.6128e-06 | 0.022787 | 0.022787 | 0.022787 | 0.97153 | -0.54958 | 0.97186 | -0.54318 | 6.2602
226 | 0.0057577 | 0.0014428 | -0.0057572 | -0.0014427 | 4.5689e-07 | 9.8748e-08 | 0.0088222 | 0.0088223 | 0.0088223 | 0.97112 | -0.55768 | 0.97104 | -0.55935 | 2.4237
227 | 0.003515 | 0.00088083 | -0.0035148 | -0.0008809 | 1.313e-07 | -6.5306e-08 | 0.0053858 | 0.0053859 | 0.0053859 | 0.97112 | -0.55768 | 0.97108 | -0.55847 | 1.4796
228 | 0.0018424 | 0.00046155 | -0.0018423 | -0.00046173 | 4.9528e-08 | -1.7364e-07 | 0.0028219 | 0.002822 | 0.002822 | 0.97147 | -0.55085 | 0.97144 | -0.55141 | 0.77527
229 | -0.017096 | -0.0042864 | 0.017103 | 0.0042906 | 7.0612e-06 | 4.1785e-06 | 0.026176 | 0.026176 | 0.026176 | 0.97186 | -0.54318 | 0.97229 | -0.53452 | 7.1912
230 | 0.0057572 | 0.0014427 | -0.0057568 | -0.0014426 | 4.7078e-07 | 1.0179e-07 | 0.0088223 | 0.0088223 | 0.0088223 | 0.97104 | -0.55935 | 0.97095 | -0.56107 | 2.4237
231 | -0.019674 | -0.0049351 | 0.019679 | 0.0049378 | 4.5405e-06 | 2.7402e-06 | 0.030111 | 0.030111 | 0.030111 | 0.97229 | -0.53452 | 0.97254 | -0.52968 | 8.2724
232 | 0.0028828 | 0.00072228 | -0.0028827 | -0.00072243 | 1.4537e-07 | -1.5259e-07 | 0.004418 | 0.0044181 | 0.0044181 | 0.97095 | -0.56107 | 0.9709 | -0.56213 | 1.2138
233 | -0.020436 | -0.0051275 | 0.020438 | 0.0051288 | 2.1274e-06 | 1.2896e-06 | 0.031269 | 0.031269 | 0.031269 | 0.97254 | -0.52968 | 0.97265 | -0.5275 | 8.5905
234 | 0.0028827 | 0.00072243 | -0.0028827 | -0.00072247 | 2.9471e-08 | -3.0929e-08 | 0.0044181 | 0.0044181 | 0.0044181 | 0.9709 | -0.56213 | 0.97089 | -0.56234 | 1.2138
235 | -0.001437 | -0.00036014 | 0.001437 | 0.0003599 | 3.5378e-08 | -2.3341e-07 | 0.0021682 | 0.0021681 | 0.0021682 | 0.98617 | -0.26632 | 0.98619 | -0.26581 | 0.59567
236 | -0.0029624 | -0.0007422 | 0.0029627 | 0.00074187 | 3.1519e-07 | -3.3517e-07 | 0.0044697 | 0.0044695 | 0.0044697 | 0.98619 | -0.26581 | 0.98631 | -0.26357 | 1.2279
237 | -0.01227 | -0.0030745 | 0.012274 | 0.0030768 | 4.3378e-06 | 2.3452e-06 | 0.018511 | 0.018511 | 0.018511 | 0.98631 | -0.26357 | 0.98669 | -0.25615 | 5.0855
238 | -0.012274 | -0.0030768 | 0.012278 | 0.0030786 | 3.1841e-06 | 1.7212e-06 | 0.018511 | 0.018511 | 0.018511 | 0.98669 | -0.25615 | 0.98697 | -0.25071 | 5.0855
239 | -0.0054128 | -0.0013566 | 0.0054135 | 0.0013567 | 7.3198e-07 | 9.3005e-08 | 0.0081562 | 0.008156 | 0.0081562 | 0.98752 | -0.24002 | 0.98766 | -0.23718 | 2.2407
240 | 0.014465 | 0.0036297 | -0.014459 | -0.0036261 | 6.3136e-06 | 3.5873e-06 | 0.021795 | 0.021795 | 0.021795 | 0.98766 | -0.23718 | 0.98719 | -0.24634 | 5.9876
241 | -0.019879 | -0.0049864 | 0.019886 | 0.0049909 | 7.5971e-06 | 4.573e-06 | 0.029951 | 0.029951 | 0.029951 | 0.98766 | -0.23718 | 0.98808 | -0.22917 | 8.2282
242 | 0.013819 | 0.0034657 | -0.013816 | -0.0034641 | 2.8769e-06 | 1.6152e-06 | 0.02083 | 0.02083 | 0.02083 | 0.98719 | -0.24634 | 0.98697 | -0.25071 | 5.7226
243 | -0.02101 | -0.0052726 | 0.021019 | 0.005278 | 8.9035e-06 | 5.3944e-06 | 0.031643 | 0.031643 | 0.031643 | 0.98808 | -0.22917 | 0.98853 | -0.22029 | 8.6931
244 | -0.022777 | -0.0057186 | 0.022783 | 0.0057227 | 6.7069e-06 | 4.0973e-06 | 0.034289 | 0.034289 | 0.034289 | 0.98853 | -0.22029 | 0.98885 | -0.21412 | 9.42
245 | -0.023206 | -0.0058286 | 0.023213 | 0.0058327 | 6.8264e-06 | 4.1774e-06 | 0.034925 | 0.034925 | 0.034925 | 0.98885 | -0.21412 | 0.98917 | -0.20795 | 9.5947
246 | -0.0017013 | -0.0004264 | 0.0017015 | 0.00042576 | 1.4965e-07 | -6.398e-07 | 0.002599 | 0.0025987 | 0.002599 | 0.97409 | -0.4991 | 0.97418 | -0.49725 | 0.714
247 | -0.0032972 | -0.00082568 | 0.0032975 | 0.00082546 | 3.2761e-07 | -2.1926e-07 | 0.0050361 | 0.0050359 | 0.0050361 | 0.97418 | -0.49725 | 0.97429 | -0.49516 | 1.3835
248 | 0.0064651 | 0.00162 | -0.0064645 | -0.0016198 | 6.4062e-07 | 1.9076e-07 | 0.009862 | 0.0098621 | 0.0098621 | 0.97547 | -0.47194 | 0.97536 | -0.47402 | 2.7094
249 | 0.040894 | 0.010286 | -0.040874 | -0.010274 | 2.0014e-05 | 1.2638e-05 | 0.062394 | 0.062394 | 0.062394 | 0.97547 | -0.47194 | 0.97495 | -0.48219 | 17.1413
250 | 0.0047706 | 0.0011953 | -0.0047703 | -0.0011953 | 2.6565e-07 | 3.1072e-09 | 0.0072779 | 0.007278 | 0.007278 | 0.97536 | -0.47402 | 0.9753 | -0.47519 | 1.9994
251 | 0.037887 | 0.0095251 | -0.037884 | -0.009523 | 3.3788e-06 | 2.1288e-06 | 0.057836 | 0.057836 | 0.057836 | 0.97495 | -0.48219 | 0.97485 | -0.48406 | 15.8889
252 | 0.0030846 | 0.00077281 | -0.0030845 | -0.00077286 | 5.6886e-08 | -4.9068e-08 | 0.0047061 | 0.0047061 | 0.0047061 | 0.9753 | -0.47519 | 0.97529 | -0.47558 | 1.2929
253 | 0.035202 | 0.0088509 | -0.035181 | -0.0088379 | 2.0658e-05 | 1.2983e-05 | 0.053742 | 0.053743 | 0.053743 | 0.97485 | -0.48406 | 0.97423 | -0.49635 | 14.7644
254 | 0.033323 | 0.0083721 | -0.03332 | -0.0083706 | 2.372e-06 | 1.4877e-06 | 0.050904 | 0.050904 | 0.050904 | 0.97423 | -0.49635 | 0.97415 | -0.49785 | 13.9845
255 | 0.030072 | 0.0075564 | -0.030056 | -0.0075468 | 1.5527e-05 | 9.6933e-06 | 0.045942 | 0.045942 | 0.045942 | 0.97415 | -0.49785 | 0.9736 | -0.50867 | 12.6213
256 | 0.026524 | 0.0066615 | -0.026522 | -0.0066605 | 1.504e-06 | 9.3223e-07 | 0.040543 | 0.040543 | 0.040543 | 0.9736 | -0.50867 | 0.97354 | -0.50986 | 11.1381
257 | 0.023361 | 0.0058683 | -0.023359 | -0.0058669 | 2.2847e-06 | 1.4028e-06 | 0.035712 | 0.035712 | 0.035712 | 0.97354 | -0.50986 | 0.97344 | -0.51191 | 9.8109
258 | 0.0021852 | 0.00054747 | -0.0021851 | -0.00054765 | 7.6572e-08 | -1.8022e-07 | 0.003334 | 0.0033341 | 0.0033341 | 0.97529 | -0.47558 | 0.97525 | -0.47631 | 0.91595
259 | 0.022282 | 0.0055971 | -0.022266 | -0.005587 | 1.6564e-05 | 1.0128e-05 | 0.034066 | 0.034066 | 0.034066 | 0.97344 | -0.51191 | 0.97265 | -0.5275 | 9.3588
260 | -0.00074725 | -0.00018728 | 0.00074725 | 0.00018723 | 1.9608e-09 | -4.8751e-08 | 0.0011412 | 0.0011412 | 0.0011412 | 0.97434 | -0.4941 | 0.97435 | -0.49405 | 0.31352
261 | -0.0024447 | -0.00061265 | 0.002445 | 0.0006122 | 2.6265e-07 | -4.5783e-07 | 0.0037335 | 0.0037333 | 0.0037335 | 0.97435 | -0.49405 | 0.97446 | -0.49179 | 1.0257
262 | -0.217 | -0.055468 | 0.21702 | 0.05548 | 1.8191e-05 | 1.1589e-05 | 0.32546 | 0.32546 | 0.32546 | 0.99332 | -0.12655 | 0.99341 | -0.12482 | 29.8039
263 | 0.020406 | 0.005119 | -0.020396 | -0.0051132 | 9.7529e-06 | 5.8834e-06 | 0.030604 | 0.030604 | 0.030604 | 0.99221 | -0.14923 | 0.99169 | -0.15926 | 8.4078
264 | 0.018064 | 0.0045287 | -0.01806 | -0.0045261 | 4.272e-06 | 2.5341e-06 | 0.027105 | 0.027105 | 0.027105 | 0.99169 | -0.15926 | 0.99143 | -0.16422 | 7.4465
265 | -0.21843 | -0.055832 | 0.21869 | 0.056 | 0.00026372 | 0.00016802 | 0.32757 | 0.32757 | 0.32757 | 0.99341 | -0.12482 | 0.99472 | -0.099891 | 29.9968
266 | 0.032953 | 0.0082908 | -0.032921 | -0.0082709 | 3.1901e-05 | 1.997e-05 | 0.049501 | 0.049501 | 0.049501 | 0.99081 | -0.17617 | 0.98976 | -0.19645 | 13.5992
267 | 0.02489 | 0.0062581 | -0.024887 | -0.006256 | 3.5065e-06 | 2.1584e-06 | 0.037428 | 0.037428 | 0.037428 | 0.98976 | -0.19645 | 0.98961 | -0.1994 | 10.2823
268 | 0.024887 | 0.006256 | -0.024877 | -0.0062497 | 1.0159e-05 | 6.2533e-06 | 0.037428 | 0.037428 | 0.037428 | 0.98961 | -0.1994 | 0.98917 | -0.20795 | 10.2823
269 | 0.0096475 | 0.002418 | -0.0096465 | -0.0024175 | 1.0224e-06 | 4.9847e-07 | 0.014746 | 0.014747 | 0.014747 | 0.9735 | -0.51032 | 0.97339 | -0.51254 | 4.0513
270 | 0.0035973 | 0.00090142 | -0.0035971 | -0.00090151 | 2.1297e-07 | -9.7123e-08 | 0.0054991 | 0.0054992 | 0.0054992 | 0.97339 | -0.51254 | 0.97332 | -0.51378 | 1.5108
271 | 0.0014586 | 0.0003654 | -0.0014585 | -0.00036554 | 2.3e-08 | -1.4493e-07 | 0.0022073 | 0.0022074 | 0.0022074 | 0.98324 | -0.32199 | 0.98323 | -0.32232 | 0.60642

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.615 | 0.15729

## res_load
| p_mw | q_mvar
0 | 0.0024365 | 0.00061065
1 | 0.0013513 | 0.00033866
2 | 0.0032672 | 0.00081885
3 | 0.0037565 | 0.00094146
4 | 0.00076155 | 0.00019086
5 | 0.0041595 | 0.0010425
6 | 0.0030536 | 0.00076531
7 | 0.0050211 | 0.0012584
8 | 0.0019677 | 0.00049315
9 | 0.0018721 | 0.00046919
10 | 0.0019695 | 0.0004936
11 | 0.0014839 | 0.00037191
12 | 0.0053276 | 0.0013352
13 | 0.0023142 | 0.00058
14 | 0.0037738 | 0.0009458
15 | 0.00046926 | 0.00011761
16 | 0.00078536 | 0.00019683
17 | 0.0040561 | 0.0010166
18 | 0.0020956 | 0.00052521
19 | 0.0027072 | 0.00067849
20 | 0.0018758 | 0.00047013
21 | 0.0025176 | 0.00063097
22 | 0.0024954 | 0.00062541
23 | 0.0051623 | 0.0012938
24 | 0.005542 | 0.001389
25 | 0.0043214 | 0.001083
26 | 0.0016713 | 0.00041886
27 | 0.0013108 | 0.00032851
28 | 0.0018458 | 0.00046261
29 | 0.0013793 | 0.00034568
30 | 0.0016862 | 0.0004226
31 | 0.0012709 | 0.00031853
32 | 0.001713 | 0.00042931
33 | 0.0027784 | 0.00069634
34 | 0.0025114 | 0.00062942
35 | 0.0016538 | 0.00041449
36 | 0.0026305 | 0.00065926
37 | 0.0025472 | 0.00063838
38 | 0.0022229 | 0.00055711
39 | 0.0010769 | 0.00026989
40 | 0.0077713 | 0.0019477
41 | 0.0025128 | 0.00062976
42 | 0.002207 | 0.00055313
43 | 0.0016827 | 0.00042172
44 | 0.0022245 | 0.00055751
45 | 0.0015646 | 0.00039213
46 | 0.002157 | 0.0005406
47 | 0.0029616 | 0.00074224
48 | 0.008736 | 0.0021894
49 | 0.0020346 | 0.00050993
50 | 0.001857 | 0.0004654
51 | 0.0011355 | 0.00028458
52 | 0.0028505 | 0.00071441
53 | 0.00083545 | 0.00020938
54 | 0.0031921 | 0.00080002
55 | 0.00057497 | 0.0001441
56 | 0.0084184 | 0.0021099
57 | 0.0045863 | 0.0011494
58 | 0.0014711 | 0.00036869
59 | 0.0022082 | 0.00055344
60 | 0.003084 | 0.00077292
61 | 0.0032297 | 0.00080945
62 | 0.001667 | 0.00041778
63 | 0.0016372 | 0.00041032
64 | 0.0057652 | 0.0014449
65 | 0.0010846 | 0.00027184
66 | 0.0023329 | 0.00058468
67 | 0.0030084 | 0.00075398
68 | 0.00284 | 0.00071176
69 | 0.002702 | 0.00067718
70 | 0.0014538 | 0.00036435
71 | 0.0013323 | 0.00033391
72 | 0.0063792 | 0.0015988
73 | 0.0028142 | 0.0007053
74 | 0.0037713 | 0.00094518
75 | 0.0038669 | 0.00096913
76 | 0.00072395 | 0.00018144
77 | 0.0014273 | 0.00035771
78 | 0.00037754 | 9.4622e-05
79 | 0.0011898 | 0.00029818
80 | 0.0025264 | 0.00063317
81 | 0.0049901 | 0.0012506
82 | 0.0026937 | 0.0006751
83 | 0.0026445 | 0.00066278
84 | 0.0044846 | 0.001124
85 | 0.004002 | 0.001003
86 | 0.0048464 | 0.0012146
87 | 0.0034983 | 0.00087675
88 | 0.0055542 | 0.001392
89 | 0.0043178 | 0.0010821
90 | 0.00097146 | 0.00024347
91 | 0.0035266 | 0.00088386
92 | 0.0045489 | 0.0011401
93 | 0.0013487 | 0.00033802
94 | 0.0019547 | 0.0004899
95 | 0.0012805 | 0.00032094
96 | 0.0012205 | 0.0003059
97 | 0.0014894 | 0.00037328
98 | 0.00035558 | 8.9118e-05
99 | 0.002493 | 0.0006248
100 | 0.0033812 | 0.0008474
101 | 0.0029957 | 0.00075079
102 | 0.0034832 | 0.00087298
103 | 0.0047517 | 0.0011909
104 | 0.0038167 | 0.00095657
105 | 0.0021339 | 0.00053481
106 | 0.00098418 | 0.00024666
107 | 0.0029141 | 0.00073035
108 | 0.0010149 | 0.00025435
109 | 0.002839 | 0.00071151
110 | 0.0024442 | 0.00061259
111 | 0.0021339 | 0.00053481
112 | 0.0048591 | 0.0012178
113 | 0.010604 | 0.0026577
114 | 0.0035127 | 0.00088037
115 | 0.0067999 | 0.0017042
116 | 0.0013757 | 0.00034479
117 | 0.0043628 | 0.0010934
118 | 0.00086222 | 0.00021609
119 | 0.0029829 | 0.00074758
120 | 0.0052943 | 0.0013269
121 | 0.005812 | 0.0014566
122 | 0.0045083 | 0.0011299
123 | 0.0059006 | 0.0014788
124 | 0.0043132 | 0.001081
125 | 0.0056076 | 0.0014054
126 | 0.0066674 | 0.001671
127 | 0.003663 | 0.00091804
128 | 0.0050882 | 0.0012752
129 | 0.00057536 | 0.0001442
130 | 0.0028199 | 0.00070673
131 | 0.0011097 | 0.00027811
132 | 0.0013099 | 0.00032829
133 | 0.0030455 | 0.00076326
134 | 0.0023998 | 0.00060144
135 | 0.0037451 | 0.00093862
136 | 0.0022169 | 0.00055562
137 | 0.0045905 | 0.0011505
138 | 0.00061057 | 0.00015302
139 | 0.0013714 | 0.00034371
140 | 0.0049913 | 0.001251
141 | 0.022148 | 0.0055509
142 | 0.0010795 | 0.00027054
143 | 0.0017894 | 0.00044846
144 | 0.0011611 | 0.000291
145 | 0.00076643 | 0.00019208
146 | 0.00053978 | 0.00013528
147 | 0.00075997 | 0.00019047
148 | 0.0012934 | 0.00032416
149 | 0.0016205 | 0.00040615
150 | 0.0018261 | 0.00045766
151 | 0.0011745 | 0.00029436
152 | 0.0013221 | 0.00033135
153 | 0.0019888 | 0.00049843
154 | 0.00060905 | 0.00015264
155 | 0.0057748 | 0.0014473
156 | 0.0025011 | 0.00062684
157 | 0.001499 | 0.00037569
158 | 0.0022595 | 0.00056628
159 | 0.0022133 | 0.00055471
160 | 0.0035148 | 0.0008809
161 | 0.0018423 | 0.00046173
162 | 0.0025717 | 0.00064452
163 | 0.0028739 | 0.00072027
164 | 0.00075676 | 0.00018966
165 | 0.0028827 | 0.00072247
166 | 0.001437 | 0.00036014
167 | 0.0015254 | 0.0003823
168 | 0.0093073 | 0.0023326
169 | 0.0054128 | 0.0013566
170 | 0.00064004 | 0.00016041
171 | 0.0011237 | 0.00028163
172 | 0.0015382 | 0.00038552
173 | 0.001758 | 0.00044059
174 | 0.00042254 | 0.0001059
175 | 0.0017013 | 0.0004264
176 | 0.0015957 | 0.00039993
177 | 0.00092988 | 0.00023305
178 | 0.0016939 | 0.00042453
179 | 0.0029869 | 0.00074859
180 | 0.0016857 | 0.00042248
181 | 0.0026816 | 0.00067208
182 | 0.0062169 | 0.0015581
183 | 0.0018586 | 0.00046581
184 | 0.0032486 | 0.00081418
185 | 0.0035324 | 0.0008853
186 | 0.0031609 | 0.0007922
187 | 0.00089933 | 0.00022539
188 | 0.0010766 | 0.00026983
189 | 0.0018281 | 0.00045816
190 | 0.00074725 | 0.00018728
191 | 0.0016975 | 0.00042542
192 | 0.0045724 | 0.0011459
193 | 0.0023321 | 0.00058447
194 | 0.0014065 | 0.00035249
195 | 0.01806 | 0.0045261
196 | 0.0021851 | 0.00054765
197 | 0.0031929 | 0.00080021
198 | 0.0080308 | 0.0020127
199 | 0.0029011 | 0.00072708
200 | 0.0016639 | 0.000417
201 | 0.0028315 | 0.00070965
202 | 0.002625 | 0.0006579
203 | 0.0060492 | 0.0015161
204 | 0.0035971 | 0.00090151
205 | 0.00044187 | 0.00011074
206 | 0.0014585 | 0.00036554

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1