## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2135-2_1_2_node_6 | 0.4 | n |  | TRUE
1 | bus_LV_2135-2_1_2_node_7 | 0.4 | n |  | TRUE
2 | bus_LV_2135-2_1_2_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_2135-2_1_2_node_13 | 0.4 | n |  | TRUE
4 | bus_LV_2135-2_1_2_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_2135-2_1_2_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_2135-2_1_2_node_266 | 0.4 | n |  | TRUE
7 | bus_LV_2135-2_1_2_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_2135-2_1_2_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_2135-2_1_2_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_2135-2_1_2_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_2135-2_1_2_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_2135-2_1_2_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_2135-2_1_2_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_2135-2_1_2_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_2135-2_1_2_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_2135-2_1_2_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_2135-2_1_2_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_2135-2_1_2_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_2135-2_1_2_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_2135-2_1_2_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_2135-2_1_2_node_44 | 0.4 | n |  | TRUE
22 | bus_LV_2135-2_1_2_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_2135-2_1_2_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_2135-2_1_2_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_2135-2_1_2_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_2135-2_1_2_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_2135-2_1_2_node_63 | 0.4 | n |  | TRUE
28 | bus_LV_2135-2_1_2_node_267 | 0.4 | n |  | TRUE
29 | bus_LV_2135-2_1_2_node_268 | 0.4 | n |  | TRUE
30 | bus_LV_2135-2_1_2_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_2135-2_1_2_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_2135-2_1_2_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_2135-2_1_2_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_2135-2_1_2_node_68 | 0.4 | n |  | TRUE
35 | bus_LV_2135-2_1_2_node_249 | 0.4 | n |  | TRUE
36 | bus_LV_2135-2_1_2_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_2135-2_1_2_node_256 | 0.4 | n |  | TRUE
38 | bus_LV_2135-2_1_2_node_254 | 0.4 | n |  | TRUE
39 | bus_LV_2135-2_1_2_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_2135-2_1_2_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_2135-2_1_2_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_2135-2_1_2_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_2135-2_1_2_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_2135-2_1_2_node_64 | 0.4 | n |  | TRUE
45 | bus_LV_2135-2_1_2_node_62 | 0.4 | n |  | TRUE
46 | bus_LV_2135-2_1_2_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_2135-2_1_2_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_2135-2_1_2_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_2135-2_1_2_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_2135-2_1_2_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_2135-2_1_2_node_53 | 0.4 | n |  | TRUE
52 | bus_LV_2135-2_1_2_node_65 | 0.4 | n |  | TRUE
53 | bus_LV_2135-2_1_2_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_2135-2_1_2_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_2135-2_1_2_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_2135-2_1_2_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_2135-2_1_2_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_2135-2_1_2_node_52 | 0.4 | n |  | TRUE
59 | bus_LV_2135-2_1_2_node_58 | 0.4 | n |  | TRUE
60 | bus_LV_2135-2_1_2_node_60 | 0.4 | n |  | TRUE
61 | bus_LV_2135-2_1_2_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_2135-2_1_2_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_2135-2_1_2_node_66 | 0.4 | n |  | TRUE
64 | bus_LV_2135-2_1_2_node_67 | 0.4 | n |  | TRUE
65 | bus_LV_2135-2_1_2_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_2135-2_1_2_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_2135-2_1_2_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_2135-2_1_2_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_2135-2_1_2_node_69 | 0.4 | n |  | TRUE
70 | bus_LV_2135-2_1_2_node_258 | 0.4 | n |  | TRUE
71 | bus_LV_2135-2_1_2_node_78 | 0.4 | n |  | TRUE
72 | bus_LV_2135-2_1_2_node_270 | 0.4 | n |  | TRUE
73 | bus_LV_2135-2_1_2_node_250 | 0.4 | n |  | TRUE
74 | bus_LV_2135-2_1_2_node_251 | 0.4 | n |  | TRUE
75 | bus_LV_2135-2_1_2_node_252 | 0.4 | n |  | TRUE
76 | bus_LV_2135-2_1_2_node_253 | 0.4 | n |  | TRUE
77 | bus_LV_2135-2_1_2_node_257 | 0.4 | n |  | TRUE
78 | bus_LV_2135-2_1_2_node_255 | 0.4 | n |  | TRUE
79 | bus_LV_2135-2_1_2_node_262 | 0.4 | n |  | TRUE
80 | bus_LV_2135-2_1_2_node_263 | 0.4 | n |  | TRUE
81 | bus_LV_2135-2_1_2_node_265 | 0.4 | n |  | TRUE
82 | bus_LV_2135-2_1_2_node_269 | 0.4 | n |  | TRUE
83 | bus_MV_28_0_node_85 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2135-2_1_2_load_6 | 0 | 0.0037562 | 0.0009414 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2135-2_1_2_load_7 | 1 | 0.007762 | 0.0019453 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2135-2_1_2_load_13 | 3 | 0.0017831 | 0.00044689 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2135-2_1_2_load_266 | 6 | 0.00062505 | 0.00015665 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2135-2_1_2_load_16 | 7 | 0.0039894 | 0.00099984 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2135-2_1_2_load_11 | 8 | 0.001815 | 0.00045489 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2135-2_1_2_load_12 | 9 | 0.0043354 | 0.0010866 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2135-2_1_2_load_14 | 10 | 0.0021571 | 0.00054063 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2135-2_1_2_load_15 | 11 | 0.0018373 | 0.00046046 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2135-2_1_2_load_23 | 12 | 0.0015074 | 0.0003778 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2135-2_1_2_load_24 | 13 | 0.0019753 | 0.00049505 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2135-2_1_2_load_17 | 14 | 0.0019765 | 0.00049535 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2135-2_1_2_load_18 | 15 | 0.0027223 | 0.00068226 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2135-2_1_2_load_19 | 16 | 0.0028075 | 0.00070363 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2135-2_1_2_load_21 | 18 | 0.003853 | 0.00096565 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2135-2_1_2_load_25 | 20 | 0.002294 | 0.00057493 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2135-2_1_2_load_44 | 21 | 0.0025682 | 0.00064366 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2135-2_1_2_load_26 | 22 | 0.0012302 | 0.00030831 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2135-2_1_2_load_27 | 23 | 0.0031542 | 0.00079052 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2135-2_1_2_load_29 | 25 | 0.0010084 | 0.00025273 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2135-2_1_2_load_63 | 27 | 0.0010276 | 0.00025755 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2135-2_1_2_load_268 | 29 | 0.0055357 | 0.0013874 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2135-2_1_2_load_31 | 30 | 0.0025575 | 0.00064097 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2135-2_1_2_load_34 | 33 | 0.00087141 | 0.0002184 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2135-2_1_2_load_68 | 34 | 0.0015234 | 0.0003818 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2135-2_1_2_load_249 | 35 | 0.00070335 | 0.00017628 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2135-2_1_2_load_256 | 37 | 0.00085576 | 0.00021447 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2135-2_1_2_load_254 | 38 | 0.00093008 | 0.0002331 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2135-2_1_2_load_36 | 39 | 0.0038924 | 0.00097552 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2135-2_1_2_load_37 | 40 | 0.00023902 | 5.9903e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2135-2_1_2_load_38 | 41 | 0.0010708 | 0.00026837 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2135-2_1_2_load_39 | 42 | 0.001825 | 0.00045739 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2135-2_1_2_load_40 | 43 | 0.00064461 | 0.00016155 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2135-2_1_2_load_64 | 44 | 0.00024643 | 6.1761e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2135-2_1_2_load_62 | 45 | 0.00063366 | 0.00015881 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2135-2_1_2_load_41 | 46 | 0.0032654 | 0.00081838 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2135-2_1_2_load_42 | 47 | 0.0018019 | 0.00045161 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2135-2_1_2_load_45 | 49 | 0.0050596 | 0.0012681 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2135-2_1_2_load_46 | 50 | 0.0031263 | 0.00078353 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2135-2_1_2_load_53 | 51 | 0.0030918 | 0.00077489 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2135-2_1_2_load_65 | 52 | 0.0070526 | 0.0017676 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2135-2_1_2_load_47 | 53 | 0.0033091 | 0.00082933 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2135-2_1_2_load_48 | 54 | 0.0021241 | 0.00053236 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2135-2_1_2_load_52 | 58 | 0.0042396 | 0.0010625 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2135-2_1_2_load_60 | 60 | 0.0015842 | 0.00039703 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2135-2_1_2_load_54 | 61 | 0.0051096 | 0.0012806 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2135-2_1_2_load_66 | 63 | 0.0031116 | 0.00077985 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2135-2_1_2_load_67 | 64 | 0.00167 | 0.00041854 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2135-2_1_2_load_56 | 65 | 0.0019081 | 0.00047821 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2135-2_1_2_load_57 | 66 | 0.0013112 | 0.00032861 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2135-2_1_2_load_59 | 67 | 0.0028851 | 0.00072308 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2135-2_1_2_load_61 | 68 | 0.0005432 | 0.00013614 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2135-2_1_2_load_69 | 69 | 0.002978 | 0.00074635 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2135-2_1_2_load_258 | 70 | 0.0027457 | 0.00068814 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2135-2_1_2_load_78 | 71 | 0.00073684 | 0.00018467 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2135-2_1_2_load_270 | 72 | 0.0043581 | 0.0010922 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2135-2_1_2_load_250 | 73 | 0.00083764 | 0.00020993 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2135-2_1_2_load_251 | 74 | 0.00089331 | 0.00022388 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2135-2_1_2_load_252 | 75 | 0.00081994 | 0.0002055 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2135-2_1_2_load_255 | 78 | 0.00093382 | 0.00023404 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2135-2_1_2_load_262 | 79 | 0.0006041 | 0.0001514 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2135-2_1_2_load_263 | 80 | 0.0005105 | 0.00012794 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2135-2_1_2_load_265 | 81 | 0.00032959 | 8.2603e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2135-2_1_2_load_269 | 82 | 0.001473 | 0.00036916 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 70 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2135-2_1_2_line_0 |  | 0 | 1 | 0.06638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2135-2_1_2_line_1 |  | 0 | 2 | 0.057836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2135-2_1_2_line_2 |  | 1 | 3 | 0.11542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2135-2_1_2_line_3 |  | 2 | 4 | 0.034233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2135-2_1_2_line_4 |  | 2 | 5 | 0.065348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2135-2_1_2_line_5 |  | 3 | 11 | 0.0091068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2135-2_1_2_line_6 |  | 3 | 8 | 0.046391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2135-2_1_2_line_7 |  | 4 | 6 | 0.074922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2135-2_1_2_line_8 |  | 5 | 7 | 0.022436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2135-2_1_2_line_9 |  | 6 | 81 | 0.03081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2135-2_1_2_line_10 |  | 8 | 9 | 0.0033545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2135-2_1_2_line_11 |  | 9 | 10 | 0.030249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2135-2_1_2_line_12 |  | 10 | 12 | 0.035201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2135-2_1_2_line_13 |  | 10 | 13 | 0.03713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2135-2_1_2_line_14 |  | 11 | 14 | 0.011873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2135-2_1_2_line_15 |  | 12 | 20 | 0.033238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2135-2_1_2_line_16 |  | 14 | 15 | 0.01375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2135-2_1_2_line_17 |  | 16 | 17 | 0.032497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2135-2_1_2_line_18 |  | 17 | 18 | 0.061748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2135-2_1_2_line_19 |  | 17 | 19 | 0.005902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2135-2_1_2_line_20 |  | 19 | 20 | 0.0031988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2135-2_1_2_line_21 |  | 19 | 21 | 0.020729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2135-2_1_2_line_22 |  | 21 | 47 | 0.0059814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2135-2_1_2_line_23 |  | 22 | 23 | 8.707e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2135-2_1_2_line_24 |  | 22 | 24 | 0.090942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2135-2_1_2_line_25 |  | 24 | 25 | 0.034908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2135-2_1_2_line_26 |  | 24 | 26 | 0.03997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2135-2_1_2_line_27 |  | 25 | 27 | 0.018191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2135-2_1_2_line_28 |  | 26 | 28 | 0.086712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2135-2_1_2_line_29 |  | 26 | 29 | 0.23553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2135-2_1_2_line_30 |  | 27 | 56 | 0.08453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2135-2_1_2_line_31 |  | 28 | 82 | 0.10084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2135-2_1_2_line_32 |  | 30 | 31 | 0.026337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2135-2_1_2_line_33 |  | 30 | 32 | 0.01627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2135-2_1_2_line_34 |  | 31 | 33 | 0.028218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2135-2_1_2_line_35 |  | 32 | 34 | 0.11717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2135-2_1_2_line_36 |  | 33 | 35 | 0.022133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2135-2_1_2_line_37 |  | 34 | 69 | 0.036307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2135-2_1_2_line_38 |  | 35 | 73 | 0.014848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2135-2_1_2_line_39 |  | 36 | 37 | 0.0092572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2135-2_1_2_line_40 |  | 36 | 38 | 0.012509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2135-2_1_2_line_41 |  | 37 | 77 | 0.0083961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2135-2_1_2_line_42 |  | 38 | 78 | 0.0045785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2135-2_1_2_line_43 |  | 39 | 40 | 0.0019798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2135-2_1_2_line_44 |  | 39 | 41 | 0.02934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2135-2_1_2_line_45 |  | 40 | 42 | 0.0023879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2135-2_1_2_line_46 |  | 41 | 43 | 0.024959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2135-2_1_2_line_47 |  | 42 | 44 | 0.004895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2135-2_1_2_line_48 |  | 43 | 45 | 0.01691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2135-2_1_2_line_49 |  | 45 | 57 | 0.023606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2135-2_1_2_line_50 |  | 46 | 47 | 0.024988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2135-2_1_2_line_51 |  | 46 | 48 | 0.0059149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2135-2_1_2_line_52 |  | 48 | 49 | 0.024355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2135-2_1_2_line_53 |  | 48 | 50 | 0.020418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2135-2_1_2_line_54 |  | 49 | 51 | 0.013609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2135-2_1_2_line_55 |  | 50 | 52 | 0.035848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2135-2_1_2_line_56 |  | 51 | 61 | 0.015155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2135-2_1_2_line_57 |  | 52 | 58 | 0.0028862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2135-2_1_2_line_58 |  | 53 | 54 | 0.026721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2135-2_1_2_line_59 |  | 53 | 55 | 0.049706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2135-2_1_2_line_60 |  | 54 | 56 | 0.055599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2135-2_1_2_line_61 |  | 55 | 57 | 0.027116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2135-2_1_2_line_62 |  | 55 | 58 | 0.023395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2135-2_1_2_line_63 |  | 56 | 59 | 0.017974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2135-2_1_2_line_64 |  | 57 | 60 | 0.022695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2135-2_1_2_line_65 |  | 59 | 67 | 0.0051292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2135-2_1_2_line_66 |  | 59 | 65 | 0.012673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2135-2_1_2_line_67 |  | 60 | 68 | 0.013802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2135-2_1_2_line_68 |  | 61 | 62 | 0.007523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2135-2_1_2_line_69 |  | 62 | 63 | 0.022693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2135-2_1_2_line_70 |  | 62 | 64 | 0.010505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_2135-2_1_2_line_71 |  | 63 | 69 | 0.0024066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2135-2_1_2_line_72 |  | 64 | 70 | 0.018363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_2135-2_1_2_line_73 |  | 65 | 66 | 0.027501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2135-2_1_2_line_74 |  | 71 | 72 | 0.31006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2135-2_1_2_line_75 |  | 72 | 82 | 0.31975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2135-2_1_2_line_76 |  | 73 | 74 | 0.017777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2135-2_1_2_line_77 |  | 74 | 75 | 0.017114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2135-2_1_2_line_78 |  | 75 | 76 | 0.032438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2135-2_1_2_line_79 |  | 76 | 77 | 0.033467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2135-2_1_2_line_80 |  | 79 | 80 | 0.036011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2135-2_1_2_line_81 |  | 80 | 81 | 0.032382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2135-2_1_2_trafo_258 | 0.63 MVA 20/0.4 kV | 83 | 70 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2572911.9116 | 1160337.8678 | 2572901.0932 | 1160340.0623 | 2572896.3561 | 1160339.8169 | 2572892.4076 | 1160337.6892 | 2572889.4395 | 1160333.7785 | 2572887.541 | 1160329.1514 | 2572887.2538 | 1160324.9617 | 2572888.9317 | 1160321.4746 | 2572892.6766 | 1160317.5334 | 2572899.9001 | 1160313.4876 | 2572913.222 | 1160307.9787
1 | 2572970.779 | 1160305.0634 | 2572924.564 | 1160305.7056 | 2572915.1753 | 1160307.171 | 2572913.222 | 1160307.9787
2 | 2572828.6131 | 1160417.7628 | 2572911.9116 | 1160337.8678
3 | 2572963.8457 | 1160271.5445 | 2572970.779 | 1160305.0634
4 | 2572970.779 | 1160305.0634 | 2572981.0304 | 1160362.3683 | 2572988.0994 | 1160361.4137
5 | 2572827.3855 | 1160426.7562 | 2572828.4913 | 1160421.3207 | 2572828.6131 | 1160417.7628 | 2572828.6131 | 1160417.7628
6 | 2572791.1451 | 1160393.5107 | 2572823.9098 | 1160409.7245 | 2572826.4855 | 1160411.6138 | 2572827.6038 | 1160413.1762 | 2572828.2562 | 1160415.0964 | 2572828.6131 | 1160417.7628
7 | 2572963.8457 | 1160271.5445 | 2572949.7232 | 1160197.9651
8 | 2572988.0994 | 1160361.4137 | 2573010.3531 | 1160358.5628
9 | 2572949.7232 | 1160197.9651 | 2572943.9158 | 1160167.7078
10 | 2572791.1451 | 1160393.5107 | 2572788.1386 | 1160392.0229
11 | 2572762.5346 | 1160375.9749 | 2572764.4029 | 1160377.3116 | 2572779.038 | 1160387.0389 | 2572786.0448 | 1160390.9868 | 2572788.1386 | 1160392.0229
12 | 2572762.5346 | 1160375.9749 | 2572755.0617 | 1160370.6506 | 2572749.5236 | 1160366.1402 | 2572744.2259 | 1160360.5615 | 2572737.3138 | 1160351.7628
13 | 2572762.5346 | 1160375.9749 | 2572757.3195 | 1160398.6656 | 2572756.1517 | 1160401.3834 | 2572754.2659 | 1160402.9261 | 2572752.4968 | 1160403.1676 | 2572745.9367 | 1160401.9766
14 | 2572827.3855 | 1160426.7562 | 2572825.0184 | 1160438.3904
15 | 2572737.3138 | 1160351.7628 | 2572716.7806 | 1160325.6252
16 | 2572822.2771 | 1160451.8642 | 2572825.0184 | 1160438.3904
17 | 2572711.67 | 1160328.1155 | 2572708.9349 | 1160329.9511 | 2572707.2796 | 1160331.6483 | 2572706.1314 | 1160333.6101 | 2572700.4734 | 1160357.5083
18 | 2572711.67 | 1160328.1155 | 2572710.2671 | 1160333.0577 | 2572703.3106 | 1160368.774 | 2572703.3903 | 1160371.1415 | 2572704.2799 | 1160372.9606 | 2572705.7138 | 1160374.8439 | 2572707.0061 | 1160375.9163 | 2572708.6335 | 1160376.5203 | 2572718.5058 | 1160378.3873
19 | 2572714.8045 | 1160323.1098 | 2572711.67 | 1160328.1155
20 | 2572714.8045 | 1160323.1098 | 2572716.7806 | 1160325.6252
21 | 2572714.8045 | 1160323.1098 | 2572701.6484 | 1160307.0909
22 | 2572701.6484 | 1160307.0909 | 2572697.8522 | 1160302.4686
23 | 2572370.0965 | 1160354.062 | 2572370.1601 | 1160354.1215
24 | 2572442.0821 | 1160408.4001 | 2572428.9369 | 1160396.1544 | 2572424.492 | 1160391.1168 | 2572419.5839 | 1160387.015 | 2572386.6971 | 1160369.591 | 2572370.1601 | 1160354.1215
25 | 2572442.0821 | 1160408.4001 | 2572446.7358 | 1160398.8628 | 2572450.116 | 1160392.3551 | 2572456.3669 | 1160381.8433 | 2572459.0343 | 1160377.9337
26 | 2572426.2116 | 1160445.0694 | 2572432.0904 | 1160430.3127 | 2572433.7808 | 1160426.3029 | 2572440.5189 | 1160411.7535 | 2572442.0821 | 1160408.4001
27 | 2572459.0343 | 1160377.9337 | 2572469.2864 | 1160362.9075
28 | 2572348.3194 | 1160407.8205 | 2572382.6326 | 1160427.1387 | 2572400.6392 | 1160436.6939 | 2572411.9554 | 1160441.1774 | 2572426.2116 | 1160445.0694
29 | 2572426.2116 | 1160445.0694 | 2572343.6854 | 1160665.6718
30 | 2572523.5666 | 1160298.3374 | 2572493.7464 | 1160329.6343 | 2572472.8394 | 1160357.7 | 2572469.2864 | 1160362.9075
31 | 2572348.3194 | 1160407.8205 | 2572292.9601 | 1160406.1863 | 2572247.4788 | 1160411.1659
32 | 2572562.7733 | 1160495.9907 | 2572583.4937 | 1160479.7339
33 | 2572596.2942 | 1160469.6908 | 2572583.4937 | 1160479.7339
34 | 2572562.7733 | 1160495.9907 | 2572580.5346 | 1160517.9177
35 | 2572581.8309 | 1160353.4158 | 2572596.2942 | 1160469.6908
36 | 2572580.5346 | 1160517.9177 | 2572592.1819 | 1160532.2967 | 2572594.145 | 1160535.3486
37 | 2572581.8309 | 1160353.4158 | 2572610.2365 | 1160330.8031
38 | 2572594.145 | 1160535.3486 | 2572602.1776 | 1160547.8363
39 | 2572644.1752 | 1160552.2693 | 2572644.5028 | 1160555.2026 | 2572647.955 | 1160560.4794
40 | 2572644.1752 | 1160552.2693 | 2572636.4945 | 1160545.0341 | 2572635.0163 | 1160543.7509
41 | 2572652.5515 | 1160567.5054 | 2572647.955 | 1160560.4794
42 | 2572635.0163 | 1160543.7509 | 2572631.8321 | 1160540.9866 | 2572631.907 | 1160540.6326
43 | 2572591.4936 | 1160121.1991 | 2572590.3338 | 1160119.5946
44 | 2572591.4936 | 1160121.1991 | 2572608.6802 | 1160144.9781
45 | 2572588.935 | 1160117.6592 | 2572590.3338 | 1160119.5946
46 | 2572623.3007 | 1160165.2066 | 2572608.6802 | 1160144.9781
47 | 2572588.935 | 1160117.6592 | 2572586.0676 | 1160113.692
48 | 2572633.2064 | 1160178.9118 | 2572623.3007 | 1160165.2066
49 | 2572647.0336 | 1160198.0445 | 2572643.6633 | 1160193.3797 | 2572633.2064 | 1160178.9118
50 | 2572681.9929 | 1160283.1582 | 2572697.8522 | 1160302.4686
51 | 2572678.2388 | 1160278.5872 | 2572681.9929 | 1160283.1582
52 | 2572678.2388 | 1160278.5872 | 2572658.8145 | 1160293.2798
53 | 2572678.2388 | 1160278.5872 | 2572665.2491 | 1160262.8341
54 | 2572647.9604 | 1160301.4897 | 2572658.8145 | 1160293.2798
55 | 2572665.2491 | 1160262.8341 | 2572642.4432 | 1160235.1766
56 | 2572647.9604 | 1160301.4897 | 2572635.8734 | 1160310.6324
57 | 2572640.607 | 1160232.9498 | 2572642.4432 | 1160235.1766
58 | 2572586.2671 | 1160245.1179 | 2572565.0527 | 1160261.3654
59 | 2572625.7293 | 1160214.8947 | 2572586.2671 | 1160245.1179
60 | 2572523.5666 | 1160298.3374 | 2572557.9458 | 1160266.8085 | 2572565.0527 | 1160261.3654
61 | 2572625.7293 | 1160214.8947 | 2572647.0336 | 1160198.0445
62 | 2572625.7293 | 1160214.8947 | 2572628.2031 | 1160217.9071 | 2572640.607 | 1160232.9498
63 | 2572531.4342 | 1160314.465 | 2572528.817 | 1160310.2526 | 2572523.5666 | 1160298.3374
64 | 2572647.0336 | 1160198.0445 | 2572652.3714 | 1160193.8736 | 2572664.8022 | 1160183.9263
65 | 2572531.4342 | 1160314.465 | 2572534.1397 | 1160318.8226
66 | 2572531.4342 | 1160314.465 | 2572521.6187 | 1160322.4813
67 | 2572664.8022 | 1160183.9263 | 2572675.5789 | 1160175.3027
68 | 2572629.8735 | 1160315.1707 | 2572635.8734 | 1160310.6324
69 | 2572629.8735 | 1160315.1707 | 2572612.1193 | 1160329.3042
70 | 2572629.8735 | 1160315.1707 | 2572636.2652 | 1160323.508
71 | 2572610.2365 | 1160330.8031 | 2572612.1193 | 1160329.3042
72 | 2572641.797 | 1160340.2067 | 2572641.5513 | 1160331.7035 | 2572640.8207 | 1160329.4501 | 2572636.2652 | 1160323.508
73 | 2572521.6187 | 1160322.4813 | 2572512.8588 | 1160329.6355 | 2572521.7643 | 1160343.1571 | 2572521.7643 | 1160343.1571
74 | 2571675.8299 | 1160166.1632 | 2571976.6917 | 1160241.1174
75 | 2572247.4788 | 1160411.1659 | 2571976.6917 | 1160241.1174
76 | 2572602.1776 | 1160547.8363 | 2572611.7949 | 1160562.7878
77 | 2572611.7949 | 1160562.7878 | 2572621.0533 | 1160577.1811
78 | 2572642.5515 | 1160599.4449 | 2572636.8466 | 1160598.6483 | 2572625.9555 | 1160584.8022 | 2572621.0533 | 1160577.1811
79 | 2572642.5515 | 1160599.4449 | 2572652.5515 | 1160567.5054
80 | 2572931.2547 | 1160100.4969 | 2572937.3427 | 1160133.4612 | 2572937.8119 | 1160135.9059
81 | 2572937.8119 | 1160135.9059 | 2572943.9158 | 1160167.7078

## bus_geodata
| x | y | coords
0 | 2572913.222 | 1160307.9787
1 | 2572911.9116 | 1160337.8678
2 | 2572970.779 | 1160305.0634
3 | 2572828.6131 | 1160417.7628
4 | 2572963.8457 | 1160271.5445
5 | 2572988.0994 | 1160361.4137
6 | 2572949.7232 | 1160197.9651
7 | 2573010.3531 | 1160358.5628
8 | 2572791.1451 | 1160393.5107
9 | 2572788.1386 | 1160392.0229
10 | 2572762.5346 | 1160375.9749
11 | 2572827.3855 | 1160426.7562
12 | 2572737.3138 | 1160351.7628
13 | 2572745.9367 | 1160401.9766
14 | 2572825.0184 | 1160438.3904
15 | 2572822.2771 | 1160451.8642
16 | 2572700.4734 | 1160357.5083
17 | 2572711.67 | 1160328.1155
18 | 2572718.5058 | 1160378.3873
19 | 2572714.8045 | 1160323.1098
20 | 2572716.7806 | 1160325.6252
21 | 2572701.6484 | 1160307.0909
22 | 2572370.1601 | 1160354.1215
23 | 2572370.0965 | 1160354.062
24 | 2572442.0821 | 1160408.4001
25 | 2572459.0343 | 1160377.9337
26 | 2572426.2116 | 1160445.0694
27 | 2572469.2864 | 1160362.9075
28 | 2572348.3194 | 1160407.8205
29 | 2572343.6854 | 1160665.6718
30 | 2572583.4937 | 1160479.7339
31 | 2572562.7733 | 1160495.9907
32 | 2572596.2942 | 1160469.6908
33 | 2572580.5346 | 1160517.9177
34 | 2572581.8309 | 1160353.4158
35 | 2572594.145 | 1160535.3486
36 | 2572644.1752 | 1160552.2693
37 | 2572647.955 | 1160560.4794
38 | 2572635.0163 | 1160543.7509
39 | 2572591.4936 | 1160121.1991
40 | 2572590.3338 | 1160119.5946
41 | 2572608.6802 | 1160144.9781
42 | 2572588.935 | 1160117.6592
43 | 2572623.3007 | 1160165.2066
44 | 2572586.0676 | 1160113.692
45 | 2572633.2064 | 1160178.9118
46 | 2572681.9929 | 1160283.1582
47 | 2572697.8522 | 1160302.4686
48 | 2572678.2388 | 1160278.5872
49 | 2572658.8145 | 1160293.2798
50 | 2572665.2491 | 1160262.8341
51 | 2572647.9604 | 1160301.4897
52 | 2572642.4432 | 1160235.1766
53 | 2572586.2671 | 1160245.1179
54 | 2572565.0527 | 1160261.3654
55 | 2572625.7293 | 1160214.8947
56 | 2572523.5666 | 1160298.3374
57 | 2572647.0336 | 1160198.0445
58 | 2572640.607 | 1160232.9498
59 | 2572531.4342 | 1160314.465
60 | 2572664.8022 | 1160183.9263
61 | 2572635.8734 | 1160310.6324
62 | 2572629.8735 | 1160315.1707
63 | 2572612.1193 | 1160329.3042
64 | 2572636.2652 | 1160323.508
65 | 2572521.6187 | 1160322.4813
66 | 2572521.7643 | 1160343.1571
67 | 2572534.1397 | 1160318.8226
68 | 2572675.5789 | 1160175.3027
69 | 2572610.2365 | 1160330.8031
70 | 2572641.797 | 1160340.2067
71 | 2571675.8299 | 1160166.1632
72 | 2571976.6917 | 1160241.1174
73 | 2572602.1776 | 1160547.8363
74 | 2572611.7949 | 1160562.7878
75 | 2572621.0533 | 1160577.1811
76 | 2572642.5515 | 1160599.4449
77 | 2572652.5515 | 1160567.5054
78 | 2572631.907 | 1160540.6326
79 | 2572931.2547 | 1160100.4969
80 | 2572937.8119 | 1160135.9059
81 | 2572943.9158 | 1160167.7078
82 | 2572247.4788 | 1160411.1659
83 | 2572629.8735 | 1160315.1707

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98212 | -0.34481 | 0.0037562 | 0.0009414
1 | 0.98272 | -0.33303 | 0.007762 | 0.0019453
2 | 0.9818 | -0.35116 | 0 | 0
3 | 0.98459 | -0.29645 | 0.0017831 | 0.00044689
4 | 0.98173 | -0.35244 | 0 | 0
5 | 0.98155 | -0.35587 | 0 | 0
6 | 0.98159 | -0.35525 | 0.00062505 | 0.00015665
7 | 0.98147 | -0.35749 | 0.0039894 | 0.00099984
8 | 0.9857 | -0.27486 | 0.001815 | 0.00045489
9 | 0.98579 | -0.2732 | 0.0043354 | 0.0010866
10 | 0.98668 | -0.25581 | 0.0021571 | 0.00054063
11 | 0.98454 | -0.29752 | 0.0018373 | 0.00046046
12 | 0.98785 | -0.23303 | 0.0015074 | 0.0003778
13 | 0.98661 | -0.25713 | 0.0019753 | 0.00049505
14 | 0.98449 | -0.29853 | 0.0019765 | 0.00049535
15 | 0.98445 | -0.2992 | 0.0027223 | 0.00068226
16 | 0.98901 | -0.21071 | 0.0028075 | 0.00070363
17 | 0.98909 | -0.20909 | 0 | 0
18 | 0.98887 | -0.21333 | 0.003853 | 0.00096565
19 | 0.98913 | -0.20839 | 0 | 0
20 | 0.98901 | -0.21067 | 0.002294 | 0.00057493
21 | 0.99002 | -0.19117 | 0.0025682 | 0.00064366
22 | 0.98206 | -0.346 | 0.0012302 | 0.00030831
23 | 0.98206 | -0.346 | 0.0031542 | 0.00079052
24 | 0.98243 | -0.33879 | 0 | 0
25 | 0.98296 | -0.32838 | 0.0010084 | 0.00025273
26 | 0.98198 | -0.34755 | 0 | 0
27 | 0.98325 | -0.32262 | 0.0010276 | 0.00025755
28 | 0.98145 | -0.35789 | 0 | 0
29 | 0.98078 | -0.37117 | 0.0055357 | 0.0013874
30 | 0.99625 | -0.071846 | 0.0025575 | 0.00064097
31 | 0.99608 | -0.075016 | 0 | 0
32 | 0.99639 | -0.069158 | 0 | 0
33 | 0.99591 | -0.078413 | 0.00087141 | 0.0002184
34 | 0.99739 | -0.049814 | 0.0015234 | 0.0003818
35 | 0.99579 | -0.080739 | 0.00070335 | 0.00017628
36 | 0.99539 | -0.088429 | 0 | 0
37 | 0.99541 | -0.088125 | 0.00085576 | 0.00021447
38 | 0.99537 | -0.088839 | 0.00093008 | 0.0002331
39 | 0.9871 | -0.24783 | 0.0038924 | 0.00097552
40 | 0.98709 | -0.24791 | 0.00023902 | 5.9903e-05
41 | 0.98726 | -0.24458 | 0.0010708 | 0.00026837
42 | 0.98709 | -0.248 | 0.001825 | 0.00045739
43 | 0.98743 | -0.24133 | 0.00064461 | 0.00016155
44 | 0.98709 | -0.24802 | 0.00024643 | 6.1761e-05
45 | 0.98755 | -0.23894 | 0.00063366 | 0.00015881
46 | 0.99146 | -0.16329 | 0.0032654 | 0.00081838
47 | 0.99029 | -0.18593 | 0.0018019 | 0.00045161
48 | 0.99176 | -0.1576 | 0 | 0
49 | 0.99421 | -0.11044 | 0.0050596 | 0.0012681
50 | 0.99072 | -0.1776 | 0.0031263 | 0.00078353
51 | 0.99564 | -0.082988 | 0.0030918 | 0.00077489
52 | 0.989 | -0.21081 | 0.0070526 | 0.0017676
53 | 0.98663 | -0.25691 | 0.0033091 | 0.00082933
54 | 0.98597 | -0.26975 | 0.0021241 | 0.00053236
55 | 0.988 | -0.23015 | 0 | 0
56 | 0.9847 | -0.29437 | 0 | 0
57 | 0.98774 | -0.23533 | 0 | 0
58 | 0.98888 | -0.21313 | 0.0042396 | 0.0010625
59 | 0.9846 | -0.29635 | 0 | 0
60 | 0.98769 | -0.23619 | 0.0015842 | 0.00039703
61 | 0.99728 | -0.051683 | 0.0051096 | 0.0012806
62 | 0.99813 | -0.035509 | 0 | 0
63 | 0.99778 | -0.042272 | 0.0031116 | 0.00077985
64 | 0.99881 | -0.022669 | 0.00167 | 0.00041854
65 | 0.98456 | -0.29708 | 0.0019081 | 0.00047821
66 | 0.98453 | -0.29773 | 0.0013112 | 0.00032861
67 | 0.98459 | -0.29661 | 0.0028851 | 0.00072308
68 | 0.98769 | -0.23633 | 0.0005432 | 0.00013614
69 | 0.99775 | -0.042858 | 0.002978 | 0.00074635
70 | 1 | 0 | -0.14461 | -0.036403
71 | 0.97912 | -0.40375 | 0.00073684 | 0.00018467
72 | 0.97933 | -0.39957 | 0.0043581 | 0.0010922
73 | 0.99572 | -0.082115 | 0.00083764 | 0.00020993
74 | 0.99564 | -0.083502 | 0.00089331 | 0.00022388
75 | 0.99559 | -0.084569 | 0.00081994 | 0.0002055
76 | 0.99551 | -0.086122 | 0 | 0
77 | 0.99543 | -0.087723 | 0 | 0
78 | 0.99536 | -0.088914 | 0.00093382 | 0.00023404
79 | 0.98149 | -0.35711 | 0.0006041 | 0.0001514
80 | 0.98151 | -0.35671 | 0.0005105 | 0.00012794
81 | 0.98155 | -0.35606 | 0.00032959 | 8.2603e-05
82 | 0.98084 | -0.36993 | 0.001473 | 0.00036916
83 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0098184 | -0.0024576 | 0.0098239 | 0.0024603 | 5.5076e-06 | 2.6844e-06 | 0.014875 | 0.014875 | 0.014875 | 0.98212 | -0.34481 | 0.98272 | -0.33303 | 4.0865
1 | 0.0060622 | 0.0015162 | -0.0060604 | -0.0015158 | 1.8293e-06 | 4.3911e-07 | 0.0091838 | 0.009184 | 0.009184 | 0.98212 | -0.34481 | 0.9818 | -0.35116 | 2.5231
2 | -0.017586 | -0.0044057 | 0.017617 | 0.0044238 | 3.0688e-05 | 1.8175e-05 | 0.026628 | 0.026627 | 0.026628 | 0.98272 | -0.33303 | 0.98459 | -0.29645 | 7.3153
3 | 0.0020697 | 0.00051629 | -0.0020696 | -0.00051664 | 1.2626e-07 | -3.5208e-07 | 0.003136 | 0.0031362 | 0.0031362 | 0.9818 | -0.35116 | 0.98173 | -0.35244 | 0.86159
4 | 0.0039906 | 0.00099951 | -0.0039897 | -0.00099976 | 8.9641e-07 | -2.5248e-07 | 0.006048 | 0.0060483 | 0.0060483 | 0.9818 | -0.35116 | 0.98155 | -0.35587 | 1.6616
5 | 0.0065367 | 0.0016381 | -0.0065363 | -0.001638 | 3.3328e-07 | 9.7483e-08 | 0.0098788 | 0.0098788 | 0.0098788 | 0.98459 | -0.29645 | 0.98454 | -0.29752 | 2.714
6 | -0.025936 | -0.0065088 | 0.025963 | 0.0065253 | 2.6733e-05 | 1.6519e-05 | 0.039201 | 0.039201 | 0.039201 | 0.98459 | -0.29645 | 0.9857 | -0.27486 | 10.7694
7 | 0.0020696 | 0.00051664 | -0.0020693 | -0.00051741 | 2.7637e-07 | -7.7032e-07 | 0.0031362 | 0.0031365 | 0.0031365 | 0.98173 | -0.35244 | 0.98159 | -0.35525 | 0.86169
8 | 0.0039897 | 0.00099976 | -0.0039894 | -0.00099984 | 3.0778e-07 | -8.6577e-08 | 0.0060483 | 0.0060484 | 0.0060484 | 0.98155 | -0.35587 | 0.98147 | -0.35749 | 1.6616
9 | 0.0014443 | 0.00036076 | -0.0014442 | -0.00036111 | 5.5366e-08 | -3.54e-07 | 0.002189 | 0.0021892 | 0.0021892 | 0.98159 | -0.35525 | 0.98155 | -0.35606 | 0.60142
10 | -0.027778 | -0.0069802 | 0.02778 | 0.0069816 | 2.2127e-06 | 1.3734e-06 | 0.04194 | 0.04194 | 0.04194 | 0.9857 | -0.27486 | 0.98579 | -0.2732 | 11.5221
11 | -0.032116 | -0.0080681 | 0.032142 | 0.0080848 | 2.6665e-05 | 1.668e-05 | 0.048485 | 0.048484 | 0.048485 | 0.98579 | -0.2732 | 0.98668 | -0.25581 | 13.3199
12 | -0.036275 | -0.0091201 | 0.036314 | 0.0091449 | 3.952e-05 | 2.4843e-05 | 0.054717 | 0.054716 | 0.054717 | 0.98668 | -0.25581 | 0.98785 | -0.23303 | 15.032
13 | 0.0019754 | 0.00049465 | -0.0019753 | -0.00049505 | 1.2357e-07 | -3.9511e-07 | 0.0029789 | 0.0029791 | 0.0029791 | 0.98668 | -0.25581 | 0.98661 | -0.25713 | 0.81844
14 | 0.0046991 | 0.0011775 | -0.0046988 | -0.0011775 | 2.2457e-07 | -7.251e-09 | 0.007102 | 0.0071021 | 0.0071021 | 0.98454 | -0.29752 | 0.98449 | -0.29853 | 1.9511
15 | -0.037822 | -0.0095227 | 0.037862 | 0.0095482 | 4.0478e-05 | 2.548e-05 | 0.056987 | 0.056987 | 0.056987 | 0.98785 | -0.23303 | 0.98901 | -0.21067 | 15.6558
16 | 0.0027223 | 0.00068214 | -0.0027223 | -0.00068226 | 8.7299e-08 | -1.1896e-07 | 0.0041147 | 0.0041147 | 0.0041147 | 0.98449 | -0.29853 | 0.98445 | -0.2992 | 1.1304
17 | -0.0028075 | -0.00070363 | 0.0028077 | 0.00070335 | 2.1743e-07 | -2.7789e-07 | 0.0042241 | 0.0042239 | 0.0042241 | 0.98901 | -0.21071 | 0.98909 | -0.20909 | 1.1605
18 | 0.0038538 | 0.00096535 | -0.003853 | -0.00096565 | 7.7833e-07 | -2.9421e-07 | 0.0057975 | 0.0057978 | 0.0057978 | 0.98909 | -0.20909 | 0.98887 | -0.21333 | 1.5928
19 | -0.0066615 | -0.0016687 | 0.0066617 | 0.0016688 | 2.2227e-07 | 6.6503e-08 | 0.010021 | 0.010021 | 0.010021 | 0.98909 | -0.20909 | 0.98913 | -0.20839 | 2.7531
20 | 0.040161 | 0.010126 | -0.040156 | -0.010123 | 4.3817e-06 | 2.7633e-06 | 0.060438 | 0.060438 | 0.060438 | 0.98913 | -0.20839 | 0.98901 | -0.21067 | 16.6039
21 | -0.046822 | -0.011795 | 0.046861 | 0.011819 | 3.8591e-05 | 2.4432e-05 | 0.07046 | 0.07046 | 0.07046 | 0.98913 | -0.20839 | 0.99002 | -0.19117 | 19.3571
22 | -0.049429 | -0.012463 | 0.049442 | 0.012471 | 1.2389e-05 | 7.8521e-06 | 0.07432 | 0.07432 | 0.07432 | 0.99002 | -0.19117 | 0.99029 | -0.18593 | 20.4175
23 | 0.0031542 | 0.00079052 | -0.0031542 | -0.00079052 | 7.4451e-10 | -6.2488e-10 | 0.0047793 | 0.0047793 | 0.0047793 | 0.98206 | -0.346 | 0.98206 | -0.346 | 1.313
24 | -0.0043844 | -0.0010988 | 0.0043859 | 0.0010986 | 1.505e-06 | -1.8792e-07 | 0.0066432 | 0.0066428 | 0.0066432 | 0.98206 | -0.346 | 0.98243 | -0.33879 | 1.8251
25 | -0.016515 | -0.0041347 | 0.016523 | 0.0041395 | 8.1899e-06 | 4.7993e-06 | 0.025013 | 0.025013 | 0.025013 | 0.98243 | -0.33879 | 0.98296 | -0.32838 | 6.8716
26 | 0.012129 | 0.0030361 | -0.012124 | -0.0030333 | 5.058e-06 | 2.7313e-06 | 0.01837 | 0.01837 | 0.01837 | 0.98243 | -0.33879 | 0.98198 | -0.34755 | 5.0467
27 | -0.017532 | -0.0043922 | 0.017537 | 0.0043951 | 4.8045e-06 | 2.8442e-06 | 0.026539 | 0.026539 | 0.026539 | 0.98296 | -0.32838 | 0.98325 | -0.32262 | 7.291
28 | 0.0065822 | 0.0016449 | -0.006579 | -0.001644 | 3.234e-06 | 9.7335e-07 | 0.0099725 | 0.0099729 | 0.0099729 | 0.98198 | -0.34755 | 0.98145 | -0.35789 | 2.7398
29 | 0.0055419 | 0.0013884 | -0.0055357 | -0.0013874 | 6.2295e-06 | 1.0108e-06 | 0.0083976 | 0.0083987 | 0.0083987 | 0.98198 | -0.34755 | 0.98078 | -0.37117 | 2.3073
30 | -0.018564 | -0.0046526 | 0.018589 | 0.0046676 | 2.5019e-05 | 1.4938e-05 | 0.028094 | 0.028094 | 0.028094 | 0.98325 | -0.32262 | 0.9847 | -0.29437 | 7.7182
31 | 0.006579 | 0.001644 | -0.0065752 | -0.0016428 | 3.7613e-06 | 1.1337e-06 | 0.0099729 | 0.0099733 | 0.0099733 | 0.98145 | -0.35789 | 0.98084 | -0.36993 | 2.7399
32 | 0.0068495 | 0.0017153 | -0.0068484 | -0.001715 | 1.0336e-06 | 3.1863e-07 | 0.01023 | 0.01023 | 0.01023 | 0.99625 | -0.071846 | 0.99608 | -0.075016 | 2.8105
33 | -0.009407 | -0.0023563 | 0.0094082 | 0.0023568 | 1.2044e-06 | 5.5893e-07 | 0.01405 | 0.01405 | 0.01405 | 0.99625 | -0.071846 | 0.99639 | -0.069158 | 3.8599
34 | 0.0068484 | 0.001715 | -0.0068473 | -0.0017146 | 1.1075e-06 | 3.4153e-07 | 0.01023 | 0.01023 | 0.01023 | 0.99608 | -0.075016 | 0.99591 | -0.078413 | 2.8105
35 | -0.0094082 | -0.0023568 | 0.0094168 | 0.0023609 | 8.6732e-06 | 4.0232e-06 | 0.01405 | 0.014049 | 0.01405 | 0.99639 | -0.069158 | 0.99739 | -0.049814 | 3.8599
36 | 0.0059759 | 0.0014962 | -0.0059752 | -0.0014961 | 6.6163e-07 | 1.3548e-07 | 0.0089283 | 0.0089284 | 0.0089284 | 0.99591 | -0.078413 | 0.99579 | -0.080739 | 2.4528
37 | -0.01094 | -0.0027427 | 0.010944 | 0.0027445 | 3.6272e-06 | 1.8474e-06 | 0.016322 | 0.016322 | 0.016322 | 0.99739 | -0.049814 | 0.99775 | -0.042858 | 4.4841
38 | 0.0052719 | 0.0013198 | -0.0052715 | -0.0013198 | 3.4551e-07 | 2.7983e-08 | 0.0078773 | 0.0078774 | 0.0078774 | 0.99579 | -0.080739 | 0.99572 | -0.082115 | 2.1641
39 | -0.0018639 | -0.00046694 | 0.001864 | 0.00046684 | 2.6951e-08 | -1.0308e-07 | 0.0027864 | 0.0027863 | 0.0027864 | 0.99539 | -0.088429 | 0.99541 | -0.088125 | 0.76548
40 | 0.0018639 | 0.00046694 | -0.0018639 | -0.00046708 | 3.6421e-08 | -1.3929e-07 | 0.0027864 | 0.0027864 | 0.0027864 | 0.99539 | -0.088429 | 0.99537 | -0.088839 | 0.7655
41 | -0.0027197 | -0.00068131 | 0.0027198 | 0.00068124 | 5.2041e-08 | -7.5836e-08 | 0.0040656 | 0.0040655 | 0.0040656 | 0.99541 | -0.088125 | 0.99543 | -0.087723 | 1.1169
42 | 0.00093383 | 0.00023398 | -0.00093382 | -0.00023404 | 3.346e-09 | -5.7369e-08 | 0.001396 | 0.001396 | 0.001396 | 0.99537 | -0.088839 | 0.99536 | -0.088914 | 0.38352
43 | 0.0023105 | 0.00057894 | -0.0023104 | -0.00057896 | 9.006e-09 | -1.9544e-08 | 0.0034829 | 0.0034829 | 0.0034829 | 0.9871 | -0.24783 | 0.98709 | -0.24791 | 0.95684
44 | -0.0062028 | -0.0015545 | 0.0062038 | 0.0015547 | 9.6195e-07 | 2.4054e-07 | 0.0093505 | 0.0093504 | 0.0093505 | 0.9871 | -0.24783 | 0.98726 | -0.24458 | 2.5688
45 | 0.0020714 | 0.00051906 | -0.0020714 | -0.00051908 | 8.7314e-09 | -2.4936e-08 | 0.0031226 | 0.0031226 | 0.0031226 | 0.98709 | -0.24791 | 0.98709 | -0.248 | 0.85786
46 | -0.0072746 | -0.0018231 | 0.0072757 | 0.0018235 | 1.1252e-06 | 4.009e-07 | 0.010964 | 0.010964 | 0.010964 | 0.98726 | -0.24458 | 0.98743 | -0.24133 | 3.0122
47 | 0.00024643 | 6.1698e-05 | -0.00024643 | -6.1761e-05 | 2.533e-10 | -6.2409e-08 | 0.00037146 | 0.00037149 | 0.00037149 | 0.98709 | -0.248 | 0.98709 | -0.24802 | 0.10206
48 | -0.0079204 | -0.001985 | 0.0079213 | 0.0019854 | 9.0338e-07 | 3.6183e-07 | 0.011936 | 0.011936 | 0.011936 | 0.98743 | -0.24133 | 0.98755 | -0.23894 | 3.279
49 | -0.0085549 | -0.0021442 | 0.0085564 | 0.0021448 | 1.4709e-06 | 6.3928e-07 | 0.01289 | 0.01289 | 0.01289 | 0.98755 | -0.23894 | 0.98774 | -0.23533 | 3.5413
50 | 0.051299 | 0.012957 | -0.051244 | -0.012922 | 5.5598e-05 | 3.5261e-05 | 0.077027 | 0.077027 | 0.077027 | 0.99146 | -0.16329 | 0.99029 | -0.18593 | 21.1614
51 | -0.054565 | -0.013776 | 0.054579 | 0.013785 | 1.4888e-05 | 9.4522e-06 | 0.081928 | 0.081928 | 0.081928 | 0.99146 | -0.16329 | 0.99176 | -0.1576 | 22.5077
52 | -0.11007 | -0.027799 | 0.11032 | 0.027959 | 0.00024933 | 0.00015925 | 0.16522 | 0.16522 | 0.16522 | 0.99176 | -0.1576 | 0.99421 | -0.11044 | 45.3912
53 | 0.055491 | 0.014014 | -0.055438 | -0.01398 | 5.3124e-05 | 3.3736e-05 | 0.083296 | 0.083296 | 0.083296 | 0.99176 | -0.1576 | 0.99072 | -0.1776 | 22.8835
54 | -0.11538 | -0.029227 | 0.11553 | 0.029324 | 0.00015238 | 9.7349e-05 | 0.1728 | 0.1728 | 0.1728 | 0.99421 | -0.11044 | 0.99564 | -0.082988 | 47.4715
55 | 0.052312 | 0.013197 | -0.052229 | -0.013144 | 8.3051e-05 | 5.2692e-05 | 0.0786 | 0.078601 | 0.078601 | 0.99072 | -0.1776 | 0.989 | -0.21081 | 21.5936
56 | -0.11862 | -0.030099 | 0.1188 | 0.030213 | 0.00017889 | 0.00011429 | 0.17742 | 0.17742 | 0.17742 | 0.99564 | -0.082988 | 0.99728 | -0.051683 | 48.741
57 | 0.045176 | 0.011377 | -0.045171 | -0.011373 | 5.0032e-06 | 3.165e-06 | 0.067989 | 0.067989 | 0.067989 | 0.989 | -0.21081 | 0.98888 | -0.21313 | 18.6784
58 | 0.026864 | 0.0067576 | -0.026848 | -0.0067474 | 1.6456e-05 | 1.0191e-05 | 0.040525 | 0.040525 | 0.040525 | 0.98663 | -0.25691 | 0.98597 | -0.26975 | 11.1332
59 | -0.030173 | -0.0075869 | 0.030212 | 0.007611 | 3.8615e-05 | 2.4078e-05 | 0.045515 | 0.045515 | 0.045515 | 0.98663 | -0.25691 | 0.988 | -0.23015 | 12.5042
60 | 0.024723 | 0.006215 | -0.024694 | -0.0061972 | 2.9038e-05 | 1.7876e-05 | 0.037319 | 0.037319 | 0.037319 | 0.98597 | -0.26975 | 0.9847 | -0.29437 | 10.2526
61 | 0.010686 | 0.0026789 | -0.010684 | -0.0026776 | 2.6341e-06 | 1.3387e-06 | 0.016095 | 0.016095 | 0.016095 | 0.988 | -0.23015 | 0.98774 | -0.23533 | 4.4217
62 | -0.040898 | -0.01029 | 0.040931 | 0.010311 | 3.3301e-05 | 2.1013e-05 | 0.06161 | 0.06161 | 0.06161 | 0.988 | -0.23015 | 0.98888 | -0.21313 | 16.9259
63 | 0.0061052 | 0.0015296 | -0.0061046 | -0.0015295 | 5.7367e-07 | 1.3853e-07 | 0.0092255 | 0.0092256 | 0.0092256 | 0.9847 | -0.29437 | 0.9846 | -0.29635 | 2.5345
64 | 0.0021275 | 0.00053276 | -0.0021274 | -0.00053299 | 8.7415e-08 | -2.3453e-07 | 0.0032048 | 0.0032049 | 0.0032049 | 0.98774 | -0.23533 | 0.98769 | -0.23619 | 0.88048
65 | 0.0028852 | 0.00072304 | -0.0028851 | -0.00072308 | 3.657e-08 | -4.183e-08 | 0.0043603 | 0.0043603 | 0.0043603 | 0.9846 | -0.29635 | 0.98459 | -0.29661 | 1.1979
66 | 0.0032194 | 0.00080641 | -0.0032193 | -0.0008065 | 1.125e-07 | -8.9177e-08 | 0.0048653 | 0.0048654 | 0.0048654 | 0.9846 | -0.29635 | 0.98456 | -0.29708 | 1.3366
67 | 0.0005432 | 0.00013596 | -0.0005432 | -0.00013614 | 3.4661e-09 | -1.7443e-07 | 0.0008183 | 0.00081836 | 0.00081836 | 0.98769 | -0.23619 | 0.98769 | -0.23633 | 0.22482
68 | -0.12391 | -0.031494 | 0.12401 | 0.031556 | 9.6595e-05 | 6.1723e-05 | 0.18504 | 0.18504 | 0.18504 | 0.99728 | -0.051683 | 0.99813 | -0.035509 | 50.8354
69 | 0.017039 | 0.0042741 | -0.017034 | -0.0042709 | 5.4917e-06 | 3.2182e-06 | 0.025404 | 0.025404 | 0.025404 | 0.99813 | -0.035509 | 0.99778 | -0.042272 | 6.979
70 | -0.14105 | -0.03583 | 0.14114 | 0.035885 | 8.7235e-05 | 5.5555e-05 | 0.21044 | 0.21044 | 0.21044 | 0.99813 | -0.035509 | 0.99881 | -0.022669 | 28.9072
71 | 0.013922 | 0.0034911 | -0.013922 | -0.0034908 | 3.8907e-07 | 2.1757e-07 | 0.020763 | 0.020763 | 0.020763 | 0.99778 | -0.042272 | 0.99775 | -0.042858 | 5.7042
72 | -0.14281 | -0.036304 | 0.14296 | 0.036403 | 0.00015611 | 9.9428e-05 | 0.21293 | 0.21293 | 0.21293 | 0.99881 | -0.022669 | 1 | 0 | 29.2489
73 | 0.0013112 | 0.00032829 | -0.0013112 | -0.00032861 | 4.0498e-08 | -3.2381e-07 | 0.0019816 | 0.0019817 | 0.0019817 | 0.98456 | -0.29708 | 0.98453 | -0.29773 | 0.54443
74 | -0.00073684 | -0.00018467 | 0.00073699 | 0.00018086 | 1.4562e-07 | -3.8073e-06 | 0.0011198 | 0.0011184 | 0.0011198 | 0.97912 | -0.40375 | 0.97933 | -0.39957 | 0.30764
75 | -0.0050951 | -0.0012731 | 0.0051022 | 0.0012737 | 7.1823e-06 | 5.6713e-07 | 0.0077401 | 0.0077387 | 0.0077401 | 0.97933 | -0.39957 | 0.98084 | -0.36993 | 2.1264
76 | 0.0044339 | 0.0011099 | -0.0044336 | -0.0011099 | 2.9266e-07 | -4.3916e-08 | 0.0066256 | 0.0066257 | 0.0066257 | 0.99572 | -0.082115 | 0.99564 | -0.083502 | 1.8202
77 | 0.0035403 | 0.00088603 | -0.0035401 | -0.00088614 | 1.7964e-07 | -1.0759e-07 | 0.0052906 | 0.0052907 | 0.0052907 | 0.99564 | -0.083502 | 0.99559 | -0.084569 | 1.4535
78 | 0.0027202 | 0.00068064 | -0.00272 | -0.00068094 | 2.0104e-07 | -2.9312e-07 | 0.0040652 | 0.0040654 | 0.0040654 | 0.99559 | -0.084569 | 0.99551 | -0.086122 | 1.1169
79 | 0.00272 | 0.00068094 | -0.0027198 | -0.00068124 | 2.0743e-07 | -3.0234e-07 | 0.0040654 | 0.0040655 | 0.0040655 | 0.99551 | -0.086122 | 0.99543 | -0.087723 | 1.1169
80 | -0.0006041 | -0.0001514 | 0.00060411 | 0.00015095 | 1.1325e-08 | -4.4788e-07 | 0.00091586 | 0.0009157 | 0.00091586 | 0.98149 | -0.35711 | 0.98151 | -0.35671 | 0.25161
81 | -0.0011146 | -0.0002789 | 0.0011146 | 0.00027851 | 3.4665e-08 | -3.871e-07 | 0.0016896 | 0.0016895 | 0.0016896 | 0.98151 | -0.35671 | 0.98155 | -0.35606 | 0.46419

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.14736 | 0.037092

## res_load
| p_mw | q_mvar
0 | 0.0037562 | 0.0009414
1 | 0.007762 | 0.0019453
2 | 0.0017831 | 0.00044689
3 | 0.00062505 | 0.00015665
4 | 0.0039894 | 0.00099984
5 | 0.001815 | 0.00045489
6 | 0.0043354 | 0.0010866
7 | 0.0021571 | 0.00054063
8 | 0.0018373 | 0.00046046
9 | 0.0015074 | 0.0003778
10 | 0.0019753 | 0.00049505
11 | 0.0019765 | 0.00049535
12 | 0.0027223 | 0.00068226
13 | 0.0028075 | 0.00070363
14 | 0.003853 | 0.00096565
15 | 0.002294 | 0.00057493
16 | 0.0025682 | 0.00064366
17 | 0.0012302 | 0.00030831
18 | 0.0031542 | 0.00079052
19 | 0.0010084 | 0.00025273
20 | 0.0010276 | 0.00025755
21 | 0.0055357 | 0.0013874
22 | 0.0025575 | 0.00064097
23 | 0.00087141 | 0.0002184
24 | 0.0015234 | 0.0003818
25 | 0.00070335 | 0.00017628
26 | 0.00085576 | 0.00021447
27 | 0.00093008 | 0.0002331
28 | 0.0038924 | 0.00097552
29 | 0.00023902 | 5.9903e-05
30 | 0.0010708 | 0.00026837
31 | 0.001825 | 0.00045739
32 | 0.00064461 | 0.00016155
33 | 0.00024643 | 6.1761e-05
34 | 0.00063366 | 0.00015881
35 | 0.0032654 | 0.00081838
36 | 0.0018019 | 0.00045161
37 | 0.0050596 | 0.0012681
38 | 0.0031263 | 0.00078353
39 | 0.0030918 | 0.00077489
40 | 0.0070526 | 0.0017676
41 | 0.0033091 | 0.00082933
42 | 0.0021241 | 0.00053236
43 | 0.0042396 | 0.0010625
44 | 0.0015842 | 0.00039703
45 | 0.0051096 | 0.0012806
46 | 0.0031116 | 0.00077985
47 | 0.00167 | 0.00041854
48 | 0.0019081 | 0.00047821
49 | 0.0013112 | 0.00032861
50 | 0.0028851 | 0.00072308
51 | 0.0005432 | 0.00013614
52 | 0.002978 | 0.00074635
53 | 0.0027457 | 0.00068814
54 | 0.00073684 | 0.00018467
55 | 0.0043581 | 0.0010922
56 | 0.00083764 | 0.00020993
57 | 0.00089331 | 0.00022388
58 | 0.00081994 | 0.0002055
59 | 0.00093382 | 0.00023404
60 | 0.0006041 | 0.0001514
61 | 0.0005105 | 0.00012794
62 | 0.00032959 | 8.2603e-05
63 | 0.001473 | 0.00036916

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1