## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2135-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2135-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2135-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2135-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2135-4_0_4_node_35 | 0.4 | n |  | TRUE
5 | bus_LV_2135-4_0_4_node_223 | 0.4 | n |  | TRUE
6 | bus_LV_2135-4_0_4_node_33 | 0.4 | n |  | TRUE
7 | bus_LV_2135-4_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_2135-4_0_4_node_224 | 0.4 | n |  | TRUE
9 | bus_LV_2135-4_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2135-4_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2135-4_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2135-4_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2135-4_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2135-4_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2135-4_0_4_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_2135-4_0_4_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_2135-4_0_4_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2135-4_0_4_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_2135-4_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2135-4_0_4_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_2135-4_0_4_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_2135-4_0_4_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_2135-4_0_4_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_2135-4_0_4_node_84 | 0.4 | n |  | TRUE
25 | bus_LV_2135-4_0_4_node_87 | 0.4 | n |  | TRUE
26 | bus_LV_2135-4_0_4_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_2135-4_0_4_node_11 | 0.4 | n |  | TRUE
28 | bus_LV_2135-4_0_4_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_2135-4_0_4_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_2135-4_0_4_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_2135-4_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_2135-4_0_4_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_2135-4_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_2135-4_0_4_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_2135-4_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_2135-4_0_4_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_2135-4_0_4_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_2135-4_0_4_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_2135-4_0_4_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_2135-4_0_4_node_91 | 0.4 | n |  | TRUE
41 | bus_LV_2135-4_0_4_node_92 | 0.4 | n |  | TRUE
42 | bus_LV_2135-4_0_4_node_90 | 0.4 | n |  | TRUE
43 | bus_LV_2135-4_0_4_node_86 | 0.4 | n |  | TRUE
44 | bus_LV_2135-4_0_4_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_2135-4_0_4_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_2135-4_0_4_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_2135-4_0_4_node_77 | 0.4 | n |  | TRUE
48 | bus_LV_2135-4_0_4_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_2135-4_0_4_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_2135-4_0_4_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_2135-4_0_4_node_85 | 0.4 | n |  | TRUE
52 | bus_LV_2135-4_0_4_node_94 | 0.4 | n |  | TRUE
53 | bus_LV_2135-4_0_4_node_88 | 0.4 | n |  | TRUE
54 | bus_LV_2135-4_0_4_node_89 | 0.4 | n |  | TRUE
55 | bus_LV_2135-4_0_4_node_93 | 0.4 | n |  | TRUE
56 | bus_LV_2135-4_0_4_node_144 | 0.4 | n |  | TRUE
57 | bus_LV_2135-4_0_4_node_95 | 0.4 | n |  | TRUE
58 | bus_LV_2135-4_0_4_node_99 | 0.4 | n |  | TRUE
59 | bus_LV_2135-4_0_4_node_149 | 0.4 | n |  | TRUE
60 | bus_LV_2135-4_0_4_node_142 | 0.4 | n |  | TRUE
61 | bus_LV_2135-4_0_4_node_137 | 0.4 | n |  | TRUE
62 | bus_LV_2135-4_0_4_node_96 | 0.4 | n |  | TRUE
63 | bus_LV_2135-4_0_4_node_97 | 0.4 | n |  | TRUE
64 | bus_LV_2135-4_0_4_node_98 | 0.4 | n |  | TRUE
65 | bus_LV_2135-4_0_4_node_169 | 0.4 | n |  | TRUE
66 | bus_LV_2135-4_0_4_node_172 | 0.4 | n |  | TRUE
67 | bus_LV_2135-4_0_4_node_136 | 0.4 | n |  | TRUE
68 | bus_LV_2135-4_0_4_node_100 | 0.4 | n |  | TRUE
69 | bus_LV_2135-4_0_4_node_101 | 0.4 | n |  | TRUE
70 | bus_LV_2135-4_0_4_node_102 | 0.4 | n |  | TRUE
71 | bus_LV_2135-4_0_4_node_123 | 0.4 | n |  | TRUE
72 | bus_LV_2135-4_0_4_node_153 | 0.4 | n |  | TRUE
73 | bus_LV_2135-4_0_4_node_120 | 0.4 | n |  | TRUE
74 | bus_LV_2135-4_0_4_node_151 | 0.4 | n |  | TRUE
75 | bus_LV_2135-4_0_4_node_103 | 0.4 | n |  | TRUE
76 | bus_LV_2135-4_0_4_node_104 | 0.4 | n |  | TRUE
77 | bus_LV_2135-4_0_4_node_105 | 0.4 | n |  | TRUE
78 | bus_LV_2135-4_0_4_node_106 | 0.4 | n |  | TRUE
79 | bus_LV_2135-4_0_4_node_107 | 0.4 | n |  | TRUE
80 | bus_LV_2135-4_0_4_node_108 | 0.4 | n |  | TRUE
81 | bus_LV_2135-4_0_4_node_109 | 0.4 | n |  | TRUE
82 | bus_LV_2135-4_0_4_node_168 | 0.4 | n |  | TRUE
83 | bus_LV_2135-4_0_4_node_122 | 0.4 | n |  | TRUE
84 | bus_LV_2135-4_0_4_node_173 | 0.4 | n |  | TRUE
85 | bus_LV_2135-4_0_4_node_119 | 0.4 | n |  | TRUE
86 | bus_LV_2135-4_0_4_node_110 | 0.4 | n |  | TRUE
87 | bus_LV_2135-4_0_4_node_111 | 0.4 | n |  | TRUE
88 | bus_LV_2135-4_0_4_node_112 | 0.4 | n |  | TRUE
89 | bus_LV_2135-4_0_4_node_113 | 0.4 | n |  | TRUE
90 | bus_LV_2135-4_0_4_node_114 | 0.4 | n |  | TRUE
91 | bus_LV_2135-4_0_4_node_115 | 0.4 | n |  | TRUE
92 | bus_LV_2135-4_0_4_node_116 | 0.4 | n |  | TRUE
93 | bus_LV_2135-4_0_4_node_134 | 0.4 | n |  | TRUE
94 | bus_LV_2135-4_0_4_node_148 | 0.4 | n |  | TRUE
95 | bus_LV_2135-4_0_4_node_135 | 0.4 | n |  | TRUE
96 | bus_LV_2135-4_0_4_node_147 | 0.4 | n |  | TRUE
97 | bus_LV_2135-4_0_4_node_117 | 0.4 | n |  | TRUE
98 | bus_LV_2135-4_0_4_node_118 | 0.4 | n |  | TRUE
99 | bus_LV_2135-4_0_4_node_124 | 0.4 | n |  | TRUE
100 | bus_LV_2135-4_0_4_node_125 | 0.4 | n |  | TRUE
101 | bus_LV_2135-4_0_4_node_126 | 0.4 | n |  | TRUE
102 | bus_LV_2135-4_0_4_node_127 | 0.4 | n |  | TRUE
103 | bus_LV_2135-4_0_4_node_128 | 0.4 | n |  | TRUE
104 | bus_LV_2135-4_0_4_node_129 | 0.4 | n |  | TRUE
105 | bus_LV_2135-4_0_4_node_130 | 0.4 | n |  | TRUE
106 | bus_LV_2135-4_0_4_node_131 | 0.4 | n |  | TRUE
107 | bus_LV_2135-4_0_4_node_132 | 0.4 | n |  | TRUE
108 | bus_LV_2135-4_0_4_node_165 | 0.4 | n |  | TRUE
109 | bus_LV_2135-4_0_4_node_133 | 0.4 | n |  | TRUE
110 | bus_LV_2135-4_0_4_node_163 | 0.4 | n |  | TRUE
111 | bus_LV_2135-4_0_4_node_138 | 0.4 | n |  | TRUE
112 | bus_LV_2135-4_0_4_node_139 | 0.4 | n |  | TRUE
113 | bus_LV_2135-4_0_4_node_140 | 0.4 | n |  | TRUE
114 | bus_LV_2135-4_0_4_node_141 | 0.4 | n |  | TRUE
115 | bus_LV_2135-4_0_4_node_143 | 0.4 | n |  | TRUE
116 | bus_LV_2135-4_0_4_node_145 | 0.4 | n |  | TRUE
117 | bus_LV_2135-4_0_4_node_171 | 0.4 | n |  | TRUE
118 | bus_LV_2135-4_0_4_node_146 | 0.4 | n |  | TRUE
119 | bus_LV_2135-4_0_4_node_170 | 0.4 | n |  | TRUE
120 | bus_LV_2135-4_0_4_node_162 | 0.4 | n |  | TRUE
121 | bus_LV_2135-4_0_4_node_150 | 0.4 | n |  | TRUE
122 | bus_LV_2135-4_0_4_node_152 | 0.4 | n |  | TRUE
123 | bus_LV_2135-4_0_4_node_154 | 0.4 | n |  | TRUE
124 | bus_LV_2135-4_0_4_node_155 | 0.4 | n |  | TRUE
125 | bus_LV_2135-4_0_4_node_156 | 0.4 | n |  | TRUE
126 | bus_LV_2135-4_0_4_node_157 | 0.4 | n |  | TRUE
127 | bus_LV_2135-4_0_4_node_158 | 0.4 | n |  | TRUE
128 | bus_LV_2135-4_0_4_node_159 | 0.4 | n |  | TRUE
129 | bus_LV_2135-4_0_4_node_160 | 0.4 | n |  | TRUE
130 | bus_LV_2135-4_0_4_node_161 | 0.4 | n |  | TRUE
131 | bus_LV_2135-4_0_4_node_167 | 0.4 | n |  | TRUE
132 | bus_LV_2135-4_0_4_node_166 | 0.4 | n |  | TRUE
133 | bus_LV_2135-4_0_4_node_164 | 0.4 | n |  | TRUE
134 | bus_MV_28_0_node_80 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2135-4_0_4_load_0 | 0 | 0.0053024 | 0.0013289 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2135-4_0_4_load_1 | 1 | 0.00073375 | 0.00018389 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2135-4_0_4_load_2 | 2 | 0.0015167 | 0.00038012 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2135-4_0_4_load_35 | 4 | 0.00028327 | 7.0995e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2135-4_0_4_load_223 | 5 | 0.007259 | 0.0018193 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2135-4_0_4_load_224 | 8 | 0.0055671 | 0.0013953 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2135-4_0_4_load_5 | 9 | 0.004874 | 0.0012215 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2135-4_0_4_load_7 | 11 | 0.0041256 | 0.001034 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2135-4_0_4_load_8 | 12 | 0.00047961 | 0.0001202 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2135-4_0_4_load_18 | 15 | 0.00049723 | 0.00012462 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2135-4_0_4_load_29 | 16 | 0.0014557 | 0.00036484 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2135-4_0_4_load_34 | 18 | 0.00020157 | 5.0518e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2135-4_0_4_load_15 | 19 | 0.0022864 | 0.00057303 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2135-4_0_4_load_30 | 20 | 0.00058121 | 0.00014567 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2135-4_0_4_load_21 | 22 | 0.00079973 | 0.00020043 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2135-4_0_4_load_84 | 24 | 0.0036022 | 0.0009028 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2135-4_0_4_load_32 | 26 | 0.0002271 | 5.6916e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2135-4_0_4_load_11 | 27 | 0.00082814 | 0.00020755 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2135-4_0_4_load_12 | 28 | 0.00097245 | 0.00024372 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2135-4_0_4_load_14 | 30 | 0.00091795 | 0.00023006 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2135-4_0_4_load_16 | 31 | 0.0016708 | 0.00041874 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2135-4_0_4_load_27 | 34 | 0.0015551 | 0.00038974 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2135-4_0_4_load_28 | 35 | 0.001378 | 0.00034536 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2135-4_0_4_load_41 | 37 | 0.0018219 | 0.00045662 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2135-4_0_4_load_20 | 38 | 0.00087973 | 0.00022048 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2135-4_0_4_load_23 | 39 | 0.0010859 | 0.00027214 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2135-4_0_4_load_91 | 40 | 0.00036851 | 9.2358e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2135-4_0_4_load_92 | 41 | 0.00019285 | 4.8334e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2135-4_0_4_load_90 | 42 | 9.2678e-05 | 2.3227e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2135-4_0_4_load_86 | 43 | 0.00021654 | 5.427e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2135-4_0_4_load_40 | 44 | 0.001829 | 0.0004584 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2135-4_0_4_load_77 | 47 | 0.00056949 | 0.00014273 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2135-4_0_4_load_37 | 48 | 0.002871 | 0.00071953 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2135-4_0_4_load_38 | 49 | 0.003606 | 0.00090374 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2135-4_0_4_load_39 | 50 | 0.0028783 | 0.00072137 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2135-4_0_4_load_85 | 51 | 0.00053099 | 0.00013308 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2135-4_0_4_load_94 | 52 | 0.00081384 | 0.00020397 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2135-4_0_4_load_89 | 54 | 0.00072032 | 0.00018053 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2135-4_0_4_load_93 | 55 | 0.0020204 | 0.00050637 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2135-4_0_4_load_95 | 57 | 0.00072298 | 0.00018119 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2135-4_0_4_load_99 | 58 | 0.0039816 | 0.00099788 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2135-4_0_4_load_149 | 59 | 0.0030029 | 0.00075259 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2135-4_0_4_load_137 | 61 | 0.002229 | 0.00055863 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2135-4_0_4_load_96 | 62 | 0.0032519 | 0.000815 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2135-4_0_4_load_97 | 63 | 0.0017866 | 0.00044777 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2135-4_0_4_load_98 | 64 | 0.0034459 | 0.00086361 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2135-4_0_4_load_169 | 65 | 0.0022586 | 0.00056605 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2135-4_0_4_load_172 | 66 | 0.00062999 | 0.00015789 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2135-4_0_4_load_136 | 67 | 0.0018617 | 0.00046659 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2135-4_0_4_load_100 | 68 | 0.0017767 | 0.00044529 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2135-4_0_4_load_101 | 69 | 0.0018806 | 0.00047131 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2135-4_0_4_load_153 | 72 | 0.0030117 | 0.00075481 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2135-4_0_4_load_120 | 73 | 0.0011874 | 0.0002976 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2135-4_0_4_load_151 | 74 | 0.0022134 | 0.00055472 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2135-4_0_4_load_103 | 75 | 0.0007362 | 0.00018451 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2135-4_0_4_load_104 | 76 | 0.00048645 | 0.00012192 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2135-4_0_4_load_105 | 77 | 0.0016048 | 0.00040221 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2135-4_0_4_load_106 | 78 | 0.00058419 | 0.00014641 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2135-4_0_4_load_107 | 79 | 0.00086677 | 0.00021723 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2135-4_0_4_load_168 | 82 | 0.00030791 | 7.7171e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2135-4_0_4_load_122 | 83 | 0.0012171 | 0.00030503 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2135-4_0_4_load_110 | 86 | 0.0020775 | 0.00052067 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2135-4_0_4_load_111 | 87 | 0.0016069 | 0.00040272 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2135-4_0_4_load_112 | 88 | 0.0015758 | 0.00039493 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2135-4_0_4_load_113 | 89 | 0.0018286 | 0.0004583 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2135-4_0_4_load_114 | 90 | 0.0031302 | 0.00078451 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2135-4_0_4_load_115 | 91 | 0.0023892 | 0.00059878 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2135-4_0_4_load_116 | 92 | 0.0012001 | 0.00030077 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2135-4_0_4_load_134 | 93 | 0.0022041 | 0.0005524 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2135-4_0_4_load_148 | 94 | 0.0031321 | 0.00078497 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2135-4_0_4_load_135 | 95 | 0.0017765 | 0.00044523 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2135-4_0_4_load_147 | 96 | 0.0012003 | 0.00030081 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2135-4_0_4_load_117 | 97 | 0.0017071 | 0.00042783 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2135-4_0_4_load_118 | 98 | 0.001644 | 0.00041202 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2135-4_0_4_load_124 | 99 | 0.0028935 | 0.00072517 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2135-4_0_4_load_125 | 100 | 0.0017743 | 0.00044469 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2135-4_0_4_load_126 | 101 | 0.0017767 | 0.00044529 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2135-4_0_4_load_127 | 102 | 0.0017767 | 0.00044529 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2135-4_0_4_load_128 | 103 | 0.0017767 | 0.00044529 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2135-4_0_4_load_129 | 104 | 0.0017774 | 0.00044547 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2135-4_0_4_load_130 | 105 | 0.0017775 | 0.00044547 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2135-4_0_4_load_131 | 106 | 0.0017767 | 0.00044529 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2135-4_0_4_load_132 | 107 | 0.0017767 | 0.00044529 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2135-4_0_4_load_165 | 108 | 0.0017774 | 0.00044547 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2135-4_0_4_load_133 | 109 | 0.0017762 | 0.00044515 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2135-4_0_4_load_163 | 110 | 0.0017767 | 0.00044529 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2135-4_0_4_load_138 | 111 | 0.0022147 | 0.00055506 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2135-4_0_4_load_139 | 112 | 0.0022134 | 0.00055473 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2135-4_0_4_load_140 | 113 | 0.0022134 | 0.00055473 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2135-4_0_4_load_141 | 114 | 0.0022156 | 0.00055529 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2135-4_0_4_load_143 | 115 | 0.0022134 | 0.00055472 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2135-4_0_4_load_145 | 116 | 0.0017765 | 0.00044523 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2135-4_0_4_load_146 | 118 | 0.0031302 | 0.00078451 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2135-4_0_4_load_170 | 119 | 0.0022147 | 0.00055505 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2135-4_0_4_load_162 | 120 | 0.0022129 | 0.00055459 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2135-4_0_4_load_150 | 121 | 0.0022147 | 0.00055505 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2135-4_0_4_load_152 | 122 | 0.0022147 | 0.00055505 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2135-4_0_4_load_154 | 123 | 0.0022135 | 0.00055475 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2135-4_0_4_load_155 | 124 | 0.0022145 | 0.00055502 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2135-4_0_4_load_156 | 125 | 0.0022135 | 0.00055475 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2135-4_0_4_load_157 | 126 | 0.0017774 | 0.00044546 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2135-4_0_4_load_158 | 127 | 0.0022129 | 0.00055459 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2135-4_0_4_load_159 | 128 | 0.0022146 | 0.00055502 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2135-4_0_4_load_160 | 129 | 0.0022142 | 0.00055492 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2135-4_0_4_load_161 | 130 | 0.0017774 | 0.00044546 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2135-4_0_4_load_167 | 131 | 0.0017755 | 0.00044497 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2135-4_0_4_load_166 | 132 | 0.0017774 | 0.00044547 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2135-4_0_4_load_164 | 133 | 0.0017774 | 0.00044547 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 53 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2135-4_0_4_line_0 |  | 0 | 1 | 0.033822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2135-4_0_4_line_1 |  | 0 | 2 | 0.0064562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2135-4_0_4_line_2 |  | 1 | 3 | 0.013436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2135-4_0_4_line_3 |  | 3 | 7 | 0.011732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2135-4_0_4_line_4 |  | 4 | 5 | 0.16338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2135-4_0_4_line_5 |  | 4 | 6 | 0.063082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2135-4_0_4_line_6 |  | 5 | 7 | 0.061772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2135-4_0_4_line_7 |  | 6 | 46 | 0.053044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2135-4_0_4_line_8 |  | 6 | 45 | 0.11575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2135-4_0_4_line_9 |  | 7 | 8 | 0.050434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2135-4_0_4_line_10 |  | 9 | 10 | 0.037889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2135-4_0_4_line_11 |  | 10 | 11 | 0.03091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2135-4_0_4_line_12 |  | 10 | 12 | 0.024863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2135-4_0_4_line_13 |  | 12 | 13 | 0.047724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2135-4_0_4_line_14 |  | 13 | 17 | 0.062673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2135-4_0_4_line_15 |  | 13 | 18 | 0.048348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2135-4_0_4_line_16 |  | 14 | 15 | 0.035586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2135-4_0_4_line_17 |  | 14 | 16 | 0.0081299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2135-4_0_4_line_18 |  | 15 | 19 | 0.039744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2135-4_0_4_line_19 |  | 16 | 20 | 0.010425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_2135-4_0_4_line_20 |  | 17 | 21 | 0.017543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2135-4_0_4_line_21 |  | 17 | 22 | 0.037864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2135-4_0_4_line_22 |  | 18 | 26 | 0.0052608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_2135-4_0_4_line_23 |  | 19 | 29 | 0.048323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2135-4_0_4_line_24 |  | 20 | 45 | 0.028758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_2135-4_0_4_line_25 |  | 21 | 23 | 0.024678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2135-4_0_4_line_26 |  | 22 | 38 | 0.047986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2135-4_0_4_line_27 |  | 23 | 24 | 0.031008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2135-4_0_4_line_28 |  | 23 | 25 | 0.05145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2135-4_0_4_line_29 |  | 25 | 42 | 0.050858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_2135-4_0_4_line_30 |  | 25 | 43 | 0.076227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2135-4_0_4_line_31 |  | 26 | 45 | 0.034247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2135-4_0_4_line_32 |  | 27 | 28 | 0.031479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2135-4_0_4_line_33 |  | 27 | 29 | 0.026045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2135-4_0_4_line_34 |  | 28 | 30 | 0.0099496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2135-4_0_4_line_35 |  | 29 | 31 | 0.025766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2135-4_0_4_line_36 |  | 30 | 32 | 0.036762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2135-4_0_4_line_37 |  | 32 | 33 | 0.036314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_2135-4_0_4_line_38 |  | 32 | 34 | 0.0075841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2135-4_0_4_line_39 |  | 33 | 35 | 0.00077216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2135-4_0_4_line_40 |  | 34 | 36 | 0.10157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2135-4_0_4_line_41 |  | 35 | 37 | 0.032045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2135-4_0_4_line_42 |  | 36 | 39 | 0.019637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2135-4_0_4_line_43 |  | 37 | 44 | 0.039085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2135-4_0_4_line_44 |  | 40 | 41 | 0.048174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2135-4_0_4_line_45 |  | 41 | 51 | 0.080636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2135-4_0_4_line_46 |  | 42 | 52 | 0.19106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2135-4_0_4_line_47 |  | 43 | 51 | 0.020921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2135-4_0_4_line_48 |  | 44 | 50 | 0.0087898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2135-4_0_4_line_49 |  | 46 | 47 | 0.034997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2135-4_0_4_line_50 |  | 48 | 49 | 0.023009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2135-4_0_4_line_51 |  | 49 | 50 | 0.0044436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2135-4_0_4_line_52 |  | 52 | 57 | 0.0064801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2135-4_0_4_line_53 |  | 53 | 54 | 0.019338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2135-4_0_4_line_54 |  | 54 | 55 | 0.028761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_2135-4_0_4_line_55 |  | 55 | 56 | 0.05622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_2135-4_0_4_line_56 |  | 56 | 59 | 0.065894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2135-4_0_4_line_57 |  | 56 | 60 | 0.030059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2135-4_0_4_line_58 |  | 57 | 58 | 0.30733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_2135-4_0_4_line_59 |  | 58 | 61 | 0.35414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_2135-4_0_4_line_60 |  | 59 | 99 | 0.016525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2135-4_0_4_line_61 |  | 60 | 116 | 0.010708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_2135-4_0_4_line_62 |  | 60 | 113 | 0.012386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2135-4_0_4_line_63 |  | 61 | 67 | 0.013058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_2135-4_0_4_line_64 |  | 62 | 63 | 0.090802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2135-4_0_4_line_65 |  | 63 | 64 | 0.019592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2135-4_0_4_line_66 |  | 64 | 65 | 0.017508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2135-4_0_4_line_67 |  | 65 | 66 | 0.031784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2135-4_0_4_line_68 |  | 66 | 84 | 0.032548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2135-4_0_4_line_69 |  | 67 | 95 | 0.032294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2135-4_0_4_line_70 |  | 68 | 69 | 0.11122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2135-4_0_4_line_71 |  | 69 | 70 | 0.083013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2135-4_0_4_line_72 |  | 70 | 71 | 0.06489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2135-4_0_4_line_73 |  | 70 | 72 | 0.01773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2135-4_0_4_line_74 |  | 71 | 73 | 0.0080724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2135-4_0_4_line_75 |  | 72 | 74 | 0.028097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2135-4_0_4_line_76 |  | 73 | 98 | 0.0080793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2135-4_0_4_line_77 |  | 74 | 121 | 0.0093574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2135-4_0_4_line_78 |  | 75 | 76 | 0.018909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2135-4_0_4_line_79 |  | 75 | 77 | 0.0092203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2135-4_0_4_line_80 |  | 76 | 78 | 0.019194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2135-4_0_4_line_81 |  | 77 | 79 | 0.038436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2135-4_0_4_line_82 |  | 78 | 80 | 0.014855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2135-4_0_4_line_83 |  | 79 | 81 | 0.035606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2135-4_0_4_line_84 |  | 80 | 82 | 0.046939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2135-4_0_4_line_85 |  | 80 | 83 | 0.024076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2135-4_0_4_line_86 |  | 81 | 84 | 0.061984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2135-4_0_4_line_87 |  | 83 | 85 | 0.032447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2135-4_0_4_line_88 |  | 85 | 97 | 0.012136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2135-4_0_4_line_89 |  | 86 | 87 | 0.017894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2135-4_0_4_line_90 |  | 86 | 88 | 0.0080998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_2135-4_0_4_line_91 |  | 87 | 89 | 0.01837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_2135-4_0_4_line_92 |  | 88 | 90 | 0.024668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_2135-4_0_4_line_93 |  | 89 | 91 | 0.0076366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_2135-4_0_4_line_94 |  | 90 | 92 | 0.0033327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_2135-4_0_4_line_95 |  | 91 | 93 | 0.02423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_2135-4_0_4_line_96 |  | 92 | 94 | 0.006319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_2135-4_0_4_line_97 |  | 93 | 95 | 0.0045405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2135-4_0_4_line_98 |  | 94 | 96 | 0.0033348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_2135-4_0_4_line_99 |  | 96 | 118 | 0.006025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2135-4_0_4_line_100 |  | 97 | 98 | 0.0040489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2135-4_0_4_line_101 |  | 100 | 101 | 0.0080911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2135-4_0_4_line_102 |  | 100 | 102 | 0.0012886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2135-4_0_4_line_103 |  | 101 | 103 | 0.0015804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2135-4_0_4_line_104 |  | 102 | 104 | 0.0080913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2135-4_0_4_line_105 |  | 103 | 105 | 0.0080924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2135-4_0_4_line_106 |  | 104 | 106 | 0.0072424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2135-4_0_4_line_107 |  | 105 | 107 | 0.007294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2135-4_0_4_line_108 |  | 106 | 108 | 0.0096376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2135-4_0_4_line_109 |  | 107 | 109 | 0.0025533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2135-4_0_4_line_110 |  | 108 | 110 | 3.7385e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2135-4_0_4_line_111 |  | 110 | 133 | 0.0093776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2135-4_0_4_line_112 |  | 111 | 112 | 0.0093618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2135-4_0_4_line_113 |  | 111 | 113 | 0.0096533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2135-4_0_4_line_114 |  | 112 | 114 | 0.01567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2135-4_0_4_line_115 |  | 114 | 115 | 0.0096554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2135-4_0_4_line_116 |  | 115 | 117 | 0.0054702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2135-4_0_4_line_117 |  | 116 | 118 | 0.0033347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_2135-4_0_4_line_118 |  | 117 | 119 | 0.0037651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2135-4_0_4_line_119 |  | 117 | 120 | 0.011484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2135-4_0_4_line_120 |  | 119 | 124 | 0.0064186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2135-4_0_4_line_121 |  | 120 | 129 | 0.013813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2135-4_0_4_line_122 |  | 121 | 122 | 0.010075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2135-4_0_4_line_123 |  | 122 | 123 | 0.0025053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2135-4_0_4_line_124 |  | 123 | 124 | 0.0079916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2135-4_0_4_line_125 |  | 125 | 126 | 0.0069089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2135-4_0_4_line_126 |  | 125 | 127 | 0.0027605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2135-4_0_4_line_127 |  | 126 | 128 | 0.002468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2135-4_0_4_line_128 |  | 127 | 129 | 0.0093775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2135-4_0_4_line_129 |  | 128 | 130 | 0.0096649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2135-4_0_4_line_130 |  | 130 | 131 | 0.0059223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2135-4_0_4_line_131 |  | 131 | 132 | 0.0093818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2135-4_0_4_line_132 |  | 132 | 133 | 0.00025617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2135-4_0_4_trafo_88 | 0.63 MVA 20/0.4 kV | 134 | 53 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2573510.4097 | 1160405.2607 | 2573497.4181 | 1160416.8461 | 2573493.7433 | 1160421.109 | 2573491.0816 | 1160425.7231 | 2573489.4359 | 1160430.9287
1 | 2573513.3505 | 1160399.6226 | 2573512.6186 | 1160402.216 | 2573510.4097 | 1160405.2607
2 | 2573486.9329 | 1160444.1173 | 2573488.9806 | 1160432.369 | 2573489.4359 | 1160430.9287
3 | 2573498.6692 | 1160443.2872 | 2573489.5452 | 1160443.9279 | 2573486.9329 | 1160444.1173
4 | 2573332.1873 | 1160531.3587 | 2573493.3933 | 1160504.8193
5 | 2573288.519 | 1160485.7524 | 2573307.9406 | 1160507.1211 | 2573332.1873 | 1160531.3587
6 | 2573498.6692 | 1160443.2872 | 2573493.3933 | 1160504.8193
7 | 2573288.519 | 1160485.7524 | 2573282.1743 | 1160468.661 | 2573261.2368 | 1160440.807
8 | 2573182.0387 | 1160531.7954 | 2573255.6635 | 1160498.6943 | 2573288.519 | 1160485.7524
9 | 2573498.6692 | 1160443.2872 | 2573527.0556 | 1160440.2492 | 2573529.8155 | 1160440.5038 | 2573530.8363 | 1160440.8661 | 2573531.5773 | 1160442.0635 | 2573528.9681 | 1160458.5722
10 | 2573160.0149 | 1160624.1516 | 2573188.5065 | 1160649.1275
11 | 2573160.0149 | 1160624.1516 | 2573181.2129 | 1160601.656
12 | 2573160.0149 | 1160624.1516 | 2573141.5352 | 1160607.5183
13 | 2573106.0641 | 1160575.5912 | 2573141.5352 | 1160607.5183
14 | 2573106.0641 | 1160575.5912 | 2573095.398 | 1160580.8862 | 2573087.5327 | 1160583.634 | 2573080.741 | 1160584.8317 | 2573062.867 | 1160585.6902 | 2573063.5637 | 1160595.7811 | 2573064.2928 | 1160599.4241 | 2573065.6498 | 1160602.9864
15 | 2573106.0641 | 1160575.5912 | 2573147.0366 | 1160549.9245
16 | 2573216.8955 | 1160563.7891 | 2573243.0831 | 1160587.8841
17 | 2573216.8955 | 1160563.7891 | 2573210.9061 | 1160558.2916
18 | 2573243.0831 | 1160587.8841 | 2573272.3308 | 1160614.7948
19 | 2573203.2255 | 1160551.242 | 2573210.9061 | 1160558.2916
20 | 2573065.6498 | 1160602.9864 | 2573050.1942 | 1160594.6072
21 | 2573065.6498 | 1160602.9864 | 2573068.4712 | 1160606.709 | 2573071.9021 | 1160609.6506 | 2573074.7158 | 1160611.6612 | 2573081.5165 | 1160615.8883 | 2573088.5943 | 1160620.3699 | 2573095.7152 | 1160625.5931
22 | 2573147.0366 | 1160549.9245 | 2573151.4949 | 1160547.1317
23 | 2573307.8917 | 1160647.5142 | 2573272.3308 | 1160614.7948
24 | 2573182.0387 | 1160531.7954 | 2573203.2255 | 1160551.242
25 | 2573040.6745 | 1160600.9199 | 2573037.5579 | 1160594.6085 | 2573047.7248 | 1160589.0711 | 2573050.1942 | 1160594.6072
26 | 2573132.1158 | 1160656.7957 | 2573125.6573 | 1160650.4966 | 2573102.2871 | 1160630.4135 | 2573095.7152 | 1160625.5931
27 | 2573040.6745 | 1160600.9199 | 2573019.5353 | 1160615.2222 | 2573015.2638 | 1160618.6631
28 | 2573064.0764 | 1160646.76 | 2573060.5987 | 1160640.2279 | 2573043.5667 | 1160606.7542 | 2573040.6745 | 1160600.9199
29 | 2573064.0764 | 1160646.76 | 2573043.927 | 1160647.6621 | 2573032.2069 | 1160650.305 | 2573024.7144 | 1160655.8193 | 2573017.5329 | 1160661.8394
30 | 2573064.0764 | 1160646.76 | 2573094.7574 | 1160706.1521 | 2573099.4424 | 1160714.276
31 | 2573182.0387 | 1160531.7954 | 2573160.5258 | 1160541.4744 | 2573151.4949 | 1160547.1317
32 | 2573290.2039 | 1160666.6316 | 2573283.404 | 1160673.9811 | 2573299.1347 | 1160688.5871
33 | 2573307.8917 | 1160647.5142 | 2573290.2039 | 1160666.6316
34 | 2573306.426 | 1160695.3571 | 2573299.1347 | 1160688.5871
35 | 2573307.8917 | 1160647.5142 | 2573326.8504 | 1160664.9624
36 | 2573333.3658 | 1160720.3709 | 2573306.426 | 1160695.3571
37 | 2573358.0671 | 1160693.692 | 2573333.3658 | 1160720.3709
38 | 2573333.3658 | 1160720.3709 | 2573328.2119 | 1160725.9347
39 | 2573358.5968 | 1160694.2539 | 2573358.0671 | 1160693.692
40 | 2573255.1915 | 1160765.4863 | 2573289.1613 | 1160729.539 | 2573310.7618 | 1160744.7726 | 2573328.2119 | 1160725.9347
41 | 2573380.578 | 1160717.5713 | 2573358.5968 | 1160694.2539
42 | 2573255.1915 | 1160765.4863 | 2573240.4102 | 1160752.5589
43 | 2573380.578 | 1160717.5713 | 2573407.3885 | 1160746.0114
44 | 2573156.105 | 1160798.4811 | 2573182.2855 | 1160838.9197
45 | 2573109.8943 | 1160732.3994 | 2573156.105 | 1160798.4811
46 | 2573017.5329 | 1160661.8394 | 2572944.1523 | 1160838.2496
47 | 2573109.8943 | 1160732.3994 | 2573099.4424 | 1160714.276
48 | 2573413.4178 | 1160752.4073 | 2573407.3885 | 1160746.0114
49 | 2573261.2368 | 1160440.807 | 2573258.6113 | 1160456.9268 | 2573258.7628 | 1160459.961 | 2573259.558 | 1160463.0034 | 2573264.225 | 1160474.5804
50 | 2573432.2492 | 1160772.3834 | 2573416.4659 | 1160755.6407
51 | 2573413.4178 | 1160752.4073 | 2573416.4659 | 1160755.6407
52 | 2572944.1523 | 1160838.2496 | 2572948.0375 | 1160843.4358
53 | 2573281.1286 | 1161000.5557 | 2573291.5798 | 1161016.8258
54 | 2573307.1241 | 1161041.0245 | 2573291.5798 | 1161016.8258
55 | 2573337.509 | 1161088.3266 | 2573307.1241 | 1161041.0245
56 | 2573337.509 | 1161088.3266 | 2573369.5992 | 1161138.3314 | 2573373.2016 | 1161143.7152
57 | 2573337.509 | 1161088.3266 | 2573311.7024 | 1161103.8604
58 | 2572948.0375 | 1160843.4358 | 2572802.5754 | 1161114.1588
59 | 2573156.2934 | 1161096.8063 | 2572802.5754 | 1161114.1588
60 | 2573382.3916 | 1161157.4495 | 2573373.2016 | 1161143.7152
61 | 2573311.7024 | 1161103.8604 | 2573305.7522 | 1161094.958
62 | 2573311.7024 | 1161103.8604 | 2573318.3819 | 1161114.291
63 | 2573156.2934 | 1161096.8063 | 2573167.8174 | 1161090.6655
64 | 2573225.0253 | 1161253.3268 | 2573227.891 | 1161254.6434 | 2573243.7028 | 1161259.1418 | 2573266.2169 | 1161326.6976 | 2573266.2169 | 1161326.6976
65 | 2573277.4023 | 1161342.7821 | 2573266.2169 | 1161326.6976
66 | 2573277.4023 | 1161342.7821 | 2573278.7867 | 1161344.7728 | 2573293.3729 | 1161340.9337
67 | 2573323.1266 | 1161345.3585 | 2573320.9444 | 1161343.2954 | 2573312.2543 | 1161339.5544 | 2573303.4908 | 1161338.2706 | 2573293.3729 | 1161340.9337
68 | 2573347.4073 | 1161367.0007 | 2573337.6798 | 1161359.1178 | 2573323.1266 | 1161345.3585
69 | 2573196.3174 | 1161075.4785 | 2573167.8174 | 1161090.6655
70 | 2573193.1324 | 1161132.8978 | 2573237.1776 | 1161148.3039 | 2573288.6234 | 1161170.897 | 2573295.9817 | 1161174.8797
71 | 2573368.9871 | 1161214.3946 | 2573295.9817 | 1161174.8797
72 | 2573425.2497 | 1161246.9724 | 2573416.9356 | 1161241.6288 | 2573368.9871 | 1161214.3946
73 | 2573368.9871 | 1161214.3946 | 2573380.5434 | 1161200.9479
74 | 2573425.2497 | 1161246.9724 | 2573424.5241 | 1161250.9443 | 2573425.2696 | 1161254.9097 | 2573425.2696 | 1161254.9097
75 | 2573366.9574 | 1161189.9561 | 2573372.3001 | 1161197.7938 | 2573379.0998 | 1161193.3613 | 2573383.44 | 1161197.5775 | 2573380.5434 | 1161200.9479
76 | 2573425.2696 | 1161254.9097 | 2573427.3843 | 1161258.3465 | 2573430.5904 | 1161260.8113
77 | 2573361.6869 | 1161182.2241 | 2573366.9574 | 1161189.9561
78 | 2573458.9729 | 1161328.301 | 2573465.0315 | 1161314.3857 | 2573467.6998 | 1161311.777
79 | 2573455.2922 | 1161336.7547 | 2573458.9729 | 1161328.301
80 | 2573481.4243 | 1161298.3595 | 2573467.6998 | 1161311.777
81 | 2573455.2922 | 1161336.7547 | 2573447.2677 | 1161355.1849 | 2573440.0674 | 1161364.277 | 2573434.8917 | 1161368.5892
82 | 2573492.0461 | 1161287.9751 | 2573481.4243 | 1161298.3595
83 | 2573405.6413 | 1161388.2973 | 2573417.25 | 1161383.2877 | 2573434.8917 | 1161368.5892
84 | 2573492.0461 | 1161287.9751 | 2573495.9279 | 1161290.7704 | 2573508.0938 | 1161300.8217 | 2573527.9874 | 1161318.138
85 | 2573492.0461 | 1161287.9751 | 2573484.9721 | 1161282.3591 | 2573472.8545 | 1161273.4439
86 | 2573405.6413 | 1161388.2973 | 2573397.1293 | 1161386.6898 | 2573347.4073 | 1161367.0007
87 | 2573444.9862 | 1161257.0456 | 2573454.4673 | 1161261.1835 | 2573471.3043 | 1161272.3034 | 2573472.8545 | 1161273.4439
88 | 2573444.9862 | 1161257.0456 | 2573442.1717 | 1161259.9484 | 2573438.5092 | 1161261.6655 | 2573434.4725 | 1161261.9613
89 | 2573264.4936 | 1161064.9332 | 2573247.1709 | 1161060.447
90 | 2573272.3738 | 1161066.7909 | 2573269.5832 | 1161066.2513 | 2573264.4936 | 1161064.9332
91 | 2573229.7285 | 1161061.1066 | 2573237.5556 | 1161057.9567 | 2573247.1709 | 1161060.447
92 | 2573272.3738 | 1161066.7909 | 2573289.0855 | 1161070.0219 | 2573293.3348 | 1161076.3796
93 | 2573229.7285 | 1161061.1066 | 2573222.644 | 1161063.9575
94 | 2573293.3348 | 1161076.3796 | 2573295.1868 | 1161079.1504
95 | 2573200.3245 | 1161073.3433 | 2573203.4196 | 1161071.6939 | 2573222.644 | 1161063.9575
96 | 2573295.1868 | 1161079.1504 | 2573298.6981 | 1161084.4039
97 | 2573196.3174 | 1161075.4785 | 2573200.3245 | 1161073.3433
98 | 2573298.6981 | 1161084.4039 | 2573300.5512 | 1161087.1764
99 | 2573303.8992 | 1161092.1855 | 2573300.5512 | 1161087.1764
100 | 2573430.5904 | 1161260.8113 | 2573434.4725 | 1161261.9613
101 | 2573246.1524 | 1161116.4496 | 2573238.6199 | 1161113.4955
102 | 2573246.1524 | 1161116.4496 | 2573247.3521 | 1161116.9201
103 | 2573238.6199 | 1161113.4955 | 2573237.1485 | 1161112.9185
104 | 2573254.8848 | 1161119.8742 | 2573247.3521 | 1161116.9201
105 | 2573237.1485 | 1161112.9185 | 2573229.6148 | 1161109.9639
106 | 2573261.6272 | 1161122.5184 | 2573254.8848 | 1161119.8742
107 | 2573222.8243 | 1161107.3009 | 2573229.6148 | 1161109.9639
108 | 2573261.6272 | 1161122.5184 | 2573270.5995 | 1161126.0371
109 | 2573220.4472 | 1161106.3686 | 2573222.8243 | 1161107.3009
110 | 2573270.5995 | 1161126.0371 | 2573270.6343 | 1161126.0508
111 | 2573270.6343 | 1161126.0508 | 2573279.3645 | 1161129.4746
112 | 2573323.5878 | 1161122.4203 | 2573328.6364 | 1161130.3041
113 | 2573323.5878 | 1161122.4203 | 2573318.3819 | 1161114.291
114 | 2573328.6364 | 1161130.3041 | 2573337.0867 | 1161143.4998
115 | 2573337.0867 | 1161143.4998 | 2573342.2937 | 1161151.6309
116 | 2573345.2437 | 1161156.2375 | 2573342.2937 | 1161151.6309
117 | 2573303.8992 | 1161092.1855 | 2573305.7522 | 1161094.958
118 | 2573345.2437 | 1161156.2375 | 2573347.2335 | 1161159.4338
119 | 2573345.2437 | 1161156.2375 | 2573333.7642 | 1161155.9218 | 2573333.7642 | 1161155.9218
120 | 2573347.2335 | 1161159.4338 | 2573350.6257 | 1161164.8828
121 | 2573333.7642 | 1161155.9218 | 2573321.5108 | 1161149.5466
122 | 2573361.6869 | 1161182.2241 | 2573358.6257 | 1161177.7333 | 2573356.1733 | 1161173.7939
123 | 2573354.8492 | 1161171.6671 | 2573356.1733 | 1161173.7939
124 | 2573350.6257 | 1161164.8828 | 2573354.8492 | 1161171.6671
125 | 2573310.743 | 1161143.9443 | 2573304.614 | 1161140.7556
126 | 2573313.1918 | 1161145.2184 | 2573310.743 | 1161143.9443
127 | 2573304.614 | 1161140.7556 | 2573302.4245 | 1161139.6165
128 | 2573313.1918 | 1161145.2184 | 2573321.5108 | 1161149.5466
129 | 2573293.8507 | 1161135.1557 | 2573302.4245 | 1161139.6165
130 | 2573293.8507 | 1161135.1557 | 2573293.8507 | 1161135.1557 | 2573288.3371 | 1161132.9934
131 | 2573279.603 | 1161129.5681 | 2573288.3371 | 1161132.9934
132 | 2573279.3645 | 1161129.4746 | 2573279.603 | 1161129.5681

## bus_geodata
| x | y | coords
0 | 2573510.4097 | 1160405.2607
1 | 2573489.4359 | 1160430.9287
2 | 2573513.3505 | 1160399.6226
3 | 2573486.9329 | 1160444.1173
4 | 2573332.1873 | 1160531.3587
5 | 2573493.3933 | 1160504.8193
6 | 2573288.519 | 1160485.7524
7 | 2573498.6692 | 1160443.2872
8 | 2573528.9681 | 1160458.5722
9 | 2573188.5065 | 1160649.1275
10 | 2573160.0149 | 1160624.1516
11 | 2573181.2129 | 1160601.656
12 | 2573141.5352 | 1160607.5183
13 | 2573106.0641 | 1160575.5912
14 | 2573216.8955 | 1160563.7891
15 | 2573243.0831 | 1160587.8841
16 | 2573210.9061 | 1160558.2916
17 | 2573065.6498 | 1160602.9864
18 | 2573147.0366 | 1160549.9245
19 | 2573272.3308 | 1160614.7948
20 | 2573203.2255 | 1160551.242
21 | 2573050.1942 | 1160594.6072
22 | 2573095.7152 | 1160625.5931
23 | 2573040.6745 | 1160600.9199
24 | 2573015.2638 | 1160618.6631
25 | 2573064.0764 | 1160646.76
26 | 2573151.4949 | 1160547.1317
27 | 2573290.2039 | 1160666.6316
28 | 2573299.1347 | 1160688.5871
29 | 2573307.8917 | 1160647.5142
30 | 2573306.426 | 1160695.3571
31 | 2573326.8504 | 1160664.9624
32 | 2573333.3658 | 1160720.3709
33 | 2573358.0671 | 1160693.692
34 | 2573328.2119 | 1160725.9347
35 | 2573358.5968 | 1160694.2539
36 | 2573255.1915 | 1160765.4863
37 | 2573380.578 | 1160717.5713
38 | 2573132.1158 | 1160656.7957
39 | 2573240.4102 | 1160752.5589
40 | 2573182.2855 | 1160838.9197
41 | 2573156.105 | 1160798.4811
42 | 2573017.5329 | 1160661.8394
43 | 2573099.4424 | 1160714.276
44 | 2573407.3885 | 1160746.0114
45 | 2573182.0387 | 1160531.7954
46 | 2573261.2368 | 1160440.807
47 | 2573264.225 | 1160474.5804
48 | 2573432.2492 | 1160772.3834
49 | 2573416.4659 | 1160755.6407
50 | 2573413.4178 | 1160752.4073
51 | 2573109.8943 | 1160732.3994
52 | 2572944.1523 | 1160838.2496
53 | 2573281.1286 | 1161000.5557
54 | 2573291.5798 | 1161016.8258
55 | 2573307.1241 | 1161041.0245
56 | 2573337.509 | 1161088.3266
57 | 2572948.0375 | 1160843.4358
58 | 2572802.5754 | 1161114.1588
59 | 2573373.2016 | 1161143.7152
60 | 2573311.7024 | 1161103.8604
61 | 2573156.2934 | 1161096.8063
62 | 2573225.0253 | 1161253.3268
63 | 2573266.2169 | 1161326.6976
64 | 2573277.4023 | 1161342.7821
65 | 2573293.3729 | 1161340.9337
66 | 2573323.1266 | 1161345.3585
67 | 2573167.8174 | 1161090.6655
68 | 2573193.1324 | 1161132.8978
69 | 2573295.9817 | 1161174.8797
70 | 2573368.9871 | 1161214.3946
71 | 2573425.2497 | 1161246.9724
72 | 2573380.5434 | 1161200.9479
73 | 2573425.2696 | 1161254.9097
74 | 2573366.9574 | 1161189.9561
75 | 2573458.9729 | 1161328.301
76 | 2573467.6998 | 1161311.777
77 | 2573455.2922 | 1161336.7547
78 | 2573481.4243 | 1161298.3595
79 | 2573434.8917 | 1161368.5892
80 | 2573492.0461 | 1161287.9751
81 | 2573405.6413 | 1161388.2973
82 | 2573527.9874 | 1161318.138
83 | 2573472.8545 | 1161273.4439
84 | 2573347.4073 | 1161367.0007
85 | 2573444.9862 | 1161257.0456
86 | 2573264.4936 | 1161064.9332
87 | 2573247.1709 | 1161060.447
88 | 2573272.3738 | 1161066.7909
89 | 2573229.7285 | 1161061.1066
90 | 2573293.3348 | 1161076.3796
91 | 2573222.644 | 1161063.9575
92 | 2573295.1868 | 1161079.1504
93 | 2573200.3245 | 1161073.3433
94 | 2573298.6981 | 1161084.4039
95 | 2573196.3174 | 1161075.4785
96 | 2573300.5512 | 1161087.1764
97 | 2573434.4725 | 1161261.9613
98 | 2573430.5904 | 1161260.8113
99 | 2573382.3916 | 1161157.4495
100 | 2573246.1524 | 1161116.4496
101 | 2573238.6199 | 1161113.4955
102 | 2573247.3521 | 1161116.9201
103 | 2573237.1485 | 1161112.9185
104 | 2573254.8848 | 1161119.8742
105 | 2573229.6148 | 1161109.9639
106 | 2573261.6272 | 1161122.5184
107 | 2573222.8243 | 1161107.3009
108 | 2573270.5995 | 1161126.0371
109 | 2573220.4472 | 1161106.3686
110 | 2573270.6343 | 1161126.0508
111 | 2573323.5878 | 1161122.4203
112 | 2573328.6364 | 1161130.3041
113 | 2573318.3819 | 1161114.291
114 | 2573337.0867 | 1161143.4998
115 | 2573342.2937 | 1161151.6309
116 | 2573305.7522 | 1161094.958
117 | 2573345.2437 | 1161156.2375
118 | 2573303.8992 | 1161092.1855
119 | 2573347.2335 | 1161159.4338
120 | 2573333.7642 | 1161155.9218
121 | 2573361.6869 | 1161182.2241
122 | 2573356.1733 | 1161173.7939
123 | 2573354.8492 | 1161171.6671
124 | 2573350.6257 | 1161164.8828
125 | 2573310.743 | 1161143.9443
126 | 2573304.614 | 1161140.7556
127 | 2573313.1918 | 1161145.2184
128 | 2573302.4245 | 1161139.6165
129 | 2573321.5108 | 1161149.5466
130 | 2573293.8507 | 1161135.1557
131 | 2573288.3371 | 1161132.9934
132 | 2573279.603 | 1161129.5681
133 | 2573279.3645 | 1161129.4746
134 | 2573337.509 | 1161088.3266

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9702 | -0.57652 | 0.0053024 | 0.0013289
1 | 0.97042 | -0.57225 | 0.00073375 | 0.00018389
2 | 0.97019 | -0.5767 | 0.0015167 | 0.00038012
3 | 0.97051 | -0.57037 | 0 | 0
4 | 0.97213 | -0.53837 | 0.00028327 | 7.0995e-05
5 | 0.97135 | -0.55374 | 0.007259 | 0.0018193
6 | 0.97243 | -0.53235 | 0 | 0
7 | 0.97059 | -0.56873 | 0 | 0
8 | 0.97033 | -0.57393 | 0.0055671 | 0.0013953
9 | 0.97318 | -0.51753 | 0.004874 | 0.0012215
10 | 0.97335 | -0.51413 | 0 | 0
11 | 0.97324 | -0.51648 | 0.0041256 | 0.001034
12 | 0.97356 | -0.51001 | 0.00047961 | 0.0001202
13 | 0.97398 | -0.50169 | 0 | 0
14 | 0.97272 | -0.52663 | 0 | 0
15 | 0.97252 | -0.5306 | 0.00049723 | 0.00012462
16 | 0.97277 | -0.52572 | 0.0014557 | 0.00036484
17 | 0.97482 | -0.48516 | 0 | 0
18 | 0.97344 | -0.51236 | 0.00020157 | 5.0518e-05
19 | 0.9723 | -0.53495 | 0.0022864 | 0.00057303
20 | 0.97283 | -0.52449 | 0.00058121 | 0.00014567
21 | 0.97506 | -0.4804 | 0 | 0
22 | 0.97476 | -0.48633 | 0.00079973 | 0.00020043
23 | 0.9754 | -0.47371 | 0 | 0
24 | 0.9753 | -0.47575 | 0.0036022 | 0.0009028
25 | 0.97616 | -0.45892 | 0 | 0
26 | 0.97338 | -0.51352 | 0.0002271 | 5.6916e-05
27 | 0.97194 | -0.5421 | 0.00082814 | 0.00020755
28 | 0.9718 | -0.54485 | 0.00097245 | 0.00024372
29 | 0.97206 | -0.53973 | 0 | 0
30 | 0.97176 | -0.54567 | 0.00091795 | 0.00023006
31 | 0.97202 | -0.54052 | 0.0016708 | 0.00041874
32 | 0.97161 | -0.54856 | 0 | 0
33 | 0.97137 | -0.55339 | 0 | 0
34 | 0.97159 | -0.54893 | 0.0015551 | 0.00038974
35 | 0.97136 | -0.55359 | 0.001378 | 0.00034536
36 | 0.97149 | -0.55098 | 0 | 0
37 | 0.97097 | -0.5613 | 0.0018219 | 0.00045662
38 | 0.97472 | -0.4871 | 0.00087973 | 0.00022048
39 | 0.97147 | -0.55137 | 0.0010859 | 0.00027214
40 | 0.97598 | -0.46233 | 0.00036851 | 9.2358e-05
41 | 0.976 | -0.46201 | 0.00019285 | 4.8334e-05
42 | 0.97691 | -0.44402 | 9.2678e-05 | 2.3227e-05
43 | 0.97606 | -0.46076 | 0.00021654 | 5.427e-05
44 | 0.97056 | -0.56938 | 0.001829 | 0.0004584
45 | 0.97301 | -0.52101 | 0 | 0
46 | 0.9724 | -0.53291 | 0 | 0
47 | 0.97239 | -0.53328 | 0.00056949 | 0.00014273
48 | 0.97039 | -0.57266 | 0.002871 | 0.00071953
49 | 0.97046 | -0.57144 | 0.003606 | 0.00090374
50 | 0.97048 | -0.57091 | 0.0028783 | 0.00072137
51 | 0.97604 | -0.46118 | 0.00053099 | 0.00013308
52 | 0.97977 | -0.38816 | 0.00081384 | 0.00020397
53 | 1 | 0 | -0.20642 | -0.052435
54 | 0.9991 | -0.017028 | 0.00072032 | 0.00018053
55 | 0.99777 | -0.042321 | 0.0020204 | 0.00050637
56 | 0.99518 | -0.091455 | 0 | 0
57 | 0.97987 | -0.38625 | 0.00072298 | 0.00018119
58 | 0.98457 | -0.29493 | 0.0039816 | 0.00099788
59 | 0.99483 | -0.098297 | 0.0030029 | 0.00075259
60 | 0.99385 | -0.11705 | 0 | 0
61 | 0.99032 | -0.18444 | 0.002229 | 0.00055863
62 | 0.98018 | -0.38237 | 0.0032519 | 0.000815
63 | 0.98045 | -0.37701 | 0.0017866 | 0.00044777
64 | 0.98054 | -0.37522 | 0.0034459 | 0.00086361
65 | 0.98068 | -0.37252 | 0.0022586 | 0.00056605
66 | 0.981 | -0.36634 | 0.00062999 | 0.00015789
67 | 0.99054 | -0.18026 | 0.0018617 | 0.00046659
68 | 0.98594 | -0.26984 | 0.0017767 | 0.00044529
69 | 0.98613 | -0.26629 | 0.0018806 | 0.00047131
70 | 0.9864 | -0.26084 | 0 | 0
71 | 0.9851 | -0.28614 | 0 | 0
72 | 0.98682 | -0.25278 | 0.0030117 | 0.00075481
73 | 0.98494 | -0.28929 | 0.0011874 | 0.0002976
74 | 0.98756 | -0.2385 | 0.0022134 | 0.00055472
75 | 0.98292 | -0.32875 | 0.0007362 | 0.00018451
76 | 0.98317 | -0.32377 | 0.00048645 | 0.00012192
77 | 0.9828 | -0.33105 | 0.0016048 | 0.00040221
78 | 0.98344 | -0.31855 | 0.00058419 | 0.00014641
79 | 0.98237 | -0.33955 | 0.00086677 | 0.00021723
80 | 0.98366 | -0.31436 | 0 | 0
81 | 0.98199 | -0.34687 | 0 | 0
82 | 0.98364 | -0.31462 | 0.00030791 | 7.7171e-05
83 | 0.98401 | -0.30743 | 0.0012171 | 0.00030503
84 | 0.98134 | -0.35963 | 0 | 0
85 | 0.98453 | -0.2974 | 0 | 0
86 | 0.99245 | -0.14373 | 0.0020775 | 0.00052067
87 | 0.9921 | -0.15036 | 0.0016069 | 0.00040272
88 | 0.99261 | -0.14066 | 0.0015758 | 0.00039493
89 | 0.99175 | -0.15705 | 0.0018286 | 0.0004583
90 | 0.99311 | -0.13113 | 0.0031302 | 0.00078451
91 | 0.99161 | -0.15976 | 0.0023892 | 0.00059878
92 | 0.99318 | -0.12979 | 0.0012001 | 0.00030077
93 | 0.99117 | -0.16813 | 0.0022041 | 0.0005524
94 | 0.99331 | -0.12723 | 0.0031321 | 0.00078497
95 | 0.99109 | -0.16966 | 0.0017765 | 0.00044523
96 | 0.99339 | -0.12583 | 0.0012003 | 0.00030081
97 | 0.98472 | -0.29365 | 0.0017071 | 0.00042783
98 | 0.98479 | -0.29227 | 0.001644 | 0.00041202
99 | 0.99479 | -0.099139 | 0.0028935 | 0.00072517
100 | 0.98623 | -0.26428 | 0.0017743 | 0.00044469
101 | 0.98617 | -0.26556 | 0.0017767 | 0.00044529
102 | 0.98625 | -0.26403 | 0.0017767 | 0.00044529
103 | 0.98616 | -0.26577 | 0.0017767 | 0.00044529
104 | 0.98634 | -0.26223 | 0.0017774 | 0.00044547
105 | 0.98612 | -0.26654 | 0.0017775 | 0.00044547
106 | 0.98643 | -0.26038 | 0.0017767 | 0.00044529
107 | 0.98609 | -0.267 | 0.0017767 | 0.00044529
108 | 0.98658 | -0.25762 | 0.0017774 | 0.00044547
109 | 0.98609 | -0.26708 | 0.0017762 | 0.00044515
110 | 0.98658 | -0.25761 | 0.0017767 | 0.00044529
111 | 0.992 | -0.15262 | 0.0022147 | 0.00055506
112 | 0.99124 | -0.1672 | 0.0022134 | 0.00055473
113 | 0.99279 | -0.13724 | 0.0022134 | 0.00055473
114 | 0.99001 | -0.19103 | 0.0022156 | 0.00055529
115 | 0.98927 | -0.20536 | 0.0022134 | 0.00055472
116 | 0.9936 | -0.12182 | 0.0017765 | 0.00044523
117 | 0.98886 | -0.21328 | 0 | 0
118 | 0.99352 | -0.12328 | 0.0031302 | 0.00078451
119 | 0.98871 | -0.21607 | 0.0022147 | 0.00055505
120 | 0.98844 | -0.22136 | 0.0022129 | 0.00055459
121 | 0.98782 | -0.23338 | 0.0022147 | 0.00055505
122 | 0.98812 | -0.22748 | 0.0022147 | 0.00055505
123 | 0.9882 | -0.22591 | 0.0022135 | 0.00055475
124 | 0.98848 | -0.22059 | 0.0022145 | 0.00055502
125 | 0.98758 | -0.23805 | 0.0022135 | 0.00055475
126 | 0.98739 | -0.24184 | 0.0017774 | 0.00044546
127 | 0.98766 | -0.23643 | 0.0022129 | 0.00055459
128 | 0.98732 | -0.24311 | 0.0022146 | 0.00055502
129 | 0.98797 | -0.23056 | 0.0022142 | 0.00055492
130 | 0.98708 | -0.24772 | 0.0017774 | 0.00044546
131 | 0.98695 | -0.25035 | 0.0017755 | 0.00044497
132 | 0.98675 | -0.25423 | 0.0017774 | 0.00044547
133 | 0.98674 | -0.25433 | 0.0017774 | 0.00044547
134 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0068191 | -0.001709 | 0.0068205 | 0.0017094 | 1.3873e-06 | 4.701e-07 | 0.010459 | 0.010458 | 0.010459 | 0.9702 | -0.57652 | 0.97042 | -0.57225 | 2.8732
1 | 0.0015167 | 0.00038005 | -0.0015167 | -0.00038012 | 1.3101e-08 | -7.1343e-08 | 0.0023262 | 0.0023262 | 0.0023262 | 0.9702 | -0.57652 | 0.97019 | -0.5767 | 0.63907
2 | -0.0075542 | -0.0018933 | 0.0075549 | 0.0018936 | 6.7605e-07 | 2.6666e-07 | 0.011584 | 0.011583 | 0.011584 | 0.97042 | -0.57225 | 0.97051 | -0.57037 | 3.1823
3 | -0.0075549 | -0.0018936 | 0.0075555 | 0.0018938 | 5.9031e-07 | 2.3281e-07 | 0.011583 | 0.011583 | 0.011583 | 0.97051 | -0.57037 | 0.97059 | -0.56873 | 3.1823
4 | 0.020407 | 0.0051153 | -0.020392 | -0.0051138 | 1.4947e-05 | 1.4702e-06 | 0.031237 | 0.03124 | 0.03124 | 0.97213 | -0.53837 | 0.97135 | -0.55374 | 2.1456
5 | -0.020691 | -0.0051863 | 0.020697 | 0.005187 | 5.9318e-06 | 6.6695e-07 | 0.031671 | 0.03167 | 0.031671 | 0.97213 | -0.53837 | 0.97243 | -0.53235 | 2.1752
6 | 0.013133 | 0.0032946 | -0.013124 | -0.0032893 | 9.3776e-06 | 5.2376e-06 | 0.02012 | 0.02012 | 0.02012 | 0.97135 | -0.55374 | 0.97059 | -0.56873 | 5.5276
7 | 0.00056952 | 0.00014165 | -0.0005695 | -0.0001423 | 1.5098e-08 | -6.4838e-07 | 0.00087109 | 0.00087132 | 0.00087132 | 0.97243 | -0.53235 | 0.9724 | -0.53291 | 0.23937
8 | -0.021266 | -0.0053286 | 0.021278 | 0.0053302 | 1.1491e-05 | 1.6064e-06 | 0.032541 | 0.032539 | 0.032541 | 0.97243 | -0.53235 | 0.97301 | -0.52101 | 2.235
9 | 0.0055685 | 0.0013955 | -0.0055671 | -0.0013953 | 1.3784e-06 | 2.5904e-07 | 0.008537 | 0.0085373 | 0.0085373 | 0.97059 | -0.56873 | 0.97033 | -0.57393 | 2.3454
10 | -0.004874 | -0.0012215 | 0.0048748 | 0.0012216 | 7.8911e-07 | 3.4176e-08 | 0.0074525 | 0.0074523 | 0.0074525 | 0.97318 | -0.51753 | 0.97335 | -0.51413 | 2.0474
11 | 0.0041261 | 0.0010339 | -0.0041256 | -0.001034 | 4.6118e-07 | -8.8985e-08 | 0.0063077 | 0.0063078 | 0.0063078 | 0.97335 | -0.51413 | 0.97324 | -0.51648 | 1.7329
12 | -0.0090009 | -0.0022555 | 0.0090027 | 0.0022563 | 1.7653e-06 | 8.2069e-07 | 0.01376 | 0.01376 | 0.01376 | 0.97335 | -0.51413 | 0.97356 | -0.51001 | 3.7802
13 | -0.0094823 | -0.0023765 | 0.009486 | 0.0023783 | 3.759e-06 | 1.8121e-06 | 0.014493 | 0.014493 | 0.014493 | 0.97356 | -0.51001 | 0.97398 | -0.50169 | 3.9816
14 | -0.057514 | -0.014425 | 0.05756 | 0.01445 | 4.5367e-05 | 2.5912e-05 | 0.087872 | 0.087871 | 0.087872 | 0.97398 | -0.50169 | 0.97482 | -0.48516 | 6.0351
15 | 0.048028 | 0.012046 | -0.048004 | -0.012033 | 2.4406e-05 | 1.3214e-05 | 0.073379 | 0.07338 | 0.07338 | 0.97398 | -0.50169 | 0.97344 | -0.51236 | 5.0398
16 | 0.024234 | 0.0060722 | -0.02423 | -0.006071 | 4.585e-06 | 1.1678e-06 | 0.037071 | 0.037072 | 0.037072 | 0.97272 | -0.52663 | 0.97252 | -0.5306 | 2.5462
17 | -0.024234 | -0.0060722 | 0.024235 | 0.0060724 | 1.0474e-06 | 2.6667e-07 | 0.037071 | 0.037071 | 0.037071 | 0.97272 | -0.52663 | 0.97277 | -0.52572 | 2.5461
18 | 0.023732 | 0.0059464 | -0.023727 | -0.0059452 | 4.9129e-06 | 1.1721e-06 | 0.036311 | 0.036312 | 0.036312 | 0.97252 | -0.5306 | 0.9723 | -0.53495 | 2.494
19 | -0.025691 | -0.0064373 | 0.025692 | 0.0064377 | 1.5094e-06 | 4.4828e-07 | 0.039298 | 0.039298 | 0.039298 | 0.97277 | -0.52572 | 0.97283 | -0.52449 | 2.699
20 | -0.059239 | -0.01487 | 0.059253 | 0.014878 | 1.345e-05 | 7.7332e-06 | 0.090434 | 0.090434 | 0.090434 | 0.97482 | -0.48516 | 0.97506 | -0.4804 | 6.2111
21 | 0.0016796 | 0.00041992 | -0.0016795 | -0.00042033 | 9.3311e-08 | -4.1231e-07 | 0.0025634 | 0.0025636 | 0.0025636 | 0.97482 | -0.48516 | 0.97476 | -0.48633 | 0.70429
22 | 0.047802 | 0.011982 | -0.0478 | -0.011981 | 2.6335e-06 | 1.4238e-06 | 0.073072 | 0.073072 | 0.073072 | 0.97344 | -0.51236 | 0.97338 | -0.51352 | 5.0187
23 | 0.021441 | 0.0053722 | -0.021436 | -0.0053715 | 4.8778e-06 | 7.2509e-07 | 0.032813 | 0.032814 | 0.032814 | 0.9723 | -0.53495 | 0.97206 | -0.53973 | 2.2537
24 | -0.026274 | -0.0065834 | 0.026278 | 0.0065848 | 4.3541e-06 | 1.3581e-06 | 0.040187 | 0.040186 | 0.040187 | 0.97283 | -0.52449 | 0.97301 | -0.52101 | 2.7601
25 | -0.059253 | -0.014878 | 0.059272 | 0.014889 | 1.8921e-05 | 1.0878e-05 | 0.090434 | 0.090433 | 0.090434 | 0.97506 | -0.4804 | 0.9754 | -0.47371 | 6.2111
26 | 0.00087976 | 0.0002199 | -0.00087973 | -0.00022048 | 3.2451e-08 | -5.7737e-07 | 0.0013428 | 0.001343 | 0.001343 | 0.97476 | -0.48633 | 0.97472 | -0.4871 | 0.36896
27 | 0.0036026 | 0.00090264 | -0.0036022 | -0.0009028 | 3.5122e-07 | -1.6222e-07 | 0.0054958 | 0.0054959 | 0.0054959 | 0.9754 | -0.47371 | 0.9753 | -0.47575 | 1.5099
28 | -0.062874 | -0.015792 | 0.062918 | 0.015817 | 4.4387e-05 | 2.5837e-05 | 0.095929 | 0.095928 | 0.095929 | 0.9754 | -0.47371 | 0.97616 | -0.45892 | 6.5885
29 | -0.064228 | -0.016143 | 0.064273 | 0.016169 | 4.5718e-05 | 2.6715e-05 | 0.097923 | 0.097922 | 0.097923 | 0.97616 | -0.45892 | 0.97691 | -0.44402 | 6.7255
30 | 0.0013091 | 0.00032532 | -0.0013089 | -0.0003262 | 1.1373e-07 | -8.8004e-07 | 0.0019945 | 0.0019948 | 0.0019948 | 0.97616 | -0.45892 | 0.97606 | -0.46076 | 0.54803
31 | 0.047572 | 0.011924 | -0.047555 | -0.011915 | 1.6981e-05 | 9.1655e-06 | 0.072725 | 0.072725 | 0.072725 | 0.97338 | -0.51352 | 0.97301 | -0.52101 | 4.9949
32 | 0.018935 | 0.0047453 | -0.018932 | -0.0047453 | 2.48e-06 | 2.6928e-08 | 0.028989 | 0.028989 | 0.028989 | 0.97194 | -0.5421 | 0.9718 | -0.54485 | 1.991
33 | -0.019763 | -0.0049529 | 0.019765 | 0.004953 | 2.2352e-06 | 1.3927e-07 | 0.030257 | 0.030256 | 0.030257 | 0.97194 | -0.5421 | 0.97206 | -0.53973 | 2.0781
34 | 0.01796 | 0.0045016 | -0.017959 | -0.0045016 | 7.0543e-07 | -4.1598e-08 | 0.0275 | 0.0275 | 0.0275 | 0.9718 | -0.54485 | 0.97176 | -0.54567 | 1.8888
35 | 0.0016709 | 0.00041847 | -0.0016708 | -0.00041874 | 6.3208e-08 | -2.7894e-07 | 0.0025576 | 0.0025578 | 0.0025578 | 0.97206 | -0.53973 | 0.97202 | -0.54052 | 0.70268
36 | 0.017041 | 0.0042715 | -0.017039 | -0.0042719 | 2.3469e-06 | -3.1946e-07 | 0.026095 | 0.026095 | 0.026095 | 0.97176 | -0.54567 | 0.97161 | -0.54856 | 1.7923
37 | 0.014398 | 0.0036115 | -0.014394 | -0.0036102 | 3.3109e-06 | 1.2197e-06 | 0.022051 | 0.022051 | 0.022051 | 0.97161 | -0.54856 | 0.97137 | -0.55339 | 3.0291
38 | 0.0026411 | 0.0006604 | -0.0026411 | -0.00066046 | 4.6519e-08 | -6.4156e-08 | 0.0040443 | 0.0040443 | 0.0040443 | 0.97161 | -0.54856 | 0.97159 | -0.54893 | 1.1111
39 | 0.014394 | 0.0036102 | -0.014394 | -0.0036102 | 1.408e-07 | 8.0557e-08 | 0.022051 | 0.022051 | 0.022051 | 0.97137 | -0.55339 | 0.97136 | -0.55359 | 6.0581
40 | 0.001086 | 0.00027072 | -0.0010859 | -0.00027191 | 1.0533e-07 | -1.1903e-06 | 0.0016627 | 0.0016632 | 0.0016632 | 0.97159 | -0.54893 | 0.97149 | -0.55098 | 0.45691
41 | 0.013016 | 0.0032648 | -0.013012 | -0.0032621 | 4.7782e-06 | 2.6616e-06 | 0.019941 | 0.019941 | 0.019941 | 0.97136 | -0.55359 | 0.97097 | -0.5613 | 5.4782
42 | 0.0010859 | 0.00027191 | -0.0010859 | -0.00027214 | 2.037e-08 | -2.301e-07 | 0.0016632 | 0.0016632 | 0.0016632 | 0.97149 | -0.55098 | 0.97147 | -0.55137 | 0.45694
43 | 0.01119 | 0.0028055 | -0.011185 | -0.0028032 | 4.3102e-06 | 2.2753e-06 | 0.017149 | 0.017149 | 0.017149 | 0.97097 | -0.5613 | 0.97056 | -0.56938 | 4.7112
44 | -0.00036851 | -9.2358e-05 | 0.00036852 | 9.176e-05 | 5.7004e-09 | -5.9837e-07 | 0.00056185 | 0.00056163 | 0.00056185 | 0.97598 | -0.46233 | 0.976 | -0.46201 | 0.15435
45 | -0.00056137 | -0.00014009 | 0.0005614 | 0.0001391 | 2.213e-08 | -9.936e-07 | 0.00085566 | 0.0008553 | 0.00085566 | 0.976 | -0.46201 | 0.97604 | -0.46118 | 0.23507
46 | -0.064366 | -0.016193 | 0.064538 | 0.016293 | 0.00017224 | 0.00010064 | 0.098063 | 0.098059 | 0.098063 | 0.97691 | -0.44402 | 0.97977 | -0.38816 | 6.7351
47 | 0.0010924 | 0.00027193 | -0.0010924 | -0.00027218 | 2.1743e-08 | -2.4757e-07 | 0.0016647 | 0.0016648 | 0.0016648 | 0.97606 | -0.46076 | 0.97604 | -0.46118 | 0.45737
48 | 0.0093563 | 0.0023448 | -0.0093556 | -0.0023445 | 6.7824e-07 | 3.2546e-07 | 0.014345 | 0.014345 | 0.014345 | 0.97056 | -0.56938 | 0.97048 | -0.57091 | 3.9408
49 | 0.0005695 | 0.0001423 | -0.00056949 | -0.00014273 | 9.9655e-09 | -4.2776e-07 | 0.00087132 | 0.00087148 | 0.00087148 | 0.9724 | -0.53291 | 0.97239 | -0.53328 | 0.23942
50 | -0.002871 | -0.00071953 | 0.0028711 | 0.00071935 | 1.6722e-07 | -1.7725e-07 | 0.0044024 | 0.0044023 | 0.0044024 | 0.97039 | -0.57266 | 0.97046 | -0.57144 | 1.2094
51 | -0.0064771 | -0.0016231 | 0.0064773 | 0.0016231 | 1.6435e-07 | 5.0282e-08 | 0.0099314 | 0.0099313 | 0.0099314 | 0.97046 | -0.57144 | 0.97048 | -0.57091 | 2.7284
52 | -0.065352 | -0.016497 | 0.065358 | 0.016501 | 5.9898e-06 | 3.507e-06 | 0.099295 | 0.099295 | 0.099295 | 0.97977 | -0.38816 | 0.97987 | -0.38625 | 6.8197
53 | 0.20477 | 0.052435 | -0.2046 | -0.052328 | 0.00016876 | 0.00010699 | 0.3051 | 0.3051 | 0.3051 | 1 | 0 | 0.9991 | -0.017028 | 20.9547
54 | 0.20388 | 0.052148 | -0.20363 | -0.05199 | 0.00024923 | 0.000158 | 0.30403 | 0.30403 | 0.30403 | 0.9991 | -0.017028 | 0.99777 | -0.042321 | 20.8811
55 | 0.20161 | 0.051483 | -0.20114 | -0.051181 | 0.00047758 | 0.00030272 | 0.30102 | 0.30102 | 0.30102 | 0.99777 | -0.042321 | 0.99518 | -0.091455 | 20.6742
56 | 0.0058984 | 0.001478 | -0.0058965 | -0.0014776 | 1.922e-06 | 3.7422e-07 | 0.0088193 | 0.0088196 | 0.0088196 | 0.99518 | -0.091455 | 0.99483 | -0.098297 | 2.423
57 | 0.19524 | 0.049703 | -0.195 | -0.04955 | 0.0002406 | 0.00015242 | 0.2922 | 0.2922 | 0.2922 | 0.99518 | -0.091455 | 0.99385 | -0.11705 | 20.0685
58 | -0.066081 | -0.016682 | 0.066371 | 0.016852 | 0.00029037 | 0.00017028 | 0.10039 | 0.10039 | 0.10039 | 0.97987 | -0.38625 | 0.98457 | -0.29493 | 6.8951
59 | -0.070353 | -0.01785 | 0.070729 | 0.018073 | 0.00037588 | 0.00022244 | 0.10641 | 0.1064 | 0.10641 | 0.98457 | -0.29493 | 0.99032 | -0.18444 | 7.308
60 | 0.0028936 | 0.00072503 | -0.0028935 | -0.00072517 | 1.1608e-07 | -1.4026e-07 | 0.004328 | 0.0043281 | 0.0043281 | 0.99483 | -0.098297 | 0.99479 | -0.099139 | 1.189
61 | 0.10212 | 0.026038 | -0.1021 | -0.026024 | 2.3518e-05 | 1.4496e-05 | 0.15306 | 0.15306 | 0.15306 | 0.99385 | -0.11705 | 0.9936 | -0.12182 | 10.5123
62 | 0.092875 | 0.023512 | -0.092785 | -0.023454 | 8.992e-05 | 5.7388e-05 | 0.13914 | 0.13914 | 0.13914 | 0.99385 | -0.11705 | 0.99279 | -0.13724 | 38.2248
63 | -0.072958 | -0.018631 | 0.072973 | 0.01864 | 1.4745e-05 | 8.7645e-06 | 0.10975 | 0.10975 | 0.10975 | 0.99032 | -0.18444 | 0.99054 | -0.18026 | 7.5376
64 | -0.0032519 | -0.000815 | 0.0032527 | 0.00081439 | 8.2979e-07 | -6.1375e-07 | 0.0049367 | 0.0049363 | 0.0049367 | 0.98018 | -0.38237 | 0.98045 | -0.37701 | 1.3562
65 | -0.0050393 | -0.0012622 | 0.0050398 | 0.0012622 | 4.2971e-07 | 2.7912e-08 | 0.0076478 | 0.0076477 | 0.0076478 | 0.98045 | -0.37701 | 0.98054 | -0.37522 | 2.1011
66 | -0.0084856 | -0.0021258 | 0.0084867 | 0.0021263 | 1.0886e-06 | 4.7587e-07 | 0.012877 | 0.012877 | 0.012877 | 0.98054 | -0.37522 | 0.98068 | -0.37252 | 3.5376
67 | -0.010745 | -0.0026923 | 0.010748 | 0.002694 | 3.1682e-06 | 1.6265e-06 | 0.016304 | 0.016304 | 0.016304 | 0.98068 | -0.37252 | 0.981 | -0.36634 | 4.4791
68 | -0.011378 | -0.0028518 | 0.011382 | 0.0028538 | 3.6359e-06 | 1.9159e-06 | 0.017259 | 0.017259 | 0.017259 | 0.981 | -0.36634 | 0.98134 | -0.35963 | 4.7416
69 | -0.074834 | -0.019107 | 0.074873 | 0.019129 | 3.8347e-05 | 2.2879e-05 | 0.11254 | 0.11254 | 0.11254 | 0.99054 | -0.18026 | 0.99109 | -0.16966 | 7.7297
70 | -0.0017767 | -0.00044529 | 0.001777 | 0.00044407 | 2.9983e-07 | -1.2267e-06 | 0.0026815 | 0.002681 | 0.0026815 | 0.98594 | -0.26984 | 0.98613 | -0.26629 | 0.73668
71 | -0.0036576 | -0.00091538 | 0.0036585 | 0.00091493 | 9.4802e-07 | -4.5263e-07 | 0.0055187 | 0.0055183 | 0.0055187 | 0.98613 | -0.26629 | 0.9864 | -0.26084 | 1.5161
72 | 0.021802 | 0.0054907 | -0.021776 | -0.0054746 | 2.6337e-05 | 1.6029e-05 | 0.032899 | 0.032899 | 0.032899 | 0.9864 | -0.26084 | 0.9851 | -0.28614 | 9.0382
73 | -0.025461 | -0.0064056 | 0.025471 | 0.0064116 | 9.8127e-06 | 6.0537e-06 | 0.038417 | 0.038417 | 0.038417 | 0.9864 | -0.26084 | 0.98682 | -0.25278 | 10.5541
74 | 0.021776 | 0.0054746 | -0.021773 | -0.0054726 | 3.2764e-06 | 1.9942e-06 | 0.032899 | 0.032899 | 0.032899 | 0.9851 | -0.28614 | 0.98494 | -0.28929 | 9.0382
75 | -0.028482 | -0.0071664 | 0.028502 | 0.0071785 | 1.9444e-05 | 1.2085e-05 | 0.042958 | 0.042958 | 0.042958 | 0.98682 | -0.25278 | 0.98756 | -0.2385 | 11.8017
76 | 0.020585 | 0.005175 | -0.020582 | -0.0051733 | 2.9313e-06 | 1.7732e-06 | 0.031105 | 0.031105 | 0.031105 | 0.98494 | -0.28929 | 0.98479 | -0.29227 | 8.5453
77 | -0.030715 | -0.0077333 | 0.030723 | 0.0077379 | 7.52e-06 | 4.6931e-06 | 0.046293 | 0.046293 | 0.046293 | 0.98756 | -0.2385 | 0.98782 | -0.23338 | 12.7179
78 | -0.014607 | -0.003667 | 0.014611 | 0.003669 | 3.4681e-06 | 1.9799e-06 | 0.022116 | 0.022116 | 0.022116 | 0.98292 | -0.32875 | 0.98317 | -0.32377 | 6.0758
79 | 0.013871 | 0.0034825 | -0.01387 | -0.0034816 | 1.525e-06 | 8.5914e-07 | 0.021001 | 0.021001 | 0.021001 | 0.98292 | -0.32875 | 0.9828 | -0.33105 | 5.7696
80 | -0.015097 | -0.0037909 | 0.015101 | 0.0037931 | 3.7586e-06 | 2.1621e-06 | 0.022852 | 0.022852 | 0.022852 | 0.98317 | -0.32377 | 0.98344 | -0.31855 | 6.278
81 | 0.012265 | 0.0030794 | -0.01226 | -0.0030767 | 4.9713e-06 | 2.6948e-06 | 0.018572 | 0.018572 | 0.018572 | 0.9828 | -0.33105 | 0.98237 | -0.33955 | 5.1021
82 | -0.015685 | -0.0039395 | 0.015688 | 0.0039413 | 3.1383e-06 | 1.82e-06 | 0.023736 | 0.023736 | 0.023736 | 0.98344 | -0.31855 | 0.98366 | -0.31436 | 6.5208
83 | 0.011393 | 0.0028595 | -0.011389 | -0.0028574 | 3.9772e-06 | 2.0948e-06 | 0.017259 | 0.017259 | 0.017259 | 0.98237 | -0.33955 | 0.98199 | -0.34687 | 4.7415
84 | 0.00030792 | 7.6577e-05 | -0.00030791 | -7.7171e-05 | 3.8174e-09 | -5.9339e-07 | 0.00046559 | 0.0004658 | 0.0004658 | 0.98366 | -0.31436 | 0.98364 | -0.31462 | 0.12797
85 | -0.015996 | -0.0040179 | 0.016002 | 0.004021 | 5.288e-06 | 3.0786e-06 | 0.024201 | 0.024201 | 0.024201 | 0.98366 | -0.31436 | 0.98401 | -0.30743 | 6.6487
86 | 0.011389 | 0.0028574 | -0.011382 | -0.0028538 | 6.9238e-06 | 3.6476e-06 | 0.017259 | 0.017259 | 0.017259 | 0.98199 | -0.34687 | 0.98134 | -0.35963 | 4.7415
87 | -0.017219 | -0.004326 | 0.017227 | 0.0043308 | 8.2516e-06 | 4.8686e-06 | 0.026042 | 0.026041 | 0.026042 | 0.98401 | -0.30743 | 0.98453 | -0.2974 | 7.1543
88 | -0.017227 | -0.0043308 | 0.01723 | 0.0043327 | 3.0862e-06 | 1.8208e-06 | 0.026041 | 0.026041 | 0.026041 | 0.98453 | -0.2974 | 0.98472 | -0.29365 | 7.1543
89 | 0.08478 | 0.021649 | -0.084753 | -0.021632 | 2.7167e-05 | 1.6463e-05 | 0.12726 | 0.12726 | 0.12726 | 0.99245 | -0.14373 | 0.9921 | -0.15036 | 8.7402
90 | -0.086858 | -0.022169 | 0.086871 | 0.022177 | 1.2907e-05 | 7.8416e-06 | 0.13037 | 0.13037 | 0.13037 | 0.99245 | -0.14373 | 0.99261 | -0.14066 | 8.9541
91 | 0.083146 | 0.021229 | -0.083119 | -0.021213 | 2.6843e-05 | 1.6231e-05 | 0.12485 | 0.12485 | 0.12485 | 0.9921 | -0.15036 | 0.99175 | -0.15705 | 8.5747
92 | -0.088446 | -0.022572 | 0.088487 | 0.022597 | 4.0745e-05 | 2.4801e-05 | 0.13273 | 0.13273 | 0.13273 | 0.99261 | -0.14066 | 0.99311 | -0.13113 | 9.1164
93 | 0.081291 | 0.020755 | -0.08128 | -0.020748 | 1.0674e-05 | 6.4373e-06 | 0.1221 | 0.1221 | 0.1221 | 0.99175 | -0.15705 | 0.99161 | -0.15976 | 8.3863
94 | -0.091617 | -0.023381 | 0.091623 | 0.023385 | 5.9005e-06 | 3.6038e-06 | 0.13742 | 0.13742 | 0.13742 | 0.99311 | -0.13113 | 0.99318 | -0.12979 | 9.4384
95 | 0.078891 | 0.02015 | -0.078859 | -0.02013 | 3.1908e-05 | 1.9171e-05 | 0.11852 | 0.11852 | 0.11852 | 0.99161 | -0.15976 | 0.99117 | -0.16813 | 8.1401
96 | -0.092823 | -0.023686 | 0.092835 | 0.023693 | 1.1482e-05 | 7.0216e-06 | 0.13922 | 0.13922 | 0.13922 | 0.99318 | -0.12979 | 0.99331 | -0.12723 | 9.5619
97 | 0.076655 | 0.019578 | -0.076649 | -0.019575 | 5.6501e-06 | 3.382e-06 | 0.11521 | 0.11521 | 0.11521 | 0.99117 | -0.16813 | 0.99109 | -0.16966 | 7.9128
98 | -0.095967 | -0.024478 | 0.095973 | 0.024482 | 6.475e-06 | 3.9713e-06 | 0.14391 | 0.14391 | 0.14391 | 0.99331 | -0.12723 | 0.99339 | -0.12583 | 9.8842
99 | -0.097174 | -0.024783 | 0.097186 | 0.02479 | 1.1993e-05 | 7.3632e-06 | 0.14571 | 0.14571 | 0.14571 | 0.99339 | -0.12583 | 0.99352 | -0.12328 | 10.0076
100 | -0.018937 | -0.0047605 | 0.018938 | 0.0047612 | 1.2438e-06 | 7.445e-07 | 0.028621 | 0.028621 | 0.028621 | 0.98472 | -0.29365 | 0.98479 | -0.29227 | 7.8629
101 | 0.0088847 | 0.0022267 | -0.0088842 | -0.0022265 | 5.4523e-07 | 2.4571e-07 | 0.013405 | 0.013405 | 0.013405 | 0.98623 | -0.26428 | 0.98617 | -0.26556 | 3.6827
102 | -0.010659 | -0.0026714 | 0.010659 | 0.0026715 | 1.2498e-07 | 6.3546e-08 | 0.016082 | 0.016082 | 0.016082 | 0.98623 | -0.26428 | 0.98625 | -0.26403 | 4.4182
103 | 0.0071074 | 0.0017812 | -0.0071074 | -0.0017812 | 6.8162e-08 | 2.3459e-08 | 0.010724 | 0.010724 | 0.010724 | 0.98617 | -0.26556 | 0.98616 | -0.26577 | 2.9462
104 | -0.012436 | -0.0031168 | 0.012437 | 0.0031173 | 1.0682e-06 | 5.8038e-07 | 0.018763 | 0.018763 | 0.018763 | 0.98625 | -0.26403 | 0.98634 | -0.26223 | 5.1547
105 | 0.0053306 | 0.0013359 | -0.0053304 | -0.0013358 | 1.9633e-07 | 2.2408e-08 | 0.0080434 | 0.0080434 | 0.0080434 | 0.98616 | -0.26577 | 0.98612 | -0.26654 | 2.2097
106 | -0.014214 | -0.0035628 | 0.014216 | 0.0035635 | 1.2489e-06 | 7.0687e-07 | 0.021444 | 0.021444 | 0.021444 | 0.98634 | -0.26223 | 0.98643 | -0.26038 | 5.8913
107 | 0.003553 | 0.00089037 | -0.0035529 | -0.00089041 | 7.8622e-08 | -4.2734e-08 | 0.0053613 | 0.0053613 | 0.0053613 | 0.98612 | -0.26654 | 0.98609 | -0.267 | 1.4729
108 | -0.015992 | -0.0040088 | 0.015995 | 0.00401 | 2.1034e-06 | 1.2231e-06 | 0.024125 | 0.024124 | 0.024125 | 0.98643 | -0.26038 | 0.98658 | -0.25762 | 6.6276
109 | 0.0017762 | 0.00044512 | -0.0017762 | -0.00044515 | 6.8785e-09 | -2.8171e-08 | 0.0026802 | 0.0026803 | 0.0026803 | 0.98609 | -0.267 | 0.98609 | -0.26708 | 0.73633
110 | -0.017772 | -0.0044555 | 0.017772 | 0.0044555 | 1.0075e-08 | 5.9696e-09 | 0.026805 | 0.026805 | 0.026805 | 0.98658 | -0.25762 | 0.98658 | -0.25761 | 7.3641
111 | -0.019549 | -0.0049008 | 0.019552 | 0.0049026 | 3.0572e-06 | 1.8369e-06 | 0.029485 | 0.029485 | 0.029485 | 0.98658 | -0.25761 | 0.98674 | -0.25433 | 8.1003
112 | 0.08829 | 0.022302 | -0.088228 | -0.022263 | 6.1633e-05 | 3.9325e-05 | 0.1325 | 0.1325 | 0.1325 | 0.992 | -0.15262 | 0.99124 | -0.1672 | 36.4008
113 | -0.090505 | -0.022857 | 0.090571 | 0.0229 | 6.6779e-05 | 4.2614e-05 | 0.13582 | 0.13582 | 0.13582 | 0.992 | -0.15262 | 0.99279 | -0.13724 | 37.3135
114 | 0.086015 | 0.021708 | -0.085917 | -0.021645 | 9.8051e-05 | 6.2551e-05 | 0.12918 | 0.12918 | 0.12918 | 0.99124 | -0.1672 | 0.99001 | -0.19103 | 35.488
115 | 0.083701 | 0.02109 | -0.083644 | -0.021053 | 5.7343e-05 | 3.6576e-05 | 0.12585 | 0.12585 | 0.12585 | 0.99001 | -0.19103 | 0.98927 | -0.20536 | 34.5731
116 | 0.081431 | 0.020499 | -0.0814 | -0.020479 | 3.0791e-05 | 1.9636e-05 | 0.12252 | 0.12252 | 0.12252 | 0.98927 | -0.20536 | 0.98886 | -0.21328 | 33.6585
117 | 0.10032 | 0.025579 | -0.10032 | -0.025574 | 7.0717e-06 | 4.3532e-06 | 0.1504 | 0.1504 | 0.1504 | 0.9936 | -0.12182 | 0.99352 | -0.12328 | 10.3296
118 | 0.04183 | 0.010535 | -0.041825 | -0.010532 | 5.5974e-06 | 3.534e-06 | 0.062964 | 0.062964 | 0.062964 | 0.98886 | -0.21328 | 0.98871 | -0.21607 | 17.2978
119 | 0.03957 | 0.0099438 | -0.039554 | -0.0099342 | 1.5273e-05 | 9.6276e-06 | 0.059553 | 0.059553 | 0.059553 | 0.98886 | -0.21328 | 0.98844 | -0.22136 | 16.3608
120 | 0.03961 | 0.0099767 | -0.039601 | -0.0099713 | 8.5587e-06 | 5.3953e-06 | 0.059631 | 0.059631 | 0.059631 | 0.98871 | -0.21607 | 0.98848 | -0.22059 | 16.3821
121 | 0.037341 | 0.0093796 | -0.037325 | -0.0093693 | 1.6373e-05 | 1.0302e-05 | 0.056222 | 0.056222 | 0.056222 | 0.98844 | -0.22136 | 0.98797 | -0.23056 | 15.4456
122 | -0.032937 | -0.008293 | 0.032947 | 0.0082988 | 9.306e-06 | 5.8268e-06 | 0.049629 | 0.049629 | 0.049629 | 0.98782 | -0.23338 | 0.98812 | -0.22748 | 13.6344
123 | -0.035161 | -0.0088539 | 0.035164 | 0.0088555 | 2.6354e-06 | 1.6546e-06 | 0.052964 | 0.052964 | 0.052964 | 0.98812 | -0.22748 | 0.9882 | -0.22591 | 14.5506
124 | -0.037377 | -0.0094103 | 0.037387 | 0.0094163 | 9.4981e-06 | 5.9764e-06 | 0.056297 | 0.056297 | 0.056297 | 0.9882 | -0.22591 | 0.98848 | -0.22059 | 15.4662
125 | 0.030672 | 0.0076973 | -0.030667 | -0.0076938 | 5.5343e-06 | 3.4536e-06 | 0.046218 | 0.046218 | 0.046218 | 0.98758 | -0.23805 | 0.98739 | -0.24184 | 12.6973
126 | -0.032886 | -0.008252 | 0.032888 | 0.0082536 | 2.5419e-06 | 1.5915e-06 | 0.049553 | 0.049553 | 0.049553 | 0.98758 | -0.23805 | 0.98766 | -0.23643 | 13.6135
127 | 0.028889 | 0.0072484 | -0.028887 | -0.0072473 | 1.7545e-06 | 1.0913e-06 | 0.04354 | 0.04354 | 0.04354 | 0.98739 | -0.24184 | 0.98732 | -0.24311 | 11.9614
128 | -0.035101 | -0.0088082 | 0.035111 | 0.0088144 | 9.836e-06 | 6.175e-06 | 0.052887 | 0.052887 | 0.052887 | 0.98766 | -0.23643 | 0.98797 | -0.23056 | 14.5294
129 | 0.026673 | 0.0066922 | -0.026667 | -0.0066886 | 5.8577e-06 | 3.6253e-06 | 0.040202 | 0.040202 | 0.040202 | 0.98732 | -0.24311 | 0.98708 | -0.24772 | 11.0445
130 | 0.02489 | 0.0062432 | -0.024886 | -0.0062412 | 3.1269e-06 | 1.9255e-06 | 0.037523 | 0.037523 | 0.037523 | 0.98708 | -0.24772 | 0.98695 | -0.25035 | 10.3084
131 | 0.023111 | 0.0057963 | -0.023107 | -0.0057936 | 4.2719e-06 | 2.6141e-06 | 0.034846 | 0.034846 | 0.034846 | 0.98695 | -0.25035 | 0.98675 | -0.25423 | 9.573
132 | 0.021329 | 0.0053482 | -0.021329 | -0.0053481 | 9.939e-08 | 6.0338e-08 | 0.032165 | 0.032165 | 0.032165 | 0.98675 | -0.25423 | 0.98674 | -0.25433 | 8.8367

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.20642 | 0.052435

## res_load
| p_mw | q_mvar
0 | 0.0053024 | 0.0013289
1 | 0.00073375 | 0.00018389
2 | 0.0015167 | 0.00038012
3 | 0.00028327 | 7.0995e-05
4 | 0.007259 | 0.0018193
5 | 0.0055671 | 0.0013953
6 | 0.004874 | 0.0012215
7 | 0.0041256 | 0.001034
8 | 0.00047961 | 0.0001202
9 | 0.00049723 | 0.00012462
10 | 0.0014557 | 0.00036484
11 | 0.00020157 | 5.0518e-05
12 | 0.0022864 | 0.00057303
13 | 0.00058121 | 0.00014567
14 | 0.00079973 | 0.00020043
15 | 0.0036022 | 0.0009028
16 | 0.0002271 | 5.6916e-05
17 | 0.00082814 | 0.00020755
18 | 0.00097245 | 0.00024372
19 | 0.00091795 | 0.00023006
20 | 0.0016708 | 0.00041874
21 | 0.0015551 | 0.00038974
22 | 0.001378 | 0.00034536
23 | 0.0018219 | 0.00045662
24 | 0.00087973 | 0.00022048
25 | 0.0010859 | 0.00027214
26 | 0.00036851 | 9.2358e-05
27 | 0.00019285 | 4.8334e-05
28 | 9.2678e-05 | 2.3227e-05
29 | 0.00021654 | 5.427e-05
30 | 0.001829 | 0.0004584
31 | 0.00056949 | 0.00014273
32 | 0.002871 | 0.00071953
33 | 0.003606 | 0.00090374
34 | 0.0028783 | 0.00072137
35 | 0.00053099 | 0.00013308
36 | 0.00081384 | 0.00020397
37 | 0.00072032 | 0.00018053
38 | 0.0020204 | 0.00050637
39 | 0.00072298 | 0.00018119
40 | 0.0039816 | 0.00099788
41 | 0.0030029 | 0.00075259
42 | 0.002229 | 0.00055863
43 | 0.0032519 | 0.000815
44 | 0.0017866 | 0.00044777
45 | 0.0034459 | 0.00086361
46 | 0.0022586 | 0.00056605
47 | 0.00062999 | 0.00015789
48 | 0.0018617 | 0.00046659
49 | 0.0017767 | 0.00044529
50 | 0.0018806 | 0.00047131
51 | 0.0030117 | 0.00075481
52 | 0.0011874 | 0.0002976
53 | 0.0022134 | 0.00055472
54 | 0.0007362 | 0.00018451
55 | 0.00048645 | 0.00012192
56 | 0.0016048 | 0.00040221
57 | 0.00058419 | 0.00014641
58 | 0.00086677 | 0.00021723
59 | 0.00030791 | 7.7171e-05
60 | 0.0012171 | 0.00030503
61 | 0.0020775 | 0.00052067
62 | 0.0016069 | 0.00040272
63 | 0.0015758 | 0.00039493
64 | 0.0018286 | 0.0004583
65 | 0.0031302 | 0.00078451
66 | 0.0023892 | 0.00059878
67 | 0.0012001 | 0.00030077
68 | 0.0022041 | 0.0005524
69 | 0.0031321 | 0.00078497
70 | 0.0017765 | 0.00044523
71 | 0.0012003 | 0.00030081
72 | 0.0017071 | 0.00042783
73 | 0.001644 | 0.00041202
74 | 0.0028935 | 0.00072517
75 | 0.0017743 | 0.00044469
76 | 0.0017767 | 0.00044529
77 | 0.0017767 | 0.00044529
78 | 0.0017767 | 0.00044529
79 | 0.0017774 | 0.00044547
80 | 0.0017775 | 0.00044547
81 | 0.0017767 | 0.00044529
82 | 0.0017767 | 0.00044529
83 | 0.0017774 | 0.00044547
84 | 0.0017762 | 0.00044515
85 | 0.0017767 | 0.00044529
86 | 0.0022147 | 0.00055506
87 | 0.0022134 | 0.00055473
88 | 0.0022134 | 0.00055473
89 | 0.0022156 | 0.00055529
90 | 0.0022134 | 0.00055472
91 | 0.0017765 | 0.00044523
92 | 0.0031302 | 0.00078451
93 | 0.0022147 | 0.00055505
94 | 0.0022129 | 0.00055459
95 | 0.0022147 | 0.00055505
96 | 0.0022147 | 0.00055505
97 | 0.0022135 | 0.00055475
98 | 0.0022145 | 0.00055502
99 | 0.0022135 | 0.00055475
100 | 0.0017774 | 0.00044546
101 | 0.0022129 | 0.00055459
102 | 0.0022146 | 0.00055502
103 | 0.0022142 | 0.00055492
104 | 0.0017774 | 0.00044546
105 | 0.0017755 | 0.00044497
106 | 0.0017774 | 0.00044547
107 | 0.0017774 | 0.00044547

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1