## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2135-4_1_3_node_42 | 0.4 | n |  | TRUE
1 | bus_LV_2135-4_1_3_node_43 | 0.4 | n |  | TRUE
2 | bus_LV_2135-4_1_3_node_44 | 0.4 | n |  | TRUE
3 | bus_LV_2135-4_1_3_node_46 | 0.4 | n |  | TRUE
4 | bus_LV_2135-4_1_3_node_45 | 0.4 | n |  | TRUE
5 | bus_LV_2135-4_1_3_node_50 | 0.4 | n |  | TRUE
6 | bus_LV_2135-4_1_3_node_83 | 0.4 | n |  | TRUE
7 | bus_LV_2135-4_1_3_node_74 | 0.4 | n |  | TRUE
8 | bus_LV_2135-4_1_3_node_69 | 0.4 | n |  | TRUE
9 | bus_LV_2135-4_1_3_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_2135-4_1_3_node_49 | 0.4 | n |  | TRUE
11 | bus_LV_2135-4_1_3_node_51 | 0.4 | n |  | TRUE
12 | bus_LV_2135-4_1_3_node_53 | 0.4 | n |  | TRUE
13 | bus_LV_2135-4_1_3_node_54 | 0.4 | n |  | TRUE
14 | bus_LV_2135-4_1_3_node_52 | 0.4 | n |  | TRUE
15 | bus_LV_2135-4_1_3_node_70 | 0.4 | n |  | TRUE
16 | bus_LV_2135-4_1_3_node_78 | 0.4 | n |  | TRUE
17 | bus_LV_2135-4_1_3_node_62 | 0.4 | n |  | TRUE
18 | bus_LV_2135-4_1_3_node_55 | 0.4 | n |  | TRUE
19 | bus_LV_2135-4_1_3_node_56 | 0.4 | n |  | TRUE
20 | bus_LV_2135-4_1_3_node_58 | 0.4 | n |  | TRUE
21 | bus_LV_2135-4_1_3_node_174 | 0.4 | n |  | TRUE
22 | bus_LV_2135-4_1_3_node_60 | 0.4 | n |  | TRUE
23 | bus_LV_2135-4_1_3_node_175 | 0.4 | n |  | TRUE
24 | bus_LV_2135-4_1_3_node_61 | 0.4 | n |  | TRUE
25 | bus_LV_2135-4_1_3_node_63 | 0.4 | n |  | TRUE
26 | bus_LV_2135-4_1_3_node_64 | 0.4 | n |  | TRUE
27 | bus_LV_2135-4_1_3_node_65 | 0.4 | n |  | TRUE
28 | bus_LV_2135-4_1_3_node_182 | 0.4 | n |  | TRUE
29 | bus_LV_2135-4_1_3_node_66 | 0.4 | n |  | TRUE
30 | bus_LV_2135-4_1_3_node_67 | 0.4 | n |  | TRUE
31 | bus_LV_2135-4_1_3_node_68 | 0.4 | n |  | TRUE
32 | bus_LV_2135-4_1_3_node_71 | 0.4 | n |  | TRUE
33 | bus_LV_2135-4_1_3_node_72 | 0.4 | n |  | TRUE
34 | bus_LV_2135-4_1_3_node_73 | 0.4 | n |  | TRUE
35 | bus_LV_2135-4_1_3_node_75 | 0.4 | n |  | TRUE
36 | bus_LV_2135-4_1_3_node_76 | 0.4 | n |  | TRUE
37 | bus_LV_2135-4_1_3_node_208 | 0.4 | n |  | TRUE
38 | bus_LV_2135-4_1_3_node_200 | 0.4 | n |  | TRUE
39 | bus_LV_2135-4_1_3_node_210 | 0.4 | n |  | TRUE
40 | bus_LV_2135-4_1_3_node_203 | 0.4 | n |  | TRUE
41 | bus_LV_2135-4_1_3_node_184 | 0.4 | n |  | TRUE
42 | bus_LV_2135-4_1_3_node_79 | 0.4 | n |  | TRUE
43 | bus_LV_2135-4_1_3_node_80 | 0.4 | n |  | TRUE
44 | bus_LV_2135-4_1_3_node_81 | 0.4 | n |  | TRUE
45 | bus_LV_2135-4_1_3_node_176 | 0.4 | n |  | TRUE
46 | bus_LV_2135-4_1_3_node_177 | 0.4 | n |  | TRUE
47 | bus_LV_2135-4_1_3_node_178 | 0.4 | n |  | TRUE
48 | bus_LV_2135-4_1_3_node_179 | 0.4 | n |  | TRUE
49 | bus_LV_2135-4_1_3_node_180 | 0.4 | n |  | TRUE
50 | bus_LV_2135-4_1_3_node_181 | 0.4 | n |  | TRUE
51 | bus_LV_2135-4_1_3_node_213 | 0.4 | n |  | TRUE
52 | bus_LV_2135-4_1_3_node_183 | 0.4 | n |  | TRUE
53 | bus_LV_2135-4_1_3_node_185 | 0.4 | n |  | TRUE
54 | bus_LV_2135-4_1_3_node_186 | 0.4 | n |  | TRUE
55 | bus_LV_2135-4_1_3_node_187 | 0.4 | n |  | TRUE
56 | bus_LV_2135-4_1_3_node_188 | 0.4 | n |  | TRUE
57 | bus_LV_2135-4_1_3_node_189 | 0.4 | n |  | TRUE
58 | bus_LV_2135-4_1_3_node_217 | 0.4 | n |  | TRUE
59 | bus_LV_2135-4_1_3_node_190 | 0.4 | n |  | TRUE
60 | bus_LV_2135-4_1_3_node_191 | 0.4 | n |  | TRUE
61 | bus_LV_2135-4_1_3_node_192 | 0.4 | n |  | TRUE
62 | bus_LV_2135-4_1_3_node_193 | 0.4 | n |  | TRUE
63 | bus_LV_2135-4_1_3_node_194 | 0.4 | n |  | TRUE
64 | bus_LV_2135-4_1_3_node_195 | 0.4 | n |  | TRUE
65 | bus_LV_2135-4_1_3_node_196 | 0.4 | n |  | TRUE
66 | bus_LV_2135-4_1_3_node_197 | 0.4 | n |  | TRUE
67 | bus_LV_2135-4_1_3_node_198 | 0.4 | n |  | TRUE
68 | bus_LV_2135-4_1_3_node_199 | 0.4 | n |  | TRUE
69 | bus_LV_2135-4_1_3_node_204 | 0.4 | n |  | TRUE
70 | bus_LV_2135-4_1_3_node_218 | 0.4 | n |  | TRUE
71 | bus_LV_2135-4_1_3_node_209 | 0.4 | n |  | TRUE
72 | bus_LV_2135-4_1_3_node_201 | 0.4 | n |  | TRUE
73 | bus_LV_2135-4_1_3_node_202 | 0.4 | n |  | TRUE
74 | bus_LV_2135-4_1_3_node_219 | 0.4 | n |  | TRUE
75 | bus_LV_2135-4_1_3_node_205 | 0.4 | n |  | TRUE
76 | bus_LV_2135-4_1_3_node_222 | 0.4 | n |  | TRUE
77 | bus_LV_2135-4_1_3_node_211 | 0.4 | n |  | TRUE
78 | bus_LV_2135-4_1_3_node_212 | 0.4 | n |  | TRUE
79 | bus_LV_2135-4_1_3_node_214 | 0.4 | n |  | TRUE
80 | bus_LV_2135-4_1_3_node_215 | 0.4 | n |  | TRUE
81 | bus_LV_2135-4_1_3_node_216 | 0.4 | n |  | TRUE
82 | bus_LV_2135-4_1_3_node_220 | 0.4 | n |  | TRUE
83 | bus_LV_2135-4_1_3_node_221 | 0.4 | n |  | TRUE
84 | bus_MV_28_0_node_31 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2135-4_1_3_load_42 | 0 | 0.011916 | 0.0029865 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2135-4_1_3_load_44 | 2 | 0.010206 | 0.0025579 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2135-4_1_3_load_50 | 5 | 0.0045039 | 0.0011288 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2135-4_1_3_load_74 | 7 | 0.004929 | 0.0012353 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2135-4_1_3_load_48 | 9 | 0.0026197 | 0.00065656 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2135-4_1_3_load_53 | 12 | 0.0024606 | 0.00061669 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2135-4_1_3_load_54 | 13 | 0.0010626 | 0.00026632 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2135-4_1_3_load_78 | 16 | 0.0064253 | 0.0016103 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2135-4_1_3_load_62 | 17 | 0.0024228 | 0.00060721 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2135-4_1_3_load_55 | 18 | 0.00080777 | 0.00020245 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2135-4_1_3_load_56 | 19 | 0.0026567 | 0.00066584 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2135-4_1_3_load_58 | 20 | 0.0010324 | 0.00025875 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2135-4_1_3_load_174 | 21 | 0.00047393 | 0.00011878 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2135-4_1_3_load_60 | 22 | 0.00059972 | 0.0001503 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2135-4_1_3_load_175 | 23 | 0.0013442 | 0.00033688 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2135-4_1_3_load_61 | 24 | 0.0056859 | 0.001425 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2135-4_1_3_load_63 | 25 | 0.0022113 | 0.0005542 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2135-4_1_3_load_64 | 26 | 0.0021211 | 0.00053159 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2135-4_1_3_load_65 | 27 | 0.0021382 | 0.0005359 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2135-4_1_3_load_182 | 28 | 0.0029549 | 0.00074058 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2135-4_1_3_load_66 | 29 | 0.014894 | 0.0037327 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2135-4_1_3_load_67 | 30 | 0.00704 | 0.0017644 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2135-4_1_3_load_68 | 31 | 0.007096 | 0.0017784 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2135-4_1_3_load_71 | 32 | 0.0059738 | 0.0014972 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2135-4_1_3_load_72 | 33 | 0.0037039 | 0.00092828 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2135-4_1_3_load_75 | 35 | 0.0012815 | 0.00032118 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2135-4_1_3_load_208 | 37 | 0.0023214 | 0.00058179 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2135-4_1_3_load_200 | 38 | 0.0023306 | 0.0005841 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2135-4_1_3_load_210 | 39 | 0.00088679 | 0.00022225 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2135-4_1_3_load_203 | 40 | 0.0087933 | 0.0022038 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2135-4_1_3_load_184 | 41 | 0.0018987 | 0.00047586 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2135-4_1_3_load_79 | 42 | 0.0065307 | 0.0016368 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2135-4_1_3_load_80 | 43 | 0.0009572 | 0.0002399 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2135-4_1_3_load_81 | 44 | 0.00086781 | 0.00021749 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2135-4_1_3_load_176 | 45 | 0.00069138 | 0.00017328 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2135-4_1_3_load_178 | 47 | 0.0029284 | 0.00073393 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2135-4_1_3_load_181 | 50 | 0.0021405 | 0.00053646 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2135-4_1_3_load_213 | 51 | 0.0012693 | 0.00031813 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2135-4_1_3_load_183 | 52 | 0.0079152 | 0.0019837 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2135-4_1_3_load_185 | 53 | 0.00065319 | 0.00016371 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2135-4_1_3_load_186 | 54 | 0.00053539 | 0.00013418 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2135-4_1_3_load_187 | 55 | 0.0014079 | 0.00035285 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2135-4_1_3_load_189 | 57 | 0.0019766 | 0.00049538 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2135-4_1_3_load_217 | 58 | 0.0027776 | 0.00069614 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2135-4_1_3_load_190 | 59 | 0.0026452 | 0.00066294 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2135-4_1_3_load_191 | 60 | 0.0031753 | 0.0007958 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2135-4_1_3_load_193 | 62 | 0.007835 | 0.0019636 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2135-4_1_3_load_194 | 63 | 0.00097548 | 0.00024448 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2135-4_1_3_load_196 | 65 | 0.0039479 | 0.00098945 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2135-4_1_3_load_199 | 68 | 0.0019698 | 0.00049369 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2135-4_1_3_load_204 | 69 | 0.0034075 | 0.000854 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2135-4_1_3_load_218 | 70 | 0.0009088 | 0.00022777 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2135-4_1_3_load_201 | 72 | 0.0019545 | 0.00048984 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2135-4_1_3_load_202 | 73 | 0.0030552 | 0.00076571 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2135-4_1_3_load_219 | 74 | 0.0021415 | 0.00053672 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2135-4_1_3_load_205 | 75 | 0.002266 | 0.00056792 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2135-4_1_3_load_222 | 76 | 0.0018385 | 0.00046077 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2135-4_1_3_load_211 | 77 | 0.010175 | 0.0025502 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2135-4_1_3_load_212 | 78 | 0.010887 | 0.0027287 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2135-4_1_3_load_214 | 79 | 0.0022598 | 0.00056636 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2135-4_1_3_load_215 | 80 | 0.0035229 | 0.00088293 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2135-4_1_3_load_216 | 81 | 0.006545 | 0.0016403 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2135-4_1_3_load_220 | 82 | 0.0022599 | 0.00056639 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2135-4_1_3_load_221 | 83 | 0.0026577 | 0.00066608 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2135-4_1_3_line_0 |  | 0 | 1 | 0.018213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2135-4_1_3_line_1 |  | 1 | 2 | 0.023268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2135-4_1_3_line_2 |  | 1 | 3 | 0.05547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2135-4_1_3_line_3 |  | 3 | 7 | 0.023143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2135-4_1_3_line_4 |  | 3 | 8 | 0.046724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2135-4_1_3_line_5 |  | 3 | 4 | 0.029841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2135-4_1_3_line_6 |  | 4 | 5 | 0.032618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2135-4_1_3_line_7 |  | 4 | 6 | 0.54921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2135-4_1_3_line_8 |  | 6 | 44 | 0.11815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2135-4_1_3_line_9 |  | 7 | 38 | 0.034869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2135-4_1_3_line_10 |  | 8 | 32 | 0.020377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2135-4_1_3_line_11 |  | 8 | 33 | 0.019219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2135-4_1_3_line_12 |  | 8 | 30 | 0.045666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2135-4_1_3_line_13 |  | 9 | 10 | 0.083376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2135-4_1_3_line_14 |  | 10 | 11 | 0.067959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2135-4_1_3_line_15 |  | 11 | 12 | 0.11956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2135-4_1_3_line_16 |  | 11 | 13 | 0.05391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2135-4_1_3_line_17 |  | 13 | 17 | 0.0060506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2135-4_1_3_line_18 |  | 14 | 15 | 0.10752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2135-4_1_3_line_19 |  | 14 | 16 | 0.082601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2135-4_1_3_line_20 |  | 15 | 34 | 0.049149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2135-4_1_3_line_21 |  | 15 | 31 | 0.022302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2135-4_1_3_line_22 |  | 16 | 42 | 0.019146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2135-4_1_3_line_23 |  | 17 | 24 | 0.0032576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2135-4_1_3_line_24 |  | 18 | 19 | 0.0061827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2135-4_1_3_line_25 |  | 18 | 20 | 0.17027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2135-4_1_3_line_26 |  | 19 | 21 | 0.31185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2135-4_1_3_line_27 |  | 21 | 23 | 0.01948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2135-4_1_3_line_28 |  | 21 | 45 | 0.083602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2135-4_1_3_line_29 |  | 22 | 23 | 0.0038065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2135-4_1_3_line_30 |  | 24 | 25 | 0.023962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2135-4_1_3_line_31 |  | 25 | 26 | 0.0032588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2135-4_1_3_line_32 |  | 26 | 27 | 0.018057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2135-4_1_3_line_33 |  | 27 | 28 | 0.015138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2135-4_1_3_line_34 |  | 28 | 52 | 0.0082069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2135-4_1_3_line_35 |  | 29 | 30 | 0.013366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2135-4_1_3_line_36 |  | 29 | 31 | 0.01206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2135-4_1_3_line_37 |  | 32 | 35 | 0.02385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2135-4_1_3_line_38 |  | 33 | 36 | 0.014191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2135-4_1_3_line_39 |  | 34 | 37 | 0.024226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2135-4_1_3_line_40 |  | 35 | 39 | 0.039534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2135-4_1_3_line_41 |  | 36 | 40 | 0.033526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2135-4_1_3_line_42 |  | 36 | 41 | 0.027911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2135-4_1_3_line_43 |  | 37 | 66 | 0.017169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2135-4_1_3_line_44 |  | 38 | 72 | 0.0026411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2135-4_1_3_line_45 |  | 39 | 77 | 0.017132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2135-4_1_3_line_46 |  | 41 | 52 | 0.024713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2135-4_1_3_line_47 |  | 43 | 44 | 0.0086147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2135-4_1_3_line_48 |  | 45 | 46 | 0.07773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2135-4_1_3_line_49 |  | 46 | 47 | 0.023713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2135-4_1_3_line_50 |  | 47 | 48 | 0.024097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2135-4_1_3_line_51 |  | 48 | 49 | 0.31526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2135-4_1_3_line_52 |  | 49 | 50 | 0.081741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2135-4_1_3_line_53 |  | 50 | 51 | 0.0304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2135-4_1_3_line_54 |  | 51 | 79 | 0.014844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2135-4_1_3_line_55 |  | 53 | 54 | 0.025881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2135-4_1_3_line_56 |  | 53 | 55 | 0.016866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2135-4_1_3_line_57 |  | 54 | 56 | 0.044414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2135-4_1_3_line_58 |  | 56 | 57 | 0.03693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2135-4_1_3_line_59 |  | 57 | 58 | 0.030935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2135-4_1_3_line_60 |  | 58 | 71 | 0.024728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2135-4_1_3_line_61 |  | 59 | 60 | 0.020061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2135-4_1_3_line_62 |  | 59 | 61 | 0.022437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2135-4_1_3_line_63 |  | 60 | 62 | 0.023137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2135-4_1_3_line_64 |  | 61 | 63 | 0.0077827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2135-4_1_3_line_65 |  | 61 | 64 | 0.009632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2135-4_1_3_line_66 |  | 62 | 65 | 0.026388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2135-4_1_3_line_67 |  | 63 | 66 | 0.0057065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2135-4_1_3_line_68 |  | 64 | 67 | 0.003291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2135-4_1_3_line_69 |  | 64 | 68 | 0.023207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2135-4_1_3_line_70 |  | 65 | 69 | 0.0043922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2135-4_1_3_line_71 |  | 67 | 70 | 0.021851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2135-4_1_3_line_72 |  | 67 | 71 | 0.008802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2135-4_1_3_line_73 |  | 69 | 75 | 0.0077626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2135-4_1_3_line_74 |  | 69 | 76 | 0.045354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2135-4_1_3_line_75 |  | 72 | 73 | 0.025601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2135-4_1_3_line_76 |  | 73 | 74 | 0.02272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2135-4_1_3_line_77 |  | 74 | 82 | 0.0096879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2135-4_1_3_line_78 |  | 76 | 81 | 0.0036563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2135-4_1_3_line_79 |  | 77 | 78 | 0.0081338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2135-4_1_3_line_80 |  | 79 | 80 | 0.022065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2135-4_1_3_line_81 |  | 80 | 81 | 0.030729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2135-4_1_3_line_82 |  | 82 | 83 | 0.013392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2135-4_1_3_trafo_71 | 0.63 MVA 20/0.4 kV | 84 | 32 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2572768.772 | 1159976.1786 | 2572778.9379 | 1159961.067
1 | 2572768.772 | 1159976.1786 | 2572787.9892 | 1159989.298
2 | 2572768.772 | 1159976.1786 | 2572728.3425 | 1159948.5818 | 2572732.0965 | 1159943.251
3 | 2572732.0965 | 1159943.251 | 2572713.3703 | 1159929.6518
4 | 2572760.2139 | 1159905.8821 | 2572732.0965 | 1159943.251
5 | 2572717.1616 | 1159968.9318 | 2572722.8066 | 1159956.4332 | 2572728.3425 | 1159948.5818 | 2572732.0965 | 1159943.251
6 | 2572717.1616 | 1159968.9318 | 2572707.9616 | 1159964.8161 | 2572689.7995 | 1159951.4689
7 | 2572562.7733 | 1160495.9907 | 2572717.1616 | 1159968.9318
8 | 2572562.7733 | 1160495.9907 | 2572592.1819 | 1160532.2967 | 2572625.9555 | 1160584.8022 | 2572631.5206 | 1160591.8773
9 | 2572713.3703 | 1159929.6518 | 2572685.156 | 1159909.1622
10 | 2572760.2139 | 1159905.8821 | 2572766.5681 | 1159892.5688 | 2572768.6389 | 1159887.3386
11 | 2572760.2139 | 1159905.8821 | 2572744.3072 | 1159895.0961
12 | 2572760.2139 | 1159905.8821 | 2572766.9004 | 1159908.3641 | 2572799.0336 | 1159929.6316
13 | 2572542.6001 | 1159729.1191 | 2572552.4942 | 1159759.1778 | 2572551.9498 | 1159765.8169 | 2572541.4136 | 1159779.6166 | 2572537.7993 | 1159785.3138 | 2572541.2625 | 1159801.8396 | 2572543.4592 | 1159805.272
14 | 2572542.6001 | 1159729.1191 | 2572596.8571 | 1159763.2213 | 2572600.8073 | 1159763.937
15 | 2572701.1365 | 1159750.1947 | 2572690.3338 | 1159749.3323 | 2572647.0807 | 1159734.8777 | 2572634.4282 | 1159731.7228 | 2572623.4081 | 1159733.6074 | 2572614.6998 | 1159738.2272 | 2572606.7179 | 1159750.859 | 2572600.8073 | 1159763.937
16 | 2572600.8073 | 1159763.937 | 2572614.7419 | 1159797.7681 | 2572628.5428 | 1159808.2358
17 | 2572633.3637 | 1159811.8923 | 2572628.5428 | 1159808.2358
18 | 2572805.6739 | 1160048.9366 | 2572813.4565 | 1160036.295 | 2572823.02 | 1160019.1986 | 2572831.9329 | 1160000.6044 | 2572840.3605 | 1159978.0548 | 2572842.9675 | 1159968.2047 | 2572833.5805 | 1159965.079 | 2572826.1679 | 1159961.333
19 | 2572805.6739 | 1160048.9366 | 2572812.5873 | 1160052.4737 | 2572819.077 | 1160050.4655 | 2572827.8645 | 1160038.0305 | 2572831.3372 | 1160023.0295 | 2572846.8004 | 1159988.9567
20 | 2572826.1679 | 1159961.333 | 2572833.5805 | 1159965.079 | 2572842.9675 | 1159968.2047 | 2572846.5617 | 1159954.6372 | 2572850.2191 | 1159938.1234
21 | 2572826.1679 | 1159961.333 | 2572826.3986 | 1159958.1303 | 2572827.997 | 1159954.0099 | 2572828.2731 | 1159948.9839 | 2572820.2365 | 1159943.6648
22 | 2572860.1499 | 1159978.3876 | 2572852.4661 | 1159979.0338 | 2572847.5299 | 1159987.3493 | 2572846.8004 | 1159988.9567
23 | 2572633.3637 | 1159811.8923 | 2572635.9591 | 1159813.8609
24 | 2573614.7559 | 1159950.6225 | 2573616.4669 | 1159955.7335 | 2573616.7853 | 1159956.4596
25 | 2573614.7559 | 1159950.6225 | 2573589.8281 | 1159782.1887
26 | 2573333.355 | 1160086.5201 | 2573616.7853 | 1159956.4596
27 | 2573333.355 | 1160086.5201 | 2573335.1895 | 1160095.2704 | 2573334.2473 | 1160105.7673
28 | 2573333.355 | 1160086.5201 | 2573330.3114 | 1160072.0026 | 2573315.9189 | 1160034.1031 | 2573305.9784 | 1160007.6822
29 | 2573334.2473 | 1160105.7673 | 2573333.9071 | 1160109.5585
30 | 2572655.0504 | 1159828.3412 | 2572635.9591 | 1159813.8609
31 | 2572657.6468 | 1159830.3105 | 2572655.0504 | 1159828.3412
32 | 2572672.0333 | 1159841.2223 | 2572657.6468 | 1159830.3105
33 | 2572672.0333 | 1159841.2223 | 2572684.0946 | 1159850.3706
34 | 2572684.0946 | 1159850.3706 | 2572690.6334 | 1159855.3301
35 | 2572810.1797 | 1159937.0086 | 2572799.0336 | 1159929.6316
36 | 2572820.2365 | 1159943.6648 | 2572810.1797 | 1159937.0086
37 | 2572775.3481 | 1159864.6322 | 2572774.289 | 1159873.0683 | 2572768.6389 | 1159887.3386
38 | 2572732.5616 | 1159887.1317 | 2572744.3072 | 1159895.0961
39 | 2572850.2191 | 1159938.1234 | 2572849.1672 | 1159929.2348 | 2572850.8345 | 1159918.3107 | 2572851.7852 | 1159914.1946
40 | 2572775.3481 | 1159864.6322 | 2572780.2727 | 1159825.4061 | 2572780.2727 | 1159825.4061
41 | 2572732.5616 | 1159887.1317 | 2572740.5754 | 1159854.5781
42 | 2572732.5616 | 1159887.1317 | 2572710.3236 | 1159870.2647
43 | 2572854.2567 | 1159897.229 | 2572852.9165 | 1159909.2967 | 2572851.7852 | 1159914.1946
44 | 2572685.156 | 1159909.1622 | 2572683.0189 | 1159907.6103
45 | 2572780.2727 | 1159825.4061 | 2572774.7353 | 1159819.4838 | 2572766.5034 | 1159815.785
46 | 2572690.6334 | 1159855.3301 | 2572710.3236 | 1159870.2647
47 | 2572631.5206 | 1160591.8773 | 2572636.8466 | 1160598.6483
48 | 2573278.6065 | 1159934.9306 | 2573305.9784 | 1160007.6822
49 | 2573278.6065 | 1159934.9306 | 2573270.2704 | 1159912.7312
50 | 2573261.7992 | 1159890.1719 | 2573270.2704 | 1159912.7312
51 | 2573261.7992 | 1159890.1719 | 2573024.2049 | 1159682.9542
52 | 2573024.2049 | 1159682.9542 | 2572974.5932 | 1159747.9173
53 | 2572955.5085 | 1159771.5789 | 2572973.5678 | 1159749.26 | 2572974.5932 | 1159747.9173
54 | 2572955.5085 | 1159771.5789 | 2572946.171 | 1159783.1188
55 | 2572935.2451 | 1159932.7614 | 2572940.0354 | 1159958.1955
56 | 2572932.1233 | 1159916.1865 | 2572935.2451 | 1159932.7614
57 | 2572907.9694 | 1159974.4138 | 2572941.8678 | 1159967.9241 | 2572940.0354 | 1159958.1955
58 | 2572907.9694 | 1159974.4138 | 2572905.814 | 1159963.8404 | 2572901.1718 | 1159942.2505 | 2572899.6044 | 1159938.51
59 | 2572884.8122 | 1159911.5345 | 2572893.6257 | 1159924.2423 | 2572899.6044 | 1159938.51
60 | 2572868.2651 | 1159893.5749 | 2572875.932 | 1159899.3097 | 2572876.8473 | 1159900.0504 | 2572884.8122 | 1159911.5345
61 | 2572854.4426 | 1159862.6811 | 2572853.9036 | 1159842.6274
62 | 2572854.4394 | 1159885.111 | 2572854.7129 | 1159872.7368 | 2572854.4426 | 1159862.6811
63 | 2572853.9036 | 1159842.6274 | 2572853.282 | 1159819.4984
64 | 2572854.4394 | 1159885.111 | 2572852.8087 | 1159887.1861 | 2572851.9079 | 1159889.6581 | 2572851.8243 | 1159892.1692
65 | 2572863.491 | 1159883.5359 | 2572860.3457 | 1159882.8609 | 2572857.1753 | 1159883.4088 | 2572854.4394 | 1159885.111
66 | 2572853.282 | 1159819.4984 | 2572852.573 | 1159793.1201
67 | 2572854.2567 | 1159897.229 | 2572852.5521 | 1159894.8244 | 2572851.8202 | 1159892.2931 | 2572851.8243 | 1159892.1692
68 | 2572866.1971 | 1159885.3912 | 2572864.9354 | 1159884.3297 | 2572863.491 | 1159883.5359
69 | 2572863.491 | 1159883.5359 | 2572859.8166 | 1159872.6359 | 2572858.7115 | 1159860.9843
70 | 2572852.455 | 1159788.7296 | 2572852.573 | 1159793.1201
71 | 2572866.1971 | 1159885.3912 | 2572869.6869 | 1159882.6074 | 2572880.3855 | 1159874.088 | 2572884.0533 | 1159874.6507
72 | 2572866.1971 | 1159885.3912 | 2572867.8558 | 1159887.8072 | 2572868.5738 | 1159890.6609 | 2572868.2651 | 1159893.5749
73 | 2572852.721 | 1159780.974 | 2572852.6889 | 1159781.2222 | 2572852.4361 | 1159788.0267 | 2572852.455 | 1159788.7296
74 | 2572852.455 | 1159788.7296 | 2572897.7897 | 1159787.3906
75 | 2572683.0189 | 1159907.6103 | 2572662.3037 | 1159892.5666
76 | 2572643.9199 | 1159879.2161 | 2572662.3037 | 1159892.5666
77 | 2572636.081 | 1159873.5234 | 2572643.9199 | 1159879.2161
78 | 2572897.7897 | 1159787.3906 | 2572900.6266 | 1159789.6972
79 | 2572759.0841 | 1159812.4513 | 2572766.5034 | 1159815.785
80 | 2572946.171 | 1159783.1188 | 2572942.5023 | 1159787.6528 | 2572928.9852 | 1159796.6405 | 2572928.9852 | 1159796.6405
81 | 2572928.9852 | 1159796.6405 | 2572912.9105 | 1159797.6247 | 2572901.1583 | 1159790.1296 | 2572900.6266 | 1159789.6972
82 | 2572625.2452 | 1159865.6543 | 2572636.081 | 1159873.5234

## bus_geodata
| x | y | coords
0 | 2572778.9379 | 1159961.067
1 | 2572768.772 | 1159976.1786
2 | 2572787.9892 | 1159989.298
3 | 2572732.0965 | 1159943.251
4 | 2572717.1616 | 1159968.9318
5 | 2572689.7995 | 1159951.4689
6 | 2572562.7733 | 1160495.9907
7 | 2572713.3703 | 1159929.6518
8 | 2572760.2139 | 1159905.8821
9 | 2572543.4592 | 1159805.272
10 | 2572542.6001 | 1159729.1191
11 | 2572600.8073 | 1159763.937
12 | 2572701.1365 | 1159750.1947
13 | 2572628.5428 | 1159808.2358
14 | 2572805.6739 | 1160048.9366
15 | 2572826.1679 | 1159961.333
16 | 2572846.8004 | 1159988.9567
17 | 2572633.3637 | 1159811.8923
18 | 2573614.7559 | 1159950.6225
19 | 2573616.7853 | 1159956.4596
20 | 2573589.8281 | 1159782.1887
21 | 2573333.355 | 1160086.5201
22 | 2573333.9071 | 1160109.5585
23 | 2573334.2473 | 1160105.7673
24 | 2572635.9591 | 1159813.8609
25 | 2572655.0504 | 1159828.3412
26 | 2572657.6468 | 1159830.3105
27 | 2572672.0333 | 1159841.2223
28 | 2572684.0946 | 1159850.3706
29 | 2572810.1797 | 1159937.0086
30 | 2572799.0336 | 1159929.6316
31 | 2572820.2365 | 1159943.6648
32 | 2572768.6389 | 1159887.3386
33 | 2572744.3072 | 1159895.0961
34 | 2572850.2191 | 1159938.1234
35 | 2572775.3481 | 1159864.6322
36 | 2572732.5616 | 1159887.1317
37 | 2572851.7852 | 1159914.1946
38 | 2572685.156 | 1159909.1622
39 | 2572780.2727 | 1159825.4061
40 | 2572740.5754 | 1159854.5781
41 | 2572710.3236 | 1159870.2647
42 | 2572860.1499 | 1159978.3876
43 | 2572636.8466 | 1160598.6483
44 | 2572631.5206 | 1160591.8773
45 | 2573305.9784 | 1160007.6822
46 | 2573278.6065 | 1159934.9306
47 | 2573270.2704 | 1159912.7312
48 | 2573261.7992 | 1159890.1719
49 | 2573024.2049 | 1159682.9542
50 | 2572974.5932 | 1159747.9173
51 | 2572955.5085 | 1159771.5789
52 | 2572690.6334 | 1159855.3301
53 | 2572935.2451 | 1159932.7614
54 | 2572940.0354 | 1159958.1955
55 | 2572932.1233 | 1159916.1865
56 | 2572907.9694 | 1159974.4138
57 | 2572899.6044 | 1159938.51
58 | 2572884.8122 | 1159911.5345
59 | 2572854.4426 | 1159862.6811
60 | 2572853.9036 | 1159842.6274
61 | 2572854.4394 | 1159885.111
62 | 2572853.282 | 1159819.4984
63 | 2572851.8243 | 1159892.1692
64 | 2572863.491 | 1159883.5359
65 | 2572852.573 | 1159793.1201
66 | 2572854.2567 | 1159897.229
67 | 2572866.1971 | 1159885.3912
68 | 2572858.7115 | 1159860.9843
69 | 2572852.455 | 1159788.7296
70 | 2572884.0533 | 1159874.6507
71 | 2572868.2651 | 1159893.5749
72 | 2572683.0189 | 1159907.6103
73 | 2572662.3037 | 1159892.5666
74 | 2572643.9199 | 1159879.2161
75 | 2572852.721 | 1159780.974
76 | 2572897.7897 | 1159787.3906
77 | 2572766.5034 | 1159815.785
78 | 2572759.0841 | 1159812.4513
79 | 2572946.171 | 1159783.1188
80 | 2572928.9852 | 1159796.6405
81 | 2572900.6266 | 1159789.6972
82 | 2572636.081 | 1159873.5234
83 | 2572625.2452 | 1159865.6543
84 | 2572760.2139 | 1159905.8821

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99477 | -0.10029 | 0.011916 | 0.0029865
1 | 0.99497 | -0.096469 | 0 | 0
2 | 0.99475 | -0.10065 | 0.010206 | 0.0025579
3 | 0.99609 | -0.074886 | 0 | 0
4 | 0.99592 | -0.078217 | 0 | 0
5 | 0.99578 | -0.080799 | 0.0045039 | 0.0011288
6 | 0.99501 | -0.095976 | 0 | 0
7 | 0.99568 | -0.082749 | 0.004929 | 0.0012353
8 | 0.99812 | -0.035722 | 0 | 0
9 | 0.99341 | -0.12672 | 0.0026197 | 0.00065656
10 | 0.99361 | -0.12286 | 0 | 0
11 | 0.99377 | -0.11971 | 0 | 0
12 | 0.9935 | -0.12491 | 0.0024606 | 0.00061669
13 | 0.99402 | -0.11487 | 0.0010626 | 0.00026632
14 | 0.98855 | -0.21903 | 0 | 0
15 | 0.98983 | -0.19421 | 0 | 0
16 | 0.98757 | -0.23814 | 0.0064253 | 0.0016103
17 | 0.99405 | -0.11421 | 0.0024228 | 0.00060721
18 | 0.97019 | -0.57832 | 0.00080777 | 0.00020245
19 | 0.9702 | -0.57811 | 0.0026567 | 0.00066584
20 | 0.97002 | -0.58158 | 0.0010324 | 0.00025875
21 | 0.97151 | -0.55212 | 0.00047393 | 0.00011878
22 | 0.97147 | -0.55286 | 0.00059972 | 0.0001503
23 | 0.97147 | -0.55282 | 0.0013442 | 0.00033688
24 | 0.99408 | -0.11372 | 0.0056859 | 0.001425
25 | 0.99439 | -0.1077 | 0.0022113 | 0.0005542
26 | 0.99444 | -0.10675 | 0.0021211 | 0.00053159
27 | 0.99474 | -0.10083 | 0.0021382 | 0.0005359
28 | 0.99503 | -0.095305 | 0.0029549 | 0.00074058
29 | 0.99239 | -0.14517 | 0.014894 | 0.0037327
30 | 0.99362 | -0.12157 | 0.00704 | 0.0017644
31 | 0.99144 | -0.16334 | 0.007096 | 0.0017784
32 | 1 | 0 | -0.22763 | -0.057402
33 | 0.99732 | -0.051203 | 0.0037039 | 0.00092828
34 | 0.98687 | -0.25118 | 0 | 0
35 | 0.9995 | -0.0096631 | 0.0012815 | 0.00032118
36 | 0.99677 | -0.061728 | 0 | 0
37 | 0.98542 | -0.27939 | 0.0023214 | 0.00058179
38 | 0.99522 | -0.091582 | 0.0023306 | 0.0005841
39 | 0.99871 | -0.024816 | 0.00088679 | 0.00022225
40 | 0.9965 | -0.066902 | 0.0087933 | 0.0022038
41 | 0.99592 | -0.078148 | 0.0018987 | 0.00047586
42 | 0.98746 | -0.24037 | 0.0065307 | 0.0016368
43 | 0.9948 | -0.099922 | 0.0009572 | 0.0002399
44 | 0.99481 | -0.099777 | 0.00086781 | 0.00021749
45 | 0.97205 | -0.54142 | 0.00069138 | 0.00017328
46 | 0.9726 | -0.53049 | 0 | 0
47 | 0.97277 | -0.52716 | 0.0029284 | 0.00073393
48 | 0.973 | -0.52247 | 0 | 0
49 | 0.9761 | -0.46136 | 0 | 0
50 | 0.97691 | -0.44557 | 0.0021405 | 0.00053646
51 | 0.97726 | -0.43852 | 0.0012693 | 0.00031813
52 | 0.99521 | -0.091883 | 0.0079152 | 0.0019837
53 | 0.98293 | -0.32783 | 0.00065319 | 0.00016371
54 | 0.98298 | -0.32686 | 0.00053539 | 0.00013418
55 | 0.98291 | -0.32825 | 0.0014079 | 0.00035285
56 | 0.98308 | -0.32478 | 0 | 0
57 | 0.98317 | -0.32305 | 0.0019766 | 0.00049538
58 | 0.9833 | -0.3205 | 0.0027776 | 0.00069614
59 | 0.98258 | -0.3346 | 0.0026452 | 0.00066294
60 | 0.98167 | -0.35228 | 0.0031753 | 0.0007958
61 | 0.98365 | -0.31379 | 0 | 0
62 | 0.98069 | -0.37138 | 0.007835 | 0.0019636
63 | 0.98409 | -0.30514 | 0.00097548 | 0.00024448
64 | 0.98356 | -0.31556 | 0 | 0
65 | 0.97977 | -0.38947 | 0.0039479 | 0.00098945
66 | 0.98442 | -0.29871 | 0 | 0
67 | 0.98353 | -0.31605 | 0 | 0
68 | 0.98351 | -0.31639 | 0.0019698 | 0.00049369
69 | 0.97963 | -0.39216 | 0.0034075 | 0.000854
70 | 0.98351 | -0.31641 | 0.0009088 | 0.00022777
71 | 0.98347 | -0.31722 | 0 | 0
72 | 0.9952 | -0.092143 | 0.0019545 | 0.00048984
73 | 0.99496 | -0.096702 | 0.0030552 | 0.00076571
74 | 0.99481 | -0.099527 | 0.0021415 | 0.00053672
75 | 0.97961 | -0.39248 | 0.002266 | 0.00056792
76 | 0.97844 | -0.41538 | 0.0018385 | 0.00046077
77 | 0.99838 | -0.031124 | 0.010175 | 0.0025502
78 | 0.9983 | -0.032673 | 0.010887 | 0.0027287
79 | 0.97746 | -0.43473 | 0.0022598 | 0.00056636
80 | 0.97779 | -0.4282 | 0.0035229 | 0.00088293
81 | 0.97835 | -0.41713 | 0.006545 | 0.0016403
82 | 0.99477 | -0.10037 | 0.0022599 | 0.00056639
83 | 0.99474 | -0.10099 | 0.0026577 | 0.00066608
84 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.011916 | -0.0029865 | 0.011918 | 0.0029876 | 2.17e-06 | 1.1523e-06 | 0.017825 | 0.017825 | 0.017825 | 0.99477 | -0.10029 | 0.99497 | -0.096469 | 4.8969
1 | 0.010208 | 0.0025589 | -0.010206 | -0.0025579 | 2.0338e-06 | 9.9948e-07 | 0.015267 | 0.015267 | 0.015267 | 0.99497 | -0.096469 | 0.99475 | -0.10065 | 4.1942
2 | -0.022127 | -0.0055465 | 0.022149 | 0.0055604 | 2.2778e-05 | 1.3857e-05 | 0.033092 | 0.033091 | 0.033092 | 0.99497 | -0.096469 | 0.99609 | -0.074886 | 9.0911
3 | 0.019345 | 0.0048534 | -0.019338 | -0.004849 | 7.2491e-06 | 4.3383e-06 | 0.028901 | 0.028901 | 0.028901 | 0.99609 | -0.074886 | 0.99568 | -0.082749 | 7.9399
4 | -0.047827 | -0.011993 | 0.047917 | 0.012049 | 8.9447e-05 | 5.6636e-05 | 0.071449 | 0.071449 | 0.071449 | 0.99609 | -0.074886 | 0.99812 | -0.035722 | 19.6289
5 | 0.0063324 | 0.0015788 | -0.0063314 | -0.0015785 | 1.0008e-06 | 2.5212e-07 | 0.0094568 | 0.0094569 | 0.0094569 | 0.99609 | -0.074886 | 0.99592 | -0.078217 | 2.598
6 | 0.0045045 | 0.0011287 | -0.0045039 | -0.0011288 | 5.5404e-07 | -6.9789e-08 | 0.0067302 | 0.0067303 | 0.0067303 | 0.99592 | -0.078217 | 0.99578 | -0.080799 | 1.849
7 | 0.0018269 | 0.0004498 | -0.0018253 | -0.00045596 | 1.5327e-06 | -6.159e-06 | 0.0027267 | 0.0027292 | 0.0027292 | 0.99592 | -0.078217 | 0.99501 | -0.095976 | 0.74979
8 | 0.0018253 | 0.00045596 | -0.001825 | -0.00045728 | 3.301e-07 | -1.3231e-06 | 0.0027292 | 0.0027298 | 0.0027298 | 0.99501 | -0.095976 | 0.99481 | -0.099777 | 0.74994
9 | 0.014409 | 0.0036137 | -0.014403 | -0.0036103 | 6.0641e-06 | 3.4277e-06 | 0.021535 | 0.021535 | 0.021535 | 0.99568 | -0.082749 | 0.99522 | -0.091582 | 5.9163
10 | -0.20237 | -0.051337 | 0.20272 | 0.05156 | 0.00034827 | 0.00022236 | 0.30192 | 0.30192 | 0.30192 | 0.99812 | -0.035722 | 1 | 0 | 41.4721
11 | 0.046115 | 0.0116 | -0.046081 | -0.011579 | 3.4079e-05 | 2.1559e-05 | 0.068764 | 0.068764 | 0.068764 | 0.99812 | -0.035722 | 0.99732 | -0.051203 | 18.8913
12 | 0.10834 | 0.027688 | -0.10789 | -0.027402 | 0.00044778 | 0.00028599 | 0.1617 | 0.1617 | 0.1617 | 0.99812 | -0.035722 | 0.99362 | -0.12157 | 44.4243
13 | -0.0026197 | -0.00065656 | 0.0026202 | 0.00065579 | 4.8138e-07 | -7.7159e-07 | 0.003924 | 0.0039236 | 0.003924 | 0.99341 | -0.12672 | 0.99361 | -0.12286 | 1.078
14 | -0.0026202 | -0.00065579 | 0.0026206 | 0.00065516 | 3.923e-07 | -6.2928e-07 | 0.0039236 | 0.0039233 | 0.0039236 | 0.99361 | -0.12286 | 0.99377 | -0.11971 | 1.0779
15 | 0.0024612 | 0.00061553 | -0.0024606 | -0.00061669 | 6.0887e-07 | -1.159e-06 | 0.0036848 | 0.0036854 | 0.0036854 | 0.99377 | -0.11971 | 0.9935 | -0.12491 | 1.0125
16 | -0.0050818 | -0.0012707 | 0.005083 | 0.0012707 | 1.1702e-06 | 5.0256e-08 | 0.0076082 | 0.0076079 | 0.0076082 | 0.99377 | -0.11971 | 0.99402 | -0.11487 | 2.0902
17 | -0.0061456 | -0.0015371 | 0.0061458 | 0.0015371 | 1.9199e-07 | 4.4438e-08 | 0.0091987 | 0.0091986 | 0.0091987 | 0.99402 | -0.11487 | 0.99405 | -0.11421 | 2.5271
18 | -0.012969 | -0.0032538 | 0.012984 | 0.0032622 | 1.5366e-05 | 8.4538e-06 | 0.019522 | 0.019522 | 0.019522 | 0.98855 | -0.21903 | 0.98983 | -0.19421 | 5.3632
19 | 0.012969 | 0.0032538 | -0.012957 | -0.0032473 | 1.1805e-05 | 6.4975e-06 | 0.019522 | 0.019523 | 0.019523 | 0.98855 | -0.21903 | 0.98757 | -0.23814 | 5.3633
20 | 0.065572 | 0.016669 | -0.065392 | -0.016554 | 0.00017939 | 0.00011418 | 0.098658 | 0.098658 | 0.098658 | 0.98983 | -0.19421 | 0.98687 | -0.25118 | 27.1039
21 | -0.078556 | -0.019931 | 0.078673 | 0.020005 | 0.0001168 | 7.4466e-05 | 0.11818 | 0.11818 | 0.11818 | 0.98983 | -0.19421 | 0.99144 | -0.16334 | 32.4669
22 | 0.0065314 | 0.001637 | -0.0065307 | -0.0016368 | 6.9537e-07 | 2.0009e-07 | 0.0098412 | 0.0098413 | 0.0098413 | 0.98757 | -0.23814 | 0.98746 | -0.24037 | 2.7037
23 | -0.0085686 | -0.0021443 | 0.0085688 | 0.0021444 | 2.0094e-07 | 8.637e-08 | 0.012825 | 0.012825 | 0.012825 | 0.99405 | -0.11421 | 0.99408 | -0.11372 | 3.5235
24 | -0.0018403 | -0.00045919 | 0.0018404 | 0.00045913 | 1.8462e-08 | -6.4533e-08 | 0.0028219 | 0.0028219 | 0.0028219 | 0.97019 | -0.57832 | 0.9702 | -0.57811 | 0.77524
25 | 0.0010326 | 0.00025675 | -0.0010324 | -0.00025875 | 1.6007e-07 | -1.9998e-06 | 0.001583 | 0.0015837 | 0.0015837 | 0.97019 | -0.57832 | 0.97002 | -0.58158 | 0.43509
26 | -0.0044971 | -0.001125 | 0.0045027 | 0.0011247 | 5.561e-06 | -2.9715e-07 | 0.0068966 | 0.0068952 | 0.0068966 | 0.9702 | -0.57811 | 0.97151 | -0.55212 | 1.8947
27 | 0.001944 | 0.00048694 | -0.0019439 | -0.00048714 | 6.4758e-08 | -1.9975e-07 | 0.0029774 | 0.0029775 | 0.0029775 | 0.97151 | -0.55212 | 0.97147 | -0.55282 | 0.81798
28 | -0.0069205 | -0.0017304 | 0.0069241 | 0.0017316 | 3.5214e-06 | 1.218e-06 | 0.010598 | 0.010598 | 0.010598 | 0.97151 | -0.55212 | 0.97205 | -0.54142 | 2.9117
29 | -0.00059972 | -0.0001503 | 0.00059972 | 0.00015026 | 1.2045e-09 | -4.6359e-08 | 0.00091861 | 0.00091859 | 0.00091861 | 0.97147 | -0.55286 | 0.97147 | -0.55282 | 0.25236
30 | -0.014255 | -0.0035694 | 0.014259 | 0.0035717 | 4.0906e-06 | 2.3072e-06 | 0.021336 | 0.021336 | 0.021336 | 0.99408 | -0.11372 | 0.99439 | -0.1077 | 5.8617
31 | -0.01647 | -0.0041259 | 0.016471 | 0.0041264 | 7.4227e-07 | 4.3277e-07 | 0.024645 | 0.024645 | 0.024645 | 0.99439 | -0.1077 | 0.99444 | -0.10675 | 6.7707
32 | -0.018592 | -0.0046579 | 0.018597 | 0.0046611 | 5.2402e-06 | 3.1194e-06 | 0.027819 | 0.027819 | 0.027819 | 0.99444 | -0.10675 | 0.99474 | -0.10083 | 7.6426
33 | -0.020735 | -0.005197 | 0.020741 | 0.0052003 | 5.4616e-06 | 3.2989e-06 | 0.031018 | 0.031018 | 0.031018 | 0.99474 | -0.10083 | 0.99503 | -0.095305 | 8.5213
34 | -0.023696 | -0.0059408 | 0.0237 | 0.0059432 | 3.8647e-06 | 2.3668e-06 | 0.035437 | 0.035436 | 0.035437 | 0.99503 | -0.095305 | 0.99521 | -0.091883 | 9.7353
35 | -0.10074 | -0.025564 | 0.10085 | 0.025637 | 0.00011453 | 7.3127e-05 | 0.15116 | 0.15116 | 0.15116 | 0.99239 | -0.14517 | 0.99362 | -0.12157 | 41.5279
36 | 0.085844 | 0.021832 | -0.085769 | -0.021784 | 7.5061e-05 | 4.7883e-05 | 0.12883 | 0.12883 | 0.12883 | 0.99239 | -0.14517 | 0.99144 | -0.16334 | 35.3928
37 | 0.023265 | 0.0058427 | -0.023254 | -0.0058362 | 1.0721e-05 | 6.549e-06 | 0.034623 | 0.034623 | 0.034623 | 1 | 0 | 0.9995 | -0.0096631 | 9.5118
38 | 0.042377 | 0.01065 | -0.042356 | -0.010637 | 2.1282e-05 | 1.3435e-05 | 0.063238 | 0.063238 | 0.063238 | 0.99732 | -0.051203 | 0.99677 | -0.061728 | 17.3731
39 | 0.065392 | 0.016554 | -0.065304 | -0.016498 | 8.8425e-05 | 5.6283e-05 | 0.098658 | 0.098658 | 0.098658 | 0.98687 | -0.25118 | 0.98542 | -0.27939 | 27.1039
40 | 0.021973 | 0.005515 | -0.021957 | -0.0055054 | 1.5867e-05 | 9.6373e-06 | 0.032715 | 0.032715 | 0.032715 | 0.9995 | -0.0096631 | 0.99871 | -0.024816 | 8.9877
41 | 0.0087955 | 0.0022048 | -0.0087933 | -0.0022038 | 2.1675e-06 | 9.5033e-07 | 0.01313 | 0.01313 | 0.01313 | 0.99677 | -0.061728 | 0.9965 | -0.066902 | 3.6073
42 | 0.033561 | 0.0084322 | -0.033534 | -0.0084157 | 2.628e-05 | 1.6455e-05 | 0.050108 | 0.050108 | 0.050108 | 0.99677 | -0.061728 | 0.99592 | -0.078148 | 13.7659
43 | 0.062983 | 0.015916 | -0.062924 | -0.015879 | 5.8293e-05 | 3.7089e-05 | 0.095153 | 0.095153 | 0.095153 | 0.98542 | -0.27939 | 0.98442 | -0.29871 | 26.141
44 | 0.012073 | 0.0030262 | -0.012072 | -0.003026 | 3.2271e-07 | 1.7221e-07 | 0.018051 | 0.018051 | 0.018051 | 0.99522 | -0.091582 | 0.9952 | -0.092143 | 4.959
45 | 0.02107 | 0.0052831 | -0.021064 | -0.0052793 | 6.3321e-06 | 3.8284e-06 | 0.031394 | 0.031394 | 0.031394 | 0.99871 | -0.024816 | 0.99838 | -0.031124 | 8.6247
46 | 0.031636 | 0.0079399 | -0.031615 | -0.007927 | 2.0709e-05 | 1.2932e-05 | 0.047271 | 0.047271 | 0.047271 | 0.99592 | -0.078148 | 0.99521 | -0.091883 | 12.9866
47 | -0.0009572 | -0.0002399 | 0.0009572 | 0.00023979 | 6.6222e-09 | -1.0761e-07 | 0.0014318 | 0.0014317 | 0.0014318 | 0.9948 | -0.099922 | 0.99481 | -0.099777 | 0.39334
48 | -0.0076154 | -0.0019049 | 0.0076194 | 0.0019065 | 3.9604e-06 | 1.5706e-06 | 0.011656 | 0.011656 | 0.011656 | 0.97205 | -0.54142 | 0.9726 | -0.53049 | 3.2023
49 | -0.0076194 | -0.0019065 | 0.0076206 | 0.0019069 | 1.2081e-06 | 4.7888e-07 | 0.011656 | 0.011656 | 0.011656 | 0.9726 | -0.53049 | 0.97277 | -0.52716 | 3.2022
50 | -0.010549 | -0.0026409 | 0.010551 | 0.0026421 | 2.3527e-06 | 1.2065e-06 | 0.016136 | 0.016135 | 0.016136 | 0.97277 | -0.52716 | 0.973 | -0.52247 | 4.4328
51 | -0.010551 | -0.0026421 | 0.010582 | 0.0026578 | 3.0777e-05 | 1.5769e-05 | 0.016135 | 0.016134 | 0.016135 | 0.973 | -0.52247 | 0.9761 | -0.46136 | 4.4328
52 | -0.010582 | -0.0026578 | 0.01059 | 0.0026619 | 7.9789e-06 | 4.0839e-06 | 0.016134 | 0.016134 | 0.016134 | 0.9761 | -0.46136 | 0.97691 | -0.44557 | 4.4324
53 | -0.012731 | -0.0031984 | 0.012735 | 0.0032007 | 4.2878e-06 | 2.3634e-06 | 0.019394 | 0.019394 | 0.019394 | 0.97691 | -0.44557 | 0.97726 | -0.43852 | 5.328
54 | -0.014004 | -0.0035189 | 0.014007 | 0.0035203 | 2.5319e-06 | 1.4344e-06 | 0.021327 | 0.021327 | 0.021327 | 0.97726 | -0.43852 | 0.97746 | -0.43473 | 5.859
55 | -0.0020611 | -0.00051636 | 0.0020612 | 0.0005161 | 9.4484e-08 | -2.676e-07 | 0.0031202 | 0.0031201 | 0.0031202 | 0.98293 | -0.32783 | 0.98298 | -0.32686 | 0.85719
56 | 0.0014079 | 0.00035266 | -0.0014079 | -0.00035285 | 2.8732e-08 | -1.9539e-07 | 0.0021313 | 0.0021314 | 0.0021314 | 0.98293 | -0.32783 | 0.98291 | -0.32825 | 0.58555
57 | -0.0025966 | -0.00065028 | 0.0025969 | 0.00064988 | 2.5729e-07 | -3.984e-07 | 0.0039305 | 0.0039303 | 0.0039305 | 0.98298 | -0.32686 | 0.98308 | -0.32478 | 1.0798
58 | -0.0025969 | -0.00064988 | 0.0025971 | 0.00064955 | 2.1392e-07 | -3.3138e-07 | 0.0039303 | 0.0039302 | 0.0039303 | 0.98308 | -0.32478 | 0.98317 | -0.32305 | 1.0798
59 | -0.0045737 | -0.0011449 | 0.0045742 | 0.0011449 | 5.5577e-07 | -3.666e-08 | 0.0069217 | 0.0069215 | 0.0069217 | 0.98317 | -0.32305 | 0.9833 | -0.3205 | 1.9016
60 | -0.0073519 | -0.001841 | 0.007353 | 0.0018415 | 1.1476e-06 | 4.2076e-07 | 0.011125 | 0.011125 | 0.011125 | 0.9833 | -0.3205 | 0.98347 | -0.31722 | 3.0563
61 | 0.048974 | 0.012348 | -0.048933 | -0.012321 | 4.141e-05 | 2.6249e-05 | 0.074193 | 0.074193 | 0.074193 | 0.98258 | -0.3346 | 0.98167 | -0.35228 | 20.3826
62 | -0.051619 | -0.01301 | 0.051671 | 0.013043 | 5.145e-05 | 3.2643e-05 | 0.078199 | 0.078198 | 0.078199 | 0.98258 | -0.3346 | 0.98365 | -0.31379 | 21.4831
63 | 0.045757 | 0.011525 | -0.045716 | -0.011499 | 4.1765e-05 | 2.6437e-05 | 0.06938 | 0.06938 | 0.06938 | 0.98167 | -0.35228 | 0.98069 | -0.37138 | 19.0604
64 | -0.061904 | -0.015606 | 0.061929 | 0.015622 | 2.5612e-05 | 1.6293e-05 | 0.093678 | 0.093678 | 0.093678 | 0.98365 | -0.31379 | 0.98409 | -0.30514 | 25.7358
65 | 0.010233 | 0.0025631 | -0.010232 | -0.0025626 | 8.6552e-07 | 4.3168e-07 | 0.01548 | 0.01548 | 0.01548 | 0.98365 | -0.31379 | 0.98356 | -0.31556 | 4.2527
66 | 0.037881 | 0.0095354 | -0.037848 | -0.0095148 | 3.2707e-05 | 2.06e-05 | 0.057492 | 0.057492 | 0.057492 | 0.98069 | -0.37138 | 0.97977 | -0.38947 | 15.7945
67 | -0.062905 | -0.015867 | 0.062924 | 0.015879 | 1.9375e-05 | 1.2328e-05 | 0.095153 | 0.095153 | 0.095153 | 0.98409 | -0.30514 | 0.98442 | -0.29871 | 26.141
68 | 0.0082624 | 0.0020692 | -0.0082622 | -0.0020691 | 1.9282e-07 | 8.1639e-08 | 0.0125 | 0.0125 | 0.0125 | 0.98356 | -0.31556 | 0.98353 | -0.31605 | 3.434
69 | 0.0019699 | 0.00049344 | -0.0019698 | -0.00049369 | 7.7293e-08 | -2.4504e-07 | 0.0029802 | 0.0029803 | 0.0029803 | 0.98356 | -0.31556 | 0.98351 | -0.31639 | 0.81876
70 | 0.0339 | 0.0085254 | -0.033896 | -0.0085226 | 4.3677e-06 | 2.74e-06 | 0.051496 | 0.051496 | 0.051496 | 0.97977 | -0.38947 | 0.97963 | -0.39216 | 14.1472
71 | 0.00090881 | 0.0002275 | -0.0009088 | -0.00022777 | 1.549e-08 | -2.6739e-07 | 0.0013749 | 0.001375 | 0.001375 | 0.98353 | -0.31605 | 0.98351 | -0.31641 | 0.37774
72 | 0.0073534 | 0.0018416 | -0.007353 | -0.0018415 | 4.085e-07 | 1.4974e-07 | 0.011125 | 0.011125 | 0.011125 | 0.98353 | -0.31605 | 0.98347 | -0.31722 | 3.0563
73 | 0.0022661 | 0.00056784 | -0.002266 | -0.00056792 | 3.4488e-08 | -7.5659e-08 | 0.003442 | 0.0034421 | 0.0034421 | 0.97963 | -0.39216 | 0.97961 | -0.39248 | 0.94562
74 | 0.028222 | 0.0071008 | -0.028191 | -0.0070814 | 3.127e-05 | 1.9442e-05 | 0.042878 | 0.042878 | 0.042878 | 0.97963 | -0.39216 | 0.97844 | -0.41538 | 11.7798
75 | 0.010118 | 0.0025362 | -0.010116 | -0.0025351 | 2.1972e-06 | 1.0737e-06 | 0.015128 | 0.015128 | 0.015128 | 0.9952 | -0.092143 | 0.99496 | -0.096702 | 4.1562
76 | 0.0070604 | 0.0017694 | -0.0070594 | -0.0017691 | 9.4996e-07 | 3.1294e-07 | 0.010559 | 0.010559 | 0.010559 | 0.99496 | -0.096702 | 0.99481 | -0.099527 | 2.9009
77 | 0.0049179 | 0.0012323 | -0.0049177 | -0.0012323 | 1.9658e-07 | 3.5327e-11 | 0.007356 | 0.007356 | 0.007356 | 0.99481 | -0.099527 | 0.99477 | -0.10037 | 2.0209
78 | 0.026352 | 0.0066206 | -0.02635 | -0.0066192 | 2.2028e-06 | 1.3639e-06 | 0.040082 | 0.040082 | 0.040082 | 0.97844 | -0.41538 | 0.97835 | -0.41713 | 11.0116
79 | 0.010888 | 0.0027291 | -0.010887 | -0.0027287 | 8.0329e-07 | 4.0775e-07 | 0.016228 | 0.016228 | 0.016228 | 0.99838 | -0.031124 | 0.9983 | -0.032673 | 4.4583
80 | -0.016267 | -0.0040867 | 0.016272 | 0.0040896 | 5.0753e-06 | 2.9716e-06 | 0.024767 | 0.024767 | 0.024767 | 0.97746 | -0.43473 | 0.97779 | -0.4282 | 6.804
81 | -0.019795 | -0.0049726 | 0.019805 | 0.0049789 | 1.046e-05 | 6.3085e-06 | 0.030128 | 0.030128 | 0.030128 | 0.97779 | -0.4282 | 0.97835 | -0.41713 | 8.2769
82 | 0.0026578 | 0.00066596 | -0.0026577 | -0.00066608 | 7.9371e-08 | -1.2305e-07 | 0.0039755 | 0.0039756 | 0.0039756 | 0.99477 | -0.10037 | 0.99474 | -0.10099 | 1.0922

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.23361 | 0.0589

## res_load
| p_mw | q_mvar
0 | 0.011916 | 0.0029865
1 | 0.010206 | 0.0025579
2 | 0.0045039 | 0.0011288
3 | 0.004929 | 0.0012353
4 | 0.0026197 | 0.00065656
5 | 0.0024606 | 0.00061669
6 | 0.0010626 | 0.00026632
7 | 0.0064253 | 0.0016103
8 | 0.0024228 | 0.00060721
9 | 0.00080777 | 0.00020245
10 | 0.0026567 | 0.00066584
11 | 0.0010324 | 0.00025875
12 | 0.00047393 | 0.00011878
13 | 0.00059972 | 0.0001503
14 | 0.0013442 | 0.00033688
15 | 0.0056859 | 0.001425
16 | 0.0022113 | 0.0005542
17 | 0.0021211 | 0.00053159
18 | 0.0021382 | 0.0005359
19 | 0.0029549 | 0.00074058
20 | 0.014894 | 0.0037327
21 | 0.00704 | 0.0017644
22 | 0.007096 | 0.0017784
23 | 0.0059738 | 0.0014972
24 | 0.0037039 | 0.00092828
25 | 0.0012815 | 0.00032118
26 | 0.0023214 | 0.00058179
27 | 0.0023306 | 0.0005841
28 | 0.00088679 | 0.00022225
29 | 0.0087933 | 0.0022038
30 | 0.0018987 | 0.00047586
31 | 0.0065307 | 0.0016368
32 | 0.0009572 | 0.0002399
33 | 0.00086781 | 0.00021749
34 | 0.00069138 | 0.00017328
35 | 0.0029284 | 0.00073393
36 | 0.0021405 | 0.00053646
37 | 0.0012693 | 0.00031813
38 | 0.0079152 | 0.0019837
39 | 0.00065319 | 0.00016371
40 | 0.00053539 | 0.00013418
41 | 0.0014079 | 0.00035285
42 | 0.0019766 | 0.00049538
43 | 0.0027776 | 0.00069614
44 | 0.0026452 | 0.00066294
45 | 0.0031753 | 0.0007958
46 | 0.007835 | 0.0019636
47 | 0.00097548 | 0.00024448
48 | 0.0039479 | 0.00098945
49 | 0.0019698 | 0.00049369
50 | 0.0034075 | 0.000854
51 | 0.0009088 | 0.00022777
52 | 0.0019545 | 0.00048984
53 | 0.0030552 | 0.00076571
54 | 0.0021415 | 0.00053672
55 | 0.002266 | 0.00056792
56 | 0.0018385 | 0.00046077
57 | 0.010175 | 0.0025502
58 | 0.010887 | 0.0027287
59 | 0.0022598 | 0.00056636
60 | 0.0035229 | 0.00088293
61 | 0.006545 | 0.0016403
62 | 0.0022599 | 0.00056639
63 | 0.0026577 | 0.00066608

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1