## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2135-7_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2135-7_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2135-7_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2135-7_0_7_node_127 | 0.4 | n |  | TRUE
4 | bus_LV_2135-7_0_7_node_135 | 0.4 | n |  | TRUE
5 | bus_LV_2135-7_0_7_node_126 | 0.4 | n |  | TRUE
6 | bus_LV_2135-7_0_7_node_123 | 0.4 | n |  | TRUE
7 | bus_LV_2135-7_0_7_node_128 | 0.4 | n |  | TRUE
8 | bus_LV_2135-7_0_7_node_129 | 0.4 | n |  | TRUE
9 | bus_LV_2135-7_0_7_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_2135-7_0_7_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_2135-7_0_7_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2135-7_0_7_node_108 | 0.4 | n |  | TRUE
13 | bus_LV_2135-7_0_7_node_122 | 0.4 | n |  | TRUE
14 | bus_LV_2135-7_0_7_node_121 | 0.4 | n |  | TRUE
15 | bus_LV_2135-7_0_7_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2135-7_0_7_node_109 | 0.4 | n |  | TRUE
17 | bus_LV_2135-7_0_7_node_110 | 0.4 | n |  | TRUE
18 | bus_LV_2135-7_0_7_node_105 | 0.4 | n |  | TRUE
19 | bus_LV_2135-7_0_7_node_104 | 0.4 | n |  | TRUE
20 | bus_LV_2135-7_0_7_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_2135-7_0_7_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_2135-7_0_7_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2135-7_0_7_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2135-7_0_7_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2135-7_0_7_node_73 | 0.4 | n |  | TRUE
26 | bus_LV_2135-7_0_7_node_75 | 0.4 | n |  | TRUE
27 | bus_LV_2135-7_0_7_node_71 | 0.4 | n |  | TRUE
28 | bus_LV_2135-7_0_7_node_46 | 0.4 | n |  | TRUE
29 | bus_LV_2135-7_0_7_node_42 | 0.4 | n |  | TRUE
30 | bus_LV_2135-7_0_7_node_43 | 0.4 | n |  | TRUE
31 | bus_LV_2135-7_0_7_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_2135-7_0_7_node_13 | 0.4 | n |  | TRUE
33 | bus_LV_2135-7_0_7_node_14 | 0.4 | n |  | TRUE
34 | bus_LV_2135-7_0_7_node_15 | 0.4 | n |  | TRUE
35 | bus_LV_2135-7_0_7_node_16 | 0.4 | n |  | TRUE
36 | bus_LV_2135-7_0_7_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_2135-7_0_7_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_2135-7_0_7_node_69 | 0.4 | n |  | TRUE
39 | bus_LV_2135-7_0_7_node_74 | 0.4 | n |  | TRUE
40 | bus_LV_2135-7_0_7_node_67 | 0.4 | n |  | TRUE
41 | bus_LV_2135-7_0_7_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_2135-7_0_7_node_17 | 0.4 | n |  | TRUE
43 | bus_LV_2135-7_0_7_node_48 | 0.4 | n |  | TRUE
44 | bus_LV_2135-7_0_7_node_66 | 0.4 | n |  | TRUE
45 | bus_LV_2135-7_0_7_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_2135-7_0_7_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_2135-7_0_7_node_137 | 0.4 | n |  | TRUE
48 | bus_LV_2135-7_0_7_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_2135-7_0_7_node_27 | 0.4 | n |  | TRUE
50 | bus_LV_2135-7_0_7_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_2135-7_0_7_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_2135-7_0_7_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_2135-7_0_7_node_23 | 0.4 | n |  | TRUE
54 | bus_LV_2135-7_0_7_node_20 | 0.4 | n |  | TRUE
55 | bus_LV_2135-7_0_7_node_21 | 0.4 | n |  | TRUE
56 | bus_LV_2135-7_0_7_node_22 | 0.4 | n |  | TRUE
57 | bus_LV_2135-7_0_7_node_24 | 0.4 | n |  | TRUE
58 | bus_LV_2135-7_0_7_node_26 | 0.4 | n |  | TRUE
59 | bus_LV_2135-7_0_7_node_28 | 0.4 | n |  | TRUE
60 | bus_LV_2135-7_0_7_node_30 | 0.4 | n |  | TRUE
61 | bus_LV_2135-7_0_7_node_31 | 0.4 | n |  | TRUE
62 | bus_LV_2135-7_0_7_node_95 | 0.4 | n |  | TRUE
63 | bus_LV_2135-7_0_7_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_2135-7_0_7_node_93 | 0.4 | n |  | TRUE
65 | bus_LV_2135-7_0_7_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_2135-7_0_7_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_2135-7_0_7_node_33 | 0.4 | n |  | TRUE
68 | bus_LV_2135-7_0_7_node_51 | 0.4 | n |  | TRUE
69 | bus_LV_2135-7_0_7_node_37 | 0.4 | n |  | TRUE
70 | bus_LV_2135-7_0_7_node_38 | 0.4 | n |  | TRUE
71 | bus_LV_2135-7_0_7_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_2135-7_0_7_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_2135-7_0_7_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_2135-7_0_7_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_2135-7_0_7_node_49 | 0.4 | n |  | TRUE
76 | bus_LV_2135-7_0_7_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_2135-7_0_7_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_2135-7_0_7_node_44 | 0.4 | n |  | TRUE
79 | bus_LV_2135-7_0_7_node_45 | 0.4 | n |  | TRUE
80 | bus_LV_2135-7_0_7_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_2135-7_0_7_node_57 | 0.4 | n |  | TRUE
82 | bus_LV_2135-7_0_7_node_62 | 0.4 | n |  | TRUE
83 | bus_LV_2135-7_0_7_node_124 | 0.4 | n |  | TRUE
84 | bus_LV_2135-7_0_7_node_63 | 0.4 | n |  | TRUE
85 | bus_LV_2135-7_0_7_node_64 | 0.4 | n |  | TRUE
86 | bus_LV_2135-7_0_7_node_136 | 0.4 | n |  | TRUE
87 | bus_LV_2135-7_0_7_node_68 | 0.4 | n |  | TRUE
88 | bus_LV_2135-7_0_7_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_2135-7_0_7_node_106 | 0.4 | n |  | TRUE
90 | bus_LV_2135-7_0_7_node_107 | 0.4 | n |  | TRUE
91 | bus_LV_2135-7_0_7_node_83 | 0.4 | n |  | TRUE
92 | bus_LV_2135-7_0_7_node_77 | 0.4 | n |  | TRUE
93 | bus_LV_2135-7_0_7_node_78 | 0.4 | n |  | TRUE
94 | bus_LV_2135-7_0_7_node_92 | 0.4 | n |  | TRUE
95 | bus_LV_2135-7_0_7_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_2135-7_0_7_node_80 | 0.4 | n |  | TRUE
97 | bus_LV_2135-7_0_7_node_79 | 0.4 | n |  | TRUE
98 | bus_LV_2135-7_0_7_node_81 | 0.4 | n |  | TRUE
99 | bus_LV_2135-7_0_7_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_2135-7_0_7_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_2135-7_0_7_node_85 | 0.4 | n |  | TRUE
102 | bus_LV_2135-7_0_7_node_84 | 0.4 | n |  | TRUE
103 | bus_LV_2135-7_0_7_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_2135-7_0_7_node_114 | 0.4 | n |  | TRUE
105 | bus_LV_2135-7_0_7_node_117 | 0.4 | n |  | TRUE
106 | bus_LV_2135-7_0_7_node_113 | 0.4 | n |  | TRUE
107 | bus_LV_2135-7_0_7_node_88 | 0.4 | n |  | TRUE
108 | bus_LV_2135-7_0_7_node_89 | 0.4 | n |  | TRUE
109 | bus_LV_2135-7_0_7_node_90 | 0.4 | n |  | TRUE
110 | bus_LV_2135-7_0_7_node_98 | 0.4 | n |  | TRUE
111 | bus_LV_2135-7_0_7_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_2135-7_0_7_node_119 | 0.4 | n |  | TRUE
113 | bus_LV_2135-7_0_7_node_115 | 0.4 | n |  | TRUE
114 | bus_LV_2135-7_0_7_node_94 | 0.4 | n |  | TRUE
115 | bus_LV_2135-7_0_7_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_2135-7_0_7_node_99 | 0.4 | n |  | TRUE
117 | bus_LV_2135-7_0_7_node_100 | 0.4 | n |  | TRUE
118 | bus_LV_2135-7_0_7_node_133 | 0.4 | n |  | TRUE
119 | bus_LV_2135-7_0_7_node_132 | 0.4 | n |  | TRUE
120 | bus_LV_2135-7_0_7_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_2135-7_0_7_node_102 | 0.4 | n |  | TRUE
122 | bus_LV_2135-7_0_7_node_103 | 0.4 | n |  | TRUE
123 | bus_LV_2135-7_0_7_node_134 | 0.4 | n |  | TRUE
124 | bus_LV_2135-7_0_7_node_111 | 0.4 | n |  | TRUE
125 | bus_LV_2135-7_0_7_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_2135-7_0_7_node_120 | 0.4 | n |  | TRUE
127 | bus_LV_2135-7_0_7_node_116 | 0.4 | n |  | TRUE
128 | bus_LV_2135-7_0_7_node_118 | 0.4 | n |  | TRUE
129 | bus_LV_2135-7_0_7_node_125 | 0.4 | n |  | TRUE
130 | bus_LV_2135-7_0_7_node_130 | 0.4 | n |  | TRUE
131 | bus_LV_2135-7_0_7_node_131 | 0.4 | n |  | TRUE
132 | bus_MV_30_0_node_143 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2135-7_0_7_load_0 | 0 | 0.00060153 | 0.00015076 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2135-7_0_7_load_2 | 2 | 0.0011158 | 0.00027965 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2135-7_0_7_load_127 | 3 | 0.0036248 | 0.00090847 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2135-7_0_7_load_126 | 5 | 0.00282 | 0.00070676 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2135-7_0_7_load_123 | 6 | 0.0010271 | 0.00025742 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2135-7_0_7_load_128 | 7 | 0.0021226 | 0.00053197 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2135-7_0_7_load_3 | 9 | 0.0011754 | 0.00029458 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2135-7_0_7_load_6 | 11 | 0.0013164 | 0.00032993 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2135-7_0_7_load_108 | 12 | 0.0012188 | 0.00030545 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2135-7_0_7_load_122 | 13 | 0.0026811 | 0.00067195 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2135-7_0_7_load_121 | 14 | 0.0032083 | 0.00080407 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2135-7_0_7_load_7 | 15 | 0.0040181 | 0.001007 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2135-7_0_7_load_109 | 16 | 0.0013925 | 0.000349 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2135-7_0_7_load_110 | 17 | 0.0018762 | 0.00047023 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2135-7_0_7_load_105 | 18 | 0.0059368 | 0.0014879 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2135-7_0_7_load_104 | 19 | 0.0034364 | 0.00086125 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2135-7_0_7_load_8 | 20 | 0.013424 | 0.0033644 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2135-7_0_7_load_9 | 21 | 0.0043504 | 0.0010903 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2135-7_0_7_load_11 | 23 | 0.010138 | 0.0025408 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2135-7_0_7_load_12 | 24 | 0.0036343 | 0.00091083 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2135-7_0_7_load_75 | 26 | 0.0018358 | 0.00046009 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2135-7_0_7_load_71 | 27 | 0.0046323 | 0.001161 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2135-7_0_7_load_46 | 28 | 0.042118 | 0.010556 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2135-7_0_7_load_43 | 30 | 0.0029932 | 0.00075016 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2135-7_0_7_load_41 | 31 | 0.0061187 | 0.0015335 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2135-7_0_7_load_13 | 32 | 0.0031125 | 0.00078006 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2135-7_0_7_load_18 | 36 | 0.0017374 | 0.00043544 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2135-7_0_7_load_19 | 37 | 0.0020575 | 0.00051565 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2135-7_0_7_load_69 | 38 | 0.0026533 | 0.00066499 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2135-7_0_7_load_67 | 40 | 0.0028199 | 0.00070673 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2135-7_0_7_load_35 | 41 | 0.0017287 | 0.00043326 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2135-7_0_7_load_17 | 42 | 0.0030865 | 0.00077356 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2135-7_0_7_load_66 | 44 | 0.0033572 | 0.00084139 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2135-7_0_7_load_25 | 45 | 0.0011844 | 0.00029683 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2135-7_0_7_load_137 | 47 | 0.0023762 | 0.00059553 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2135-7_0_7_load_32 | 50 | 0.0024526 | 0.00061469 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2135-7_0_7_load_50 | 51 | 0.0012008 | 0.00030095 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2135-7_0_7_load_23 | 53 | 0.0032066 | 0.00080364 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2135-7_0_7_load_20 | 54 | 0.0017278 | 0.00043304 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2135-7_0_7_load_21 | 55 | 0.0037386 | 0.00093698 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2135-7_0_7_load_22 | 56 | 0.0025042 | 0.0006276 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2135-7_0_7_load_24 | 57 | 0.0024877 | 0.00062347 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2135-7_0_7_load_26 | 58 | 0.0010817 | 0.00027109 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2135-7_0_7_load_30 | 60 | 0.0025981 | 0.00065115 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2135-7_0_7_load_31 | 61 | 0.0017959 | 0.00045009 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2135-7_0_7_load_95 | 62 | 0.0059487 | 0.0014909 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2135-7_0_7_load_52 | 63 | 0.00072032 | 0.00018053 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2135-7_0_7_load_93 | 64 | 0.0023752 | 0.00059528 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2135-7_0_7_load_55 | 65 | 0.00098661 | 0.00024727 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2135-7_0_7_load_56 | 66 | 0.002389 | 0.00059873 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2135-7_0_7_load_33 | 67 | 0.003202 | 0.00080249 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2135-7_0_7_load_51 | 68 | 0.00091262 | 0.00022872 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2135-7_0_7_load_37 | 69 | 0.0020045 | 0.00050237 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2135-7_0_7_load_38 | 70 | 0.0043588 | 0.0010924 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2135-7_0_7_load_39 | 71 | 0.010276 | 0.0025754 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2135-7_0_7_load_40 | 72 | 0.0034647 | 0.00086832 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2135-7_0_7_load_61 | 74 | 0.0062072 | 0.0015557 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2135-7_0_7_load_59 | 76 | 0.001779 | 0.00044587 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2135-7_0_7_load_72 | 77 | 0.0038327 | 0.00096056 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2135-7_0_7_load_44 | 78 | 0.0012781 | 0.00032033 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2135-7_0_7_load_45 | 79 | 0.0011286 | 0.00028284 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2135-7_0_7_load_58 | 80 | 0.0013278 | 0.00033279 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2135-7_0_7_load_57 | 81 | 0.00088235 | 0.00022114 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2135-7_0_7_load_124 | 83 | 0.00066461 | 0.00016657 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2135-7_0_7_load_63 | 84 | 0.0068141 | 0.0017078 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2135-7_0_7_load_64 | 85 | 0.0027984 | 0.00070134 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2135-7_0_7_load_136 | 86 | 0.0024157 | 0.00060542 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2135-7_0_7_load_68 | 87 | 0.0018114 | 0.00045399 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2135-7_0_7_load_70 | 88 | 0.0024923 | 0.00062463 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2135-7_0_7_load_107 | 90 | 0.00093966 | 0.0002355 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2135-7_0_7_load_83 | 91 | 0.004032 | 0.0010105 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2135-7_0_7_load_77 | 92 | 0.0058287 | 0.0014608 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2135-7_0_7_load_92 | 94 | 0.0014551 | 0.00036467 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2135-7_0_7_load_80 | 96 | 0.0059369 | 0.0014879 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2135-7_0_7_load_79 | 97 | 0.0049959 | 0.0012521 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2135-7_0_7_load_81 | 98 | 0.0039204 | 0.00098255 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2135-7_0_7_load_82 | 99 | 0.0007646 | 0.00019163 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2135-7_0_7_load_84 | 102 | 0.011306 | 0.0028336 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2135-7_0_7_load_87 | 103 | 0.0031385 | 0.00078659 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2135-7_0_7_load_114 | 104 | 0.0035629 | 0.00089294 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2135-7_0_7_load_113 | 106 | 0.0009107 | 0.00022824 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2135-7_0_7_load_89 | 108 | 0.0052736 | 0.0013217 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2135-7_0_7_load_90 | 109 | 0.0032617 | 0.00081746 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2135-7_0_7_load_98 | 110 | 0.0027073 | 0.00067851 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2135-7_0_7_load_97 | 111 | 0.0046661 | 0.0011694 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2135-7_0_7_load_115 | 113 | 0.0042449 | 0.0010639 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2135-7_0_7_load_94 | 114 | 0.0016295 | 0.00040839 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2135-7_0_7_load_96 | 115 | 0.0019818 | 0.00049668 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2135-7_0_7_load_99 | 116 | 0.0012691 | 0.00031806 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2135-7_0_7_load_100 | 117 | 0.002271 | 0.00056916 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2135-7_0_7_load_133 | 118 | 0.001097 | 0.00027494 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2135-7_0_7_load_132 | 119 | 0.0014377 | 0.00036031 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2135-7_0_7_load_101 | 120 | 0.0023311 | 0.00058422 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2135-7_0_7_load_102 | 121 | 0.0042908 | 0.0010754 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2135-7_0_7_load_103 | 122 | 0.0026171 | 0.00065592 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2135-7_0_7_load_134 | 123 | 0.0034157 | 0.00085605 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2135-7_0_7_load_111 | 124 | 0.0031993 | 0.00080182 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2135-7_0_7_load_112 | 125 | 0.0016893 | 0.00042339 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2135-7_0_7_load_120 | 126 | 0.0028077 | 0.00070367 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2135-7_0_7_load_116 | 127 | 0.0035128 | 0.0008804 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2135-7_0_7_load_118 | 128 | 0.0021138 | 0.00052977 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2135-7_0_7_load_125 | 129 | 0.00086925 | 0.00021785 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2135-7_0_7_load_130 | 130 | 0.0016185 | 0.00040562 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2135-7_0_7_load_131 | 131 | 0.00078562 | 0.00019689 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 95 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2135-7_0_7_line_0 |  | 0 | 1 | 0.025793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2135-7_0_7_line_1 |  | 1 | 2 | 0.43872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2135-7_0_7_line_2 |  | 2 | 7 | 2.6678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2135-7_0_7_line_3 |  | 3 | 4 | 0.27096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2135-7_0_7_line_4 |  | 3 | 5 | 0.42818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2135-7_0_7_line_5 |  | 4 | 86 | 0.073658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2135-7_0_7_line_6 |  | 5 | 6 | 0.29643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2135-7_0_7_line_7 |  | 6 | 83 | 0.012752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2135-7_0_7_line_8 |  | 6 | 73 | 0.18192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2135-7_0_7_line_9 |  | 7 | 8 | 0.072278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2135-7_0_7_line_10 |  | 8 | 86 | 0.26394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2135-7_0_7_line_11 |  | 9 | 10 | 0.11272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2135-7_0_7_line_12 |  | 10 | 11 | 0.11446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2135-7_0_7_line_13 |  | 10 | 12 | 0.32762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2135-7_0_7_line_14 |  | 11 | 15 | 0.010772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2135-7_0_7_line_15 |  | 12 | 16 | 0.051582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2135-7_0_7_line_16 |  | 12 | 17 | 0.0095144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2135-7_0_7_line_17 |  | 13 | 14 | 0.01188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2135-7_0_7_line_18 |  | 14 | 126 | 0.023724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2135-7_0_7_line_19 |  | 16 | 124 | 0.027326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2135-7_0_7_line_20 |  | 17 | 125 | 0.026522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2135-7_0_7_line_21 |  | 18 | 19 | 0.025334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2135-7_0_7_line_22 |  | 19 | 108 | 0.051261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2135-7_0_7_line_23 |  | 20 | 21 | 0.011781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2135-7_0_7_line_24 |  | 20 | 22 | 0.093964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2135-7_0_7_line_25 |  | 21 | 23 | 0.01524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2135-7_0_7_line_26 |  | 22 | 24 | 0.039103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2135-7_0_7_line_27 |  | 23 | 29 | 0.030347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2135-7_0_7_line_28 |  | 25 | 26 | 0.015821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2135-7_0_7_line_29 |  | 25 | 27 | 0.015478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2135-7_0_7_line_30 |  | 25 | 28 | 0.065317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2135-7_0_7_line_31 |  | 26 | 92 | 0.016969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2135-7_0_7_line_32 |  | 27 | 77 | 0.036357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2135-7_0_7_line_33 |  | 28 | 78 | 0.015699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2135-7_0_7_line_34 |  | 29 | 30 | 0.059551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2135-7_0_7_line_35 |  | 29 | 31 | 0.045611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2135-7_0_7_line_36 |  | 30 | 75 | 0.044147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2135-7_0_7_line_37 |  | 31 | 71 | 0.0037249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_2135-7_0_7_line_38 |  | 32 | 33 | 0.020589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2135-7_0_7_line_39 |  | 32 | 34 | 0.013617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2135-7_0_7_line_40 |  | 33 | 35 | 0.012639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2135-7_0_7_line_41 |  | 34 | 36 | 0.013624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2135-7_0_7_line_42 |  | 34 | 37 | 0.0027997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2135-7_0_7_line_43 |  | 35 | 41 | 0.0036641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2135-7_0_7_line_44 |  | 37 | 45 | 0.013021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2135-7_0_7_line_45 |  | 38 | 39 | 0.039132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2135-7_0_7_line_46 |  | 38 | 40 | 0.035641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2135-7_0_7_line_47 |  | 39 | 77 | 0.020486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2135-7_0_7_line_48 |  | 40 | 44 | 0.00043166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2135-7_0_7_line_49 |  | 41 | 48 | 0.044169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2135-7_0_7_line_50 |  | 42 | 43 | 0.042335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2135-7_0_7_line_51 |  | 43 | 51 | 0.036296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2135-7_0_7_line_52 |  | 43 | 52 | 0.032838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2135-7_0_7_line_53 |  | 44 | 87 | 0.0011439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2135-7_0_7_line_54 |  | 45 | 53 | 0.011282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2135-7_0_7_line_55 |  | 46 | 47 | 0.043531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2135-7_0_7_line_56 |  | 46 | 48 | 0.040761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2135-7_0_7_line_57 |  | 46 | 49 | 0.054794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2135-7_0_7_line_58 |  | 48 | 50 | 0.031459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2135-7_0_7_line_59 |  | 49 | 58 | 0.020824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2135-7_0_7_line_60 |  | 50 | 67 | 0.012965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2135-7_0_7_line_61 |  | 51 | 57 | 0.01436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2135-7_0_7_line_62 |  | 52 | 75 | 0.007663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_2135-7_0_7_line_63 |  | 52 | 79 | 0.055261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_2135-7_0_7_line_64 |  | 53 | 55 | 0.0043655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2135-7_0_7_line_65 |  | 54 | 55 | 0.018936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2135-7_0_7_line_66 |  | 54 | 56 | 0.024757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2135-7_0_7_line_67 |  | 56 | 57 | 0.0060377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2135-7_0_7_line_68 |  | 58 | 59 | 0.016863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2135-7_0_7_line_69 |  | 59 | 60 | 0.017225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2135-7_0_7_line_70 |  | 59 | 61 | 0.016941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2135-7_0_7_line_71 |  | 60 | 65 | 0.016629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2135-7_0_7_line_72 |  | 62 | 63 | 0.10849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2135-7_0_7_line_73 |  | 62 | 64 | 0.039734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2135-7_0_7_line_74 |  | 63 | 68 | 0.0013674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2135-7_0_7_line_75 |  | 64 | 114 | 0.031855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2135-7_0_7_line_76 |  | 65 | 66 | 0.02445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2135-7_0_7_line_77 |  | 69 | 70 | 0.016218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_2135-7_0_7_line_78 |  | 69 | 71 | 0.019184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_2135-7_0_7_line_79 |  | 70 | 72 | 0.021808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_2135-7_0_7_line_80 |  | 72 | 73 | 0.12097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_2135-7_0_7_line_81 |  | 73 | 74 | 0.14315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2135-7_0_7_line_82 |  | 74 | 82 | 0.33436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2135-7_0_7_line_83 |  | 75 | 76 | 0.017336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2135-7_0_7_line_84 |  | 76 | 80 | 0.0033561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2135-7_0_7_line_85 |  | 78 | 79 | 0.012229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_2135-7_0_7_line_86 |  | 80 | 81 | 0.03204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2135-7_0_7_line_87 |  | 82 | 84 | 0.018513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2135-7_0_7_line_88 |  | 83 | 129 | 0.012657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2135-7_0_7_line_89 |  | 84 | 85 | 0.42956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2135-7_0_7_line_90 |  | 87 | 88 | 0.022733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2135-7_0_7_line_91 |  | 88 | 89 | 0.035808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2135-7_0_7_line_92 |  | 89 | 90 | 0.0052806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2135-7_0_7_line_93 |  | 89 | 91 | 0.025048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2135-7_0_7_line_94 |  | 90 | 115 | 0.013899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2135-7_0_7_line_95 |  | 91 | 99 | 0.001949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2135-7_0_7_line_96 |  | 92 | 93 | 0.020159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_2135-7_0_7_line_97 |  | 93 | 96 | 0.019611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2135-7_0_7_line_98 |  | 94 | 95 | 0.0072107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2135-7_0_7_line_99 |  | 95 | 100 | 0.021654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2135-7_0_7_line_100 |  | 95 | 101 | 0.11661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2135-7_0_7_line_101 |  | 95 | 96 | 0.035005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2135-7_0_7_line_102 |  | 97 | 98 | 0.027463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2135-7_0_7_line_103 |  | 98 | 99 | 0.048865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2135-7_0_7_line_104 |  | 100 | 105 | 0.032061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2135-7_0_7_line_105 |  | 101 | 103 | 0.0068264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2135-7_0_7_line_106 |  | 101 | 102 | 0.076411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2135-7_0_7_line_107 |  | 103 | 104 | 0.015398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2135-7_0_7_line_108 |  | 104 | 106 | 0.016472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2135-7_0_7_line_109 |  | 105 | 112 | 0.024565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2135-7_0_7_line_110 |  | 105 | 113 | 0.024383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2135-7_0_7_line_111 |  | 106 | 124 | 0.041855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2135-7_0_7_line_112 |  | 107 | 108 | 0.0085353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2135-7_0_7_line_113 |  | 107 | 109 | 0.025949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2135-7_0_7_line_114 |  | 109 | 110 | 0.02597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2135-7_0_7_line_115 |  | 110 | 111 | 0.013815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2135-7_0_7_line_116 |  | 111 | 116 | 0.012339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2135-7_0_7_line_117 |  | 112 | 123 | 0.016186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2135-7_0_7_line_118 |  | 112 | 122 | 0.0051511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2135-7_0_7_line_119 |  | 113 | 127 | 0.0055044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2135-7_0_7_line_120 |  | 114 | 115 | 0.0056461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2135-7_0_7_line_121 |  | 116 | 117 | 0.015606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2135-7_0_7_line_122 |  | 117 | 118 | 0.010592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2135-7_0_7_line_123 |  | 118 | 119 | 0.014291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2135-7_0_7_line_124 |  | 119 | 131 | 0.011306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2135-7_0_7_line_125 |  | 120 | 121 | 0.016632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2135-7_0_7_line_126 |  | 121 | 122 | 0.0099693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2135-7_0_7_line_127 |  | 125 | 126 | 0.0031722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2135-7_0_7_line_128 |  | 127 | 128 | 0.0036744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2135-7_0_7_line_129 |  | 129 | 130 | 0.0064778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2135-7_0_7_line_130 |  | 130 | 131 | 0.019242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2135-7_0_7_trafo_86 | 0.63 MVA 20/0.4 kV | 132 | 95 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2567922.9518 | 1160811.0312 | 2567897.7123 | 1160805.717
1 | 2567922.9518 | 1160811.0312 | 2568161.7825 | 1160443.0136
2 | 2569895.2954 | 1158415.2487 | 2568161.7825 | 1160443.0136
3 | 2570193.8672 | 1158519.5894 | 2570252.037 | 1158784.2291
4 | 2570643.3733 | 1158610.467 | 2570252.037 | 1158784.2291
5 | 2570173.8227 | 1158448.9756 | 2570181.744 | 1158488.0115 | 2570193.8672 | 1158519.5894
6 | 2570927.9403 | 1158693.4724 | 2570643.3733 | 1158610.467
7 | 2570927.9403 | 1158693.4724 | 2570936.6192 | 1158702.8159
8 | 2570927.9403 | 1158693.4724 | 2570947.8844 | 1158512.6531
9 | 2569920.0208 | 1158376.5397 | 2569884.5156 | 1158387.868 | 2569879.4781 | 1158395.2859 | 2569886.181 | 1158408.0921 | 2569895.2954 | 1158415.2487
10 | 2570173.8227 | 1158448.9756 | 2569920.0208 | 1158376.5397
11 | 2571201.1936 | 1159215.5302 | 2571246.3455 | 1159293.5306 | 2571261.0598 | 1159310.6752
12 | 2571201.1936 | 1159215.5302 | 2571191.4748 | 1159220.3571 | 2571173.9965 | 1159251.6902 | 2571163.2503 | 1159262.7919 | 2571150.9436 | 1159268.1649 | 2571136.6952 | 1159273.0026 | 2571126.7956 | 1159272.0942 | 2571116.8907 | 1159265.294 | 2571115.1253 | 1159264.7315
13 | 2571263.2091 | 1158893.8376 | 2571201.1936 | 1159215.5302
14 | 2571104.8616 | 1159261.4612 | 2571115.1253 | 1159264.7315
15 | 2571263.2091 | 1158893.8376 | 2571250.2608 | 1158893.7103 | 2571243.3801 | 1158887.8737 | 2571244.1293 | 1158877.8762 | 2571243.7579 | 1158865.972 | 2571237.8768 | 1158861.0409
16 | 2571263.2091 | 1158893.8376 | 2571272.7231 | 1158893.9311
17 | 2571336.9758 | 1158901.4325 | 2571331.3297 | 1158898.8804 | 2571325.7758 | 1158897.6693
18 | 2571302.4154 | 1158894.223 | 2571310.3281 | 1158894.3008 | 2571325.7758 | 1158897.6693
19 | 2571214.8428 | 1158846.4349 | 2571234.1607 | 1158857.9251 | 2571237.8768 | 1158861.0409
20 | 2571299.2434 | 1158894.1918 | 2571272.7231 | 1158893.9311
21 | 2571037.0197 | 1158877.8659 | 2571017.0998 | 1158893.519
22 | 2571037.0197 | 1158877.8659 | 2571045.1246 | 1158871.4971 | 2571056.3579 | 1158856.3908 | 2571057.1343 | 1158844.1476 | 2571053.1792 | 1158835.1155
23 | 2571172.9642 | 1158522.4632 | 2571176.8984 | 1158511.3587
24 | 2571230.833 | 1158434.4276 | 2571195.8804 | 1158484.5984 | 2571185.2848 | 1158500.2128 | 2571176.8984 | 1158511.3587
25 | 2571172.9642 | 1158522.4632 | 2571169.5169 | 1158532.1935 | 2571168.8306 | 1158537.0624
26 | 2571230.833 | 1158434.4276 | 2571234.443 | 1158424.7277 | 2571235.0428 | 1158415.5202 | 2571237.0532 | 1158403.1376 | 2571241.4886 | 1158399.3033 | 2571242.4968 | 1158398.8199
27 | 2571164.5949 | 1158567.1126 | 2571168.8306 | 1158537.0624
28 | 2571172.6611 | 1158683.8882 | 2571164.4647 | 1158697.42
29 | 2571172.6611 | 1158683.8882 | 2571187.2676 | 1158689.0081
30 | 2571172.6611 | 1158683.8882 | 2571175.2141 | 1158618.6208
31 | 2571155.6735 | 1158711.9339 | 2571164.4647 | 1158697.42
32 | 2571187.2676 | 1158689.0081 | 2571204.9794 | 1158695.2164 | 2571218.0775 | 1158706.9546
33 | 2571175.2141 | 1158618.6208 | 2571190.7771 | 1158620.6804
34 | 2571164.5949 | 1158567.1126 | 2571170.5571 | 1158569.9742 | 2571191.7109 | 1158582.0453 | 2571214.8374 | 1158598.8416
35 | 2571164.5949 | 1158567.1126 | 2571154.9281 | 1158562.2566 | 2571123.1921 | 1158547.9943
36 | 2571250.5578 | 1158624.7845 | 2571214.8374 | 1158598.8416
37 | 2571119.7945 | 1158546.4674 | 2571123.1921 | 1158547.9943
38 | 2571387.4142 | 1158676.9008 | 2571388.1115 | 1158659.1774 | 2571387.932 | 1158656.3309
39 | 2571387.0749 | 1158642.7407 | 2571387.932 | 1158656.3309
40 | 2571399.7391 | 1158679.8546 | 2571387.4142 | 1158676.9008
41 | 2571387.0749 | 1158642.7407 | 2571400.6941 | 1158643.843
42 | 2571387.0749 | 1158642.7407 | 2571384.3953 | 1158641.9295
43 | 2571399.7391 | 1158679.8546 | 2571403.3594 | 1158680.4194
44 | 2571371.9333 | 1158638.1568 | 2571384.3953 | 1158641.9295
45 | 2571233.3333 | 1158720.6265 | 2571268.7619 | 1158737.2444
46 | 2571290.9226 | 1158764.0766 | 2571288.2716 | 1158757.4929 | 2571273.5445 | 1158739.4877 | 2571268.7619 | 1158737.2444
47 | 2571233.3333 | 1158720.6265 | 2571218.0775 | 1158706.9546
48 | 2571291.0838 | 1158764.477 | 2571290.9226 | 1158764.0766
49 | 2571446.9788 | 1158687.3666 | 2571420.4129 | 1158683.0799 | 2571403.3594 | 1158680.4194
50 | 2571285.2675 | 1158645.6176 | 2571310.6247 | 1158656.7574 | 2571324.6917 | 1158660.807
51 | 2571285.2675 | 1158645.6176 | 2571286.5603 | 1158621.0546 | 2571289.169 | 1158616.7511 | 2571295.6152 | 1158615.0527 | 2571295.6152 | 1158615.0527
52 | 2571285.2675 | 1158645.6176 | 2571279.9364 | 1158643.2753 | 2571261.3655 | 1158632.6367 | 2571256.7655 | 1158629.3015
53 | 2571291.0838 | 1158764.477 | 2571291.5111 | 1158765.5381
54 | 2571371.9333 | 1158638.1568 | 2571361.1348 | 1158634.8878
55 | 2571494.2984 | 1158650.434 | 2571489.9275 | 1158671.0541 | 2571487.2969 | 1158693.3445
56 | 2571446.9788 | 1158687.3666 | 2571459.3758 | 1158689.3753 | 2571487.2969 | 1158693.3445
57 | 2571540.449 | 1158706.2207 | 2571525.1666 | 1158700.2903 | 2571508.9968 | 1158696.354 | 2571487.2969 | 1158693.3445
58 | 2571446.9788 | 1158687.3666 | 2571453.3771 | 1158656.5656
59 | 2571540.449 | 1158706.2207 | 2571544.426 | 1158696.2413 | 2571548.1617 | 1158686.8775
60 | 2571453.3771 | 1158656.5656 | 2571454.0753 | 1158653.2045 | 2571455.1634 | 1158643.7342
61 | 2571295.6152 | 1158615.0527 | 2571309.3594 | 1158619.2135
62 | 2571250.5578 | 1158624.7845 | 2571256.7655 | 1158629.3015
63 | 2571256.7655 | 1158629.3015 | 2571247.2341 | 1158631.8373 | 2571213.6353 | 1158623.7055 | 2571202.9 | 1158622.2848
64 | 2571356.9566 | 1158633.6229 | 2571361.1348 | 1158634.8878
65 | 2571338.8332 | 1158628.1363 | 2571356.9566 | 1158633.6229
66 | 2571338.8332 | 1158628.1363 | 2571315.138 | 1158620.9629
67 | 2571309.3594 | 1158619.2135 | 2571315.138 | 1158620.9629
68 | 2571554.4103 | 1158671.2147 | 2571548.1617 | 1158686.8775
69 | 2571554.4103 | 1158671.2147 | 2571540.8171 | 1158660.6347
70 | 2571554.4103 | 1158671.2147 | 2571557.5162 | 1158663.4293 | 2571563.0889 | 1158656.933
71 | 2571527.6947 | 1158650.4211 | 2571540.8171 | 1158660.6347
72 | 2571381.3495 | 1158850.028 | 2571486.3987 | 1158822.9052
73 | 2571381.3495 | 1158850.028 | 2571370.6545 | 1158843.1979 | 2571348.0953 | 1158835.1126 | 2571345.0151 | 1158835.1148
74 | 2571487.1776 | 1158824.0291 | 2571486.3987 | 1158822.9052
75 | 2571345.0151 | 1158835.1148 | 2571320.853 | 1158835.1317 | 2571313.2101 | 1158834.2606
76 | 2571508.4005 | 1158635.4039 | 2571527.6947 | 1158650.4211
77 | 2571102.297 | 1158538.6027 | 2571093.4776 | 1158534.6385 | 2571087.2517 | 1158532.6079
78 | 2571119.7945 | 1158546.4674 | 2571117.262 | 1158545.3293 | 2571102.297 | 1158538.6027
79 | 2571087.2517 | 1158532.6079 | 2571082.629 | 1158531.1001 | 2571077.7656 | 1158530.4121 | 2571065.7948 | 1158529.1832
80 | 2570947.8844 | 1158512.6531 | 2570968.7912 | 1158522.6458 | 2571004.0873 | 1158529.6786 | 2571053.4611 | 1158527.917 | 2571065.7948 | 1158529.1832
81 | 2570947.8844 | 1158512.6531 | 2570933.53 | 1158370.225
82 | 2570933.53 | 1158370.225 | 2570806.4607 | 1158060.9566
83 | 2571250.5578 | 1158624.7845 | 2571254.1087 | 1158618.7645 | 2571256.7865 | 1158608.7699
84 | 2571256.7865 | 1158608.7699 | 2571257.6551 | 1158605.5281
85 | 2571190.7771 | 1158620.6804 | 2571202.9 | 1158622.2848
86 | 2571265.9468 | 1158574.5801 | 2571257.6551 | 1158605.5281
87 | 2570806.4607 | 1158060.9566 | 2570804.3185 | 1158058.7103 | 2570797.1551 | 1158056.4885 | 2570789.5559 | 1158058.6818
88 | 2570945.2331 | 1158712.0894 | 2570936.6192 | 1158702.8159
89 | 2570789.5559 | 1158058.6818 | 2570378.2948 | 1157934.6428
90 | 2571294.5687 | 1158787.684 | 2571294.5398 | 1158773.0597 | 2571291.5111 | 1158765.5381
91 | 2571291.7207 | 1158823.0428 | 2571294.6204 | 1158813.9132 | 2571294.5687 | 1158787.684
92 | 2571291.7207 | 1158823.0428 | 2571295.7662 | 1158826.4367
93 | 2571291.7207 | 1158823.0428 | 2571286.6553 | 1158820.1211 | 2571268.8262 | 1158812.9939
94 | 2571307.6003 | 1158833.6211 | 2571307.5618 | 1158833.6168 | 2571302.0758 | 1158830.8972 | 2571297.439 | 1158827.8401 | 2571295.7662 | 1158826.4367
95 | 2571267.0165 | 1158812.2704 | 2571268.8262 | 1158812.9939
96 | 2571145.2297 | 1158729.1762 | 2571155.6735 | 1158711.9339
97 | 2571145.2297 | 1158729.1762 | 2571136.9446 | 1158724.6472 | 2571132.5749 | 1158721.3888 | 2571128.7223 | 1158718.6659
98 | 2571103.7908 | 1158694.2582 | 2571101.47 | 1158687.4311
99 | 2571083.0176 | 1158687.944 | 2571103.7908 | 1158694.2582
100 | 2571103.7908 | 1158694.2582 | 2571107.3782 | 1158714.9402 | 2571111.2205 | 1158721.6917 | 2571132.0267 | 1158742.8578 | 2571173.891 | 1158772.2935 | 2571178.1498 | 1158778.0092
101 | 2571103.7908 | 1158694.2582 | 2571117.193 | 1158709.19 | 2571125.0448 | 1158716.0668 | 2571128.7223 | 1158718.6659
102 | 2571231.6068 | 1158781.547 | 2571218.5774 | 1158757.3714
103 | 2571231.6068 | 1158781.547 | 2571239.8156 | 1158796.7782 | 2571253.3777 | 1158806.8183 | 2571267.0165 | 1158812.2704
104 | 2571083.0176 | 1158687.944 | 2571059.344 | 1158709.6358
105 | 2571178.1498 | 1158778.0092 | 2571184.2736 | 1158781.0258 | 2571184.2736 | 1158781.0258
106 | 2571178.1498 | 1158778.0092 | 2571183.841 | 1158789.9101 | 2571189.0901 | 1158826.2365 | 2571187.9175 | 1158835.847 | 2571183.2543 | 1158843.262 | 2571176.9316 | 1158848.2838
107 | 2571191.924 | 1158794.3883 | 2571184.2736 | 1158781.0258
108 | 2571197.242 | 1158809.9081 | 2571193.4262 | 1158797.0121 | 2571191.924 | 1158794.3883
109 | 2571041.2035 | 1158726.2539 | 2571059.344 | 1158709.6358
110 | 2571059.344 | 1158709.6358 | 2571074.8221 | 1158728.476
111 | 2571214.8428 | 1158846.4349 | 2571211.6526 | 1158844.5374 | 2571206.1046 | 1158838.5055 | 2571203.7893 | 1158832.0355 | 2571197.242 | 1158809.9081
112 | 2571049.7555 | 1158827.2969 | 2571053.1792 | 1158835.1155
113 | 2571049.7555 | 1158827.2969 | 2571033.0071 | 1158807.4772
114 | 2571015.7875 | 1158788.0468 | 2571024.6538 | 1158797.592 | 2571033.0071 | 1158807.4772
115 | 2571006.3852 | 1158777.9245 | 2571015.7875 | 1158788.0468
116 | 2571006.3852 | 1158777.9245 | 2570997.9876 | 1158768.8838
117 | 2571041.2035 | 1158726.2539 | 2571042.3583 | 1158730.4505 | 2571049.7312 | 1158739.7195
118 | 2571041.2035 | 1158726.2539 | 2571036.4567 | 1158724.2536 | 2571036.4567 | 1158724.2536
119 | 2571074.8221 | 1158728.476 | 2571078.3162 | 1158732.7291
120 | 2571307.6003 | 1158833.6211 | 2571313.2101 | 1158834.2606
121 | 2570997.9876 | 1158768.8838 | 2570987.3668 | 1158757.4497
122 | 2570980.158 | 1158749.6888 | 2570987.3668 | 1158757.4497
123 | 2570980.158 | 1158749.6888 | 2570970.4319 | 1158739.2179
124 | 2570962.7374 | 1158730.9342 | 2570970.4319 | 1158739.2179
125 | 2571018.9396 | 1158704.2415 | 2571023.5861 | 1158709.9197 | 2571029.7961 | 1158716.8358
126 | 2571029.7961 | 1158716.8358 | 2571036.4567 | 1158724.2536
127 | 2571299.2434 | 1158894.1918 | 2571302.4154 | 1158894.223
128 | 2571080.6487 | 1158735.5683 | 2571078.3162 | 1158732.7291
129 | 2570945.2331 | 1158712.0894 | 2570949.6417 | 1158716.8356
130 | 2570962.7374 | 1158730.9342 | 2570949.6417 | 1158716.8356

## bus_geodata
| x | y | coords
0 | 2567897.7123 | 1160805.717
1 | 2567922.9518 | 1160811.0312
2 | 2568161.7825 | 1160443.0136
3 | 2570252.037 | 1158784.2291
4 | 2570193.8672 | 1158519.5894
5 | 2570643.3733 | 1158610.467
6 | 2570927.9403 | 1158693.4724
7 | 2569895.2954 | 1158415.2487
8 | 2569920.0208 | 1158376.5397
9 | 2571261.0598 | 1159310.6752
10 | 2571201.1936 | 1159215.5302
11 | 2571115.1253 | 1159264.7315
12 | 2571263.2091 | 1158893.8376
13 | 2571336.9758 | 1158901.4325
14 | 2571325.7758 | 1158897.6693
15 | 2571104.8616 | 1159261.4612
16 | 2571237.8768 | 1158861.0409
17 | 2571272.7231 | 1158893.9311
18 | 2571017.0998 | 1158893.519
19 | 2571037.0197 | 1158877.8659
20 | 2571176.8984 | 1158511.3587
21 | 2571172.9642 | 1158522.4632
22 | 2571230.833 | 1158434.4276
23 | 2571168.8306 | 1158537.0624
24 | 2571242.4968 | 1158398.8199
25 | 2571172.6611 | 1158683.8882
26 | 2571164.4647 | 1158697.42
27 | 2571187.2676 | 1158689.0081
28 | 2571175.2141 | 1158618.6208
29 | 2571164.5949 | 1158567.1126
30 | 2571214.8374 | 1158598.8416
31 | 2571123.1921 | 1158547.9943
32 | 2571387.932 | 1158656.3309
33 | 2571387.4142 | 1158676.9008
34 | 2571387.0749 | 1158642.7407
35 | 2571399.7391 | 1158679.8546
36 | 2571400.6941 | 1158643.843
37 | 2571384.3953 | 1158641.9295
38 | 2571268.7619 | 1158737.2444
39 | 2571233.3333 | 1158720.6265
40 | 2571290.9226 | 1158764.0766
41 | 2571403.3594 | 1158680.4194
42 | 2571324.6917 | 1158660.807
43 | 2571285.2675 | 1158645.6176
44 | 2571291.0838 | 1158764.477
45 | 2571371.9333 | 1158638.1568
46 | 2571487.2969 | 1158693.3445
47 | 2571494.2984 | 1158650.434
48 | 2571446.9788 | 1158687.3666
49 | 2571540.449 | 1158706.2207
50 | 2571453.3771 | 1158656.5656
51 | 2571295.6152 | 1158615.0527
52 | 2571256.7655 | 1158629.3015
53 | 2571361.1348 | 1158634.8878
54 | 2571338.8332 | 1158628.1363
55 | 2571356.9566 | 1158633.6229
56 | 2571315.138 | 1158620.9629
57 | 2571309.3593 | 1158619.2135
58 | 2571548.1617 | 1158686.8775
59 | 2571554.4103 | 1158671.2147
60 | 2571540.8171 | 1158660.6347
61 | 2571563.0889 | 1158656.933
62 | 2571381.3495 | 1158850.028
63 | 2571486.3987 | 1158822.9052
64 | 2571345.0151 | 1158835.1148
65 | 2571527.6947 | 1158650.4211
66 | 2571508.4005 | 1158635.4039
67 | 2571455.1634 | 1158643.7342
68 | 2571487.1776 | 1158824.0291
69 | 2571102.297 | 1158538.6027
70 | 2571087.2517 | 1158532.6079
71 | 2571119.7945 | 1158546.4674
72 | 2571065.7948 | 1158529.1832
73 | 2570947.8844 | 1158512.6531
74 | 2570933.53 | 1158370.225
75 | 2571250.5578 | 1158624.7845
76 | 2571256.7865 | 1158608.7699
77 | 2571218.0775 | 1158706.9546
78 | 2571190.7771 | 1158620.6804
79 | 2571202.9 | 1158622.2848
80 | 2571257.6551 | 1158605.5281
81 | 2571265.9468 | 1158574.5801
82 | 2570806.4607 | 1158060.9566
83 | 2570936.6192 | 1158702.8159
84 | 2570789.5559 | 1158058.6818
85 | 2570378.2948 | 1157934.6428
86 | 2570173.8227 | 1158448.9756
87 | 2571291.5111 | 1158765.5381
88 | 2571294.5687 | 1158787.684
89 | 2571291.7207 | 1158823.0428
90 | 2571295.7662 | 1158826.4367
91 | 2571268.8262 | 1158812.9939
92 | 2571155.6735 | 1158711.9339
93 | 2571145.2297 | 1158729.1762
94 | 2571101.47 | 1158687.4311
95 | 2571103.7908 | 1158694.2582
96 | 2571128.7223 | 1158718.6659
97 | 2571218.5774 | 1158757.3714
98 | 2571231.6068 | 1158781.547
99 | 2571267.0165 | 1158812.2704
100 | 2571083.0176 | 1158687.944
101 | 2571178.1498 | 1158778.0092
102 | 2571176.9316 | 1158848.2838
103 | 2571184.2736 | 1158781.0258
104 | 2571191.924 | 1158794.3883
105 | 2571059.344 | 1158709.6358
106 | 2571197.242 | 1158809.9081
107 | 2571049.7555 | 1158827.2969
108 | 2571053.1792 | 1158835.1155
109 | 2571033.0071 | 1158807.4772
110 | 2571015.7875 | 1158788.0468
111 | 2571006.3852 | 1158777.9245
112 | 2571041.2035 | 1158726.2539
113 | 2571074.8221 | 1158728.476
114 | 2571313.2101 | 1158834.2606
115 | 2571307.6003 | 1158833.6211
116 | 2570997.9876 | 1158768.8838
117 | 2570987.3668 | 1158757.4497
118 | 2570980.158 | 1158749.6888
119 | 2570970.4319 | 1158739.2179
120 | 2571018.9396 | 1158704.2415
121 | 2571029.7961 | 1158716.8358
122 | 2571036.4567 | 1158724.2536
123 | 2571049.7312 | 1158739.7195
124 | 2571214.8428 | 1158846.4349
125 | 2571299.2434 | 1158894.1918
126 | 2571302.4154 | 1158894.223
127 | 2571078.3162 | 1158732.7291
128 | 2571080.6487 | 1158735.5683
129 | 2570945.2331 | 1158712.0894
130 | 2570949.6417 | 1158716.8356
131 | 2570962.7374 | 1158730.9342
132 | 2571083.0176 | 1158687.944

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97002 | -0.58681 | 0.00060153 | 0.00015076
1 | 0.97003 | -0.58652 | 0 | 0
2 | 0.97028 | -0.58157 | 0.0011158 | 0.00027965
3 | 0.97552 | -0.47418 | 0.0036248 | 0.00090847
4 | 0.97513 | -0.48214 | 0 | 0
5 | 0.9765 | -0.45442 | 0.00282 | 0.00070676
6 | 0.97737 | -0.43689 | 0.0010271 | 0.00025742
7 | 0.97453 | -0.49432 | 0.0021226 | 0.00053197
8 | 0.97479 | -0.48909 | 0 | 0
9 | 0.98988 | -0.19511 | 0.0011754 | 0.00029458
10 | 0.99 | -0.19275 | 0 | 0
11 | 0.98944 | -0.20362 | 0.0013164 | 0.00032993
12 | 0.99195 | -0.15482 | 0.0012188 | 0.00030545
13 | 0.99141 | -0.1653 | 0.0026811 | 0.00067195
14 | 0.99144 | -0.16474 | 0.0032083 | 0.00080407
15 | 0.9894 | -0.20439 | 0.0040181 | 0.001007
16 | 0.9929 | -0.13656 | 0.0013925 | 0.000349
17 | 0.99185 | -0.15689 | 0.0018762 | 0.00047023
18 | 0.97232 | -0.53641 | 0.0059368 | 0.0014879
19 | 0.97246 | -0.53363 | 0.0034364 | 0.00086125
20 | 0.98189 | -0.34823 | 0.013424 | 0.0033644
21 | 0.98207 | -0.3446 | 0.0043504 | 0.0010903
22 | 0.98157 | -0.35441 | 0 | 0
23 | 0.98238 | -0.3387 | 0.010138 | 0.0025408
24 | 0.98144 | -0.35698 | 0.0036343 | 0.00091083
25 | 0.99314 | -0.13053 | 0 | 0
26 | 0.99412 | -0.11175 | 0.0018358 | 0.00046009
27 | 0.99243 | -0.14417 | 0.0046323 | 0.001161
28 | 0.98984 | -0.19399 | 0.042118 | 0.010556
29 | 0.98326 | -0.32142 | 0 | 0
30 | 0.98495 | -0.28847 | 0.0029932 | 0.00075016
31 | 0.9823 | -0.34024 | 0.0061187 | 0.0015335
32 | 0.98052 | -0.37483 | 0.0031125 | 0.00078006
33 | 0.98017 | -0.38179 | 0 | 0
34 | 0.9808 | -0.36947 | 0 | 0
35 | 0.97995 | -0.38606 | 0 | 0
36 | 0.98078 | -0.3699 | 0.0017374 | 0.00043544
37 | 0.98086 | -0.36828 | 0.0020575 | 0.00051565
38 | 0.98865 | -0.21718 | 0.0026533 | 0.00066499
39 | 0.99014 | -0.18836 | 0 | 0
40 | 0.98738 | -0.24181 | 0.0028199 | 0.00070673
41 | 0.97989 | -0.3873 | 0.0017287 | 0.00043326
42 | 0.98499 | -0.28772 | 0.0030865 | 0.00077356
43 | 0.98511 | -0.28537 | 0 | 0
44 | 0.98737 | -0.24209 | 0.0033572 | 0.00084139
45 | 0.98117 | -0.36226 | 0.0011844 | 0.00029683
46 | 0.97877 | -0.40918 | 0 | 0
47 | 0.97868 | -0.41106 | 0.0023762 | 0.00059553
48 | 0.9792 | -0.40085 | 0 | 0
49 | 0.97832 | -0.41801 | 0 | 0
50 | 0.97903 | -0.40409 | 0.0024526 | 0.00061469
51 | 0.98372 | -0.31252 | 0.0012008 | 0.00030095
52 | 0.98647 | -0.25906 | 0 | 0
53 | 0.98145 | -0.3568 | 0.0032066 | 0.00080364
54 | 0.98216 | -0.34292 | 0.0017278 | 0.00043304
55 | 0.98157 | -0.35444 | 0.0037386 | 0.00093698
56 | 0.98297 | -0.3271 | 0.0025042 | 0.0006276
57 | 0.98318 | -0.32297 | 0.0024877 | 0.00062347
58 | 0.97815 | -0.42137 | 0.0010817 | 0.00027109
59 | 0.97803 | -0.42376 | 0 | 0
60 | 0.97794 | -0.42563 | 0.0025981 | 0.00065115
61 | 0.978 | -0.42431 | 0.0017959 | 0.00045009
62 | 0.98489 | -0.29042 | 0.0059487 | 0.0014909
63 | 0.98473 | -0.2936 | 0.00072032 | 0.00018053
64 | 0.98517 | -0.285 | 0.0023752 | 0.00059528
65 | 0.97788 | -0.42666 | 0.00098661 | 0.00024727
66 | 0.97783 | -0.42772 | 0.002389 | 0.00059873
67 | 0.97899 | -0.40484 | 0.003202 | 0.00080249
68 | 0.98473 | -0.29363 | 0.00091262 | 0.00022872
69 | 0.98189 | -0.34818 | 0.0020045 | 0.00050237
70 | 0.98162 | -0.35353 | 0.0043588 | 0.0010924
71 | 0.98222 | -0.34167 | 0.010276 | 0.0025754
72 | 0.98127 | -0.3603 | 0.0034647 | 0.00086832
73 | 0.97945 | -0.39605 | 0 | 0
74 | 0.97734 | -0.43735 | 0.0062072 | 0.0015557
75 | 0.98624 | -0.26352 | 0 | 0
76 | 0.98617 | -0.26476 | 0.001779 | 0.00044587
77 | 0.99092 | -0.1733 | 0.0038327 | 0.00096056
78 | 0.98919 | -0.20636 | 0.0012781 | 0.00032033
79 | 0.9887 | -0.21594 | 0.0011286 | 0.00028284
80 | 0.98617 | -0.2649 | 0.0013278 | 0.00033279
81 | 0.98614 | -0.2654 | 0.00088235 | 0.00022114
82 | 0.97435 | -0.4963 | 0 | 0
83 | 0.97695 | -0.4451 | 0.00066461 | 0.00016657
84 | 0.97418 | -0.49957 | 0.0068141 | 0.0017078
85 | 0.97306 | -0.52173 | 0.0027984 | 0.00070134
86 | 0.97502 | -0.4843 | 0.0024157 | 0.00060542
87 | 0.98734 | -0.24276 | 0.0018114 | 0.00045399
88 | 0.98669 | -0.25525 | 0.0024923 | 0.00062463
89 | 0.98576 | -0.27337 | 0 | 0
90 | 0.98569 | -0.27474 | 0.00093966 | 0.0002355
91 | 0.98545 | -0.27953 | 0.004032 | 0.0010105
92 | 0.99518 | -0.091504 | 0.0058287 | 0.0014608
93 | 0.99647 | -0.066994 | 0 | 0
94 | 0.99999 | -0.00018289 | 0.0014551 | 0.00036467
95 | 1 | 0 | -0.35615 | -0.090531
96 | 0.99772 | -0.043211 | 0.0059369 | 0.0014879
97 | 0.9849 | -0.29016 | 0.0049959 | 0.0012521
98 | 0.98503 | -0.2877 | 0.0039204 | 0.00098255
99 | 0.98543 | -0.27987 | 0.0007646 | 0.00019163
100 | 0.99956 | -0.0085074 | 0 | 0
101 | 0.99537 | -0.088885 | 0 | 0
102 | 0.99458 | -0.1041 | 0.011306 | 0.0028336
103 | 0.99517 | -0.092755 | 0.0031385 | 0.00078659
104 | 0.99476 | -0.10064 | 0.0035629 | 0.00089294
105 | 0.9989 | -0.021117 | 0 | 0
106 | 0.99437 | -0.10805 | 0.0009107 | 0.00022824
107 | 0.97302 | -0.52248 | 0 | 0
108 | 0.97291 | -0.52478 | 0.0052736 | 0.0013217
109 | 0.97338 | -0.51548 | 0.0032617 | 0.00081746
110 | 0.97381 | -0.50693 | 0.0027073 | 0.00067851
111 | 0.97408 | -0.50169 | 0.0046661 | 0.0011694
112 | 0.99862 | -0.026549 | 0 | 0
113 | 0.99868 | -0.025323 | 0.0042449 | 0.0010639
114 | 0.98546 | -0.2793 | 0.0016295 | 0.00040839
115 | 0.98552 | -0.27813 | 0.0019818 | 0.00049668
116 | 0.97437 | -0.49596 | 0.0012691 | 0.00031806
117 | 0.97475 | -0.48836 | 0.002271 | 0.00056916
118 | 0.97504 | -0.48276 | 0.001097 | 0.00027494
119 | 0.97544 | -0.47492 | 0.0014377 | 0.00036031
120 | 0.99848 | -0.029213 | 0.0023311 | 0.00058422
121 | 0.99852 | -0.028535 | 0.0042908 | 0.0010754
122 | 0.99858 | -0.027381 | 0.0026171 | 0.00065592
123 | 0.99857 | -0.027516 | 0.0034157 | 0.00085605
124 | 0.99343 | -0.12622 | 0.0031993 | 0.00080182
125 | 0.9916 | -0.16177 | 0.0016893 | 0.00042339
126 | 0.99157 | -0.16226 | 0.0028077 | 0.00070367
127 | 0.99865 | -0.025864 | 0.0035128 | 0.0008804
128 | 0.99865 | -0.026 | 0.0021138 | 0.00052977
129 | 0.97655 | -0.45311 | 0.00086925 | 0.00021785
130 | 0.97634 | -0.45711 | 0.0016185 | 0.00040562
131 | 0.97577 | -0.46843 | 0.00078562 | 0.00019689
132 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00060153 | -0.00015076 | 0.00060154 | 0.00015045 | 8.2348e-09 | -3.1313e-07 | 0.00092276 | 0.00092264 | 0.00092276 | 0.97002 | -0.58681 | 0.97003 | -0.58652 | 0.2535
1 | -0.00060154 | -0.00015045 | 0.00060168 | 0.00014512 | 1.3976e-07 | -5.3278e-06 | 0.00092264 | 0.00092072 | 0.00092264 | 0.97003 | -0.58652 | 0.97028 | -0.58157 | 0.25347
2 | -0.0017175 | -0.00042477 | 0.0017244 | 0.00039609 | 6.8994e-06 | -2.8679e-05 | 0.0026319 | 0.0026205 | 0.0026319 | 0.97028 | -0.58157 | 0.97453 | -0.49432 | 0.72305
3 | 0.0062674 | 0.0015052 | -0.0062651 | -0.0015173 | 2.3115e-06 | -1.2047e-05 | 0.0095369 | 0.0095416 | 0.0095416 | 0.97552 | -0.47418 | 0.97513 | -0.48214 | 0.65533
4 | -0.0098922 | -0.0024137 | 0.0099013 | 0.0023981 | 9.1068e-06 | -1.5576e-05 | 0.015066 | 0.015058 | 0.015066 | 0.97552 | -0.47418 | 0.9765 | -0.45442 | 1.0347
5 | 0.0062651 | 0.0015173 | -0.0062644 | -0.0015206 | 6.2876e-07 | -3.2727e-06 | 0.0095416 | 0.0095428 | 0.0095428 | 0.97513 | -0.48214 | 0.97502 | -0.4843 | 0.65541
6 | -0.012721 | -0.0031049 | 0.012732 | 0.0030967 | 1.0408e-05 | -8.1851e-06 | 0.019355 | 0.01935 | 0.019355 | 0.9765 | -0.45442 | 0.97737 | -0.43689 | 1.3294
7 | 0.035414 | 0.0089191 | -0.035401 | -0.0089104 | 1.391e-05 | 8.7427e-06 | 0.053933 | 0.053933 | 0.053933 | 0.97737 | -0.43689 | 0.97695 | -0.4451 | 14.8167
8 | -0.049173 | -0.012273 | 0.049269 | 0.012325 | 9.5535e-05 | 5.2004e-05 | 0.074846 | 0.074843 | 0.074846 | 0.97737 | -0.43689 | 0.97945 | -0.39605 | 5.1405
9 | -0.003847 | -0.00092806 | 0.0038479 | 0.00092776 | 9.3109e-07 | -3.0489e-07 | 0.0058612 | 0.0058609 | 0.0058612 | 0.97453 | -0.49432 | 0.97479 | -0.48909 | 1.6102
10 | -0.0038479 | -0.00092776 | 0.0038488 | 0.00091514 | 8.4931e-07 | -1.2621e-05 | 0.0058609 | 0.0058564 | 0.0058609 | 0.97479 | -0.48909 | 0.97502 | -0.4843 | 0.40254
11 | -0.0011754 | -0.00029458 | 0.0011755 | 0.00029321 | 1.3192e-07 | -1.3648e-06 | 0.0017669 | 0.0017664 | 0.0017669 | 0.98988 | -0.19511 | 0.99 | -0.19275 | 0.4854
12 | 0.0053374 | 0.0013372 | -0.0053346 | -0.0013369 | 2.7626e-06 | 2.9709e-07 | 0.0080222 | 0.0080227 | 0.0080227 | 0.99 | -0.19275 | 0.98944 | -0.20362 | 2.204
13 | -0.0065129 | -0.0016304 | 0.0065247 | 0.0016337 | 1.177e-05 | 3.3118e-06 | 0.0097886 | 0.0097871 | 0.0097886 | 0.99 | -0.19275 | 0.99195 | -0.15482 | 2.6892
14 | 0.0040182 | 0.001007 | -0.0040181 | -0.001007 | 1.4752e-07 | -4.3939e-08 | 0.006043 | 0.006043 | 0.006043 | 0.98944 | -0.20362 | 0.9894 | -0.20439 | 1.6602
15 | -0.020011 | -0.0050145 | 0.020028 | 0.005025 | 1.7429e-05 | 1.0488e-05 | 0.030018 | 0.030017 | 0.030018 | 0.99195 | -0.15482 | 0.9929 | -0.13656 | 8.2466
16 | 0.012267 | 0.0030753 | -0.012266 | -0.0030746 | 1.2082e-06 | 6.5047e-07 | 0.018402 | 0.018402 | 0.018402 | 0.99195 | -0.15482 | 0.99185 | -0.15689 | 5.0556
17 | -0.0026811 | -0.00067195 | 0.0026812 | 0.00067185 | 7.2144e-08 | -1.0703e-07 | 0.0040241 | 0.0040241 | 0.0040241 | 0.99141 | -0.1653 | 0.99144 | -0.16474 | 1.1055
18 | -0.0058895 | -0.0014759 | 0.0058902 | 0.0014761 | 6.9509e-07 | 1.3888e-07 | 0.0088392 | 0.0088391 | 0.0088392 | 0.99144 | -0.16474 | 0.99157 | -0.16226 | 2.4284
19 | -0.021421 | -0.005374 | 0.021431 | 0.0053804 | 1.0562e-05 | 6.4059e-06 | 0.032104 | 0.032104 | 0.032104 | 0.9929 | -0.13656 | 0.99343 | -0.12622 | 8.8198
20 | 0.01039 | 0.0026044 | -0.010387 | -0.0026032 | 2.4165e-06 | 1.2043e-06 | 0.015587 | 0.015588 | 0.015588 | 0.99185 | -0.15689 | 0.9916 | -0.16177 | 4.2823
21 | -0.0059368 | -0.0014879 | 0.0059375 | 0.0014881 | 7.842e-07 | 1.8763e-07 | 0.0090855 | 0.0090854 | 0.0090855 | 0.97232 | -0.53641 | 0.97246 | -0.53363 | 2.496
22 | -0.0093739 | -0.0023493 | 0.0093779 | 0.0023512 | 3.9548e-06 | 1.8948e-06 | 0.014344 | 0.014343 | 0.014344 | 0.97246 | -0.53363 | 0.97291 | -0.52478 | 3.9406
23 | -0.01706 | -0.0042745 | 0.017063 | 0.0042763 | 2.9529e-06 | 1.7408e-06 | 0.025853 | 0.025853 | 0.025853 | 0.98189 | -0.34823 | 0.98207 | -0.3446 | 7.1026
24 | 0.0036358 | 0.00091012 | -0.0036347 | -0.00091063 | 1.0697e-06 | -5.0352e-07 | 0.0055095 | 0.0055099 | 0.0055099 | 0.98189 | -0.34823 | 0.98157 | -0.35441 | 1.5137
25 | -0.021413 | -0.0053666 | 0.021419 | 0.0053703 | 6.016e-06 | 3.6574e-06 | 0.032445 | 0.032445 | 0.032445 | 0.98207 | -0.3446 | 0.98238 | -0.3387 | 8.9135
26 | 0.0036347 | 0.00091063 | -0.0036343 | -0.00091083 | 4.4519e-07 | -2.0928e-07 | 0.0055099 | 0.0055101 | 0.0055101 | 0.98157 | -0.35441 | 0.98144 | -0.35698 | 1.5138
27 | -0.031557 | -0.0079111 | 0.031583 | 0.0079274 | 2.6003e-05 | 1.6258e-05 | 0.047801 | 0.047801 | 0.047801 | 0.98238 | -0.3387 | 0.98326 | -0.32142 | 13.1322
28 | -0.27133 | -0.068897 | 0.27158 | 0.069054 | 0.00024551 | 0.00015631 | 0.40686 | 0.40686 | 0.40686 | 0.99314 | -0.13053 | 0.99412 | -0.11175 | 27.9434
29 | 0.05011 | 0.012665 | -0.050077 | -0.012644 | 3.275e-05 | 2.076e-05 | 0.075117 | 0.075117 | 0.075117 | 0.99314 | -0.13053 | 0.99243 | -0.14417 | 20.6365
30 | 0.22122 | 0.056232 | -0.22055 | -0.055804 | 0.0006739 | 0.00042793 | 0.33174 | 0.33174 | 0.33174 | 0.99314 | -0.13053 | 0.98984 | -0.19399 | 22.7844
31 | -0.27342 | -0.069514 | 0.27368 | 0.069684 | 0.0002669 | 0.00016993 | 0.4096 | 0.4096 | 0.4096 | 0.99412 | -0.11175 | 0.99518 | -0.091504 | 28.1321
32 | 0.045445 | 0.011483 | -0.045381 | -0.011443 | 6.336e-05 | 4.0082e-05 | 0.068171 | 0.068171 | 0.068171 | 0.99243 | -0.14417 | 0.99092 | -0.1733 | 18.7284
33 | 0.17843 | 0.045249 | -0.17833 | -0.045182 | 0.00010604 | 6.706e-05 | 0.26842 | 0.26842 | 0.26842 | 0.98984 | -0.19399 | 0.98919 | -0.20636 | 18.4358
34 | -0.12322 | -0.030975 | 0.12342 | 0.031096 | 0.00019421 | 0.00012127 | 0.18651 | 0.18651 | 0.18651 | 0.98326 | -0.32142 | 0.98495 | -0.28847 | 12.8097
35 | 0.091637 | 0.023048 | -0.091555 | -0.022997 | 8.2272e-05 | 5.0342e-05 | 0.13871 | 0.13871 | 0.13871 | 0.98326 | -0.32142 | 0.9823 | -0.34024 | 9.5267
36 | -0.12641 | -0.031847 | 0.12656 | 0.031941 | 0.00015104 | 9.4412e-05 | 0.19103 | 0.19103 | 0.19103 | 0.98495 | -0.28847 | 0.98624 | -0.26352 | 13.1202
37 | 0.085436 | 0.021464 | -0.08543 | -0.02146 | 5.8509e-06 | 3.556e-06 | 0.12944 | 0.12944 | 0.12944 | 0.9823 | -0.34024 | 0.98222 | -0.34167 | 8.8901
38 | 0.018645 | 0.0046817 | -0.018639 | -0.004678 | 6.1831e-06 | 3.6976e-06 | 0.028299 | 0.028299 | 0.028299 | 0.98052 | -0.37483 | 0.98017 | -0.38179 | 7.7744
39 | -0.021758 | -0.0054617 | 0.021763 | 0.0054651 | 5.5684e-06 | 3.3919e-06 | 0.033022 | 0.033022 | 0.033022 | 0.98052 | -0.37483 | 0.9808 | -0.36947 | 9.072
40 | 0.018639 | 0.004678 | -0.018635 | -0.0046757 | 3.7956e-06 | 2.2699e-06 | 0.028299 | 0.028299 | 0.028299 | 0.98017 | -0.38179 | 0.97995 | -0.38606 | 7.7744
41 | 0.0017375 | 0.00043529 | -0.0017374 | -0.00043544 | 3.5499e-08 | -1.4922e-07 | 0.0026359 | 0.002636 | 0.002636 | 0.9808 | -0.36947 | 0.98078 | -0.3699 | 0.72417
42 | -0.023501 | -0.0059004 | 0.023502 | 0.0059012 | 1.3349e-06 | 8.1902e-07 | 0.035658 | 0.035658 | 0.035658 | 0.9808 | -0.36947 | 0.98086 | -0.36828 | 9.7962
43 | 0.018635 | 0.0046757 | -0.018634 | -0.0046751 | 1.1004e-06 | 6.5808e-07 | 0.028299 | 0.028299 | 0.028299 | 0.97995 | -0.38606 | 0.97989 | -0.3873 | 7.7744
44 | -0.02556 | -0.0064169 | 0.025567 | 0.0064214 | 7.3428e-06 | 4.535e-06 | 0.038779 | 0.038779 | 0.038779 | 0.98086 | -0.36828 | 0.98117 | -0.36226 | 10.6537
45 | -0.041461 | -0.010428 | 0.041519 | 0.010464 | 5.7169e-05 | 3.6086e-05 | 0.062416 | 0.062416 | 0.062416 | 0.98865 | -0.21718 | 0.99014 | -0.18836 | 17.1474
46 | 0.038808 | 0.0097626 | -0.038763 | -0.0097339 | 4.5619e-05 | 2.874e-05 | 0.058423 | 0.058423 | 0.058423 | 0.98865 | -0.21718 | 0.98738 | -0.24181 | 16.0503
47 | -0.041519 | -0.010464 | 0.041549 | 0.010483 | 2.9928e-05 | 1.889e-05 | 0.062416 | 0.062416 | 0.062416 | 0.99014 | -0.18836 | 0.99092 | -0.1733 | 17.1473
48 | 0.035943 | 0.0090271 | -0.035942 | -0.0090268 | 4.7506e-07 | 2.9852e-07 | 0.054173 | 0.054173 | 0.054173 | 0.98738 | -0.24181 | 0.98737 | -0.24209 | 14.8828
49 | 0.016906 | 0.0042418 | -0.016895 | -0.0042354 | 1.0918e-05 | 6.4314e-06 | 0.025674 | 0.025674 | 0.025674 | 0.97989 | -0.3873 | 0.9792 | -0.40085 | 7.0533
50 | -0.0030865 | -0.00077356 | 0.0030869 | 0.00077324 | 3.4514e-07 | -3.1803e-07 | 0.0046628 | 0.0046626 | 0.0046628 | 0.98499 | -0.28772 | 0.98511 | -0.28537 | 1.281
51 | 0.041755 | 0.010531 | -0.0417 | -0.010496 | 5.4183e-05 | 3.4216e-05 | 0.063094 | 0.063094 | 0.063094 | 0.98511 | -0.28537 | 0.98372 | -0.31252 | 17.3336
52 | -0.044841 | -0.011304 | 0.044898 | 0.01134 | 5.6534e-05 | 3.5763e-05 | 0.067757 | 0.067756 | 0.067757 | 0.98511 | -0.28537 | 0.98647 | -0.25906 | 18.6145
53 | 0.032585 | 0.0081854 | -0.032584 | -0.0081848 | 1.0348e-06 | 6.4762e-07 | 0.049114 | 0.049114 | 0.049114 | 0.98737 | -0.24209 | 0.98734 | -0.24276 | 13.4928
54 | -0.026751 | -0.0067183 | 0.026758 | 0.0067226 | 6.9656e-06 | 4.3155e-06 | 0.040575 | 0.040575 | 0.040575 | 0.98117 | -0.36226 | 0.98145 | -0.3568 | 11.1471
55 | 0.0023764 | 0.00059512 | -0.0023762 | -0.00059553 | 2.1306e-07 | -4.107e-07 | 0.0036126 | 0.0036128 | 0.0036128 | 0.97877 | -0.40918 | 0.97868 | -0.41106 | 0.99254
56 | -0.011235 | -0.0028158 | 0.011239 | 0.0028181 | 4.4589e-06 | 2.3412e-06 | 0.01708 | 0.01708 | 0.01708 | 0.97877 | -0.40918 | 0.9792 | -0.40085 | 4.6923
57 | 0.0088582 | 0.0022206 | -0.0088544 | -0.0022189 | 3.7267e-06 | 1.6967e-06 | 0.013467 | 0.013467 | 0.013467 | 0.97877 | -0.40918 | 0.97832 | -0.41801 | 3.6998
58 | 0.0056556 | 0.0014173 | -0.0056547 | -0.0014171 | 8.7137e-07 | 1.6202e-07 | 0.0085944 | 0.0085945 | 0.0085945 | 0.9792 | -0.40085 | 0.97903 | -0.40409 | 2.3611
59 | 0.0088544 | 0.0022189 | -0.008853 | -0.0022183 | 1.4163e-06 | 6.4502e-07 | 0.013467 | 0.013467 | 0.013467 | 0.97832 | -0.41801 | 0.97815 | -0.42137 | 3.6999
60 | 0.0032021 | 0.0008024 | -0.003202 | -0.00080249 | 1.1516e-07 | -8.933e-08 | 0.0048668 | 0.0048668 | 0.0048668 | 0.97903 | -0.40409 | 0.97899 | -0.40484 | 1.337
61 | 0.0405 | 0.010195 | -0.040479 | -0.010183 | 2.0221e-05 | 1.2759e-05 | 0.061278 | 0.061278 | 0.061278 | 0.98372 | -0.31252 | 0.98318 | -0.32297 | 16.8346
62 | 0.13058 | 0.032958 | -0.13055 | -0.03294 | 2.7894e-05 | 1.7461e-05 | 0.19705 | 0.19705 | 0.19705 | 0.98647 | -0.25906 | 0.98624 | -0.26352 | 13.5336
63 | -0.17547 | -0.044297 | 0.17584 | 0.044527 | 0.00036328 | 0.00022967 | 0.2648 | 0.2648 | 0.2648 | 0.98647 | -0.25906 | 0.9887 | -0.21594 | 18.1872
64 | -0.029965 | -0.0075262 | 0.029968 | 0.0075283 | 3.3797e-06 | 2.1078e-06 | 0.045437 | 0.045437 | 0.045437 | 0.98145 | -0.3568 | 0.98157 | -0.35444 | 12.4827
65 | 0.033725 | 0.0084769 | -0.033707 | -0.0084653 | 1.8545e-05 | 1.1629e-05 | 0.051104 | 0.051105 | 0.051105 | 0.98216 | -0.34292 | 0.98157 | -0.35444 | 14.0397
66 | -0.035453 | -0.00891 | 0.03548 | 0.0089268 | 2.6794e-05 | 1.6835e-05 | 0.053722 | 0.053722 | 0.053722 | 0.98216 | -0.34292 | 0.98297 | -0.3271 | 14.7588
67 | -0.037984 | -0.0095544 | 0.037992 | 0.0095591 | 7.4891e-06 | 4.7165e-06 | 0.057513 | 0.057513 | 0.057513 | 0.98297 | -0.3271 | 0.98318 | -0.32297 | 15.8002
68 | 0.0077713 | 0.0019472 | -0.0077705 | -0.0019469 | 8.8381e-07 | 3.5399e-07 | 0.011822 | 0.011822 | 0.011822 | 0.97815 | -0.42137 | 0.97803 | -0.42376 | 3.2478
69 | 0.0059745 | 0.0014969 | -0.005974 | -0.0014968 | 5.3371e-07 | 1.2543e-07 | 0.0090897 | 0.0090898 | 0.0090898 | 0.97803 | -0.42376 | 0.97794 | -0.42563 | 2.4972
70 | 0.0017959 | 0.00044991 | -0.0017959 | -0.00045009 | 4.743e-08 | -1.8224e-07 | 0.0027323 | 0.0027324 | 0.0027324 | 0.97803 | -0.42376 | 0.978 | -0.42431 | 0.75066
71 | 0.0033759 | 0.00084567 | -0.0033757 | -0.00084577 | 1.6453e-07 | -1.0333e-07 | 0.0051365 | 0.0051366 | 0.0051366 | 0.97794 | -0.42563 | 0.97788 | -0.42666 | 1.4112
72 | 0.0016332 | 0.00040802 | -0.0016329 | -0.00040924 | 2.4767e-07 | -1.2219e-06 | 0.002467 | 0.0024675 | 0.0024675 | 0.98489 | -0.29042 | 0.98473 | -0.2936 | 0.67789
73 | -0.0075819 | -0.0018989 | 0.0075839 | 0.0018996 | 1.955e-06 | 7.4542e-07 | 0.011455 | 0.011454 | 0.011455 | 0.98489 | -0.29042 | 0.98517 | -0.285 | 3.1469
74 | 0.00091262 | 0.00022871 | -0.00091262 | -0.00022872 | 9.7518e-10 | -1.6772e-08 | 0.0013791 | 0.0013791 | 0.0013791 | 0.98473 | -0.2936 | 0.98473 | -0.29363 | 0.37886
75 | -0.0099591 | -0.0024949 | 0.0099618 | 0.0024963 | 2.7028e-06 | 1.3241e-06 | 0.015042 | 0.015042 | 0.015042 | 0.98517 | -0.285 | 0.98546 | -0.2793 | 4.1324
76 | 0.0023891 | 0.0005985 | -0.002389 | -0.00059873 | 1.2117e-07 | -2.2916e-07 | 0.0036353 | 0.0036354 | 0.0036354 | 0.97788 | -0.42666 | 0.97783 | -0.42772 | 0.99874
77 | 0.073127 | 0.018369 | -0.073108 | -0.018357 | 1.8678e-05 | 1.1134e-05 | 0.11084 | 0.11084 | 0.11084 | 0.98189 | -0.34818 | 0.98162 | -0.35353 | 7.6123
78 | -0.075131 | -0.018871 | 0.075154 | 0.018885 | 2.3321e-05 | 1.3955e-05 | 0.11387 | 0.11387 | 0.11387 | 0.98189 | -0.34818 | 0.98222 | -0.34167 | 7.821
79 | 0.068749 | 0.017265 | -0.068727 | -0.017252 | 2.221e-05 | 1.3112e-05 | 0.10423 | 0.10423 | 0.10423 | 0.98162 | -0.35353 | 0.98127 | -0.3603 | 7.1586
80 | 0.065262 | 0.016384 | -0.065151 | -0.016319 | 0.00011109 | 6.4999e-05 | 0.098975 | 0.098977 | 0.098977 | 0.98127 | -0.3603 | 0.97945 | -0.39605 | 6.7979
81 | 0.015882 | 0.0039934 | -0.015851 | -0.0039752 | 3.1267e-05 | 1.8213e-05 | 0.024134 | 0.024134 | 0.024134 | 0.97945 | -0.39605 | 0.97734 | -0.43735 | 6.6303
82 | 0.0096439 | 0.0024195 | -0.0096169 | -0.0024064 | 2.7038e-05 | 1.3127e-05 | 0.014684 | 0.014685 | 0.014685 | 0.97734 | -0.43735 | 0.97435 | -0.4963 | 4.0345
83 | 0.0039895 | 0.00099929 | -0.0039893 | -0.00099936 | 2.3553e-07 | -7.0468e-08 | 0.0060191 | 0.0060191 | 0.0060191 | 0.98624 | -0.26352 | 0.98617 | -0.26476 | 1.6536
84 | 0.0022102 | 0.0005535 | -0.0022102 | -0.00055353 | 1.3996e-08 | -3.3863e-08 | 0.0033348 | 0.0033348 | 0.0033348 | 0.98617 | -0.26476 | 0.98617 | -0.2649 | 0.91616
85 | 0.17705 | 0.044861 | -0.17697 | -0.04481 | 8.1424e-05 | 5.1484e-05 | 0.2665 | 0.2665 | 0.2665 | 0.98919 | -0.20636 | 0.9887 | -0.21594 | 18.3037
86 | 0.00088237 | 0.00022074 | -0.00088235 | -0.00022114 | 2.1296e-08 | -3.9515e-07 | 0.0013313 | 0.0013314 | 0.0013314 | 0.98617 | -0.2649 | 0.98614 | -0.2654 | 0.36577
87 | 0.0096169 | 0.0024064 | -0.0096154 | -0.0024057 | 1.4972e-06 | 7.2769e-07 | 0.014685 | 0.014686 | 0.014686 | 0.97435 | -0.4963 | 0.97418 | -0.49957 | 4.0345
88 | 0.034736 | 0.0087438 | -0.034723 | -0.0087354 | 1.3293e-05 | 8.3489e-06 | 0.052921 | 0.052921 | 0.052921 | 0.97695 | -0.4451 | 0.97655 | -0.45311 | 14.5387
89 | 0.0028013 | 0.00069788 | -0.0027984 | -0.00070134 | 2.9485e-06 | -3.4551e-06 | 0.0042774 | 0.0042793 | 0.0042793 | 0.97418 | -0.49957 | 0.97306 | -0.52173 | 1.1756
90 | 0.030773 | 0.0077308 | -0.030754 | -0.0077194 | 1.8341e-05 | 1.1448e-05 | 0.046384 | 0.046384 | 0.046384 | 0.98734 | -0.24276 | 0.98669 | -0.25525 | 12.7429
91 | 0.028262 | 0.0070947 | -0.028237 | -0.0070796 | 2.4398e-05 | 1.5158e-05 | 0.042625 | 0.042626 | 0.042626 | 0.98669 | -0.25525 | 0.98576 | -0.27337 | 11.7103
92 | 0.014516 | 0.0036389 | -0.014516 | -0.0036384 | 9.5087e-07 | 5.4124e-07 | 0.021913 | 0.021913 | 0.021913 | 0.98576 | -0.27337 | 0.98569 | -0.27474 | 6.0201
93 | 0.013721 | 0.0034406 | -0.013717 | -0.0034384 | 4.0298e-06 | 2.2599e-06 | 0.020713 | 0.020713 | 0.020713 | 0.98576 | -0.27337 | 0.98545 | -0.27953 | 5.6903
94 | 0.013576 | 0.0034029 | -0.013574 | -0.0034017 | 2.1893e-06 | 1.224e-06 | 0.020494 | 0.020495 | 0.020495 | 0.98569 | -0.27474 | 0.98552 | -0.27813 | 5.6304
95 | 0.0096849 | 0.0024279 | -0.0096848 | -0.0024278 | 1.5631e-07 | 7.521e-08 | 0.014624 | 0.014624 | 0.014624 | 0.98545 | -0.27953 | 0.98543 | -0.27987 | 4.0177
96 | -0.27951 | -0.071144 | 0.27984 | 0.071355 | 0.00033071 | 0.00021061 | 0.41832 | 0.41832 | 0.41832 | 0.99518 | -0.091504 | 0.99647 | -0.066994 | 28.7307
97 | -0.27984 | -0.071355 | 0.28016 | 0.07156 | 0.00032172 | 0.00020488 | 0.41832 | 0.41832 | 0.41832 | 0.99647 | -0.066994 | 0.99772 | -0.043211 | 28.7306
98 | -0.0014551 | -0.00036467 | 0.0014551 | 0.00036459 | 1.2676e-08 | -8.6486e-08 | 0.0021652 | 0.0021651 | 0.0021652 | 0.99999 | -0.00018289 | 1 | 0 | 0.59483
99 | 0.022555 | 0.0056621 | -0.022546 | -0.0056565 | 9.1489e-06 | 5.5713e-06 | 0.033566 | 0.033566 | 0.033566 | 1 | 0 | 0.99956 | -0.0085074 | 9.2214
100 | 0.04379 | 0.011074 | -0.043604 | -0.010957 | 0.00018586 | 0.00011743 | 0.065195 | 0.065196 | 0.065196 | 1 | 0 | 0.99537 | -0.088885 | 17.911
101 | 0.2867 | 0.073429 | -0.2861 | -0.073048 | 0.00059884 | 0.00038142 | 0.42717 | 0.42717 | 0.42717 | 1 | 0 | 0.99772 | -0.043211 | 29.3387
102 | -0.0049959 | -0.0012521 | 0.0049964 | 0.0012521 | 5.8671e-07 | 2.5951e-08 | 0.0075479 | 0.0075478 | 0.0075479 | 0.9849 | -0.29016 | 0.98503 | -0.2877 | 2.0736
103 | -0.0089169 | -0.0022347 | 0.0089202 | 0.0022362 | 3.3247e-06 | 1.5056e-06 | 0.01347 | 0.01347 | 0.01347 | 0.98503 | -0.2877 | 0.98543 | -0.27987 | 3.7006
104 | 0.022546 | 0.0056565 | -0.022533 | -0.0056483 | 1.3546e-05 | 8.2494e-06 | 0.033566 | 0.033566 | 0.033566 | 0.99956 | -0.0085074 | 0.9989 | -0.021117 | 9.2215
105 | 0.03229 | 0.0081192 | -0.032284 | -0.0081155 | 5.9673e-06 | 3.7304e-06 | 0.048281 | 0.048281 | 0.048281 | 0.99537 | -0.088885 | 0.99517 | -0.092755 | 13.264
106 | 0.011314 | 0.0028378 | -0.011306 | -0.0028336 | 8.1985e-06 | 4.2547e-06 | 0.016915 | 0.016915 | 0.016915 | 0.99537 | -0.088885 | 0.99458 | -0.1041 | 4.6471
107 | 0.029145 | 0.0073289 | -0.029135 | -0.0073221 | 1.097e-05 | 6.8211e-06 | 0.043588 | 0.043588 | 0.043588 | 0.99517 | -0.092755 | 0.99476 | -0.10064 | 11.9748
108 | 0.025572 | 0.0064291 | -0.025563 | -0.0064236 | 9.0415e-06 | 5.5728e-06 | 0.038259 | 0.038259 | 0.038259 | 0.99476 | -0.10064 | 0.99437 | -0.10805 | 10.5107
109 | 0.012659 | 0.0031733 | -0.012656 | -0.0031716 | 3.2759e-06 | 1.7751e-06 | 0.018858 | 0.018858 | 0.018858 | 0.9989 | -0.021117 | 0.99862 | -0.026549 | 5.1807
110 | 0.0098737 | 0.002475 | -0.0098717 | -0.002474 | 1.9781e-06 | 9.4689e-07 | 0.014708 | 0.014709 | 0.014709 | 0.9989 | -0.021117 | 0.99868 | -0.025323 | 4.0408
111 | 0.024652 | 0.0061953 | -0.024631 | -0.0061822 | 2.1367e-05 | 1.3132e-05 | 0.036896 | 0.036896 | 0.036896 | 0.99437 | -0.10805 | 0.99343 | -0.12622 | 10.1363
112 | 0.014653 | 0.0036738 | -0.014651 | -0.0036729 | 1.6073e-06 | 9.2267e-07 | 0.022409 | 0.022409 | 0.022409 | 0.97302 | -0.52248 | 0.97291 | -0.52478 | 6.1563
113 | -0.014653 | -0.0036738 | 0.014658 | 0.0036766 | 4.8864e-06 | 2.8049e-06 | 0.022409 | 0.022409 | 0.022409 | 0.97302 | -0.52248 | 0.97338 | -0.51548 | 6.1563
114 | -0.01792 | -0.0044941 | 0.017927 | 0.0044984 | 7.3087e-06 | 4.3546e-06 | 0.027395 | 0.027395 | 0.027395 | 0.97338 | -0.51548 | 0.97381 | -0.50693 | 7.5261
115 | -0.020634 | -0.0051769 | 0.020639 | 0.0051801 | 5.151e-06 | 3.1247e-06 | 0.031532 | 0.031532 | 0.031532 | 0.97381 | -0.50693 | 0.97408 | -0.50169 | 8.6626
116 | -0.025305 | -0.0063495 | 0.025312 | 0.0063538 | 6.9157e-06 | 4.2724e-06 | 0.03866 | 0.03866 | 0.03866 | 0.97408 | -0.50169 | 0.97437 | -0.49596 | 10.6208
117 | 0.0034158 | 0.00085594 | -0.0034157 | -0.00085605 | 1.5724e-07 | -1.1112e-07 | 0.0050898 | 0.0050899 | 0.0050899 | 0.99862 | -0.026549 | 0.99857 | -0.027516 | 1.3983
118 | 0.0092398 | 0.0023156 | -0.0092395 | -0.0023154 | 3.6616e-07 | 1.6696e-07 | 0.013768 | 0.013768 | 0.013768 | 0.99862 | -0.026549 | 0.99858 | -0.027381 | 3.7824
119 | 0.0056268 | 0.0014102 | -0.0056267 | -0.0014101 | 1.4509e-07 | 2.0833e-08 | 0.0083838 | 0.0083838 | 0.0083838 | 0.99868 | -0.025323 | 0.99865 | -0.025864 | 2.3032
120 | -0.011591 | -0.0029046 | 0.011592 | 0.002905 | 6.4859e-07 | 3.4316e-07 | 0.017502 | 0.017502 | 0.017502 | 0.98546 | -0.2793 | 0.98552 | -0.27813 | 4.8083
121 | -0.026581 | -0.0066718 | 0.026591 | 0.0066778 | 9.6454e-06 | 5.9786e-06 | 0.040598 | 0.040598 | 0.040598 | 0.97437 | -0.49596 | 0.97475 | -0.48836 | 11.1532
122 | -0.028862 | -0.007247 | 0.02887 | 0.0072518 | 7.7126e-06 | 4.804e-06 | 0.044064 | 0.044064 | 0.044064 | 0.97475 | -0.48836 | 0.97504 | -0.48276 | 12.1056
123 | -0.029967 | -0.0075267 | 0.029978 | 0.0075337 | 1.1212e-05 | 6.9971e-06 | 0.045739 | 0.045739 | 0.045739 | 0.97504 | -0.48276 | 0.97544 | -0.47492 | 12.5655
124 | -0.031416 | -0.007894 | 0.031425 | 0.0079001 | 9.7406e-06 | 6.0928e-06 | 0.047932 | 0.047932 | 0.047932 | 0.97544 | -0.47492 | 0.97577 | -0.46843 | 13.168
125 | -0.0023311 | -0.00058422 | 0.0023311 | 0.00058405 | 7.5268e-08 | -1.6937e-07 | 0.0034739 | 0.0034739 | 0.0034739 | 0.99848 | -0.029213 | 0.99852 | -0.028535 | 0.95438
126 | -0.006622 | -0.0016594 | 0.0066223 | 0.0016595 | 3.6405e-07 | 1.0258e-07 | 0.0098682 | 0.0098681 | 0.0098682 | 0.99852 | -0.028535 | 0.99858 | -0.027381 | 2.711
127 | 0.0086981 | 0.0021798 | -0.0086979 | -0.0021797 | 2.0266e-07 | 8.8786e-08 | 0.013053 | 0.013053 | 0.013053 | 0.9916 | -0.16177 | 0.99157 | -0.16226 | 3.5859
128 | 0.0021138 | 0.00052973 | -0.0021138 | -0.00052977 | 1.3669e-08 | -3.9328e-08 | 0.0031496 | 0.0031496 | 0.0031496 | 0.99865 | -0.025864 | 0.99865 | -0.026 | 0.86528
129 | 0.033853 | 0.0085176 | -0.033847 | -0.0085135 | 6.4669e-06 | 4.0578e-06 | 0.051596 | 0.051596 | 0.051596 | 0.97655 | -0.45311 | 0.97634 | -0.45711 | 14.1748
130 | 0.032228 | 0.0081079 | -0.032211 | -0.008097 | 1.7417e-05 | 1.0906e-05 | 0.04913 | 0.04913 | 0.04913 | 0.97634 | -0.45711 | 0.97577 | -0.46843 | 13.4972

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35615 | 0.090531

## res_load
| p_mw | q_mvar
0 | 0.00060153 | 0.00015076
1 | 0.0011158 | 0.00027965
2 | 0.0036248 | 0.00090847
3 | 0.00282 | 0.00070676
4 | 0.0010271 | 0.00025742
5 | 0.0021226 | 0.00053197
6 | 0.0011754 | 0.00029458
7 | 0.0013164 | 0.00032993
8 | 0.0012188 | 0.00030545
9 | 0.0026811 | 0.00067195
10 | 0.0032083 | 0.00080407
11 | 0.0040181 | 0.001007
12 | 0.0013925 | 0.000349
13 | 0.0018762 | 0.00047023
14 | 0.0059368 | 0.0014879
15 | 0.0034364 | 0.00086125
16 | 0.013424 | 0.0033644
17 | 0.0043504 | 0.0010903
18 | 0.010138 | 0.0025408
19 | 0.0036343 | 0.00091083
20 | 0.0018358 | 0.00046009
21 | 0.0046323 | 0.001161
22 | 0.042118 | 0.010556
23 | 0.0029932 | 0.00075016
24 | 0.0061187 | 0.0015335
25 | 0.0031125 | 0.00078006
26 | 0.0017374 | 0.00043544
27 | 0.0020575 | 0.00051565
28 | 0.0026533 | 0.00066499
29 | 0.0028199 | 0.00070673
30 | 0.0017287 | 0.00043326
31 | 0.0030865 | 0.00077356
32 | 0.0033572 | 0.00084139
33 | 0.0011844 | 0.00029683
34 | 0.0023762 | 0.00059553
35 | 0.0024526 | 0.00061469
36 | 0.0012008 | 0.00030095
37 | 0.0032066 | 0.00080364
38 | 0.0017278 | 0.00043304
39 | 0.0037386 | 0.00093698
40 | 0.0025042 | 0.0006276
41 | 0.0024877 | 0.00062347
42 | 0.0010817 | 0.00027109
43 | 0.0025981 | 0.00065115
44 | 0.0017959 | 0.00045009
45 | 0.0059487 | 0.0014909
46 | 0.00072032 | 0.00018053
47 | 0.0023752 | 0.00059528
48 | 0.00098661 | 0.00024727
49 | 0.002389 | 0.00059873
50 | 0.003202 | 0.00080249
51 | 0.00091262 | 0.00022872
52 | 0.0020045 | 0.00050237
53 | 0.0043588 | 0.0010924
54 | 0.010276 | 0.0025754
55 | 0.0034647 | 0.00086832
56 | 0.0062072 | 0.0015557
57 | 0.001779 | 0.00044587
58 | 0.0038327 | 0.00096056
59 | 0.0012781 | 0.00032033
60 | 0.0011286 | 0.00028284
61 | 0.0013278 | 0.00033279
62 | 0.00088235 | 0.00022114
63 | 0.00066461 | 0.00016657
64 | 0.0068141 | 0.0017078
65 | 0.0027984 | 0.00070134
66 | 0.0024157 | 0.00060542
67 | 0.0018114 | 0.00045399
68 | 0.0024923 | 0.00062463
69 | 0.00093966 | 0.0002355
70 | 0.004032 | 0.0010105
71 | 0.0058287 | 0.0014608
72 | 0.0014551 | 0.00036467
73 | 0.0059369 | 0.0014879
74 | 0.0049959 | 0.0012521
75 | 0.0039204 | 0.00098255
76 | 0.0007646 | 0.00019163
77 | 0.011306 | 0.0028336
78 | 0.0031385 | 0.00078659
79 | 0.0035629 | 0.00089294
80 | 0.0009107 | 0.00022824
81 | 0.0052736 | 0.0013217
82 | 0.0032617 | 0.00081746
83 | 0.0027073 | 0.00067851
84 | 0.0046661 | 0.0011694
85 | 0.0042449 | 0.0010639
86 | 0.0016295 | 0.00040839
87 | 0.0019818 | 0.00049668
88 | 0.0012691 | 0.00031806
89 | 0.002271 | 0.00056916
90 | 0.001097 | 0.00027494
91 | 0.0014377 | 0.00036031
92 | 0.0023311 | 0.00058422
93 | 0.0042908 | 0.0010754
94 | 0.0026171 | 0.00065592
95 | 0.0034157 | 0.00085605
96 | 0.0031993 | 0.00080182
97 | 0.0016893 | 0.00042339
98 | 0.0028077 | 0.00070367
99 | 0.0035128 | 0.0008804
100 | 0.0021138 | 0.00052977
101 | 0.00086925 | 0.00021785
102 | 0.0016185 | 0.00040562
103 | 0.00078562 | 0.00019689

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1