## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2145-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2145-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2145-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2145-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2145-1_0_4_node_139 | 0.4 | n |  | TRUE
5 | bus_LV_2145-1_0_4_node_138 | 0.4 | n |  | TRUE
6 | bus_LV_2145-1_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2145-1_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_2145-1_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2145-1_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2145-1_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2145-1_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2145-1_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2145-1_0_4_node_238 | 0.4 | n |  | TRUE
14 | bus_LV_2145-1_0_4_node_244 | 0.4 | n |  | TRUE
15 | bus_LV_2145-1_0_4_node_239 | 0.4 | n |  | TRUE
16 | bus_LV_2145-1_0_4_node_197 | 0.4 | n |  | TRUE
17 | bus_LV_2145-1_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2145-1_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_2145-1_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_2145-1_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2145-1_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2145-1_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_2145-1_0_4_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_2145-1_0_4_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_2145-1_0_4_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_2145-1_0_4_node_132 | 0.4 | n |  | TRUE
27 | bus_LV_2145-1_0_4_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_2145-1_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_2145-1_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2145-1_0_4_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_2145-1_0_4_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2145-1_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_2145-1_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_2145-1_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_2145-1_0_4_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_2145-1_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_2145-1_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_2145-1_0_4_node_54 | 0.4 | n |  | TRUE
39 | bus_LV_2145-1_0_4_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_2145-1_0_4_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_2145-1_0_4_node_52 | 0.4 | n |  | TRUE
42 | bus_LV_2145-1_0_4_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_2145-1_0_4_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_2145-1_0_4_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_2145-1_0_4_node_84 | 0.4 | n |  | TRUE
46 | bus_LV_2145-1_0_4_node_83 | 0.4 | n |  | TRUE
47 | bus_LV_2145-1_0_4_node_136 | 0.4 | n |  | TRUE
48 | bus_LV_2145-1_0_4_node_90 | 0.4 | n |  | TRUE
49 | bus_LV_2145-1_0_4_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_2145-1_0_4_node_60 | 0.4 | n |  | TRUE
51 | bus_LV_2145-1_0_4_node_59 | 0.4 | n |  | TRUE
52 | bus_LV_2145-1_0_4_node_58 | 0.4 | n |  | TRUE
53 | bus_LV_2145-1_0_4_node_61 | 0.4 | n |  | TRUE
54 | bus_LV_2145-1_0_4_node_69 | 0.4 | n |  | TRUE
55 | bus_LV_2145-1_0_4_node_68 | 0.4 | n |  | TRUE
56 | bus_LV_2145-1_0_4_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_2145-1_0_4_node_33 | 0.4 | n |  | TRUE
58 | bus_LV_2145-1_0_4_node_140 | 0.4 | n |  | TRUE
59 | bus_LV_2145-1_0_4_node_141 | 0.4 | n |  | TRUE
60 | bus_LV_2145-1_0_4_node_177 | 0.4 | n |  | TRUE
61 | bus_LV_2145-1_0_4_node_133 | 0.4 | n |  | TRUE
62 | bus_LV_2145-1_0_4_node_107 | 0.4 | n |  | TRUE
63 | bus_LV_2145-1_0_4_node_82 | 0.4 | n |  | TRUE
64 | bus_LV_2145-1_0_4_node_91 | 0.4 | n |  | TRUE
65 | bus_LV_2145-1_0_4_node_39 | 0.4 | n |  | TRUE
66 | bus_LV_2145-1_0_4_node_40 | 0.4 | n |  | TRUE
67 | bus_LV_2145-1_0_4_node_41 | 0.4 | n |  | TRUE
68 | bus_LV_2145-1_0_4_node_70 | 0.4 | n |  | TRUE
69 | bus_LV_2145-1_0_4_node_55 | 0.4 | n |  | TRUE
70 | bus_LV_2145-1_0_4_node_103 | 0.4 | n |  | TRUE
71 | bus_LV_2145-1_0_4_node_100 | 0.4 | n |  | TRUE
72 | bus_LV_2145-1_0_4_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_2145-1_0_4_node_45 | 0.4 | n |  | TRUE
74 | bus_LV_2145-1_0_4_node_46 | 0.4 | n |  | TRUE
75 | bus_LV_2145-1_0_4_node_47 | 0.4 | n |  | TRUE
76 | bus_LV_2145-1_0_4_node_81 | 0.4 | n |  | TRUE
77 | bus_LV_2145-1_0_4_node_48 | 0.4 | n |  | TRUE
78 | bus_LV_2145-1_0_4_node_77 | 0.4 | n |  | TRUE
79 | bus_LV_2145-1_0_4_node_49 | 0.4 | n |  | TRUE
80 | bus_LV_2145-1_0_4_node_50 | 0.4 | n |  | TRUE
81 | bus_LV_2145-1_0_4_node_53 | 0.4 | n |  | TRUE
82 | bus_LV_2145-1_0_4_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_2145-1_0_4_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_2145-1_0_4_node_63 | 0.4 | n |  | TRUE
85 | bus_LV_2145-1_0_4_node_57 | 0.4 | n |  | TRUE
86 | bus_LV_2145-1_0_4_node_62 | 0.4 | n |  | TRUE
87 | bus_LV_2145-1_0_4_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_2145-1_0_4_node_67 | 0.4 | n |  | TRUE
89 | bus_LV_2145-1_0_4_node_131 | 0.4 | n |  | TRUE
90 | bus_LV_2145-1_0_4_node_129 | 0.4 | n |  | TRUE
91 | bus_LV_2145-1_0_4_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_2145-1_0_4_node_72 | 0.4 | n |  | TRUE
93 | bus_LV_2145-1_0_4_node_73 | 0.4 | n |  | TRUE
94 | bus_LV_2145-1_0_4_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_2145-1_0_4_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_2145-1_0_4_node_76 | 0.4 | n |  | TRUE
97 | bus_LV_2145-1_0_4_node_78 | 0.4 | n |  | TRUE
98 | bus_LV_2145-1_0_4_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_2145-1_0_4_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_2145-1_0_4_node_106 | 0.4 | n |  | TRUE
101 | bus_LV_2145-1_0_4_node_92 | 0.4 | n |  | TRUE
102 | bus_LV_2145-1_0_4_node_135 | 0.4 | n |  | TRUE
103 | bus_LV_2145-1_0_4_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_2145-1_0_4_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_2145-1_0_4_node_101 | 0.4 | n |  | TRUE
106 | bus_LV_2145-1_0_4_node_102 | 0.4 | n |  | TRUE
107 | bus_LV_2145-1_0_4_node_104 | 0.4 | n |  | TRUE
108 | bus_LV_2145-1_0_4_node_126 | 0.4 | n |  | TRUE
109 | bus_LV_2145-1_0_4_node_105 | 0.4 | n |  | TRUE
110 | bus_LV_2145-1_0_4_node_200 | 0.4 | n |  | TRUE
111 | bus_LV_2145-1_0_4_node_148 | 0.4 | n |  | TRUE
112 | bus_LV_2145-1_0_4_node_127 | 0.4 | n |  | TRUE
113 | bus_LV_2145-1_0_4_node_228 | 0.4 | n |  | TRUE
114 | bus_LV_2145-1_0_4_node_146 | 0.4 | n |  | TRUE
115 | bus_LV_2145-1_0_4_node_128 | 0.4 | n |  | TRUE
116 | bus_LV_2145-1_0_4_node_130 | 0.4 | n |  | TRUE
117 | bus_LV_2145-1_0_4_node_175 | 0.4 | n |  | TRUE
118 | bus_LV_2145-1_0_4_node_147 | 0.4 | n |  | TRUE
119 | bus_LV_2145-1_0_4_node_173 | 0.4 | n |  | TRUE
120 | bus_LV_2145-1_0_4_node_134 | 0.4 | n |  | TRUE
121 | bus_LV_2145-1_0_4_node_176 | 0.4 | n |  | TRUE
122 | bus_LV_2145-1_0_4_node_142 | 0.4 | n |  | TRUE
123 | bus_LV_2145-1_0_4_node_143 | 0.4 | n |  | TRUE
124 | bus_LV_2145-1_0_4_node_144 | 0.4 | n |  | TRUE
125 | bus_LV_2145-1_0_4_node_145 | 0.4 | n |  | TRUE
126 | bus_LV_2145-1_0_4_node_174 | 0.4 | n |  | TRUE
127 | bus_LV_2145-1_0_4_node_178 | 0.4 | n |  | TRUE
128 | bus_LV_2145-1_0_4_node_193 | 0.4 | n |  | TRUE
129 | bus_LV_2145-1_0_4_node_195 | 0.4 | n |  | TRUE
130 | bus_LV_2145-1_0_4_node_196 | 0.4 | n |  | TRUE
131 | bus_LV_2145-1_0_4_node_191 | 0.4 | n |  | TRUE
132 | bus_LV_2145-1_0_4_node_179 | 0.4 | n |  | TRUE
133 | bus_LV_2145-1_0_4_node_180 | 0.4 | n |  | TRUE
134 | bus_LV_2145-1_0_4_node_181 | 0.4 | n |  | TRUE
135 | bus_LV_2145-1_0_4_node_182 | 0.4 | n |  | TRUE
136 | bus_LV_2145-1_0_4_node_183 | 0.4 | n |  | TRUE
137 | bus_LV_2145-1_0_4_node_233 | 0.4 | n |  | TRUE
138 | bus_LV_2145-1_0_4_node_213 | 0.4 | n |  | TRUE
139 | bus_LV_2145-1_0_4_node_192 | 0.4 | n |  | TRUE
140 | bus_LV_2145-1_0_4_node_194 | 0.4 | n |  | TRUE
141 | bus_LV_2145-1_0_4_node_198 | 0.4 | n |  | TRUE
142 | bus_LV_2145-1_0_4_node_199 | 0.4 | n |  | TRUE
143 | bus_LV_2145-1_0_4_node_212 | 0.4 | n |  | TRUE
144 | bus_LV_2145-1_0_4_node_209 | 0.4 | n |  | TRUE
145 | bus_LV_2145-1_0_4_node_214 | 0.4 | n |  | TRUE
146 | bus_LV_2145-1_0_4_node_215 | 0.4 | n |  | TRUE
147 | bus_LV_2145-1_0_4_node_210 | 0.4 | n |  | TRUE
148 | bus_LV_2145-1_0_4_node_211 | 0.4 | n |  | TRUE
149 | bus_MV_32_0_node_108 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2145-1_0_4_load_0 | 0 | 0.0067606 | 0.0016944 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2145-1_0_4_load_139 | 4 | 0.006397 | 0.0016032 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2145-1_0_4_load_7 | 6 | 0.0015755 | 0.00039486 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2145-1_0_4_load_6 | 9 | 0.00076839 | 0.00019258 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2145-1_0_4_load_8 | 10 | 0.0020347 | 0.00050994 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2145-1_0_4_load_9 | 11 | 0.0013542 | 0.0003394 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2145-1_0_4_load_10 | 12 | 0.0083451 | 0.0020915 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2145-1_0_4_load_238 | 13 | 0.0036387 | 0.00091195 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2145-1_0_4_load_244 | 14 | 0.0012757 | 0.00031972 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2145-1_0_4_load_239 | 15 | 0.003668 | 0.00091928 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2145-1_0_4_load_197 | 16 | 0.0027201 | 0.00068172 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2145-1_0_4_load_11 | 17 | 0.0016684 | 0.00041814 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2145-1_0_4_load_12 | 18 | 0.0017242 | 0.00043212 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2145-1_0_4_load_13 | 19 | 0.0021846 | 0.00054751 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2145-1_0_4_load_16 | 22 | 0.0019576 | 0.00049063 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2145-1_0_4_load_34 | 23 | 0.0013063 | 0.00032739 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2145-1_0_4_load_30 | 25 | 0.0020401 | 0.00051129 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2145-1_0_4_load_132 | 26 | 0.0020822 | 0.00052186 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2145-1_0_4_load_28 | 28 | 0.0021086 | 0.00052848 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2145-1_0_4_load_25 | 29 | 0.013354 | 0.0033469 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2145-1_0_4_load_17 | 31 | 0.0022391 | 0.00056118 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2145-1_0_4_load_24 | 37 | 0.0029462 | 0.00073839 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2145-1_0_4_load_54 | 38 | 0.003076 | 0.00077092 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2145-1_0_4_load_29 | 40 | 0.0029109 | 0.00072955 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2145-1_0_4_load_52 | 41 | 0.0016145 | 0.00040463 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2145-1_0_4_load_36 | 43 | 0.0015042 | 0.00037698 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2145-1_0_4_load_37 | 44 | 0.0012785 | 0.00032041 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2145-1_0_4_load_84 | 45 | 0.0030809 | 0.00077215 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2145-1_0_4_load_83 | 46 | 0.0027002 | 0.00067673 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2145-1_0_4_load_136 | 47 | 0.0032298 | 0.00080946 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2145-1_0_4_load_90 | 48 | 0.0049463 | 0.0012397 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2145-1_0_4_load_38 | 49 | 0.00046355 | 0.00011618 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2145-1_0_4_load_60 | 50 | 0.0046522 | 0.001166 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2145-1_0_4_load_59 | 51 | 0.0056383 | 0.0014131 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2145-1_0_4_load_58 | 52 | 0.0047874 | 0.0011998 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2145-1_0_4_load_61 | 53 | 0.0044134 | 0.0011061 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2145-1_0_4_load_69 | 54 | 0.0034953 | 0.000876 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2145-1_0_4_load_68 | 55 | 0.00027778 | 6.9618e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2145-1_0_4_load_32 | 56 | 0.0042417 | 0.0010631 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2145-1_0_4_load_33 | 57 | 0.0033411 | 0.00083736 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2145-1_0_4_load_140 | 58 | 0.0019895 | 0.00049862 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2145-1_0_4_load_141 | 59 | 0.0023804 | 0.00059659 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2145-1_0_4_load_177 | 60 | 0.0022949 | 0.00057517 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2145-1_0_4_load_133 | 61 | 0.0020347 | 0.00050993 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2145-1_0_4_load_107 | 62 | 0.0010176 | 0.00025504 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2145-1_0_4_load_82 | 63 | 0.004078 | 0.001022 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2145-1_0_4_load_40 | 66 | 0.0034763 | 0.00087123 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2145-1_0_4_load_70 | 68 | 0.00033726 | 8.4525e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2145-1_0_4_load_55 | 69 | 0.00036103 | 9.0482e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2145-1_0_4_load_103 | 70 | 0.00035812 | 8.9752e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2145-1_0_4_load_56 | 72 | 0.0013151 | 0.00032958 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2145-1_0_4_load_45 | 73 | 0.0012199 | 0.00030573 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2145-1_0_4_load_46 | 74 | 0.0020863 | 0.00052287 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2145-1_0_4_load_81 | 76 | 0.00088992 | 0.00022304 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2145-1_0_4_load_48 | 77 | 0.0014924 | 0.00037404 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2145-1_0_4_load_77 | 78 | 0.0005071 | 0.00012709 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2145-1_0_4_load_49 | 79 | 0.00030557 | 7.6583e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2145-1_0_4_load_50 | 80 | 0.0076297 | 0.0019122 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2145-1_0_4_load_53 | 81 | 0.0028125 | 0.00070489 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2145-1_0_4_load_65 | 83 | 0.0072053 | 0.0018058 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2145-1_0_4_load_57 | 85 | 0.001371 | 0.00034359 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2145-1_0_4_load_62 | 86 | 0.00014581 | 3.6543e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2145-1_0_4_load_66 | 87 | 0.0026093 | 0.00065396 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2145-1_0_4_load_67 | 88 | 0.0067519 | 0.0016922 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2145-1_0_4_load_131 | 89 | 0.0047 | 0.0011779 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2145-1_0_4_load_129 | 90 | 0.0044747 | 0.0011215 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2145-1_0_4_load_71 | 91 | 0.00054244 | 0.00013595 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2145-1_0_4_load_72 | 92 | 0.0031663 | 0.00079356 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2145-1_0_4_load_73 | 93 | 0.00054003 | 0.00013534 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2145-1_0_4_load_74 | 94 | 0.0006016 | 0.00015077 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2145-1_0_4_load_75 | 95 | 0.00057975 | 0.0001453 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2145-1_0_4_load_78 | 97 | 0.002562 | 0.0006421 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2145-1_0_4_load_80 | 99 | 0.0038617 | 0.00096784 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2145-1_0_4_load_106 | 100 | 0.00043295 | 0.00010851 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2145-1_0_4_load_135 | 102 | 0.0056884 | 0.0014257 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2145-1_0_4_load_98 | 103 | 0.00045928 | 0.00011511 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2145-1_0_4_load_99 | 104 | 0.0081821 | 0.0020506 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2145-1_0_4_load_101 | 105 | 0.0051001 | 0.0012782 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2145-1_0_4_load_102 | 106 | 0.001717 | 0.00043032 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2145-1_0_4_load_104 | 107 | 0.0021638 | 0.00054229 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2145-1_0_4_load_126 | 108 | 0.0051001 | 0.0012782 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2145-1_0_4_load_200 | 110 | 0.0022975 | 0.0005758 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2145-1_0_4_load_148 | 111 | 0.003278 | 0.00082153 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2145-1_0_4_load_146 | 114 | 0.0040012 | 0.0010028 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2145-1_0_4_load_128 | 115 | 0.0010205 | 0.00025577 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2145-1_0_4_load_130 | 116 | 0.0032551 | 0.00081581 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2145-1_0_4_load_147 | 118 | 0.0022236 | 0.00055729 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2145-1_0_4_load_173 | 119 | 0.0028967 | 0.00072598 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2145-1_0_4_load_134 | 120 | 0.001452 | 0.00036391 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2145-1_0_4_load_176 | 121 | 0.0027047 | 0.00067786 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2145-1_0_4_load_142 | 122 | 0.0044682 | 0.0011198 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2145-1_0_4_load_143 | 123 | 0.00090517 | 0.00022686 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2145-1_0_4_load_144 | 124 | 0.0040798 | 0.0010225 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2145-1_0_4_load_145 | 125 | 0.0030609 | 0.00076714 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2145-1_0_4_load_174 | 126 | 0.0035385 | 0.00088682 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2145-1_0_4_load_178 | 127 | 0.0026574 | 0.00066601 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2145-1_0_4_load_195 | 129 | 0.0020809 | 0.00052152 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2145-1_0_4_load_196 | 130 | 0.0011506 | 0.00028837 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2145-1_0_4_load_191 | 131 | 0.0045533 | 0.0011412 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2145-1_0_4_load_179 | 132 | 0.0021675 | 0.00054324 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2145-1_0_4_load_180 | 133 | 0.0029189 | 0.00073155 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2145-1_0_4_load_181 | 134 | 0.0089013 | 0.0022309 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2145-1_0_4_load_182 | 135 | 0.0017128 | 0.00042927 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2145-1_0_4_load_183 | 136 | 0.0018623 | 0.00046673 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2145-1_0_4_load_233 | 137 | 0.0016033 | 0.00040183 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2145-1_0_4_load_213 | 138 | 0.0018244 | 0.00045724 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2145-1_0_4_load_192 | 139 | 0.0034925 | 0.00087531 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2145-1_0_4_load_194 | 140 | 0.0022453 | 0.00056272 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2145-1_0_4_load_198 | 141 | 0.0026855 | 0.00067305 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2145-1_0_4_load_209 | 144 | 0.0023389 | 0.00058619 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2145-1_0_4_load_214 | 145 | 0.0029239 | 0.00073279 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2145-1_0_4_load_215 | 146 | 0.0029005 | 0.00072695 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2145-1_0_4_load_210 | 147 | 0.0016386 | 0.00041067 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2145-1_0_4_load_211 | 148 | 0.0017586 | 0.00044076 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2145-1_0_4_line_0 |  | 0 | 1 | 0.013838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2145-1_0_4_line_1 |  | 1 | 2 | 0.034915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2145-1_0_4_line_2 |  | 1 | 3 | 0.01297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2145-1_0_4_line_3 |  | 2 | 4 | 0.054688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2145-1_0_4_line_4 |  | 3 | 6 | 0.067787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2145-1_0_4_line_5 |  | 4 | 5 | 0.047776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2145-1_0_4_line_6 |  | 5 | 120 | 0.021016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2145-1_0_4_line_7 |  | 7 | 8 | 0.00998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2145-1_0_4_line_8 |  | 7 | 9 | 0.018221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2145-1_0_4_line_9 |  | 8 | 10 | 0.019023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2145-1_0_4_line_10 |  | 8 | 11 | 0.054147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2145-1_0_4_line_11 |  | 9 | 12 | 0.0079144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2145-1_0_4_line_12 |  | 10 | 13 | 0.015345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2145-1_0_4_line_13 |  | 11 | 14 | 0.042969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2145-1_0_4_line_14 |  | 12 | 15 | 0.029119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2145-1_0_4_line_15 |  | 13 | 16 | 0.015227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2145-1_0_4_line_16 |  | 16 | 140 | 0.0015818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2145-1_0_4_line_17 |  | 17 | 18 | 0.014442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2145-1_0_4_line_18 |  | 17 | 19 | 0.029727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2145-1_0_4_line_19 |  | 19 | 20 | 0.020133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2145-1_0_4_line_20 |  | 20 | 21 | 0.009781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2145-1_0_4_line_21 |  | 20 | 22 | 0.018977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2145-1_0_4_line_22 |  | 21 | 23 | 0.02268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2145-1_0_4_line_23 |  | 21 | 24 | 0.046153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2145-1_0_4_line_24 |  | 22 | 25 | 0.031013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2145-1_0_4_line_25 |  | 23 | 26 | 0.00043466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2145-1_0_4_line_26 |  | 24 | 27 | 0.048759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2145-1_0_4_line_27 |  | 24 | 28 | 0.016296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2145-1_0_4_line_28 |  | 24 | 29 | 0.035213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2145-1_0_4_line_29 |  | 25 | 30 | 0.06169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2145-1_0_4_line_30 |  | 26 | 61 | 0.038644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2145-1_0_4_line_31 |  | 27 | 42 | 0.035498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2145-1_0_4_line_32 |  | 27 | 43 | 0.020724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2145-1_0_4_line_33 |  | 28 | 44 | 0.034514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2145-1_0_4_line_34 |  | 29 | 37 | 0.05149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2145-1_0_4_line_35 |  | 30 | 56 | 0.025041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2145-1_0_4_line_36 |  | 30 | 57 | 0.046632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2145-1_0_4_line_37 |  | 31 | 32 | 0.041693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2145-1_0_4_line_38 |  | 32 | 35 | 0.029793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2145-1_0_4_line_39 |  | 32 | 33 | 0.014308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2145-1_0_4_line_40 |  | 33 | 34 | 0.020619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2145-1_0_4_line_41 |  | 34 | 36 | 0.01637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2145-1_0_4_line_42 |  | 34 | 37 | 0.021327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2145-1_0_4_line_43 |  | 35 | 38 | 0.00712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2145-1_0_4_line_44 |  | 35 | 39 | 0.030789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2145-1_0_4_line_45 |  | 36 | 40 | 0.045644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2145-1_0_4_line_46 |  | 39 | 41 | 0.014049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2145-1_0_4_line_47 |  | 41 | 81 | 0.050843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2145-1_0_4_line_48 |  | 42 | 45 | 0.035018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2145-1_0_4_line_49 |  | 42 | 46 | 0.016685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2145-1_0_4_line_50 |  | 43 | 47 | 0.0103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2145-1_0_4_line_51 |  | 44 | 48 | 0.004367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2145-1_0_4_line_52 |  | 45 | 62 | 0.026242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2145-1_0_4_line_53 |  | 46 | 63 | 0.018276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2145-1_0_4_line_54 |  | 48 | 64 | 0.04534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2145-1_0_4_line_55 |  | 49 | 50 | 0.040357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2145-1_0_4_line_56 |  | 50 | 53 | 0.036841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2145-1_0_4_line_57 |  | 50 | 51 | 0.017369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2145-1_0_4_line_58 |  | 51 | 52 | 0.045673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2145-1_0_4_line_59 |  | 52 | 67 | 0.041035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2145-1_0_4_line_60 |  | 53 | 54 | 0.030114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2145-1_0_4_line_61 |  | 54 | 55 | 0.011998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2145-1_0_4_line_62 |  | 56 | 58 | 0.0063089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2145-1_0_4_line_63 |  | 57 | 59 | 0.021864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_2145-1_0_4_line_64 |  | 59 | 60 | 0.01817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_2145-1_0_4_line_65 |  | 60 | 121 | 0.042011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_2145-1_0_4_line_66 |  | 61 | 120 | 0.0056829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2145-1_0_4_line_67 |  | 62 | 100 | 0.024194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2145-1_0_4_line_68 |  | 63 | 99 | 0.0097383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2145-1_0_4_line_69 |  | 64 | 101 | 0.041476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2145-1_0_4_line_70 |  | 65 | 66 | 0.047249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2145-1_0_4_line_71 |  | 65 | 67 | 0.024578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2145-1_0_4_line_72 |  | 66 | 68 | 0.02459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2145-1_0_4_line_73 |  | 67 | 69 | 0.009408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2145-1_0_4_line_74 |  | 67 | 70 | 0.045555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2145-1_0_4_line_75 |  | 69 | 72 | 0.050268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2145-1_0_4_line_76 |  | 70 | 71 | 0.029723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2145-1_0_4_line_77 |  | 71 | 106 | 0.014158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2145-1_0_4_line_78 |  | 71 | 103 | 0.019983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2145-1_0_4_line_79 |  | 72 | 85 | 0.049348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2145-1_0_4_line_80 |  | 73 | 74 | 0.020912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2145-1_0_4_line_81 |  | 74 | 75 | 0.03857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2145-1_0_4_line_82 |  | 75 | 77 | 0.035457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2145-1_0_4_line_83 |  | 75 | 79 | 0.038714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2145-1_0_4_line_84 |  | 76 | 77 | 0.13965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2145-1_0_4_line_85 |  | 76 | 78 | 0.0066007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2145-1_0_4_line_86 |  | 78 | 95 | 0.0013855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2145-1_0_4_line_87 |  | 79 | 80 | 0.044668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2145-1_0_4_line_88 |  | 81 | 82 | 0.011953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2145-1_0_4_line_89 |  | 82 | 83 | 0.039725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2145-1_0_4_line_90 |  | 82 | 84 | 0.071152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2145-1_0_4_line_91 |  | 83 | 87 | 0.19496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2145-1_0_4_line_92 |  | 84 | 86 | 0.13596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2145-1_0_4_line_93 |  | 87 | 88 | 0.0020881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2145-1_0_4_line_94 |  | 89 | 90 | 0.031372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2145-1_0_4_line_95 |  | 90 | 112 | 0.017983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2145-1_0_4_line_96 |  | 91 | 92 | 0.020979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2145-1_0_4_line_97 |  | 91 | 93 | 0.0021249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2145-1_0_4_line_98 |  | 92 | 94 | 0.00231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2145-1_0_4_line_99 |  | 93 | 95 | 0.019656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2145-1_0_4_line_100 |  | 94 | 96 | 0.03986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2145-1_0_4_line_101 |  | 96 | 97 | 0.016505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2145-1_0_4_line_102 |  | 96 | 98 | 0.018002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2145-1_0_4_line_103 |  | 98 | 99 | 0.010289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2145-1_0_4_line_104 |  | 101 | 102 | 0.047521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2145-1_0_4_line_105 |  | 103 | 104 | 0.01832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2145-1_0_4_line_106 |  | 104 | 105 | 0.015716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2145-1_0_4_line_107 |  | 105 | 107 | 0.025944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2145-1_0_4_line_108 |  | 107 | 108 | 0.0079285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2145-1_0_4_line_109 |  | 108 | 112 | 0.017335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2145-1_0_4_line_110 |  | 109 | 110 | 0.050041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
111 | LV_2145-1_0_4_line_111 |  | 109 | 111 | 0.015973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
112 | LV_2145-1_0_4_line_112 |  | 110 | 113 | 0.014903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_2145-1_0_4_line_113 |  | 111 | 114 | 0.00026324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
114 | LV_2145-1_0_4_line_114 |  | 112 | 115 | 0.0069396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2145-1_0_4_line_115 |  | 113 | 141 | 0.041417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2145-1_0_4_line_116 |  | 114 | 124 | 0.025597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
117 | LV_2145-1_0_4_line_117 |  | 115 | 116 | 0.0097529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2145-1_0_4_line_118 |  | 116 | 117 | 0.043419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2145-1_0_4_line_119 |  | 117 | 118 | 0.018457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
120 | LV_2145-1_0_4_line_120 |  | 117 | 119 | 0.0025854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_2145-1_0_4_line_121 |  | 118 | 125 | 0.0039723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
122 | LV_2145-1_0_4_line_122 |  | 119 | 126 | 0.015188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
123 | LV_2145-1_0_4_line_123 |  | 121 | 126 | 0.019135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
124 | LV_2145-1_0_4_line_124 |  | 122 | 123 | 0.024446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
125 | LV_2145-1_0_4_line_125 |  | 122 | 124 | 0.0024966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_2145-1_0_4_line_126 |  | 123 | 125 | 0.0017976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
127 | LV_2145-1_0_4_line_127 |  | 127 | 128 | 0.014219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2145-1_0_4_line_128 |  | 128 | 129 | 0.037995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2145-1_0_4_line_129 |  | 128 | 130 | 0.023364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2145-1_0_4_line_130 |  | 128 | 131 | 0.011884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2145-1_0_4_line_131 |  | 129 | 141 | 0.0026822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2145-1_0_4_line_132 |  | 130 | 142 | 0.034723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2145-1_0_4_line_133 |  | 131 | 139 | 0.023342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2145-1_0_4_line_134 |  | 132 | 133 | 0.0043372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2145-1_0_4_line_135 |  | 132 | 134 | 0.0073911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2145-1_0_4_line_136 |  | 133 | 135 | 0.025157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2145-1_0_4_line_137 |  | 135 | 136 | 0.0030915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2145-1_0_4_line_138 |  | 136 | 137 | 0.026013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2145-1_0_4_line_139 |  | 137 | 138 | 0.00018466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2145-1_0_4_line_140 |  | 138 | 148 | 0.025645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2145-1_0_4_line_141 |  | 139 | 140 | 0.010865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2145-1_0_4_line_142 |  | 142 | 143 | 0.007142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2145-1_0_4_line_143 |  | 142 | 144 | 0.0037175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2145-1_0_4_line_144 |  | 143 | 145 | 0.01347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2145-1_0_4_line_145 |  | 143 | 146 | 0.016984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2145-1_0_4_line_146 |  | 144 | 147 | 0.03002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2145-1_0_4_line_147 |  | 147 | 148 | 0.0097982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2145-1_0_4_trafo_31 | 0.63 MVA 20/0.4 kV | 149 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2570615.9274 | 1160421.3559 | 2570606.7414 | 1160429.6273 | 2570605.9127 | 1160430.8499
1 | 2570615.9274 | 1160421.3559 | 2570618.3606 | 1160431.5491 | 2570623.7921 | 1160448.3865 | 2570626.8333 | 1160454.408
2 | 2570616.4544 | 1160408.4912 | 2570615.4005 | 1160415.4999 | 2570615.9274 | 1160421.3559
3 | 2570679.626 | 1160468.6791 | 2570626.8333 | 1160454.408
4 | 2570616.4544 | 1160408.4912 | 2570571.0805 | 1160386.725 | 2570554.8558 | 1160380.269
5 | 2570679.626 | 1160468.6791 | 2570683.8984 | 1160466.357 | 2570704.978 | 1160437.7506 | 2570708.9588 | 1160433.7736 | 2570710.6959 | 1160433.276
6 | 2570710.6959 | 1160433.276 | 2570727.9766 | 1160445.2355
7 | 2570504.4202 | 1160609.9653 | 2570510.6809 | 1160617.7496
8 | 2570504.4202 | 1160609.9653 | 2570489.3642 | 1160602.5579 | 2570488.0031 | 1160602.0831
9 | 2570510.6809 | 1160617.7496 | 2570522.5989 | 1160632.576
10 | 2570510.6809 | 1160617.7496 | 2570483.7583 | 1160625.0413 | 2570471.6765 | 1160641.1422 | 2570470.1876 | 1160647.0828
11 | 2570488.0031 | 1160602.0831 | 2570482.3558 | 1160600.1134 | 2570480.4241 | 1160600.1966
12 | 2570531.5303 | 1160644.9229 | 2570530.6811 | 1160642.6305 | 2570522.5989 | 1160632.576
13 | 2570483.6948 | 1160685.272 | 2570467.4754 | 1160657.9047 | 2570470.1876 | 1160647.0828
14 | 2570480.4241 | 1160600.1966 | 2570473.6218 | 1160600.4899 | 2570454.6889 | 1160612.2917
15 | 2570536.82 | 1160659.2016 | 2570531.5303 | 1160644.9229
16 | 2570536.82 | 1160659.2016 | 2570537.3695 | 1160660.6849
17 | 2570828.264 | 1160502.717 | 2570842.5979 | 1160500.9499
18 | 2570828.264 | 1160502.717 | 2570824.2378 | 1160503.2134 | 2570817.4511 | 1160502.2237 | 2570809.7287 | 1160499.4932 | 2570800.1863 | 1160494.8289
19 | 2570782.0984 | 1160485.9876 | 2570800.1863 | 1160494.8289
20 | 2570786.5466 | 1160477.2727 | 2570782.0984 | 1160485.9876
21 | 2570782.0984 | 1160485.9876 | 2570781.6202 | 1160486.9238 | 2570772.8893 | 1160502.5797
22 | 2570786.5466 | 1160477.2727 | 2570767.403 | 1160465.1113
23 | 2570786.5466 | 1160477.2727 | 2570807.2123 | 1160435.9845
24 | 2570755.0693 | 1160527.8562 | 2570757.3163 | 1160525.3617 | 2570768.2424 | 1160510.9122 | 2570772.8893 | 1160502.5797
25 | 2570767.0361 | 1160464.8782 | 2570767.403 | 1160465.1113
26 | 2570830.9609 | 1160393.503 | 2570819.5742 | 1160417.3038 | 2570807.2123 | 1160435.9845
27 | 2570807.2123 | 1160435.9845 | 2570793.5956 | 1160427.0325
28 | 2570807.2123 | 1160435.9845 | 2570835.133 | 1160457.4408
29 | 2570706.9682 | 1160565.8612 | 2570742.4309 | 1160541.8871 | 2570755.0693 | 1160527.8562
30 | 2570767.0361 | 1160464.8782 | 2570758.9348 | 1160459.7317 | 2570743.0752 | 1160455.6848 | 2570732.6496 | 1160448.4695
31 | 2570844.9639 | 1160360.874 | 2570830.9609 | 1160393.503
32 | 2570830.9609 | 1160393.503 | 2570827.3241 | 1160391.0306 | 2570817.9039 | 1160377.6961
33 | 2570764.7561 | 1160408.0727 | 2570793.5956 | 1160427.0325
34 | 2570875.96 | 1160488.8153 | 2570835.133 | 1160457.4408
35 | 2570706.9682 | 1160565.8612 | 2570692.2207 | 1160545.6241
36 | 2570706.9682 | 1160565.8612 | 2570667.6942 | 1160591.0031
37 | 2570927.0869 | 1160494.1092 | 2570934.8195 | 1160453.1399
38 | 2570955.6707 | 1160486.2556 | 2570948.0471 | 1160489.672 | 2570938.2193 | 1160492.0987 | 2570932.225 | 1160493.3172 | 2570927.0869 | 1160494.1092
39 | 2570912.9053 | 1160496.2902 | 2570927.0869 | 1160494.1092
40 | 2570893.0298 | 1160501.6004 | 2570898.8577 | 1160499.2376 | 2570904.9109 | 1160497.5185 | 2570908.8844 | 1160496.7655 | 2570912.9053 | 1160496.2902
41 | 2570882.0692 | 1160513.7376 | 2570888.1783 | 1160506.1819 | 2570893.0298 | 1160501.6004
42 | 2570893.0298 | 1160501.6004 | 2570879.4322 | 1160491.4836 | 2570875.96 | 1160488.8153
43 | 2570955.6707 | 1160486.2556 | 2570956.7861 | 1160479.2244
44 | 2570955.6707 | 1160486.2556 | 2570959.0352 | 1160484.7497 | 2570979.3782 | 1160466.7643
45 | 2570882.0692 | 1160513.7376 | 2570873.0997 | 1160527.1879 | 2570856.6512 | 1160551.649
46 | 2570979.3782 | 1160466.7643 | 2570987.9618 | 1160477.8866
47 | 2571024.5217 | 1160512.9056 | 2571023.5534 | 1160512.0735 | 2570999.4624 | 1160491.8909 | 2570995.3874 | 1160487.5084 | 2570987.9618 | 1160477.8866
48 | 2570844.9639 | 1160360.874 | 2570861.1631 | 1160373.2459 | 2570872.8619 | 1160382.0381
49 | 2570844.9639 | 1160360.874 | 2570851.6982 | 1160345.6081
50 | 2570811.9606 | 1160369.2832 | 2570817.9039 | 1160377.6961
51 | 2570764.7561 | 1160408.0727 | 2570761.107 | 1160405.6738
52 | 2570872.8619 | 1160382.0381 | 2570893.8399 | 1160397.804
53 | 2570859.0745 | 1160328.8866 | 2570851.6982 | 1160345.6081
54 | 2570723.2141 | 1160380.7772 | 2570725.4358 | 1160382.2227 | 2570761.107 | 1160405.6738
55 | 2570843.8006 | 1160642.9245 | 2570808.5057 | 1160623.3552
56 | 2570843.8006 | 1160642.9245 | 2570846.4995 | 1160638.7291 | 2570864.7197 | 1160620.9093 | 2570870.0237 | 1160617.3878
57 | 2570834.4037 | 1160657.532 | 2570843.8006 | 1160642.9245
58 | 2570809.6939 | 1160695.9435 | 2570834.4037 | 1160657.532
59 | 2570784.0693 | 1160726.7886 | 2570793.0262 | 1160721.8536 | 2570809.6939 | 1160695.9435
60 | 2570870.0237 | 1160617.3878 | 2570895.1117 | 1160600.7311
61 | 2570905.107 | 1160594.0948 | 2570895.1117 | 1160600.7311
62 | 2570688.5051 | 1160540.5254 | 2570692.2207 | 1160545.6241
63 | 2570667.6942 | 1160591.0031 | 2570649.2801 | 1160602.7912
64 | 2570634.7952 | 1160613.76 | 2570649.0636 | 1160602.9298 | 2570649.2801 | 1160602.7912
65 | 2570601.3321 | 1160639.1597 | 2570634.7952 | 1160613.76
66 | 2570732.6496 | 1160448.4695 | 2570727.9766 | 1160445.2355
67 | 2570913.1806 | 1160412.3393 | 2570893.8399 | 1160397.804
68 | 2570859.0745 | 1160328.8866 | 2570863.0049 | 1160319.9767
69 | 2570746.2962 | 1160346.2805 | 2570723.2141 | 1160380.7772
70 | 2570782.0802 | 1160702.297 | 2570773.2683 | 1160699.2384 | 2570765.6925 | 1160693.5391 | 2570753.8082 | 1160667.7003
71 | 2570784.0693 | 1160726.7886 | 2570782.0802 | 1160702.297
72 | 2570753.8082 | 1160667.7003 | 2570743.5331 | 1160645.3603
73 | 2570784.0693 | 1160726.7886 | 2570784.9407 | 1160736.1562
74 | 2570739.1184 | 1160734.184 | 2570784.0693 | 1160726.7886
75 | 2570784.9407 | 1160736.1562 | 2570788.5332 | 1160774.78 | 2570791.374 | 1160785.9008
76 | 2570710.4968 | 1160742.1998 | 2570739.1184 | 1160734.184
77 | 2570710.4968 | 1160742.1998 | 2570696.8953 | 1160746.1287
78 | 2570710.4968 | 1160742.1998 | 2570702.7418 | 1160723.7828
79 | 2570791.374 | 1160785.9008 | 2570795.3685 | 1160801.538 | 2570802.6498 | 1160816.0321 | 2570807.916 | 1160824.2884 | 2570812.3852 | 1160829.9275
80 | 2571141.1104 | 1160240.3092 | 2571129.7329 | 1160257.855
81 | 2571108.7478 | 1160290.2171 | 2571129.7329 | 1160257.855
82 | 2571108.7478 | 1160290.2171 | 2571088.0815 | 1160319.029
83 | 2571108.7478 | 1160290.2171 | 2571143.1658 | 1160307.943
84 | 2570951.6796 | 1160348.9945 | 2571088.0815 | 1160319.029
85 | 2570951.6796 | 1160348.9945 | 2570946.3112 | 1160345.1541
86 | 2570945.1843 | 1160344.348 | 2570946.3112 | 1160345.1541
87 | 2571143.1658 | 1160307.943 | 2571182.8768 | 1160328.395
88 | 2571033.5878 | 1160520.6961 | 2571024.5217 | 1160512.9056
89 | 2571033.5878 | 1160520.6961 | 2571065.139 | 1160544.9449
90 | 2571023.1531 | 1160590.9598 | 2571024.7958 | 1160585.1822 | 2571027.4373 | 1160570.4509 | 2571030.8037 | 1160550.3356 | 2571033.5878 | 1160520.6961
91 | 2571065.139 | 1160544.9449 | 2571214.0443 | 1160670.7895
92 | 2571023.1531 | 1160590.9598 | 2570980.8248 | 1160720.1661
93 | 2571214.0443 | 1160670.7895 | 2571216.1176 | 1160671.0374
94 | 2570704.5595 | 1160612.3743 | 2570681.4976 | 1160633.6433
95 | 2570668.2779 | 1160645.8352 | 2570681.4976 | 1160633.6433
96 | 2570927.4693 | 1160331.6752 | 2570910.407 | 1160319.4694
97 | 2570927.4693 | 1160331.6752 | 2570929.1975 | 1160332.9115
98 | 2570908.5282 | 1160318.1254 | 2570910.407 | 1160319.4694
99 | 2570945.1843 | 1160344.348 | 2570929.1975 | 1160332.9115
100 | 2570876.1092 | 1160294.9338 | 2570908.5282 | 1160318.1254
101 | 2570876.1092 | 1160294.9338 | 2570884.4797 | 1160280.7086
102 | 2570876.1092 | 1160294.9338 | 2570867.1576 | 1160310.5629
103 | 2570867.1576 | 1160310.5629 | 2570863.0049 | 1160319.9767
104 | 2570746.2962 | 1160346.2805 | 2570780.1702 | 1160379.6989
105 | 2570695.6323 | 1160706.8986 | 2570702.7418 | 1160723.7828
106 | 2570695.6323 | 1160706.8986 | 2570689.5333 | 1160692.4143
107 | 2570679.0084 | 1160668.7069 | 2570684.2997 | 1160679.9852 | 2570689.5333 | 1160692.4143
108 | 2570679.0084 | 1160668.7069 | 2570675.6408 | 1160661.5291
109 | 2570668.2779 | 1160645.8352 | 2570675.6408 | 1160661.5291
110 | 2570649.426 | 1160759.8407 | 2570601.5356 | 1160774.3546
111 | 2570649.426 | 1160759.8407 | 2570643.5139 | 1160745.0023
112 | 2570587.2732 | 1160778.677 | 2570601.5356 | 1160774.3546
113 | 2570643.5139 | 1160745.0023 | 2570643.4164 | 1160744.7577
114 | 2570668.2779 | 1160645.8352 | 2570666.1877 | 1160647.7686 | 2570662.5298 | 1160649.6035
115 | 2570587.2732 | 1160778.677 | 2570570.1743 | 1160740.9541
116 | 2570633.9419 | 1160720.9784 | 2570643.4164 | 1160744.7577
117 | 2570662.5298 | 1160649.6035 | 2570653.8121 | 1160653.9763
118 | 2570615.0024 | 1160673.4434 | 2570653.8121 | 1160653.9763
119 | 2570615.0024 | 1160673.4434 | 2570621.8339 | 1160690.5894
120 | 2570615.0024 | 1160673.4434 | 2570614.0448 | 1160671.0418
121 | 2570621.8339 | 1160690.5894 | 2570623.3042 | 1160694.2795
122 | 2570608.4195 | 1160656.9342 | 2570614.0448 | 1160671.0418
123 | 2570601.3321 | 1160639.1597 | 2570608.4195 | 1160656.9342
124 | 2570623.9696 | 1160695.9495 | 2570633.0178 | 1160718.6591
125 | 2570633.9419 | 1160720.9784 | 2570633.0178 | 1160718.6591
126 | 2570623.9696 | 1160695.9495 | 2570623.3042 | 1160694.2795
127 | 2570553.3811 | 1160703.9055 | 2570561.8436 | 1160692.4789
128 | 2570553.3811 | 1160703.9055 | 2570569.067 | 1160738.5111
129 | 2570553.3811 | 1160703.9055 | 2570539.0841 | 1160722.3848
130 | 2570553.3811 | 1160703.9055 | 2570549.2527 | 1160692.7617
131 | 2570569.067 | 1160738.5111 | 2570570.1743 | 1160740.9541
132 | 2570517.8366 | 1160749.8478 | 2570539.0841 | 1160722.3848
133 | 2570541.144 | 1160670.8735 | 2570549.2527 | 1160692.7617
134 | 2570460.3457 | 1160858.1235 | 2570459.1625 | 1160862.2963
135 | 2570457.1462 | 1160869.407 | 2570459.1625 | 1160862.2963
136 | 2570468.5381 | 1160834.376 | 2570463.6236 | 1160846.5636 | 2570460.3457 | 1160858.1235
137 | 2570468.5381 | 1160834.376 | 2570469.6943 | 1160831.5088
138 | 2570479.4226 | 1160807.3837 | 2570469.6943 | 1160831.5088
139 | 2570479.4226 | 1160807.3837 | 2570479.4916 | 1160807.2124
140 | 2570492.7331 | 1160785.4175 | 2570482.3448 | 1160800.1368 | 2570479.4916 | 1160807.2124
141 | 2570537.3695 | 1160660.6849 | 2570541.144 | 1160670.8735
142 | 2570511.9773 | 1160745.7412 | 2570517.8366 | 1160749.8478
143 | 2570517.8366 | 1160749.8478 | 2570515.6931 | 1160752.8851
144 | 2570511.9773 | 1160745.7412 | 2570501.313 | 1160754.009
145 | 2570519.3887 | 1160730.4526 | 2570511.9773 | 1160745.7412
146 | 2570498.3828 | 1160777.4122 | 2570515.6931 | 1160752.8851
147 | 2570492.7331 | 1160785.4175 | 2570498.3828 | 1160777.4122

## bus_geodata
| x | y | coords
0 | 2570605.9127 | 1160430.8499
1 | 2570615.9274 | 1160421.3559
2 | 2570626.8333 | 1160454.408
3 | 2570616.4544 | 1160408.4912
4 | 2570679.626 | 1160468.6791
5 | 2570710.6959 | 1160433.276
6 | 2570554.8558 | 1160380.269
7 | 2570504.4202 | 1160609.9653
8 | 2570510.6809 | 1160617.7496
9 | 2570488.0031 | 1160602.0831
10 | 2570522.5989 | 1160632.576
11 | 2570470.1876 | 1160647.0828
12 | 2570480.4241 | 1160600.1966
13 | 2570531.5303 | 1160644.9229
14 | 2570483.6948 | 1160685.272
15 | 2570454.6889 | 1160612.2917
16 | 2570536.82 | 1160659.2016
17 | 2570828.264 | 1160502.717
18 | 2570842.5979 | 1160500.9499
19 | 2570800.1863 | 1160494.8289
20 | 2570782.0984 | 1160485.9876
21 | 2570786.5466 | 1160477.2727
22 | 2570772.8893 | 1160502.5797
23 | 2570767.403 | 1160465.1113
24 | 2570807.2123 | 1160435.9845
25 | 2570755.0693 | 1160527.8562
26 | 2570767.0361 | 1160464.8782
27 | 2570830.9609 | 1160393.503
28 | 2570793.5956 | 1160427.0325
29 | 2570835.133 | 1160457.4408
30 | 2570706.9682 | 1160565.8612
31 | 2570934.8195 | 1160453.1399
32 | 2570927.0869 | 1160494.1092
33 | 2570912.9053 | 1160496.2902
34 | 2570893.0298 | 1160501.6004
35 | 2570955.6707 | 1160486.2556
36 | 2570882.0692 | 1160513.7376
37 | 2570875.96 | 1160488.8153
38 | 2570956.7861 | 1160479.2244
39 | 2570979.3782 | 1160466.7643
40 | 2570856.6512 | 1160551.649
41 | 2570987.9618 | 1160477.8866
42 | 2570844.9639 | 1160360.874
43 | 2570817.9039 | 1160377.6961
44 | 2570764.7561 | 1160408.0727
45 | 2570872.8619 | 1160382.0381
46 | 2570851.6982 | 1160345.6081
47 | 2570811.9606 | 1160369.2832
48 | 2570761.107 | 1160405.6738
49 | 2570808.5057 | 1160623.3552
50 | 2570843.8006 | 1160642.9245
51 | 2570834.4037 | 1160657.532
52 | 2570809.6939 | 1160695.9435
53 | 2570870.0237 | 1160617.3878
54 | 2570895.1117 | 1160600.7311
55 | 2570905.107 | 1160594.0948
56 | 2570692.2207 | 1160545.6241
57 | 2570667.6942 | 1160591.0031
58 | 2570688.5051 | 1160540.5254
59 | 2570649.2801 | 1160602.7912
60 | 2570634.7952 | 1160613.76
61 | 2570732.6496 | 1160448.4695
62 | 2570893.8399 | 1160397.804
63 | 2570859.0745 | 1160328.8866
64 | 2570723.2141 | 1160380.7772
65 | 2570782.0802 | 1160702.297
66 | 2570753.8082 | 1160667.7003
67 | 2570784.0693 | 1160726.7886
68 | 2570743.5331 | 1160645.3603
69 | 2570784.9407 | 1160736.1562
70 | 2570739.1184 | 1160734.184
71 | 2570710.4968 | 1160742.1998
72 | 2570791.374 | 1160785.9008
73 | 2571141.1104 | 1160240.3092
74 | 2571129.7329 | 1160257.855
75 | 2571108.7478 | 1160290.2171
76 | 2570951.6796 | 1160348.9945
77 | 2571088.0815 | 1160319.029
78 | 2570946.3112 | 1160345.1541
79 | 2571143.1658 | 1160307.943
80 | 2571182.8768 | 1160328.395
81 | 2571024.5217 | 1160512.9056
82 | 2571033.5878 | 1160520.6961
83 | 2571065.139 | 1160544.9449
84 | 2571023.1531 | 1160590.9598
85 | 2570812.3852 | 1160829.9274
86 | 2570980.8248 | 1160720.1662
87 | 2571214.0443 | 1160670.7895
88 | 2571216.1176 | 1160671.0374
89 | 2570704.5595 | 1160612.3743
90 | 2570681.4976 | 1160633.6433
91 | 2570927.4693 | 1160331.6752
92 | 2570910.407 | 1160319.4694
93 | 2570929.1975 | 1160332.9115
94 | 2570908.5282 | 1160318.1254
95 | 2570945.1843 | 1160344.348
96 | 2570876.1092 | 1160294.9338
97 | 2570884.4797 | 1160280.7086
98 | 2570867.1576 | 1160310.5629
99 | 2570863.0049 | 1160319.9767
100 | 2570913.1806 | 1160412.3393
101 | 2570746.2962 | 1160346.2805
102 | 2570780.1702 | 1160379.6989
103 | 2570702.7418 | 1160723.7828
104 | 2570695.6323 | 1160706.8986
105 | 2570689.5333 | 1160692.4143
106 | 2570696.8953 | 1160746.1287
107 | 2570679.0084 | 1160668.7069
108 | 2570675.6408 | 1160661.5291
109 | 2570649.426 | 1160759.8407
110 | 2570601.5355 | 1160774.3546
111 | 2570643.5139 | 1160745.0023
112 | 2570668.2779 | 1160645.8352
113 | 2570587.2732 | 1160778.677
114 | 2570643.4164 | 1160744.7577
115 | 2570662.5298 | 1160649.6035
116 | 2570653.8121 | 1160653.9763
117 | 2570615.0024 | 1160673.4434
118 | 2570621.8339 | 1160690.5894
119 | 2570614.0448 | 1160671.0418
120 | 2570727.9766 | 1160445.2355
121 | 2570601.3321 | 1160639.1597
122 | 2570633.0178 | 1160718.6591
123 | 2570623.9696 | 1160695.9495
124 | 2570633.9419 | 1160720.9784
125 | 2570623.3042 | 1160694.2795
126 | 2570608.4195 | 1160656.9342
127 | 2570561.8436 | 1160692.4789
128 | 2570553.3811 | 1160703.9055
129 | 2570569.067 | 1160738.5111
130 | 2570539.0841 | 1160722.3848
131 | 2570549.2527 | 1160692.7617
132 | 2570459.1625 | 1160862.2963
133 | 2570460.3457 | 1160858.1235
134 | 2570457.1462 | 1160869.407
135 | 2570468.5381 | 1160834.376
136 | 2570469.6943 | 1160831.5088
137 | 2570479.4226 | 1160807.3837
138 | 2570479.4916 | 1160807.2124
139 | 2570541.144 | 1160670.8735
140 | 2570537.3695 | 1160660.6849
141 | 2570570.1743 | 1160740.9541
142 | 2570517.8366 | 1160749.8478
143 | 2570511.9773 | 1160745.7412
144 | 2570515.6931 | 1160752.8851
145 | 2570501.313 | 1160754.009
146 | 2570519.3887 | 1160730.4526
147 | 2570498.3828 | 1160777.4122
148 | 2570492.7331 | 1160785.4175
149 | 2570782.0984 | 1160485.9876

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98232 | -0.33834 | 0.0067606 | 0.0016944
1 | 0.98241 | -0.33665 | 0 | 0
2 | 0.98268 | -0.33139 | 0 | 0
3 | 0.98239 | -0.33702 | 0 | 0
4 | 0.9831 | -0.32316 | 0.006397 | 0.0016032
5 | 0.98375 | -0.31047 | 0 | 0
6 | 0.98229 | -0.33895 | 0.0015755 | 0.00039486
7 | 0.97226 | -0.53443 | 0 | 0
8 | 0.97238 | -0.53208 | 0 | 0
9 | 0.97204 | -0.53873 | 0.00076839 | 0.00019258
10 | 0.97265 | -0.52667 | 0.0020347 | 0.00050994
11 | 0.97224 | -0.53471 | 0.0013542 | 0.0003394
12 | 0.97195 | -0.54048 | 0.0083451 | 0.0020915
13 | 0.9729 | -0.52174 | 0.0036387 | 0.00091195
14 | 0.97219 | -0.53572 | 0.0012757 | 0.00031972
15 | 0.97185 | -0.54245 | 0.003668 | 0.00091928
16 | 0.9732 | -0.51583 | 0.0027201 | 0.00068172
17 | 0.98615 | -0.26377 | 0.0016684 | 0.00041814
18 | 0.98613 | -0.26422 | 0.0017242 | 0.00043212
19 | 0.98625 | -0.26197 | 0.0021846 | 0.00054751
20 | 0.98635 | -0.25995 | 0 | 0
21 | 0.98523 | -0.2816 | 0 | 0
22 | 0.98862 | -0.21621 | 0.0019576 | 0.00049063
23 | 0.98478 | -0.29041 | 0.0013063 | 0.00032739
24 | 0.98087 | -0.36632 | 0 | 0
25 | 0.99239 | -0.14407 | 0.0020401 | 0.00051129
26 | 0.98477 | -0.29057 | 0.0020822 | 0.00052186
27 | 0.97896 | -0.40353 | 0 | 0
28 | 0.98065 | -0.37046 | 0.0021086 | 0.00052848
29 | 0.97937 | -0.39551 | 0.013354 | 0.0033469
30 | 1 | 0 | -0.33114 | -0.085074
31 | 0.97629 | -0.45584 | 0.0022391 | 0.00056118
32 | 0.97638 | -0.45414 | 0 | 0
33 | 0.97673 | -0.44721 | 0 | 0
34 | 0.97724 | -0.43724 | 0 | 0
35 | 0.9757 | -0.46734 | 0 | 0
36 | 0.97719 | -0.43811 | 0 | 0
37 | 0.97782 | -0.42581 | 0.0029462 | 0.00073839
38 | 0.97568 | -0.46775 | 0.003076 | 0.00077092
39 | 0.9751 | -0.47928 | 0 | 0
40 | 0.97707 | -0.44054 | 0.0029109 | 0.00072955
41 | 0.97482 | -0.48473 | 0.0016145 | 0.00040463
42 | 0.97773 | -0.42765 | 0 | 0
43 | 0.97887 | -0.40532 | 0.0015042 | 0.00037698
44 | 0.98027 | -0.37792 | 0.0012785 | 0.00032041
45 | 0.97758 | -0.43055 | 0.0030809 | 0.00077215
46 | 0.97722 | -0.43763 | 0.0027002 | 0.00067673
47 | 0.97884 | -0.40592 | 0.0032298 | 0.00080946
48 | 0.98023 | -0.37876 | 0.0049463 | 0.0012397
49 | 0.97442 | -0.49263 | 0.00046355 | 0.00011618
50 | 0.97444 | -0.49228 | 0.0046522 | 0.001166
51 | 0.97465 | -0.48804 | 0.0056383 | 0.0014131
52 | 0.97546 | -0.47218 | 0.0047874 | 0.0011998
53 | 0.97416 | -0.49782 | 0.0044134 | 0.0011061
54 | 0.97405 | -0.49991 | 0.0034953 | 0.000876
55 | 0.97405 | -0.49997 | 0.00027778 | 6.9618e-05
56 | 0.99986 | -0.0027202 | 0.0042417 | 0.0010631
57 | 0.99602 | -0.075022 | 0.0033411 | 0.00083736
58 | 0.99985 | -0.002939 | 0.0019895 | 0.00049862
59 | 0.99418 | -0.10976 | 0.0023804 | 0.00059659
60 | 0.99268 | -0.13834 | 0.0022949 | 0.00057517
61 | 0.98412 | -0.30324 | 0.0020347 | 0.00050993
62 | 0.97755 | -0.43124 | 0.0010176 | 0.00025504
63 | 0.97671 | -0.44767 | 0.004078 | 0.001022
64 | 0.97999 | -0.38344 | 0 | 0
65 | 0.97628 | -0.45607 | 0 | 0
66 | 0.97611 | -0.45937 | 0.0034763 | 0.00087123
67 | 0.97636 | -0.45436 | 0 | 0
68 | 0.9761 | -0.45952 | 0.00033726 | 8.4525e-05
69 | 0.97634 | -0.45488 | 0.00036103 | 9.0482e-05
70 | 0.97766 | -0.4289 | 0.00035812 | 8.9752e-05
71 | 0.97852 | -0.41213 | 0 | 0
72 | 0.97621 | -0.45735 | 0.0013151 | 0.00032958
73 | 0.97224 | -0.53573 | 0.0012199 | 0.00030573
74 | 0.97226 | -0.53526 | 0.0020863 | 0.00052287
75 | 0.97238 | -0.5329 | 0 | 0
76 | 0.97441 | -0.49284 | 0.00088992 | 0.00022304
77 | 0.97275 | -0.52556 | 0.0014924 | 0.00037404
78 | 0.9745 | -0.49118 | 0.0005071 | 0.00012709
79 | 0.97209 | -0.53857 | 0.00030557 | 7.6583e-05
80 | 0.97178 | -0.54486 | 0.0076297 | 0.0019122
81 | 0.9739 | -0.50297 | 0.0028125 | 0.00070489
82 | 0.97371 | -0.50664 | 0 | 0
83 | 0.9731 | -0.51875 | 0.0072053 | 0.0018058
84 | 0.9737 | -0.50684 | 0 | 0
85 | 0.97615 | -0.45859 | 0.001371 | 0.00034359
86 | 0.97368 | -0.50721 | 0.00014581 | 3.6543e-05
87 | 0.97139 | -0.55242 | 0.0026093 | 0.00065396
88 | 0.97138 | -0.55268 | 0.0067519 | 0.0016922
89 | 0.98234 | -0.33747 | 0.0047 | 0.0011779
90 | 0.98248 | -0.33481 | 0.0044747 | 0.0011215
91 | 0.97481 | -0.48492 | 0.00054244 | 0.00013595
92 | 0.97512 | -0.47884 | 0.0031663 | 0.00079356
93 | 0.97478 | -0.48552 | 0.00054003 | 0.00013534
94 | 0.97516 | -0.47804 | 0.0006016 | 0.00015077
95 | 0.97451 | -0.49082 | 0.00057975 | 0.0001453
96 | 0.97589 | -0.46375 | 0 | 0
97 | 0.97585 | -0.46452 | 0.002562 | 0.0006421
98 | 0.97626 | -0.45646 | 0 | 0
99 | 0.97647 | -0.45229 | 0.0038617 | 0.00096784
100 | 0.97754 | -0.43143 | 0.00043295 | 0.00010851
101 | 0.97977 | -0.38773 | 0 | 0
102 | 0.97952 | -0.39264 | 0.0056884 | 0.0014257
103 | 0.97912 | -0.40025 | 0.00045928 | 0.00011511
104 | 0.97969 | -0.38922 | 0.0081821 | 0.0020506
105 | 0.98029 | -0.37743 | 0.0051001 | 0.0012782
106 | 0.97849 | -0.41258 | 0.001717 | 0.00043032
107 | 0.98141 | -0.35561 | 0.0021638 | 0.00054229
108 | 0.98177 | -0.34865 | 0.0051001 | 0.0012782
109 | 0.98243 | -0.33527 | 0 | 0
110 | 0.98063 | -0.37036 | 0.0022975 | 0.0005758
111 | 0.98301 | -0.32409 | 0.003278 | 0.00082153
112 | 0.98263 | -0.33183 | 0 | 0
113 | 0.9801 | -0.38053 | 0 | 0
114 | 0.98302 | -0.3239 | 0.0040012 | 0.0010028
115 | 0.98303 | -0.32396 | 0.0010205 | 0.00025577
116 | 0.98361 | -0.31273 | 0.0032551 | 0.00081581
117 | 0.98631 | -0.26035 | 0 | 0
118 | 0.98546 | -0.27683 | 0.0022236 | 0.00055729
119 | 0.98651 | -0.25649 | 0.0028967 | 0.00072598
120 | 0.98403 | -0.30489 | 0.001452 | 0.00036391
121 | 0.98925 | -0.2039 | 0.0027047 | 0.00067786
122 | 0.98414 | -0.30234 | 0.0044682 | 0.0011198
123 | 0.9852 | -0.28182 | 0.00090517 | 0.00022686
124 | 0.98403 | -0.30434 | 0.0040798 | 0.0010225
125 | 0.98528 | -0.2803 | 0.0030609 | 0.00076714
126 | 0.98771 | -0.23346 | 0.0035385 | 0.00088682
127 | 0.97448 | -0.4905 | 0.0026574 | 0.00066601
128 | 0.97452 | -0.48981 | 0 | 0
129 | 0.97701 | -0.44079 | 0.0020809 | 0.00052152
130 | 0.97378 | -0.50427 | 0.0011506 | 0.00028837
131 | 0.97414 | -0.49725 | 0.0045533 | 0.0011412
132 | 0.97039 | -0.57127 | 0.0021675 | 0.00054324
133 | 0.97043 | -0.57038 | 0.0029189 | 0.00073155
134 | 0.97033 | -0.57249 | 0.0089013 | 0.0022309
135 | 0.97076 | -0.56387 | 0.0017128 | 0.00042927
136 | 0.97081 | -0.56297 | 0.0018623 | 0.00046673
137 | 0.97124 | -0.55453 | 0.0016033 | 0.00040183
138 | 0.97124 | -0.55446 | 0.0018244 | 0.00045724
139 | 0.9735 | -0.50993 | 0.0034925 | 0.00087531
140 | 0.97323 | -0.51514 | 0.0022453 | 0.00056272
141 | 0.9772 | -0.43724 | 0.0026855 | 0.00067305
142 | 0.97273 | -0.52508 | 0 | 0
143 | 0.97269 | -0.52584 | 0 | 0
144 | 0.97263 | -0.52691 | 0.0023389 | 0.00058619
145 | 0.97265 | -0.52657 | 0.0029239 | 0.00073279
146 | 0.97264 | -0.52675 | 0.0029005 | 0.00072695
147 | 0.97195 | -0.54041 | 0.0016386 | 0.00041067
148 | 0.97174 | -0.54452 | 0.0017586 | 0.00044076
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0067606 | -0.0016944 | 0.0067611 | 0.0016945 | 5.4422e-07 | 1.731e-07 | 0.010241 | 0.010241 | 0.010241 | 0.98232 | -0.33834 | 0.98241 | -0.33665 | 2.8134
1 | -0.0083368 | -0.0020885 | 0.0083389 | 0.0020894 | 2.0876e-06 | 8.9384e-07 | 0.012627 | 0.012627 | 0.012627 | 0.98241 | -0.33665 | 0.98268 | -0.33139 | 3.469
2 | 0.0015757 | 0.00039395 | -0.0015757 | -0.0003941 | 2.7697e-08 | -1.4649e-07 | 0.0023863 | 0.0023863 | 0.0023863 | 0.98241 | -0.33665 | 0.98239 | -0.33702 | 0.65559
3 | -0.0083389 | -0.0020894 | 0.0083421 | 0.0020908 | 3.2697e-06 | 1.3995e-06 | 0.012627 | 0.012627 | 0.012627 | 0.98268 | -0.33139 | 0.9831 | -0.32316 | 3.4689
4 | 0.0015757 | 0.0003941 | -0.0015755 | -0.00039486 | 1.4478e-07 | -7.6552e-07 | 0.0023863 | 0.0023867 | 0.0023867 | 0.98239 | -0.33702 | 0.98229 | -0.33895 | 0.65567
5 | -0.014739 | -0.003694 | 0.014748 | 0.0036991 | 8.9167e-06 | 5.1005e-06 | 0.022309 | 0.022309 | 0.022309 | 0.9831 | -0.32316 | 0.98375 | -0.31047 | 6.1289
6 | -0.014748 | -0.0036991 | 0.014752 | 0.0037014 | 3.9222e-06 | 2.2433e-06 | 0.022309 | 0.022309 | 0.022309 | 0.98375 | -0.31047 | 0.98403 | -0.30489 | 6.1288
7 | -0.012785 | -0.0032052 | 0.012787 | 0.003206 | 1.433e-06 | 7.9337e-07 | 0.019568 | 0.019568 | 0.019568 | 0.97226 | -0.53443 | 0.97238 | -0.53208 | 5.3759
8 | 0.012785 | 0.0032052 | -0.012783 | -0.0032037 | 2.6164e-06 | 1.4486e-06 | 0.019568 | 0.019568 | 0.019568 | 0.97226 | -0.53443 | 0.97204 | -0.53873 | 5.3759
9 | -0.015417 | -0.0038642 | 0.015421 | 0.0038665 | 3.9707e-06 | 2.3052e-06 | 0.023593 | 0.023593 | 0.023593 | 0.97238 | -0.53208 | 0.97265 | -0.52667 | 6.4816
10 | 0.0026303 | 0.00065817 | -0.00263 | -0.00065863 | 3.2894e-07 | -4.6105e-07 | 0.0040248 | 0.004025 | 0.004025 | 0.97238 | -0.53208 | 0.97224 | -0.53471 | 1.1058
11 | 0.012014 | 0.0030112 | -0.012013 | -0.0030106 | 1.0039e-06 | 5.4442e-07 | 0.018392 | 0.018392 | 0.018392 | 0.97204 | -0.53873 | 0.97195 | -0.54048 | 5.0527
12 | -0.017456 | -0.0043764 | 0.01746 | 0.0043788 | 4.1039e-06 | 2.436e-06 | 0.026706 | 0.026706 | 0.026706 | 0.97265 | -0.52667 | 0.9729 | -0.52174 | 7.3367
13 | 0.0012758 | 0.00031923 | -0.0012757 | -0.00031972 | 6.1427e-08 | -4.9352e-07 | 0.0019524 | 0.0019526 | 0.0019526 | 0.97224 | -0.53471 | 0.97219 | -0.53572 | 0.53642
14 | 0.0036683 | 0.00091914 | -0.003668 | -0.00091928 | 3.444e-07 | -1.4043e-07 | 0.0056159 | 0.0056161 | 0.0056161 | 0.97195 | -0.54048 | 0.97185 | -0.54245 | 1.5429
15 | -0.021099 | -0.0052908 | 0.021105 | 0.0052944 | 5.9466e-06 | 3.6167e-06 | 0.032271 | 0.032271 | 0.032271 | 0.9729 | -0.52174 | 0.9732 | -0.51583 | 8.8656
16 | -0.023825 | -0.0059761 | 0.023826 | 0.0059766 | 7.872e-07 | 4.8415e-07 | 0.03643 | 0.03643 | 0.03643 | 0.9732 | -0.51583 | 0.97323 | -0.51514 | 10.0082
17 | 0.0017242 | 0.00043195 | -0.0017242 | -0.00043212 | 3.6657e-08 | -1.608e-07 | 0.0026016 | 0.0026017 | 0.0026017 | 0.98615 | -0.26377 | 0.98613 | -0.26422 | 0.71474
18 | -0.0033926 | -0.00085009 | 0.0033929 | 0.0008499 | 2.9211e-07 | -1.9236e-07 | 0.005119 | 0.0051189 | 0.005119 | 0.98615 | -0.26377 | 0.98625 | -0.26197 | 1.4063
19 | -0.0055775 | -0.0013974 | 0.005578 | 0.0013975 | 5.3461e-07 | 8.5211e-08 | 0.008415 | 0.0084149 | 0.008415 | 0.98625 | -0.26197 | 0.98635 | -0.25995 | 2.3118
20 | 0.12437 | 0.03155 | -0.12424 | -0.031467 | 0.00012931 | 8.2631e-05 | 0.18776 | 0.18776 | 0.18776 | 0.98635 | -0.25995 | 0.98523 | -0.2816 | 51.5824
21 | -0.12995 | -0.032948 | 0.13022 | 0.033123 | 0.00027387 | 0.00017503 | 0.19617 | 0.19617 | 0.19617 | 0.98635 | -0.25995 | 0.98862 | -0.21621 | 53.8942
22 | 0.021649 | 0.0054374 | -0.02164 | -0.0054318 | 9.0947e-06 | 5.532e-06 | 0.032701 | 0.032701 | 0.032701 | 0.98523 | -0.2816 | 0.98478 | -0.29041 | 8.9838
23 | 0.10259 | 0.02603 | -0.10217 | -0.025764 | 0.00041613 | 0.00026574 | 0.15506 | 0.15506 | 0.15506 | 0.98523 | -0.2816 | 0.98087 | -0.36632 | 42.5987
24 | -0.13218 | -0.033613 | 0.13264 | 0.033908 | 0.00046112 | 0.00029472 | 0.19912 | 0.19912 | 0.19912 | 0.98862 | -0.21621 | 0.99239 | -0.14407 | 54.7036
25 | 0.020333 | 0.0051045 | -0.020333 | -0.0051044 | 1.539e-07 | 9.2964e-08 | 0.030727 | 0.030727 | 0.030727 | 0.98478 | -0.29041 | 0.98477 | -0.29057 | 8.4415
26 | 0.042249 | 0.010666 | -0.042174 | -0.010618 | 7.5177e-05 | 4.7499e-05 | 0.064121 | 0.064121 | 0.064121 | 0.98087 | -0.36632 | 0.97896 | -0.40353 | 17.6157
27 | 0.014033 | 0.003519 | -0.01403 | -0.0035174 | 2.7697e-06 | 1.567e-06 | 0.021289 | 0.021289 | 0.021289 | 0.98087 | -0.36632 | 0.98065 | -0.37046 | 5.8488
28 | 0.045893 | 0.01158 | -0.045829 | -0.011539 | 6.4057e-05 | 4.0552e-05 | 0.069649 | 0.069649 | 0.069649 | 0.98087 | -0.36632 | 0.97937 | -0.39551 | 19.1344
29 | -0.13468 | -0.034419 | 0.13562 | 0.035024 | 0.00094563 | 0.0006044 | 0.20218 | 0.20218 | 0.20218 | 0.99239 | -0.14407 | 1 | 0 | 55.5439
30 | 0.018251 | 0.0045825 | -0.01824 | -0.0045759 | 1.1024e-05 | 6.5639e-06 | 0.027581 | 0.027581 | 0.027581 | 0.98477 | -0.29057 | 0.98412 | -0.30324 | 7.5772
31 | 0.037439 | 0.0094318 | -0.037396 | -0.0094046 | 4.3136e-05 | 2.7161e-05 | 0.056925 | 0.056925 | 0.056925 | 0.97896 | -0.40353 | 0.97773 | -0.42765 | 15.6387
32 | 0.0047344 | 0.0011864 | -0.004734 | -0.0011864 | 4.0246e-07 | -2.9641e-09 | 0.0071963 | 0.0071964 | 0.0071964 | 0.97896 | -0.40353 | 0.97887 | -0.40532 | 1.977
33 | 0.011922 | 0.0029889 | -0.011917 | -0.0029867 | 4.2354e-06 | 2.2754e-06 | 0.01809 | 0.01809 | 0.01809 | 0.98065 | -0.37046 | 0.98027 | -0.37792 | 4.9698
34 | 0.032474 | 0.0081923 | -0.032427 | -0.0081628 | 4.7043e-05 | 2.9461e-05 | 0.04936 | 0.04936 | 0.04936 | 0.97937 | -0.39551 | 0.97782 | -0.42581 | 13.5604
35 | 0.006232 | 0.0015618 | -0.0062312 | -0.0015616 | 8.0751e-07 | 1.8834e-07 | 0.0092733 | 0.0092734 | 0.0092734 | 1 | 0 | 0.99986 | -0.0027202 | 2.5476
36 | 0.18763 | 0.048488 | -0.18695 | -0.048051 | 0.00068413 | 0.00043662 | 0.27972 | 0.27972 | 0.27972 | 1 | 0 | 0.99602 | -0.075022 | 38.4232
37 | -0.0022391 | -0.00056118 | 0.0022393 | 0.00056077 | 1.8209e-07 | -4.0486e-07 | 0.0034128 | 0.0034126 | 0.0034128 | 0.97629 | -0.45584 | 0.97638 | -0.45414 | 0.93757
38 | 0.024293 | 0.0061113 | -0.024278 | -0.0061019 | 1.5321e-05 | 9.4329e-06 | 0.037031 | 0.037031 | 0.037031 | 0.97638 | -0.45414 | 0.9757 | -0.46734 | 10.1734
39 | -0.026532 | -0.0066721 | 0.026541 | 0.0066775 | 8.7763e-06 | 5.4378e-06 | 0.040444 | 0.040444 | 0.040444 | 0.97638 | -0.45414 | 0.97673 | -0.44721 | 11.1109
40 | -0.026541 | -0.0066775 | 0.026554 | 0.0066853 | 1.2647e-05 | 7.8361e-06 | 0.040444 | 0.040444 | 0.040444 | 0.97673 | -0.44721 | 0.97724 | -0.43724 | 11.1109
41 | 0.0029114 | 0.00072906 | -0.0029113 | -0.00072919 | 1.2063e-07 | -1.2788e-07 | 0.0044329 | 0.004433 | 0.004433 | 0.97724 | -0.43724 | 0.97719 | -0.43811 | 1.2178
42 | -0.029465 | -0.0074144 | 0.029481 | 0.0074245 | 1.6107e-05 | 1.0041e-05 | 0.044876 | 0.044876 | 0.044876 | 0.97724 | -0.43724 | 0.97782 | -0.42581 | 12.3287
43 | 0.0030761 | 0.00077087 | -0.003076 | -0.00077092 | 5.876e-08 | -5.1318e-08 | 0.0046912 | 0.0046912 | 0.0046912 | 0.9757 | -0.46734 | 0.97568 | -0.46775 | 1.2888
44 | 0.021202 | 0.005331 | -0.02119 | -0.0053237 | 1.2076e-05 | 7.3442e-06 | 0.03234 | 0.03234 | 0.03234 | 0.9757 | -0.46734 | 0.9751 | -0.47928 | 8.8847
45 | 0.0029113 | 0.00072919 | -0.0029109 | -0.00072955 | 3.3637e-07 | -3.5646e-07 | 0.004433 | 0.0044332 | 0.0044332 | 0.97719 | -0.43811 | 0.97707 | -0.44054 | 1.2179
46 | 0.02119 | 0.0053237 | -0.021184 | -0.0053203 | 5.5103e-06 | 3.3514e-06 | 0.03234 | 0.03234 | 0.03234 | 0.9751 | -0.47928 | 0.97482 | -0.48473 | 8.8847
47 | 0.01957 | 0.0049157 | -0.019552 | -0.0049054 | 1.7018e-05 | 1.0258e-05 | 0.029876 | 0.029876 | 0.029876 | 0.97482 | -0.48473 | 0.9739 | -0.50297 | 8.2077
48 | 0.0045322 | 0.0011351 | -0.0045316 | -0.0011351 | 6.2472e-07 | -3.9282e-08 | 0.0068973 | 0.0068975 | 0.0068975 | 0.97773 | -0.42765 | 0.97758 | -0.43055 | 1.8949
49 | 0.032864 | 0.0082695 | -0.032848 | -0.0082597 | 1.566e-05 | 9.8131e-06 | 0.050028 | 0.050028 | 0.050028 | 0.97773 | -0.42765 | 0.97722 | -0.43763 | 13.7439
50 | 0.0032299 | 0.00080939 | -0.0032298 | -0.00080946 | 9.3116e-08 | -6.9886e-08 | 0.0049098 | 0.0049099 | 0.0049099 | 0.97887 | -0.40532 | 0.97884 | -0.40592 | 1.3489
51 | 0.010639 | 0.0026662 | -0.010638 | -0.002666 | 4.271e-07 | 2.1829e-07 | 0.016149 | 0.016149 | 0.016149 | 0.98027 | -0.37792 | 0.98023 | -0.37876 | 4.4367
52 | 0.0014506 | 0.00036295 | -0.0014506 | -0.00036325 | 4.7973e-08 | -2.983e-07 | 0.0022079 | 0.002208 | 0.002208 | 0.97758 | -0.43055 | 0.97755 | -0.43124 | 0.60659
53 | 0.030148 | 0.007583 | -0.030134 | -0.007574 | 1.4449e-05 | 9.0187e-06 | 0.045916 | 0.045916 | 0.045916 | 0.97722 | -0.43763 | 0.97671 | -0.44767 | 12.6144
54 | 0.0056922 | 0.0014264 | -0.0056909 | -0.0014261 | 1.2695e-06 | 2.4107e-07 | 0.0086408 | 0.008641 | 0.008641 | 0.98023 | -0.37876 | 0.97999 | -0.38344 | 2.3739
55 | -0.00046355 | -0.00011618 | 0.00046356 | 0.00011568 | 7.5815e-09 | -4.9787e-07 | 0.00070788 | 0.0007077 | 0.00070788 | 0.97442 | -0.49263 | 0.97444 | -0.49228 | 0.19447
56 | 0.008189 | 0.0020524 | -0.0081868 | -0.0020514 | 2.1604e-06 | 9.2385e-07 | 0.012505 | 0.012505 | 0.012505 | 0.97444 | -0.49228 | 0.97416 | -0.49782 | 3.4355
57 | -0.013305 | -0.003334 | 0.013307 | 0.0033355 | 2.6885e-06 | 1.5042e-06 | 0.020317 | 0.020317 | 0.020317 | 0.97444 | -0.49228 | 0.97465 | -0.48804 | 5.5815
58 | -0.018946 | -0.0047486 | 0.01896 | 0.0047572 | 1.4329e-05 | 8.6012e-06 | 0.028925 | 0.028925 | 0.028925 | 0.97465 | -0.48804 | 0.97546 | -0.47218 | 7.9464
59 | -0.023748 | -0.005957 | 0.023768 | 0.0059695 | 2.0196e-05 | 1.2413e-05 | 0.036228 | 0.036227 | 0.036228 | 0.97546 | -0.47218 | 0.97636 | -0.45436 | 9.9527
60 | 0.0037735 | 0.00094534 | -0.0037731 | -0.00094547 | 3.7517e-07 | -1.3477e-07 | 0.0057638 | 0.0057639 | 0.0057639 | 0.97416 | -0.49782 | 0.97405 | -0.49991 | 1.5835
61 | 0.00027778 | 6.9469e-05 | -0.00027778 | -6.9618e-05 | 8.1008e-10 | -1.4882e-07 | 0.0004243 | 0.00042435 | 0.00042435 | 0.97405 | -0.49991 | 0.97405 | -0.49997 | 0.11658
62 | 0.0019895 | 0.00049855 | -0.0019895 | -0.00049862 | 2.0741e-08 | -6.947e-08 | 0.0029609 | 0.0029609 | 0.0029609 | 0.99986 | -0.0027202 | 0.99985 | -0.002939 | 0.81343
63 | 0.18361 | 0.047214 | -0.1833 | -0.047017 | 0.00030942 | 0.00019746 | 0.27473 | 0.27473 | 0.27473 | 0.99602 | -0.075022 | 0.99418 | -0.10976 | 37.7376
64 | 0.18092 | 0.04642 | -0.18067 | -0.04626 | 0.00025052 | 0.00015986 | 0.27117 | 0.27117 | 0.27117 | 0.99418 | -0.10976 | 0.99268 | -0.13834 | 37.2483
65 | 0.17837 | 0.045685 | -0.17781 | -0.045325 | 0.00056461 | 0.00036027 | 0.26773 | 0.26773 | 0.26773 | 0.99268 | -0.13834 | 0.98925 | -0.2039 | 36.7758
66 | 0.016205 | 0.004066 | -0.016204 | -0.0040653 | 1.2797e-06 | 7.4678e-07 | 0.024504 | 0.024505 | 0.024505 | 0.98412 | -0.30324 | 0.98403 | -0.30489 | 6.732
67 | 0.00043296 | 0.00010821 | -0.00043295 | -0.00010851 | 3.94e-09 | -3.0079e-07 | 0.00065894 | 0.00065905 | 0.00065905 | 0.97755 | -0.43124 | 0.97754 | -0.43143 | 0.18106
68 | 0.026056 | 0.0065519 | -0.02605 | -0.0065484 | 5.7567e-06 | 3.5624e-06 | 0.039703 | 0.039704 | 0.039704 | 0.97671 | -0.44767 | 0.97647 | -0.45229 | 10.9076
69 | 0.0056909 | 0.0014261 | -0.0056897 | -0.0014259 | 1.1614e-06 | 2.208e-07 | 0.008641 | 0.0086412 | 0.0086412 | 0.97999 | -0.38344 | 0.97977 | -0.38773 | 2.374
70 | 0.0038141 | 0.00095525 | -0.0038135 | -0.00095545 | 5.9877e-07 | -2.0749e-07 | 0.0058131 | 0.0058134 | 0.0058134 | 0.97628 | -0.45607 | 0.97611 | -0.45937 | 1.5971
71 | -0.0038141 | -0.00095525 | 0.0038144 | 0.00095514 | 3.1145e-07 | -1.0803e-07 | 0.0058131 | 0.005813 | 0.0058131 | 0.97628 | -0.45607 | 0.97636 | -0.45436 | 1.597
72 | 0.00033726 | 8.422e-05 | -0.00033726 | -8.4525e-05 | 2.4369e-09 | -3.0581e-07 | 0.00051403 | 0.00051414 | 0.00051414 | 0.97611 | -0.45937 | 0.9761 | -0.45952 | 0.14125
73 | 0.0030475 | 0.0007626 | -0.0030474 | -0.00076267 | 7.6092e-08 | -6.8959e-08 | 0.0046441 | 0.0046441 | 0.0046441 | 0.97636 | -0.45436 | 0.97634 | -0.45488 | 1.2759
74 | -0.03063 | -0.0076872 | 0.030667 | 0.0077104 | 3.7232e-05 | 2.3258e-05 | 0.046685 | 0.046684 | 0.046685 | 0.97636 | -0.45436 | 0.97766 | -0.4289 | 12.8254
75 | 0.0026864 | 0.00067219 | -0.0026861 | -0.00067261 | 3.1596e-07 | -4.2635e-07 | 0.0040939 | 0.0040941 | 0.0040941 | 0.97634 | -0.45488 | 0.97621 | -0.45735 | 1.1248
76 | -0.031025 | -0.0078002 | 0.03105 | 0.0078157 | 2.4863e-05 | 1.5539e-05 | 0.047229 | 0.047229 | 0.047229 | 0.97766 | -0.4289 | 0.97852 | -0.41213 | 12.9751
77 | 0.001717 | 0.00043016 | -0.001717 | -0.00043032 | 3.6194e-08 | -1.5467e-07 | 0.002611 | 0.0026111 | 0.0026111 | 0.97852 | -0.41213 | 0.97849 | -0.41258 | 0.71732
78 | -0.032767 | -0.0082459 | 0.032786 | 0.0082576 | 1.8615e-05 | 1.1662e-05 | 0.04984 | 0.04984 | 0.04984 | 0.97852 | -0.41213 | 0.97912 | -0.40025 | 13.6924
79 | 0.001371 | 0.00034303 | -0.001371 | -0.00034359 | 8.0813e-08 | -5.6521e-07 | 0.0020896 | 0.0020899 | 0.0020899 | 0.97621 | -0.45735 | 0.97615 | -0.45859 | 0.57414
80 | -0.0012199 | -0.00030573 | 0.0012199 | 0.00030549 | 2.7334e-08 | -2.4184e-07 | 0.001867 | 0.0018669 | 0.001867 | 0.97224 | -0.53573 | 0.97226 | -0.53526 | 0.51292
81 | -0.0033062 | -0.00082836 | 0.0033065 | 0.00082812 | 3.703e-07 | -2.414e-07 | 0.0050599 | 0.0050597 | 0.0050599 | 0.97226 | -0.53526 | 0.97238 | -0.5329 | 1.3901
82 | -0.011246 | -0.0028187 | 0.01125 | 0.0028208 | 3.9381e-06 | 2.0804e-06 | 0.01721 | 0.01721 | 0.01721 | 0.97238 | -0.5329 | 0.97275 | -0.52556 | 4.728
83 | 0.0079397 | 0.0019906 | -0.0079375 | -0.0019897 | 2.1433e-06 | 8.9159e-07 | 0.01215 | 0.01215 | 0.01215 | 0.97238 | -0.5329 | 0.97209 | -0.53857 | 3.338
84 | 0.012762 | 0.0032058 | -0.012743 | -0.0031948 | 1.9898e-05 | 1.0998e-05 | 0.019492 | 0.019493 | 0.019493 | 0.97441 | -0.49284 | 0.97275 | -0.52556 | 5.3551
85 | -0.013652 | -0.0034288 | 0.013653 | 0.0034294 | 1.0762e-06 | 6.0651e-07 | 0.020851 | 0.020851 | 0.020851 | 0.97441 | -0.49284 | 0.9745 | -0.49118 | 5.7283
86 | -0.014161 | -0.0035565 | 0.014161 | 0.0035567 | 2.4298e-07 | 1.3824e-07 | 0.021625 | 0.021625 | 0.021625 | 0.9745 | -0.49118 | 0.97451 | -0.49082 | 5.941
87 | 0.0076319 | 0.0019131 | -0.0076297 | -0.0019122 | 2.2862e-06 | 9.0959e-07 | 0.011683 | 0.011683 | 0.011683 | 0.97209 | -0.53857 | 0.97178 | -0.54486 | 3.2096
88 | 0.01674 | 0.0042005 | -0.016737 | -0.0041988 | 2.9328e-06 | 1.7283e-06 | 0.025579 | 0.025579 | 0.025579 | 0.9739 | -0.50297 | 0.97371 | -0.50664 | 7.0272
89 | 0.016591 | 0.0041648 | -0.016582 | -0.0041592 | 9.5784e-06 | 5.6364e-06 | 0.025357 | 0.025357 | 0.025357 | 0.97371 | -0.50664 | 0.9731 | -0.51875 | 6.9663
90 | 0.00014581 | 3.3969e-05 | -0.00014581 | -3.4853e-05 | 1.316e-09 | -8.8418e-07 | 0.00022193 | 0.00022223 | 0.00022223 | 0.97371 | -0.50664 | 0.9737 | -0.50684 | 0.061053
91 | 0.0093763 | 0.0023534 | -0.0093613 | -0.0023462 | 1.5033e-05 | 7.2035e-06 | 0.014339 | 0.01434 | 0.01434 | 0.9731 | -0.51875 | 0.97139 | -0.55242 | 3.9396
92 | 0.00014581 | 3.4853e-05 | -0.00014581 | -3.6543e-05 | 2.5248e-09 | -1.6895e-06 | 0.00022223 | 0.00022283 | 0.00022283 | 0.9737 | -0.50684 | 0.97368 | -0.50721 | 0.061217
93 | 0.006752 | 0.0016922 | -0.0067519 | -0.0016922 | 8.3765e-08 | 2.7761e-08 | 0.010343 | 0.010343 | 0.010343 | 0.97139 | -0.55242 | 0.97138 | -0.55268 | 2.8415
94 | -0.0047 | -0.0011779 | 0.0047006 | 0.0011779 | 5.963e-07 | -1.5598e-08 | 0.0071195 | 0.0071193 | 0.0071195 | 0.98234 | -0.33747 | 0.98248 | -0.33481 | 1.9559
95 | -0.0091754 | -0.0022994 | 0.0091767 | 0.0023 | 1.3023e-06 | 6.0571e-07 | 0.013897 | 0.013896 | 0.013897 | 0.98248 | -0.33481 | 0.98263 | -0.33183 | 3.8177
96 | -0.015827 | -0.0039757 | 0.015832 | 0.0039783 | 4.5931e-06 | 2.6779e-06 | 0.024163 | 0.024163 | 0.024163 | 0.97481 | -0.48492 | 0.97512 | -0.47884 | 6.6382
97 | 0.015285 | 0.0038397 | -0.015284 | -0.0038394 | 4.3389e-07 | 2.512e-07 | 0.023335 | 0.023335 | 0.023335 | 0.97481 | -0.48492 | 0.97478 | -0.48552 | 6.4107
98 | -0.018998 | -0.0047719 | 0.018999 | 0.0047723 | 7.2825e-07 | 4.3726e-07 | 0.028995 | 0.028995 | 0.028995 | 0.97512 | -0.47884 | 0.97516 | -0.47804 | 7.9655
99 | 0.014744 | 0.0037041 | -0.014741 | -0.003702 | 3.7351e-06 | 2.1455e-06 | 0.022511 | 0.022511 | 0.022511 | 0.97478 | -0.48552 | 0.97451 | -0.49082 | 6.1842
100 | -0.0196 | -0.0049231 | 0.019614 | 0.0049312 | 1.3374e-05 | 8.062e-06 | 0.029913 | 0.029912 | 0.029913 | 0.97516 | -0.47804 | 0.97589 | -0.46375 | 8.2177
101 | 0.0025621 | 0.00064195 | -0.002562 | -0.0006421 | 9.4461e-08 | -1.4576e-07 | 0.0039066 | 0.0039067 | 0.0039067 | 0.97589 | -0.46375 | 0.97585 | -0.46452 | 1.0733
102 | -0.022176 | -0.0055731 | 0.022184 | 0.0055778 | 7.7209e-06 | 4.7164e-06 | 0.033819 | 0.033819 | 0.033819 | 0.97589 | -0.46375 | 0.97626 | -0.45646 | 9.2909
103 | -0.022184 | -0.0055778 | 0.022188 | 0.0055805 | 4.4129e-06 | 2.6956e-06 | 0.033819 | 0.033819 | 0.033819 | 0.97626 | -0.45646 | 0.97647 | -0.45229 | 9.2909
104 | 0.0056897 | 0.0014259 | -0.0056884 | -0.0014257 | 1.3307e-06 | 2.5331e-07 | 0.0086412 | 0.0086414 | 0.0086414 | 0.97977 | -0.38773 | 0.97952 | -0.39264 | 2.374
105 | -0.033245 | -0.0083727 | 0.033262 | 0.0083837 | 1.7547e-05 | 1.0999e-05 | 0.050538 | 0.050538 | 0.050538 | 0.97912 | -0.40025 | 0.97969 | -0.38922 | 13.8841
106 | -0.041444 | -0.010434 | 0.041468 | 0.010449 | 2.3366e-05 | 1.4756e-05 | 0.062966 | 0.062966 | 0.062966 | 0.97969 | -0.38922 | 0.98029 | -0.37743 | 17.2983
107 | -0.046568 | -0.011727 | 0.046617 | 0.011758 | 4.864e-05 | 3.0802e-05 | 0.070707 | 0.070707 | 0.070707 | 0.98029 | -0.37743 | 0.98141 | -0.35561 | 19.425
108 | -0.04878 | -0.0123 | 0.048797 | 0.012311 | 1.6276e-05 | 1.0316e-05 | 0.073988 | 0.073988 | 0.073988 | 0.98141 | -0.35561 | 0.98177 | -0.34865 | 20.3263
109 | -0.053897 | -0.013589 | 0.05394 | 0.013616 | 4.341e-05 | 2.7563e-05 | 0.081718 | 0.081718 | 0.081718 | 0.98177 | -0.34865 | 0.98263 | -0.33183 | 22.4499
110 | 0.078231 | 0.019875 | -0.078099 | -0.019792 | 0.00013195 | 8.3182e-05 | 0.11859 | 0.11859 | 0.11859 | 0.98243 | -0.33527 | 0.98063 | -0.37036 | 16.2894
111 | -0.078231 | -0.019875 | 0.078273 | 0.019901 | 4.2117e-05 | 2.655e-05 | 0.11859 | 0.11859 | 0.11859 | 0.98243 | -0.33527 | 0.98301 | -0.32409 | 16.2894
112 | 0.075801 | 0.019216 | -0.075764 | -0.019192 | 3.7019e-05 | 2.3317e-05 | 0.1151 | 0.1151 | 0.1151 | 0.98063 | -0.37036 | 0.9801 | -0.38053 | 15.8106
113 | -0.081551 | -0.020723 | 0.081552 | 0.020723 | 7.534e-07 | 4.755e-07 | 0.12355 | 0.12355 | 0.12355 | 0.98301 | -0.32409 | 0.98302 | -0.3239 | 16.9709
114 | -0.063117 | -0.015916 | 0.063141 | 0.015932 | 2.3791e-05 | 1.5138e-05 | 0.095614 | 0.095614 | 0.095614 | 0.98263 | -0.33183 | 0.98303 | -0.32396 | 26.2676
115 | 0.075764 | 0.019192 | -0.075559 | -0.019061 | 0.00020576 | 0.00013117 | 0.1151 | 0.1151 | 0.1151 | 0.9801 | -0.38053 | 0.9772 | -0.43724 | 31.6212
116 | -0.085553 | -0.021726 | 0.085634 | 0.021777 | 8.0619e-05 | 5.0947e-05 | 0.1296 | 0.1296 | 0.1296 | 0.98302 | -0.3239 | 0.98403 | -0.30434 | 17.8029
117 | -0.064161 | -0.016187 | 0.064196 | 0.016209 | 3.4525e-05 | 2.1972e-05 | 0.097159 | 0.097159 | 0.097159 | 0.98303 | -0.32396 | 0.98361 | -0.31273 | 26.692
118 | -0.067451 | -0.017025 | 0.06762 | 0.017133 | 0.00016967 | 0.00010804 | 0.10208 | 0.10208 | 0.10208 | 0.98361 | -0.31273 | 0.98631 | -0.26035 | 28.0448
119 | 0.10058 | 0.025601 | -0.1005 | -0.02555 | 7.9826e-05 | 5.0618e-05 | 0.15188 | 0.15188 | 0.15188 | 0.98631 | -0.26035 | 0.98546 | -0.27683 | 20.8622
120 | -0.1682 | -0.042734 | 0.16823 | 0.042754 | 3.1265e-05 | 1.9944e-05 | 0.25396 | 0.25396 | 0.25396 | 0.98631 | -0.26035 | 0.98651 | -0.25649 | 34.8846
121 | 0.098273 | 0.024993 | -0.098256 | -0.024982 | 1.6429e-05 | 1.0413e-05 | 0.14852 | 0.14852 | 0.14852 | 0.98546 | -0.27683 | 0.98528 | -0.2803 | 20.401
122 | -0.17112 | -0.04348 | 0.17131 | 0.043601 | 0.00019004 | 0.00012124 | 0.25833 | 0.25833 | 0.25833 | 0.98651 | -0.25649 | 0.98771 | -0.23346 | 35.4847
123 | 0.1751 | 0.044647 | -0.17485 | -0.044488 | 0.00024942 | 0.00015914 | 0.26366 | 0.26366 | 0.26366 | 0.98925 | -0.2039 | 0.98771 | -0.23346 | 36.217
124 | -0.09419 | -0.023925 | 0.094283 | 0.023984 | 9.3114e-05 | 5.8971e-05 | 0.14253 | 0.14253 | 0.14253 | 0.98414 | -0.30234 | 0.9852 | -0.28182 | 19.5783
125 | 0.089722 | 0.022805 | -0.089713 | -0.0228 | 8.6295e-06 | 5.4594e-06 | 0.13577 | 0.13577 | 0.13577 | 0.98414 | -0.30234 | 0.98403 | -0.30434 | 18.6503
126 | -0.095188 | -0.024211 | 0.095195 | 0.024215 | 6.9791e-06 | 4.4209e-06 | 0.1439 | 0.1439 | 0.1439 | 0.9852 | -0.28182 | 0.98528 | -0.2803 | 19.766
127 | -0.0026574 | -0.00066601 | 0.0026575 | 0.00066589 | 8.7799e-08 | -1.2096e-07 | 0.0040578 | 0.0040578 | 0.0040578 | 0.97448 | -0.4905 | 0.97452 | -0.48981 | 1.1148
128 | -0.070614 | -0.017753 | 0.07078 | 0.017859 | 0.00016571 | 0.00010558 | 0.10784 | 0.10784 | 0.10784 | 0.97452 | -0.48981 | 0.97701 | -0.44079 | 29.6271
129 | 0.033804 | 0.0085088 | -0.03378 | -0.0084941 | 2.3354e-05 | 1.4656e-05 | 0.051629 | 0.051629 | 0.051629 | 0.97452 | -0.48981 | 0.97378 | -0.50427 | 14.1838
130 | 0.034153 | 0.0085786 | -0.034141 | -0.008571 | 1.2123e-05 | 7.6105e-06 | 0.052156 | 0.052156 | 0.052156 | 0.97452 | -0.48981 | 0.97414 | -0.49725 | 14.3286
131 | -0.072861 | -0.01838 | 0.072873 | 0.018388 | 1.2395e-05 | 7.8994e-06 | 0.11101 | 0.11101 | 0.11101 | 0.97701 | -0.44079 | 0.9772 | -0.43724 | 30.4978
132 | 0.03263 | 0.0082057 | -0.032597 | -0.0081854 | 3.2385e-05 | 2.0295e-05 | 0.049871 | 0.049871 | 0.049871 | 0.97378 | -0.50427 | 0.97273 | -0.52508 | 13.7008
133 | 0.029588 | 0.0074298 | -0.02957 | -0.0074187 | 1.7884e-05 | 1.1155e-05 | 0.045201 | 0.045201 | 0.045201 | 0.97414 | -0.49725 | 0.9735 | -0.50993 | 12.4179
134 | -0.011069 | -0.0027744 | 0.01107 | 0.0027746 | 4.6861e-07 | 2.4633e-07 | 0.016974 | 0.016974 | 0.016974 | 0.97039 | -0.57127 | 0.97043 | -0.57038 | 4.6632
135 | 0.0089018 | 0.0022311 | -0.0089013 | -0.0022309 | 5.1644e-07 | 2.3922e-07 | 0.01365 | 0.01365 | 0.01365 | 0.97039 | -0.57127 | 0.97033 | -0.57249 | 3.7501
136 | -0.013989 | -0.0035061 | 0.013993 | 0.0035086 | 4.3404e-06 | 2.4669e-06 | 0.02145 | 0.02145 | 0.02145 | 0.97043 | -0.57038 | 0.97076 | -0.56387 | 5.8928
137 | -0.015706 | -0.0039379 | 0.015707 | 0.0039383 | 6.7194e-07 | 3.9182e-07 | 0.024075 | 0.024075 | 0.024075 | 0.97076 | -0.56387 | 0.97081 | -0.56297 | 6.614
138 | -0.017569 | -0.004405 | 0.017576 | 0.0044092 | 7.0741e-06 | 4.2056e-06 | 0.026929 | 0.026929 | 0.026929 | 0.97081 | -0.56297 | 0.97124 | -0.55453 | 7.3982
139 | -0.019179 | -0.004811 | 0.019179 | 0.0048111 | 5.9797e-08 | 3.5985e-08 | 0.029386 | 0.029386 | 0.029386 | 0.97124 | -0.55453 | 0.97124 | -0.55446 | 8.073
140 | -0.021004 | -0.0052683 | 0.021014 | 0.0052744 | 9.9594e-06 | 6.0565e-06 | 0.032181 | 0.032181 | 0.032181 | 0.97124 | -0.55446 | 0.97174 | -0.54452 | 8.8409
141 | 0.026077 | 0.0065433 | -0.026071 | -0.0065393 | 6.4745e-06 | 4.0086e-06 | 0.039863 | 0.039863 | 0.039863 | 0.9735 | -0.50993 | 0.97323 | -0.51514 | 10.9513
142 | 0.0058249 | 0.0014596 | -0.0058247 | -0.0014595 | 2.1264e-07 | 4.7437e-08 | 0.0089104 | 0.0089104 | 0.0089104 | 0.97273 | -0.52508 | 0.97269 | -0.52584 | 2.4479
143 | 0.026772 | 0.0067259 | -0.02677 | -0.0067244 | 2.3389e-06 | 1.4507e-06 | 0.04096 | 0.040961 | 0.040961 | 0.97273 | -0.52508 | 0.97263 | -0.52691 | 11.2529
144 | 0.002924 | 0.00073269 | -0.0029239 | -0.00073279 | 1.0107e-07 | -1.0251e-07 | 0.0044731 | 0.0044731 | 0.0044731 | 0.97269 | -0.52584 | 0.97265 | -0.52657 | 1.2289
145 | 0.0029007 | 0.00072682 | -0.0029005 | -0.00072695 | 1.2541e-07 | -1.3054e-07 | 0.0044374 | 0.0044375 | 0.0044375 | 0.97269 | -0.52584 | 0.97264 | -0.52675 | 1.2191
146 | 0.024431 | 0.0061382 | -0.024415 | -0.0061285 | 1.5732e-05 | 9.6961e-06 | 0.037382 | 0.037382 | 0.037382 | 0.97263 | -0.52691 | 0.97195 | -0.54041 | 10.2699
147 | 0.022777 | 0.0057179 | -0.022772 | -0.0057151 | 4.4686e-06 | 2.7385e-06 | 0.034874 | 0.034874 | 0.034874 | 0.97195 | -0.54041 | 0.97174 | -0.54452 | 9.5807

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33114 | 0.085074

## res_load
| p_mw | q_mvar
0 | 0.0067606 | 0.0016944
1 | 0.006397 | 0.0016032
2 | 0.0015755 | 0.00039486
3 | 0.00076839 | 0.00019258
4 | 0.0020347 | 0.00050994
5 | 0.0013542 | 0.0003394
6 | 0.0083451 | 0.0020915
7 | 0.0036387 | 0.00091195
8 | 0.0012757 | 0.00031972
9 | 0.003668 | 0.00091928
10 | 0.0027201 | 0.00068172
11 | 0.0016684 | 0.00041814
12 | 0.0017242 | 0.00043212
13 | 0.0021846 | 0.00054751
14 | 0.0019576 | 0.00049063
15 | 0.0013063 | 0.00032739
16 | 0.0020401 | 0.00051129
17 | 0.0020822 | 0.00052186
18 | 0.0021086 | 0.00052848
19 | 0.013354 | 0.0033469
20 | 0.0022391 | 0.00056118
21 | 0.0029462 | 0.00073839
22 | 0.003076 | 0.00077092
23 | 0.0029109 | 0.00072955
24 | 0.0016145 | 0.00040463
25 | 0.0015042 | 0.00037698
26 | 0.0012785 | 0.00032041
27 | 0.0030809 | 0.00077215
28 | 0.0027002 | 0.00067673
29 | 0.0032298 | 0.00080946
30 | 0.0049463 | 0.0012397
31 | 0.00046355 | 0.00011618
32 | 0.0046522 | 0.001166
33 | 0.0056383 | 0.0014131
34 | 0.0047874 | 0.0011998
35 | 0.0044134 | 0.0011061
36 | 0.0034953 | 0.000876
37 | 0.00027778 | 6.9618e-05
38 | 0.0042417 | 0.0010631
39 | 0.0033411 | 0.00083736
40 | 0.0019895 | 0.00049862
41 | 0.0023804 | 0.00059659
42 | 0.0022949 | 0.00057517
43 | 0.0020347 | 0.00050993
44 | 0.0010176 | 0.00025504
45 | 0.004078 | 0.001022
46 | 0.0034763 | 0.00087123
47 | 0.00033726 | 8.4525e-05
48 | 0.00036103 | 9.0482e-05
49 | 0.00035812 | 8.9752e-05
50 | 0.0013151 | 0.00032958
51 | 0.0012199 | 0.00030573
52 | 0.0020863 | 0.00052287
53 | 0.00088992 | 0.00022304
54 | 0.0014924 | 0.00037404
55 | 0.0005071 | 0.00012709
56 | 0.00030557 | 7.6583e-05
57 | 0.0076297 | 0.0019122
58 | 0.0028125 | 0.00070489
59 | 0.0072053 | 0.0018058
60 | 0.001371 | 0.00034359
61 | 0.00014581 | 3.6543e-05
62 | 0.0026093 | 0.00065396
63 | 0.0067519 | 0.0016922
64 | 0.0047 | 0.0011779
65 | 0.0044747 | 0.0011215
66 | 0.00054244 | 0.00013595
67 | 0.0031663 | 0.00079356
68 | 0.00054003 | 0.00013534
69 | 0.0006016 | 0.00015077
70 | 0.00057975 | 0.0001453
71 | 0.002562 | 0.0006421
72 | 0.0038617 | 0.00096784
73 | 0.00043295 | 0.00010851
74 | 0.0056884 | 0.0014257
75 | 0.00045928 | 0.00011511
76 | 0.0081821 | 0.0020506
77 | 0.0051001 | 0.0012782
78 | 0.001717 | 0.00043032
79 | 0.0021638 | 0.00054229
80 | 0.0051001 | 0.0012782
81 | 0.0022975 | 0.0005758
82 | 0.003278 | 0.00082153
83 | 0.0040012 | 0.0010028
84 | 0.0010205 | 0.00025577
85 | 0.0032551 | 0.00081581
86 | 0.0022236 | 0.00055729
87 | 0.0028967 | 0.00072598
88 | 0.001452 | 0.00036391
89 | 0.0027047 | 0.00067786
90 | 0.0044682 | 0.0011198
91 | 0.00090517 | 0.00022686
92 | 0.0040798 | 0.0010225
93 | 0.0030609 | 0.00076714
94 | 0.0035385 | 0.00088682
95 | 0.0026574 | 0.00066601
96 | 0.0020809 | 0.00052152
97 | 0.0011506 | 0.00028837
98 | 0.0045533 | 0.0011412
99 | 0.0021675 | 0.00054324
100 | 0.0029189 | 0.00073155
101 | 0.0089013 | 0.0022309
102 | 0.0017128 | 0.00042927
103 | 0.0018623 | 0.00046673
104 | 0.0016033 | 0.00040183
105 | 0.0018244 | 0.00045724
106 | 0.0034925 | 0.00087531
107 | 0.0022453 | 0.00056272
108 | 0.0026855 | 0.00067305
109 | 0.0023389 | 0.00058619
110 | 0.0029239 | 0.00073279
111 | 0.0029005 | 0.00072695
112 | 0.0016386 | 0.00041067
113 | 0.0017586 | 0.00044076

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1