## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2152-3_1_2_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_2152-3_1_2_node_127 | 0.4 | n |  | TRUE
2 | bus_LV_2152-3_1_2_node_130 | 0.4 | n |  | TRUE
3 | bus_LV_2152-3_1_2_node_126 | 0.4 | n |  | TRUE
4 | bus_LV_2152-3_1_2_node_131 | 0.4 | n |  | TRUE
5 | bus_LV_2152-3_1_2_node_132 | 0.4 | n |  | TRUE
6 | bus_LV_2152-3_1_2_node_124 | 0.4 | n |  | TRUE
7 | bus_LV_2152-3_1_2_node_135 | 0.4 | n |  | TRUE
8 | bus_LV_2152-3_1_2_node_134 | 0.4 | n |  | TRUE
9 | bus_LV_2152-3_1_2_node_133 | 0.4 | n |  | TRUE
10 | bus_LV_2152-3_1_2_node_137 | 0.4 | n |  | TRUE
11 | bus_LV_2152-3_1_2_node_106 | 0.4 | n |  | TRUE
12 | bus_LV_2152-3_1_2_node_120 | 0.4 | n |  | TRUE
13 | bus_LV_2152-3_1_2_node_138 | 0.4 | n |  | TRUE
14 | bus_LV_2152-3_1_2_node_118 | 0.4 | n |  | TRUE
15 | bus_LV_2152-3_1_2_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_2152-3_1_2_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_2152-3_1_2_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_2152-3_1_2_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_2152-3_1_2_node_89 | 0.4 | n |  | TRUE
20 | bus_LV_2152-3_1_2_node_90 | 0.4 | n |  | TRUE
21 | bus_LV_2152-3_1_2_node_105 | 0.4 | n |  | TRUE
22 | bus_LV_2152-3_1_2_node_117 | 0.4 | n |  | TRUE
23 | bus_LV_2152-3_1_2_node_119 | 0.4 | n |  | TRUE
24 | bus_LV_2152-3_1_2_node_121 | 0.4 | n |  | TRUE
25 | bus_LV_2152-3_1_2_node_123 | 0.4 | n |  | TRUE
26 | bus_LV_2152-3_1_2_node_122 | 0.4 | n |  | TRUE
27 | bus_LV_2152-3_1_2_node_125 | 0.4 | n |  | TRUE
28 | bus_MV_31_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2152-3_1_2_load_128 | 0 | 0.096891 | 0.024283 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2152-3_1_2_load_127 | 1 | 0.019188 | 0.004809 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2152-3_1_2_load_126 | 3 | 0.0484 | 0.01213 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2152-3_1_2_load_131 | 4 | 0.014173 | 0.003552 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2152-3_1_2_load_124 | 6 | 0.0086284 | 0.0021625 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2152-3_1_2_load_135 | 7 | 0.0060087 | 0.0015059 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2152-3_1_2_load_134 | 8 | 0.0043963 | 0.0011018 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2152-3_1_2_load_133 | 9 | 0.012876 | 0.0032269 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2152-3_1_2_load_137 | 10 | 0.0046453 | 0.0011642 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2152-3_1_2_load_106 | 11 | 0.0021859 | 0.00054783 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2152-3_1_2_load_120 | 12 | 0.00046901 | 0.00011754 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2152-3_1_2_load_138 | 13 | 0.0012853 | 0.00032213 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2152-3_1_2_load_118 | 14 | 0.00059219 | 0.00014842 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2152-3_1_2_load_21 | 15 | 0.00017464 | 4.3769e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2152-3_1_2_load_22 | 16 | 0.0018927 | 0.00047435 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2152-3_1_2_load_23 | 17 | 0.00016535 | 4.1442e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2152-3_1_2_load_89 | 19 | 0.0026099 | 0.00065409 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2152-3_1_2_load_90 | 20 | 0.0047652 | 0.0011943 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2152-3_1_2_load_105 | 21 | 0.00074446 | 0.00018658 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2152-3_1_2_load_117 | 22 | 0.002042 | 0.00051178 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2152-3_1_2_load_119 | 23 | 0.0020337 | 0.0005097 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2152-3_1_2_load_121 | 24 | 0.012936 | 0.003242 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2152-3_1_2_load_122 | 26 | 0.013559 | 0.0033982 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2152-3_1_2_line_0 |  | 0 | 1 | 0.037196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2152-3_1_2_line_1 |  | 1 | 27 | 0.057231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2152-3_1_2_line_2 |  | 2 | 3 | 0.036984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_2152-3_1_2_line_3 |  | 2 | 4 | 0.033786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2152-3_1_2_line_4 |  | 2 | 5 | 0.075408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2152-3_1_2_line_5 |  | 3 | 25 | 0.030127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2152-3_1_2_line_6 |  | 4 | 6 | 0.031257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2152-3_1_2_line_7 |  | 5 | 7 | 0.03561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2152-3_1_2_line_8 |  | 5 | 8 | 0.072069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2152-3_1_2_line_9 |  | 6 | 20 | 0.17384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2152-3_1_2_line_10 |  | 6 | 26 | 0.04173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2152-3_1_2_line_11 |  | 8 | 9 | 0.010685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2152-3_1_2_line_12 |  | 10 | 11 | 0.3472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2152-3_1_2_line_13 |  | 10 | 12 | 0.36134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2152-3_1_2_line_14 |  | 11 | 18 | 0.37634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2152-3_1_2_line_15 |  | 11 | 21 | 0.007451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2152-3_1_2_line_16 |  | 12 | 23 | 0.030511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2152-3_1_2_line_17 |  | 13 | 14 | 0.54864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2152-3_1_2_line_18 |  | 14 | 22 | 0.029206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2152-3_1_2_line_19 |  | 15 | 16 | 0.039247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2152-3_1_2_line_20 |  | 15 | 17 | 0.0030288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2152-3_1_2_line_21 |  | 16 | 18 | 0.020197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2152-3_1_2_line_22 |  | 18 | 19 | 0.098737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2152-3_1_2_line_23 |  | 19 | 20 | 0.32881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2152-3_1_2_line_24 |  | 22 | 23 | 0.034805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2152-3_1_2_line_25 |  | 24 | 25 | 0.011504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2152-3_1_2_line_26 |  | 25 | 27 | 0.012739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2152-3_1_2_trafo_122 | 0.63 MVA 20/0.4 kV | 28 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2563460.987 | 1163496.268 | 2563438.9338 | 1163466.3145
1 | 2563497.1187 | 1163540.5886 | 2563474.9743 | 1163515.266 | 2563460.987 | 1163496.268
2 | 2563533.4534 | 1163598.2527 | 2563508.2287 | 1163571.2053
3 | 2563533.4534 | 1163598.2527 | 2563505.0773 | 1163616.5912
4 | 2563533.4534 | 1163598.2527 | 2563543.6913 | 1163591.5314 | 2563549.4423 | 1163597.6441 | 2563554.692 | 1163603.1817 | 2563586.7874 | 1163637.7044
5 | 2563487.681 | 1163549.1727 | 2563508.2287 | 1163571.2053
6 | 2563479.9788 | 1163635.0536 | 2563488.4254 | 1163627.3528 | 2563505.0773 | 1163616.5912
7 | 2563586.7874 | 1163637.7044 | 2563590.2413 | 1163641.4187 | 2563611.1199 | 1163663.7043
8 | 2563586.7874 | 1163637.7044 | 2563577.8354 | 1163646.7968 | 2563536.7508 | 1163675.6835 | 2563530.7239 | 1163668.8849
9 | 2563479.9788 | 1163635.0536 | 2563381.9129 | 1163778.5912
10 | 2563449.883 | 1163610.1739 | 2563472.954 | 1163634.9398 | 2563475.3743 | 1163636.1924 | 2563477.0775 | 1163636.6711 | 2563478.9118 | 1163636.0263 | 2563479.9788 | 1163635.0536
11 | 2563523.6358 | 1163660.8891 | 2563530.7239 | 1163668.8849
12 | 2563326.3979 | 1164336.3451 | 2563012.295 | 1164188.4041
13 | 2562671.7737 | 1164309.2886 | 2563012.295 | 1164188.4041
14 | 2563636.0214 | 1164122.4214 | 2563326.3979 | 1164336.3451
15 | 2563326.3979 | 1164336.3451 | 2563330.4316 | 1164342.6098
16 | 2562655.2364 | 1164334.929 | 2562671.7737 | 1164309.2886
17 | 2562620.2523 | 1164388.5328 | 2562644.6689 | 1164936.6244
18 | 2562636.3717 | 1164364.178 | 2562636.1322 | 1164364.5494 | 2562620.2523 | 1164388.5328
19 | 2563656.1916 | 1164123.4534 | 2563662.245 | 1164123.7631 | 2563674.7106 | 1164127.1004 | 2563692.647 | 1164136.5665
20 | 2563695.3256 | 1164137.9802 | 2563692.647 | 1164136.5665
21 | 2563636.0214 | 1164122.4214 | 2563656.1916 | 1164123.4534
22 | 2563636.0214 | 1164122.4214 | 2563576.5463 | 1164043.6072
23 | 2563576.5463 | 1164043.6072 | 2563381.9129 | 1163778.5912
24 | 2562636.3717 | 1164364.178 | 2562655.2364 | 1164334.929
25 | 2563487.681 | 1163549.1727 | 2563479.1715 | 1163556.9146
26 | 2563497.1187 | 1163540.5886 | 2563487.681 | 1163549.1727

## bus_geodata
| x | y | coords
0 | 2563438.9338 | 1163466.3145
1 | 2563460.987 | 1163496.268
2 | 2563533.4534 | 1163598.2527
3 | 2563508.2287 | 1163571.2053
4 | 2563505.0773 | 1163616.5912
5 | 2563586.7874 | 1163637.7044
6 | 2563479.9788 | 1163635.0536
7 | 2563611.1199 | 1163663.7043
8 | 2563530.7239 | 1163668.8849
9 | 2563523.6358 | 1163660.8891
10 | 2563012.295 | 1164188.4041
11 | 2563326.3979 | 1164336.3451
12 | 2562671.7737 | 1164309.2886
13 | 2562644.6689 | 1164936.6244
14 | 2562620.2523 | 1164388.5328
15 | 2563692.647 | 1164136.5665
16 | 2563656.1916 | 1164123.4534
17 | 2563695.3256 | 1164137.9802
18 | 2563636.0214 | 1164122.4214
19 | 2563576.5463 | 1164043.6072
20 | 2563381.9129 | 1163778.5912
21 | 2563330.4316 | 1164342.6098
22 | 2562636.3717 | 1164364.178
23 | 2562655.2364 | 1164334.929
24 | 2563479.1715 | 1163556.9146
25 | 2563487.681 | 1163549.1727
26 | 2563449.883 | 1163610.1739
27 | 2563497.1187 | 1163540.5886
28 | 2563487.681 | 1163549.1727

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97133 | -0.55266 | 0.096891 | 0.024283
1 | 0.97469 | -0.48631 | 0.019188 | 0.004809
2 | 0.98895 | -0.20984 | 0 | 0
3 | 0.9859 | -0.26849 | 0.0484 | 0.01213
4 | 0.9921 | -0.14961 | 0.014173 | 0.003552
5 | 0.98734 | -0.24119 | 0 | 0
6 | 0.99522 | -0.090329 | 0.0086284 | 0.0021625
7 | 0.98714 | -0.24501 | 0.0060087 | 0.0015059
8 | 0.98619 | -0.26347 | 0.0043963 | 0.0011018
9 | 0.98607 | -0.26594 | 0.012876 | 0.0032269
10 | 0.97572 | -0.46876 | 0.0046453 | 0.0011642
11 | 0.97929 | -0.39843 | 0.0021859 | 0.00054783
12 | 0.97355 | -0.51151 | 0.00046901 | 0.00011754
13 | 0.97255 | -0.53148 | 0.0012853 | 0.00032213
14 | 0.97321 | -0.51841 | 0.00059219 | 0.00014842
15 | 0.98413 | -0.30388 | 0.00017464 | 4.3769e-05
16 | 0.98414 | -0.30364 | 0.0018927 | 0.00047435
17 | 0.98413 | -0.30389 | 0.00016535 | 4.1442e-05
18 | 0.98419 | -0.30282 | 0 | 0
19 | 0.98567 | -0.27393 | 0.0026099 | 0.00065409
20 | 0.99142 | -0.16305 | 0.0047652 | 0.0011943
21 | 0.97928 | -0.39853 | 0.00074446 | 0.00018658
22 | 0.97326 | -0.51739 | 0.002042 | 0.00051178
23 | 0.97339 | -0.51486 | 0.0020337 | 0.0005097
24 | 0.98214 | -0.34114 | 0.012936 | 0.003242
25 | 0.98228 | -0.33845 | 0 | 0
26 | 1 | 0 | -0.25354 | -0.064954
27 | 0.9809 | -0.3652 | 0 | 0
28 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.096891 | -0.024283 | 0.097198 | 0.024479 | 0.00030731 | 0.00019622 | 0.14843 | 0.14843 | 0.14843 | 0.97133 | -0.55266 | 0.97469 | -0.48631 | 40.7778
1 | -0.11639 | -0.029288 | 0.11706 | 0.029722 | 0.00067789 | 0.00043313 | 0.17772 | 0.17772 | 0.17772 | 0.97469 | -0.48631 | 0.9809 | -0.3652 | 48.8254
2 | 0.1795 | 0.045796 | -0.17899 | -0.045472 | 0.00050692 | 0.00032348 | 0.27037 | 0.27037 | 0.27037 | 0.98895 | -0.20984 | 0.9859 | -0.26849 | 37.1389
3 | -0.20284 | -0.051664 | 0.20343 | 0.052041 | 0.0005912 | 0.0003775 | 0.30549 | 0.30549 | 0.30549 | 0.98895 | -0.20984 | 0.9921 | -0.14961 | 41.963
4 | 0.023337 | 0.005868 | -0.023302 | -0.0058466 | 3.4879e-05 | 2.1356e-05 | 0.03512 | 0.03512 | 0.03512 | 0.98895 | -0.20984 | 0.98734 | -0.24119 | 9.6484
5 | 0.13059 | 0.033342 | -0.13015 | -0.033061 | 0.00043989 | 0.00028114 | 0.19732 | 0.19732 | 0.19732 | 0.9859 | -0.26849 | 0.98228 | -0.33845 | 54.2094
6 | -0.2176 | -0.055593 | 0.21823 | 0.055993 | 0.00062571 | 0.00039964 | 0.32675 | 0.32675 | 0.32675 | 0.9921 | -0.14961 | 0.99522 | -0.090329 | 44.8829
7 | 0.0060098 | 0.0015062 | -0.0060087 | -0.0015059 | 1.0955e-06 | 2.458e-07 | 0.0090574 | 0.0090576 | 0.0090576 | 0.98734 | -0.24119 | 0.98714 | -0.24501 | 2.4883
8 | 0.017292 | 0.0043404 | -0.017273 | -0.0043296 | 1.8358e-05 | 1.0829e-05 | 0.026063 | 0.026063 | 0.026063 | 0.98734 | -0.24119 | 0.98619 | -0.26347 | 7.1602
9 | 0.02393 | 0.0060936 | -0.023846 | -0.0060423 | 8.3615e-05 | 5.1263e-05 | 0.035814 | 0.035814 | 0.035814 | 0.99522 | -0.090329 | 0.99142 | -0.16305 | 9.8391
10 | -0.25078 | -0.064249 | 0.25189 | 0.064954 | 0.001103 | 0.00070483 | 0.37546 | 0.37546 | 0.37546 | 0.99522 | -0.090329 | 1 | 0 | 51.5744
11 | 0.012877 | 0.0032278 | -0.012876 | -0.0032269 | 1.5127e-06 | 8.3181e-07 | 0.01943 | 0.01943 | 0.01943 | 0.98619 | -0.26347 | 0.98607 | -0.26594 | 5.3379
12 | -0.011083 | -0.0027711 | 0.01112 | 0.0027906 | 3.7181e-05 | 1.9444e-05 | 0.0169 | 0.016898 | 0.0169 | 0.97572 | -0.46876 | 0.97929 | -0.39843 | 4.6428
13 | 0.0064376 | 0.0016069 | -0.0064246 | -0.0016031 | 1.3057e-05 | 3.8532e-06 | 0.0098154 | 0.009817 | 0.009817 | 0.97572 | -0.46876 | 0.97355 | -0.51151 | 2.697
14 | -0.01405 | -0.0035249 | 0.014115 | 0.0035613 | 6.4327e-05 | 3.6411e-05 | 0.021351 | 0.021349 | 0.021351 | 0.97929 | -0.39843 | 0.98419 | -0.30282 | 5.8656
15 | 0.00074447 | 0.00018649 | -0.00074446 | -0.00018658 | 3.5753e-09 | -9.1456e-08 | 0.0011312 | 0.0011312 | 0.0011312 | 0.97929 | -0.39843 | 0.97928 | -0.39853 | 0.31077
16 | 0.0059556 | 0.0014855 | -0.0059546 | -0.0014853 | 9.4752e-07 | 2.2709e-07 | 0.0091001 | 0.0091003 | 0.0091003 | 0.97355 | -0.51151 | 0.97339 | -0.51486 | 2.5001
17 | -0.0012853 | -0.00032213 | 0.0012861 | 0.00031582 | 7.9466e-07 | -6.304e-06 | 0.0019665 | 0.0019641 | 0.0019665 | 0.97255 | -0.53148 | 0.97321 | -0.51841 | 0.54026
18 | -0.0018783 | -0.00046424 | 0.0018784 | 0.00046394 | 9.0181e-08 | -3.0521e-07 | 0.0028696 | 0.0028694 | 0.0028696 | 0.97321 | -0.51841 | 0.97326 | -0.51739 | 0.78834
19 | -0.00033999 | -8.5172e-05 | 0.00034 | 8.4676e-05 | 3.8879e-09 | -4.962e-07 | 0.00051406 | 0.00051388 | 0.00051406 | 0.98413 | -0.30388 | 0.98414 | -0.30364 | 0.14123
20 | 0.00016535 | 4.1403e-05 | -0.00016535 | -4.1442e-05 | 7.0955e-11 | -3.8439e-08 | 0.00025 | 0.00025002 | 0.00025002 | 0.98413 | -0.30388 | 0.98413 | -0.30389 | 0.068686
21 | -0.0022327 | -0.00055902 | 0.0022328 | 0.00055882 | 8.6297e-08 | -2.0141e-07 | 0.0033756 | 0.0033755 | 0.0033756 | 0.98414 | -0.30364 | 0.98419 | -0.30282 | 0.92736
22 | -0.016347 | -0.0041201 | 0.01637 | 0.0041333 | 2.2634e-05 | 1.3229e-05 | 0.024724 | 0.024724 | 0.024724 | 0.98419 | -0.30282 | 0.98567 | -0.27393 | 6.7924
23 | -0.01898 | -0.0047874 | 0.019081 | 0.0048481 | 0.0001013 | 6.0619e-05 | 0.028664 | 0.028662 | 0.028664 | 0.98567 | -0.27393 | 0.99142 | -0.16305 | 7.8747
24 | -0.0039204 | -0.00097571 | 0.0039209 | 0.00097558 | 4.6852e-07 | -1.3273e-07 | 0.0059915 | 0.0059913 | 0.0059915 | 0.97326 | -0.51739 | 0.97339 | -0.51486 | 1.646
25 | -0.012936 | -0.003242 | 0.012937 | 0.0032429 | 1.657e-06 | 9.149e-07 | 0.019598 | 0.019598 | 0.019598 | 0.98214 | -0.34114 | 0.98228 | -0.33845 | 5.3842
26 | 0.11722 | 0.029818 | -0.11706 | -0.029722 | 0.00015089 | 9.6408e-05 | 0.17772 | 0.17772 | 0.17772 | 0.98228 | -0.33845 | 0.9809 | -0.3652 | 48.8253

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2671 | 0.068352

## res_load
| p_mw | q_mvar
0 | 0.096891 | 0.024283
1 | 0.019188 | 0.004809
2 | 0.0484 | 0.01213
3 | 0.014173 | 0.003552
4 | 0.0086284 | 0.0021625
5 | 0.0060087 | 0.0015059
6 | 0.0043963 | 0.0011018
7 | 0.012876 | 0.0032269
8 | 0.0046453 | 0.0011642
9 | 0.0021859 | 0.00054783
10 | 0.00046901 | 0.00011754
11 | 0.0012853 | 0.00032213
12 | 0.00059219 | 0.00014842
13 | 0.00017464 | 4.3769e-05
14 | 0.0018927 | 0.00047435
15 | 0.00016535 | 4.1442e-05
16 | 0.0026099 | 0.00065409
17 | 0.0047652 | 0.0011943
18 | 0.00074446 | 0.00018658
19 | 0.002042 | 0.00051178
20 | 0.0020337 | 0.0005097
21 | 0.012936 | 0.003242
22 | 0.013559 | 0.0033982

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1