## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2152-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2152-4_0_3_node_4 | 0.4 | n |  | TRUE
2 | bus_LV_2152-4_0_3_node_13 | 0.4 | n |  | TRUE
3 | bus_LV_2152-4_0_3_node_1 | 0.4 | n |  | TRUE
4 | bus_LV_2152-4_0_3_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_2152-4_0_3_node_2 | 0.4 | n |  | TRUE
6 | bus_LV_2152-4_0_3_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_2152-4_0_3_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_2152-4_0_3_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_2152-4_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2152-4_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2152-4_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2152-4_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2152-4_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2152-4_0_3_node_35 | 0.4 | n |  | TRUE
15 | bus_LV_2152-4_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2152-4_0_3_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_2152-4_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2152-4_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_2152-4_0_3_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_2152-4_0_3_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_2152-4_0_3_node_133 | 0.4 | n |  | TRUE
22 | bus_LV_2152-4_0_3_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_2152-4_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_2152-4_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_2152-4_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_2152-4_0_3_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_2152-4_0_3_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_2152-4_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_2152-4_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2152-4_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_2152-4_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_2152-4_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_2152-4_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_2152-4_0_3_node_98 | 0.4 | n |  | TRUE
35 | bus_LV_2152-4_0_3_node_99 | 0.4 | n |  | TRUE
36 | bus_LV_2152-4_0_3_node_97 | 0.4 | n |  | TRUE
37 | bus_LV_2152-4_0_3_node_95 | 0.4 | n |  | TRUE
38 | bus_LV_2152-4_0_3_node_94 | 0.4 | n |  | TRUE
39 | bus_LV_2152-4_0_3_node_107 | 0.4 | n |  | TRUE
40 | bus_LV_2152-4_0_3_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_2152-4_0_3_node_104 | 0.4 | n |  | TRUE
42 | bus_LV_2152-4_0_3_node_100 | 0.4 | n |  | TRUE
43 | bus_LV_2152-4_0_3_node_96 | 0.4 | n |  | TRUE
44 | bus_LV_2152-4_0_3_node_92 | 0.4 | n |  | TRUE
45 | bus_LV_2152-4_0_3_node_108 | 0.4 | n |  | TRUE
46 | bus_LV_2152-4_0_3_node_105 | 0.4 | n |  | TRUE
47 | bus_LV_2152-4_0_3_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_2152-4_0_3_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_2152-4_0_3_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_2152-4_0_3_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_2152-4_0_3_node_123 | 0.4 | n |  | TRUE
52 | bus_LV_2152-4_0_3_node_117 | 0.4 | n |  | TRUE
53 | bus_LV_2152-4_0_3_node_134 | 0.4 | n |  | TRUE
54 | bus_LV_2152-4_0_3_node_36 | 0.4 | n |  | TRUE
55 | bus_LV_2152-4_0_3_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_2152-4_0_3_node_112 | 0.4 | n |  | TRUE
57 | bus_LV_2152-4_0_3_node_106 | 0.4 | n |  | TRUE
58 | bus_LV_2152-4_0_3_node_103 | 0.4 | n |  | TRUE
59 | bus_LV_2152-4_0_3_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_2152-4_0_3_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_2152-4_0_3_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_2152-4_0_3_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_2152-4_0_3_node_69 | 0.4 | n |  | TRUE
64 | bus_LV_2152-4_0_3_node_73 | 0.4 | n |  | TRUE
65 | bus_LV_2152-4_0_3_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_2152-4_0_3_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_2152-4_0_3_node_45 | 0.4 | n |  | TRUE
68 | bus_LV_2152-4_0_3_node_91 | 0.4 | n |  | TRUE
69 | bus_LV_2152-4_0_3_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_2152-4_0_3_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_2152-4_0_3_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_2152-4_0_3_node_109 | 0.4 | n |  | TRUE
73 | bus_LV_2152-4_0_3_node_50 | 0.4 | n |  | TRUE
74 | bus_LV_2152-4_0_3_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_2152-4_0_3_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_2152-4_0_3_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_2152-4_0_3_node_57 | 0.4 | n |  | TRUE
78 | bus_LV_2152-4_0_3_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_2152-4_0_3_node_53 | 0.4 | n |  | TRUE
80 | bus_LV_2152-4_0_3_node_51 | 0.4 | n |  | TRUE
81 | bus_LV_2152-4_0_3_node_52 | 0.4 | n |  | TRUE
82 | bus_LV_2152-4_0_3_node_54 | 0.4 | n |  | TRUE
83 | bus_LV_2152-4_0_3_node_60 | 0.4 | n |  | TRUE
84 | bus_LV_2152-4_0_3_node_61 | 0.4 | n |  | TRUE
85 | bus_LV_2152-4_0_3_node_59 | 0.4 | n |  | TRUE
86 | bus_LV_2152-4_0_3_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_2152-4_0_3_node_83 | 0.4 | n |  | TRUE
88 | bus_LV_2152-4_0_3_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_2152-4_0_3_node_62 | 0.4 | n |  | TRUE
90 | bus_LV_2152-4_0_3_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_2152-4_0_3_node_63 | 0.4 | n |  | TRUE
92 | bus_LV_2152-4_0_3_node_65 | 0.4 | n |  | TRUE
93 | bus_LV_2152-4_0_3_node_68 | 0.4 | n |  | TRUE
94 | bus_LV_2152-4_0_3_node_84 | 0.4 | n |  | TRUE
95 | bus_LV_2152-4_0_3_node_85 | 0.4 | n |  | TRUE
96 | bus_LV_2152-4_0_3_node_71 | 0.4 | n |  | TRUE
97 | bus_LV_2152-4_0_3_node_72 | 0.4 | n |  | TRUE
98 | bus_LV_2152-4_0_3_node_74 | 0.4 | n |  | TRUE
99 | bus_LV_2152-4_0_3_node_75 | 0.4 | n |  | TRUE
100 | bus_LV_2152-4_0_3_node_76 | 0.4 | n |  | TRUE
101 | bus_LV_2152-4_0_3_node_77 | 0.4 | n |  | TRUE
102 | bus_LV_2152-4_0_3_node_78 | 0.4 | n |  | TRUE
103 | bus_LV_2152-4_0_3_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_2152-4_0_3_node_80 | 0.4 | n |  | TRUE
105 | bus_LV_2152-4_0_3_node_81 | 0.4 | n |  | TRUE
106 | bus_LV_2152-4_0_3_node_86 | 0.4 | n |  | TRUE
107 | bus_LV_2152-4_0_3_node_87 | 0.4 | n |  | TRUE
108 | bus_LV_2152-4_0_3_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_2152-4_0_3_node_89 | 0.4 | n |  | TRUE
110 | bus_LV_2152-4_0_3_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_2152-4_0_3_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_2152-4_0_3_node_113 | 0.4 | n |  | TRUE
113 | bus_LV_2152-4_0_3_node_114 | 0.4 | n |  | TRUE
114 | bus_LV_2152-4_0_3_node_101 | 0.4 | n |  | TRUE
115 | bus_LV_2152-4_0_3_node_102 | 0.4 | n |  | TRUE
116 | bus_LV_2152-4_0_3_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_2152-4_0_3_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_2152-4_0_3_node_142 | 0.4 | n |  | TRUE
119 | bus_LV_2152-4_0_3_node_138 | 0.4 | n |  | TRUE
120 | bus_LV_2152-4_0_3_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_2152-4_0_3_node_144 | 0.4 | n |  | TRUE
122 | bus_LV_2152-4_0_3_node_140 | 0.4 | n |  | TRUE
123 | bus_LV_2152-4_0_3_node_139 | 0.4 | n |  | TRUE
124 | bus_LV_2152-4_0_3_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_2152-4_0_3_node_118 | 0.4 | n |  | TRUE
126 | bus_LV_2152-4_0_3_node_119 | 0.4 | n |  | TRUE
127 | bus_LV_2152-4_0_3_node_120 | 0.4 | n |  | TRUE
128 | bus_LV_2152-4_0_3_node_128 | 0.4 | n |  | TRUE
129 | bus_LV_2152-4_0_3_node_126 | 0.4 | n |  | TRUE
130 | bus_LV_2152-4_0_3_node_124 | 0.4 | n |  | TRUE
131 | bus_LV_2152-4_0_3_node_125 | 0.4 | n |  | TRUE
132 | bus_LV_2152-4_0_3_node_121 | 0.4 | n |  | TRUE
133 | bus_LV_2152-4_0_3_node_132 | 0.4 | n |  | TRUE
134 | bus_LV_2152-4_0_3_node_122 | 0.4 | n |  | TRUE
135 | bus_LV_2152-4_0_3_node_127 | 0.4 | n |  | TRUE
136 | bus_LV_2152-4_0_3_node_131 | 0.4 | n |  | TRUE
137 | bus_LV_2152-4_0_3_node_130 | 0.4 | n |  | TRUE
138 | bus_LV_2152-4_0_3_node_129 | 0.4 | n |  | TRUE
139 | bus_LV_2152-4_0_3_node_135 | 0.4 | n |  | TRUE
140 | bus_LV_2152-4_0_3_node_136 | 0.4 | n |  | TRUE
141 | bus_LV_2152-4_0_3_node_137 | 0.4 | n |  | TRUE
142 | bus_LV_2152-4_0_3_node_141 | 0.4 | n |  | TRUE
143 | bus_LV_2152-4_0_3_node_143 | 0.4 | n |  | TRUE
144 | bus_MV_31_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2152-4_0_3_load_0 | 0 | 0.00047685 | 0.00011951 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2152-4_0_3_load_4 | 1 | 0.000367 | 9.1978e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2152-4_0_3_load_13 | 2 | 0.00074088 | 0.00018568 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2152-4_0_3_load_2 | 5 | 0.00076277 | 0.00019117 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2152-4_0_3_load_3 | 6 | 0.0001223 | 3.065e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2152-4_0_3_load_14 | 7 | 0.00068753 | 0.00017231 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2152-4_0_3_load_15 | 8 | 0.003444 | 0.00086316 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2152-4_0_3_load_5 | 9 | 0.00034703 | 8.6973e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2152-4_0_3_load_7 | 10 | 0.0022856 | 0.00057282 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2152-4_0_3_load_9 | 12 | 0.0068284 | 0.0017114 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2152-4_0_3_load_10 | 13 | 0.002583 | 0.00064736 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2152-4_0_3_load_35 | 14 | 0.0009868 | 0.00024732 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2152-4_0_3_load_34 | 16 | 0.0021323 | 0.0005344 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2152-4_0_3_load_12 | 17 | 0.001771 | 0.00044386 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2152-4_0_3_load_33 | 19 | 0.00063469 | 0.00015907 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2152-4_0_3_load_30 | 20 | 0.00019781 | 4.9575e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2152-4_0_3_load_133 | 21 | 0.00070649 | 0.00017706 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2152-4_0_3_load_28 | 22 | 0.00048227 | 0.00012087 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2152-4_0_3_load_17 | 23 | 0.00035916 | 9.0013e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2152-4_0_3_load_18 | 24 | 0.0019455 | 0.00048758 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2152-4_0_3_load_22 | 28 | 0.0014806 | 0.00037107 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2152-4_0_3_load_24 | 30 | 0.0021667 | 0.00054302 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2152-4_0_3_load_26 | 32 | 0.0013552 | 0.00033966 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2152-4_0_3_load_27 | 33 | 0.00097429 | 0.00024418 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2152-4_0_3_load_98 | 34 | 0.0019116 | 0.00047909 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2152-4_0_3_load_99 | 35 | 0.00040809 | 0.00010228 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2152-4_0_3_load_97 | 36 | 0.0024672 | 0.00061834 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2152-4_0_3_load_95 | 37 | 0.002191 | 0.00054913 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2152-4_0_3_load_94 | 38 | 0.00031388 | 7.8666e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2152-4_0_3_load_107 | 39 | 0.00032451 | 8.133e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2152-4_0_3_load_100 | 42 | 0.0010285 | 0.00025776 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2152-4_0_3_load_96 | 43 | 0.0010477 | 0.00026258 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2152-4_0_3_load_108 | 45 | 0.00028672 | 7.186e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2152-4_0_3_load_105 | 46 | 0.00049722 | 0.00012461 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2152-4_0_3_load_29 | 48 | 0.0004155 | 0.00010413 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2152-4_0_3_load_31 | 49 | 0.0047449 | 0.0011892 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2152-4_0_3_load_32 | 50 | 0.0035165 | 0.00088133 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2152-4_0_3_load_123 | 51 | 0.0030021 | 0.0007524 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2152-4_0_3_load_134 | 53 | 0.00020025 | 5.0188e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2152-4_0_3_load_36 | 54 | 0.0021867 | 0.00054805 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2152-4_0_3_load_39 | 55 | 0.00091566 | 0.00022949 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2152-4_0_3_load_112 | 56 | 0.00042767 | 0.00010718 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2152-4_0_3_load_106 | 57 | 0.0024178 | 0.00060595 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2152-4_0_3_load_103 | 58 | 0.00027613 | 6.9204e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2152-4_0_3_load_40 | 59 | 0.0023748 | 0.00059519 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2152-4_0_3_load_41 | 60 | 0.0061584 | 0.0015435 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2152-4_0_3_load_43 | 61 | 0.0047728 | 0.0011962 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2152-4_0_3_load_69 | 63 | 0.0011938 | 0.0002992 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2152-4_0_3_load_73 | 64 | 0.0057097 | 0.001431 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2152-4_0_3_load_44 | 66 | 0.00094421 | 0.00023664 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2152-4_0_3_load_45 | 67 | 0.0016365 | 0.00041014 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2152-4_0_3_load_91 | 68 | 0.0035692 | 0.00089452 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2152-4_0_3_load_67 | 69 | 0.0033993 | 0.00085195 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2152-4_0_3_load_47 | 70 | 0.0098689 | 0.0024734 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2152-4_0_3_load_48 | 71 | 0.00086239 | 0.00021614 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2152-4_0_3_load_109 | 72 | 0.00033223 | 8.3266e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2152-4_0_3_load_50 | 73 | 0.001174 | 0.00029423 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2152-4_0_3_load_55 | 75 | 0.0013761 | 0.00034488 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2152-4_0_3_load_58 | 78 | 0.0016742 | 0.0004196 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2152-4_0_3_load_53 | 79 | 0.0022233 | 0.00055721 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2152-4_0_3_load_51 | 80 | 0.0015754 | 0.00039483 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2152-4_0_3_load_52 | 81 | 0.0018736 | 0.00046957 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2152-4_0_3_load_54 | 82 | 0.00094587 | 0.00023706 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2152-4_0_3_load_61 | 84 | 0.00088616 | 0.00022209 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2152-4_0_3_load_59 | 85 | 0.0072373 | 0.0018138 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2152-4_0_3_load_83 | 87 | 0.0013801 | 0.0003459 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2152-4_0_3_load_66 | 88 | 0.00092834 | 0.00023266 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2152-4_0_3_load_62 | 89 | 0.0036285 | 0.00090938 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2152-4_0_3_load_82 | 90 | 0.0016123 | 0.00040409 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2152-4_0_3_load_63 | 91 | 0.0044925 | 0.0011259 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2152-4_0_3_load_65 | 92 | 0.0021152 | 0.00053013 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2152-4_0_3_load_68 | 93 | 0.0019421 | 0.00048673 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2152-4_0_3_load_84 | 94 | 0.0045438 | 0.0011388 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2152-4_0_3_load_71 | 96 | 0.00036413 | 9.1259e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2152-4_0_3_load_72 | 97 | 0.001994 | 0.00049975 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2152-4_0_3_load_74 | 98 | 0.00088179 | 0.000221 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2152-4_0_3_load_75 | 99 | 0.0011541 | 0.00028924 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2152-4_0_3_load_76 | 100 | 0.013048 | 0.0032702 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2152-4_0_3_load_77 | 101 | 0.0094639 | 0.0023719 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2152-4_0_3_load_78 | 102 | 0.0010002 | 0.00025067 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2152-4_0_3_load_79 | 103 | 0.0010672 | 0.00026747 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2152-4_0_3_load_80 | 104 | 0.0036395 | 0.00091215 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2152-4_0_3_load_81 | 105 | 0.002081 | 0.00052156 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2152-4_0_3_load_86 | 106 | 0.0019432 | 0.00048702 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2152-4_0_3_load_88 | 108 | 0.0018696 | 0.00046857 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2152-4_0_3_load_89 | 109 | 0.0059805 | 0.0014989 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2152-4_0_3_load_90 | 110 | 0.0023264 | 0.00058305 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2152-4_0_3_load_93 | 111 | 0.0015137 | 0.00037936 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2152-4_0_3_load_113 | 112 | 0.0014079 | 0.00035285 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2152-4_0_3_load_114 | 113 | 0.0048836 | 0.001224 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2152-4_0_3_load_110 | 116 | 0.00056172 | 0.00014078 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2152-4_0_3_load_111 | 117 | 0.00057186 | 0.00014332 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2152-4_0_3_load_142 | 118 | 0.00043063 | 0.00010793 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2152-4_0_3_load_138 | 119 | 0.00068794 | 0.00017241 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2152-4_0_3_load_115 | 120 | 0.0036374 | 0.00091163 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2152-4_0_3_load_144 | 121 | 0.0010847 | 0.00027186 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2152-4_0_3_load_140 | 122 | 0.00057433 | 0.00014394 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2152-4_0_3_load_139 | 123 | 0.00028525 | 7.1491e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2152-4_0_3_load_116 | 124 | 0.0022483 | 0.00056349 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2152-4_0_3_load_119 | 126 | 0.0080403 | 0.0020151 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2152-4_0_3_load_120 | 127 | 0.010351 | 0.0025941 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2152-4_0_3_load_128 | 128 | 0.00064263 | 0.00016106 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2152-4_0_3_load_126 | 129 | 0.0014978 | 0.00037538 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2152-4_0_3_load_124 | 130 | 0.00089567 | 0.00022448 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2152-4_0_3_load_125 | 131 | 0.00089602 | 0.00022456 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2152-4_0_3_load_121 | 132 | 0.0016968 | 0.00042525 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2152-4_0_3_load_132 | 133 | 0.0034549 | 0.00086587 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2152-4_0_3_load_122 | 134 | 0.0053221 | 0.0013338 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2152-4_0_3_load_127 | 135 | 0.0024225 | 0.00060714 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2152-4_0_3_load_131 | 136 | 0.0034562 | 0.00086621 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2152-4_0_3_load_130 | 137 | 0.00089567 | 0.00022448 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2152-4_0_3_load_129 | 138 | 0.0040849 | 0.0010238 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2152-4_0_3_load_135 | 139 | 0.00014557 | 3.6484e-05 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2152-4_0_3_load_136 | 140 | 0.00020158 | 5.052e-05 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2152-4_0_3_load_137 | 141 | 0.00045397 | 0.00011377 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2152-4_0_3_load_141 | 142 | 0.00048439 | 0.0001214 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2152-4_0_3_load_143 | 143 | 0.00069722 | 0.00017474 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 72 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2152-4_0_3_line_0 |  | 0 | 1 | 0.27246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2152-4_0_3_line_1 |  | 1 | 2 | 0.29096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2152-4_0_3_line_2 |  | 1 | 3 | 0.18968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2152-4_0_3_line_3 |  | 2 | 4 | 0.18152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2152-4_0_3_line_4 |  | 3 | 5 | 0.016468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2152-4_0_3_line_5 |  | 3 | 6 | 0.026138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2152-4_0_3_line_6 |  | 4 | 11 | 0.057622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2152-4_0_3_line_7 |  | 4 | 9 | 0.025381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2152-4_0_3_line_8 |  | 5 | 7 | 0.16196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2152-4_0_3_line_9 |  | 7 | 8 | 0.0065536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2152-4_0_3_line_10 |  | 8 | 18 | 0.056291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2152-4_0_3_line_11 |  | 9 | 10 | 0.30738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2152-4_0_3_line_12 |  | 11 | 12 | 0.025528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2152-4_0_3_line_13 |  | 11 | 13 | 0.025558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2152-4_0_3_line_14 |  | 12 | 14 | 0.006614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2152-4_0_3_line_15 |  | 13 | 15 | 0.056728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2152-4_0_3_line_16 |  | 14 | 16 | 0.0045603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2152-4_0_3_line_17 |  | 15 | 17 | 0.067851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2152-4_0_3_line_18 |  | 18 | 19 | 0.0017847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2152-4_0_3_line_19 |  | 18 | 20 | 0.031043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2152-4_0_3_line_20 |  | 19 | 21 | 0.043632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2152-4_0_3_line_21 |  | 20 | 22 | 0.00078071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2152-4_0_3_line_22 |  | 21 | 53 | 0.0083097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2152-4_0_3_line_23 |  | 22 | 48 | 0.0018194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2152-4_0_3_line_24 |  | 23 | 24 | 0.02237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_2152-4_0_3_line_25 |  | 23 | 25 | 0.014813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2152-4_0_3_line_26 |  | 24 | 26 | 0.0034951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2152-4_0_3_line_27 |  | 25 | 27 | 0.019506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2152-4_0_3_line_28 |  | 25 | 28 | 0.025198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2152-4_0_3_line_29 |  | 26 | 29 | 0.01799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_2152-4_0_3_line_30 |  | 26 | 30 | 0.02255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2152-4_0_3_line_31 |  | 27 | 31 | 0.026653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2152-4_0_3_line_32 |  | 27 | 32 | 0.0064821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_2152-4_0_3_line_33 |  | 28 | 33 | 0.020251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2152-4_0_3_line_34 |  | 29 | 34 | 0.031662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2152-4_0_3_line_35 |  | 29 | 35 | 0.013739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2152-4_0_3_line_36 |  | 30 | 36 | 0.040117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2152-4_0_3_line_37 |  | 31 | 37 | 0.016905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2152-4_0_3_line_38 |  | 31 | 38 | 0.04612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2152-4_0_3_line_39 |  | 32 | 39 | 0.021443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2152-4_0_3_line_40 |  | 33 | 40 | 0.022118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2152-4_0_3_line_41 |  | 34 | 41 | 0.030967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2152-4_0_3_line_42 |  | 35 | 42 | 0.013379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2152-4_0_3_line_43 |  | 37 | 43 | 0.025879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2152-4_0_3_line_44 |  | 38 | 44 | 0.0079759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2152-4_0_3_line_45 |  | 39 | 45 | 0.0011307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2152-4_0_3_line_46 |  | 40 | 46 | 0.057295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2152-4_0_3_line_47 |  | 40 | 47 | 0.026505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2152-4_0_3_line_48 |  | 41 | 112 | 0.042573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_2152-4_0_3_line_49 |  | 41 | 113 | 0.02313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2152-4_0_3_line_50 |  | 44 | 111 | 0.023813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2152-4_0_3_line_51 |  | 44 | 68 | 0.053875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_2152-4_0_3_line_52 |  | 45 | 72 | 0.016414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_2152-4_0_3_line_53 |  | 46 | 57 | 0.0016564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2152-4_0_3_line_54 |  | 47 | 55 | 0.043354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2152-4_0_3_line_55 |  | 47 | 54 | 0.026927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2152-4_0_3_line_56 |  | 48 | 49 | 0.016797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_2152-4_0_3_line_57 |  | 49 | 50 | 0.0047157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_2152-4_0_3_line_58 |  | 50 | 51 | 0.038853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_2152-4_0_3_line_59 |  | 51 | 52 | 0.012261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_2152-4_0_3_line_60 |  | 52 | 124 | 0.034296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_2152-4_0_3_line_61 |  | 53 | 139 | 0.0087637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2152-4_0_3_line_62 |  | 55 | 56 | 0.014347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2152-4_0_3_line_63 |  | 56 | 58 | 0.010681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2152-4_0_3_line_64 |  | 57 | 121 | 0.031069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2152-4_0_3_line_65 |  | 58 | 114 | 0.0081719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2152-4_0_3_line_66 |  | 59 | 60 | 0.022406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2152-4_0_3_line_67 |  | 60 | 61 | 0.0075004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2152-4_0_3_line_68 |  | 61 | 66 | 0.07267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2152-4_0_3_line_69 |  | 62 | 63 | 0.015701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2152-4_0_3_line_70 |  | 62 | 64 | 0.077473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2152-4_0_3_line_71 |  | 62 | 65 | 0.046526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2152-4_0_3_line_72 |  | 63 | 76 | 0.013755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2152-4_0_3_line_73 |  | 65 | 71 | 0.0083662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2152-4_0_3_line_74 |  | 65 | 66 | 0.020502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2152-4_0_3_line_75 |  | 66 | 67 | 0.014265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2152-4_0_3_line_76 |  | 67 | 70 | 0.027164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2152-4_0_3_line_77 |  | 68 | 69 | 0.14378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_2152-4_0_3_line_78 |  | 69 | 92 | 0.0066941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_2152-4_0_3_line_79 |  | 73 | 74 | 0.046248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2152-4_0_3_line_80 |  | 73 | 75 | 0.025128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2152-4_0_3_line_81 |  | 74 | 77 | 0.004461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2152-4_0_3_line_82 |  | 74 | 78 | 0.036459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2152-4_0_3_line_83 |  | 75 | 79 | 0.0043103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2152-4_0_3_line_84 |  | 76 | 96 | 0.012966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2152-4_0_3_line_85 |  | 76 | 97 | 0.020098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2152-4_0_3_line_86 |  | 77 | 83 | 0.031839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2152-4_0_3_line_87 |  | 77 | 84 | 0.041707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_2152-4_0_3_line_88 |  | 78 | 85 | 0.010061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2152-4_0_3_line_89 |  | 79 | 80 | 0.032627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2152-4_0_3_line_90 |  | 80 | 81 | 0.0011821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2152-4_0_3_line_91 |  | 81 | 82 | 0.0012643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2152-4_0_3_line_92 |  | 83 | 86 | 0.061061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_2152-4_0_3_line_93 |  | 84 | 87 | 0.0014626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2152-4_0_3_line_94 |  | 86 | 88 | 0.045988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2152-4_0_3_line_95 |  | 86 | 89 | 0.025762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_2152-4_0_3_line_96 |  | 87 | 90 | 0.035562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2152-4_0_3_line_97 |  | 88 | 93 | 0.011202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2152-4_0_3_line_98 |  | 89 | 91 | 8.3198e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_2152-4_0_3_line_99 |  | 90 | 99 | 0.027792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2152-4_0_3_line_100 |  | 91 | 92 | 0.031183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_2152-4_0_3_line_101 |  | 93 | 94 | 0.004665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2152-4_0_3_line_102 |  | 94 | 95 | 0.023483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2152-4_0_3_line_103 |  | 95 | 106 | 0.018788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2152-4_0_3_line_104 |  | 95 | 107 | 0.029323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2152-4_0_3_line_105 |  | 96 | 98 | 0.010567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2152-4_0_3_line_106 |  | 97 | 99 | 0.0044878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2152-4_0_3_line_107 |  | 98 | 100 | 0.017219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2152-4_0_3_line_108 |  | 100 | 101 | 0.013579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2152-4_0_3_line_109 |  | 101 | 102 | 0.0041069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2152-4_0_3_line_110 |  | 102 | 103 | 0.013652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2152-4_0_3_line_111 |  | 103 | 104 | 0.025584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2152-4_0_3_line_112 |  | 104 | 105 | 0.0039997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2152-4_0_3_line_113 |  | 106 | 108 | 0.027238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2152-4_0_3_line_114 |  | 107 | 109 | 0.065679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2152-4_0_3_line_115 |  | 108 | 110 | 0.0048299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2152-4_0_3_line_116 |  | 112 | 120 | 0.010278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_2152-4_0_3_line_117 |  | 114 | 115 | 0.057762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2152-4_0_3_line_118 |  | 115 | 116 | 0.016846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2152-4_0_3_line_119 |  | 115 | 117 | 0.039242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2152-4_0_3_line_120 |  | 116 | 118 | 0.032122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2152-4_0_3_line_121 |  | 117 | 119 | 0.048395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2152-4_0_3_line_122 |  | 118 | 122 | 0.017433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2152-4_0_3_line_123 |  | 119 | 123 | 0.059087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2152-4_0_3_line_124 |  | 120 | 124 | 0.047822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_2152-4_0_3_line_125 |  | 122 | 142 | 0.0035095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2152-4_0_3_line_126 |  | 124 | 128 | 0.03339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2152-4_0_3_line_127 |  | 125 | 126 | 0.054047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2152-4_0_3_line_128 |  | 125 | 127 | 0.020115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2152-4_0_3_line_129 |  | 126 | 132 | 0.014417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2152-4_0_3_line_130 |  | 126 | 133 | 0.034161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2152-4_0_3_line_131 |  | 127 | 134 | 0.010564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2152-4_0_3_line_132 |  | 128 | 129 | 0.015223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2152-4_0_3_line_133 |  | 129 | 135 | 0.020688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2152-4_0_3_line_134 |  | 130 | 131 | 0.015027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2152-4_0_3_line_135 |  | 131 | 138 | 0.0080398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2152-4_0_3_line_136 |  | 132 | 135 | 0.019239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2152-4_0_3_line_137 |  | 133 | 136 | 0.0051607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2152-4_0_3_line_138 |  | 136 | 137 | 0.011326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2152-4_0_3_line_139 |  | 137 | 138 | 0.0034609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2152-4_0_3_line_140 |  | 139 | 140 | 0.014557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2152-4_0_3_line_141 |  | 140 | 141 | 0.023907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2152-4_0_3_line_142 |  | 142 | 143 | 0.010667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2152-4_0_3_trafo_109 | 0.63 MVA 20/0.4 kV | 144 | 72 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2565582.0155 | 1166031.8444 | 2565387.0026 | 1166222.1249
1 | 2565412.5186 | 1165795.3563 | 2565582.0155 | 1166031.8444
2 | 2565639.2322 | 1165851.003 | 2565582.0155 | 1166031.8444
3 | 2565370.0538 | 1165618.8775 | 2565412.5186 | 1165795.3563
4 | 2565639.2322 | 1165851.003 | 2565647.6172 | 1165845.8856 | 2565651.8578 | 1165840.7695
5 | 2565639.2322 | 1165851.003 | 2565614.7264 | 1165841.91
6 | 2565370.0538 | 1165618.8775 | 2565370.1889 | 1165594.5643 | 2565370.9403 | 1165584.1546 | 2565373.2604 | 1165574.892 | 2565375.5898 | 1165567.2413 | 2565378.681 | 1165562.9101
7 | 2565370.0538 | 1165618.8775 | 2565344.7446 | 1165620.7818
8 | 2565762.9418 | 1165722.9096 | 2565651.8578 | 1165840.7695
9 | 2565762.9418 | 1165722.9096 | 2565764.8892 | 1165718.3936 | 2565765.9045 | 1165717.1113
10 | 2565811.4868 | 1165690.1798 | 2565792.1559 | 1165691.8687 | 2565779.1956 | 1165700.3248 | 2565765.9045 | 1165717.1113
11 | 2565344.7446 | 1165620.7818 | 2565038.1021 | 1165642.0166
12 | 2565378.681 | 1165562.9101 | 2565378.91 | 1165556.1497 | 2565376.4346 | 1165549.1382 | 2565372.059 | 1165543.2271 | 2565369.4168 | 1165540.2584
13 | 2565378.681 | 1165562.9101 | 2565382.7396 | 1165561.6638 | 2565386.5327 | 1165562.1866 | 2565397.9499 | 1165567.6568 | 2565402.0126 | 1165568.4449 | 2565402.6923 | 1165568.3584
14 | 2565369.4168 | 1165540.2584 | 2565365.0196 | 1165535.3178
15 | 2565452.4955 | 1165580.7155 | 2565428.5442 | 1165563.2891 | 2565424.8084 | 1165562.0989 | 2565421.6241 | 1165562.2507 | 2565415.8053 | 1165563.6406 | 2565410.1297 | 1165565.9634 | 2565405.402 | 1165568.014 | 2565402.6923 | 1165568.3584
16 | 2565365.0196 | 1165535.3178 | 2565361.9877 | 1165531.9113
17 | 2565452.4955 | 1165580.7155 | 2565470.2232 | 1165557.2124 | 2565494.0213 | 1165527.0611
18 | 2565811.4868 | 1165690.1798 | 2565811.5085 | 1165691.9643
19 | 2565811.4868 | 1165690.1798 | 2565810.8418 | 1165671.0736 | 2565811.7928 | 1165659.1857
20 | 2565811.5085 | 1165691.9643 | 2565811.6166 | 1165700.84 | 2565817.8044 | 1165729.2527 | 2565820.9987 | 1165733.9463
21 | 2565811.8551 | 1165658.4075 | 2565811.7928 | 1165659.1857
22 | 2565825.6739 | 1165740.816 | 2565820.9987 | 1165733.9463
23 | 2565811.8551 | 1165658.4075 | 2565812.0002 | 1165656.5939
24 | 2565749.2618 | 1165391.3073 | 2565733.5966 | 1165375.3384
25 | 2565724.279 | 1165363.8326 | 2565732.547 | 1165374.2685 | 2565733.5966 | 1165375.3384
26 | 2565751.7094 | 1165393.8023 | 2565749.2618 | 1165391.3073
27 | 2565724.279 | 1165363.8326 | 2565726.5572 | 1165355.1819 | 2565724.6448 | 1165344.7986
28 | 2565724.279 | 1165363.8326 | 2565714.9887 | 1165366.1092 | 2565700.7335 | 1165372.5257
29 | 2565764.325 | 1165406.6591 | 2565751.7094 | 1165393.8023
30 | 2565751.7094 | 1165393.8023 | 2565760.5581 | 1165385.2918 | 2565767.2981 | 1165378.9056 | 2565768.0816 | 1165378.3046
31 | 2565724.6448 | 1165344.7986 | 2565744.2736 | 1165326.7104
32 | 2565724.6448 | 1165344.7986 | 2565720.5365 | 1165339.7846
33 | 2565700.7335 | 1165372.5257 | 2565694.3756 | 1165375.3874 | 2565685.7993 | 1165385.5244
34 | 2565764.325 | 1165406.6591 | 2565787.489 | 1165428.2443
35 | 2565764.325 | 1165406.6591 | 2565755.5693 | 1165417.2471
36 | 2565793.1825 | 1165379.5693 | 2565794.6609 | 1165376.9929 | 2565795.1868 | 1165373.8772 | 2565793.8131 | 1165370.65 | 2565791.493 | 1165367.9619 | 2565788.7771 | 1165367.0325 | 2565783.3622 | 1165368.1417 | 2565778.6327 | 1165369.9252 | 2565773.5037 | 1165374.1455 | 2565768.0816 | 1165378.3046
37 | 2565744.2736 | 1165326.7104 | 2565736.1441 | 1165311.8883
38 | 2565744.2736 | 1165326.7104 | 2565785.9407 | 1165306.9387
39 | 2565706.9462 | 1165323.1983 | 2565720.5365 | 1165339.7846
40 | 2565671.5134 | 1165402.41 | 2565685.7993 | 1165385.5244
41 | 2565809.2291 | 1165450.2362 | 2565801.6753 | 1165441.4637 | 2565787.489 | 1165428.2443
42 | 2565755.5693 | 1165417.2471 | 2565747.0432 | 1165427.5576
43 | 2565723.6988 | 1165289.1977 | 2565736.1441 | 1165311.8883
44 | 2565793.1464 | 1165303.5194 | 2565785.9407 | 1165306.9387
45 | 2565706.2295 | 1165322.3237 | 2565706.9462 | 1165323.1983
46 | 2565671.5134 | 1165402.41 | 2565668.3354 | 1165399.6712 | 2565647.5716 | 1165394.6654 | 2565616.8222 | 1165386.7946
47 | 2565671.5134 | 1165402.41 | 2565654.3707 | 1165422.663
48 | 2565809.2291 | 1165450.2362 | 2565809.1751 | 1165485.0433 | 2565809.491 | 1165492.8025
49 | 2565809.2291 | 1165450.2362 | 2565827.2696 | 1165450.3778 | 2565832.3577 | 1165450.4929
50 | 2565793.1464 | 1165303.5194 | 2565807.1898 | 1165296.8581 | 2565814.7906 | 1165293.5983
51 | 2565793.1464 | 1165303.5194 | 2565770.3758 | 1165254.6926
52 | 2565706.2295 | 1165322.3237 | 2565697.2556 | 1165311.3715 | 2565696.2302 | 1165309.3629
53 | 2565616.8222 | 1165386.7946 | 2565615.2175 | 1165386.3838
54 | 2565654.3707 | 1165422.663 | 2565667.9546 | 1165434.7692 | 2565673.9051 | 1165438.9595 | 2565688.9469 | 1165448.6266
55 | 2565654.3707 | 1165422.663 | 2565638.9425 | 1165440.1049 | 2565636.4283 | 1165442.738
56 | 2565812.0002 | 1165656.5939 | 2565812.8358 | 1165646.1495 | 2565813.6034 | 1165639.8767
57 | 2565814.1762 | 1165635.196 | 2565813.6034 | 1165639.8767
58 | 2565818.8957 | 1165596.6303 | 2565814.1762 | 1165635.196
59 | 2565819.3208 | 1165584.403 | 2565819.4344 | 1165592.2286 | 2565818.8957 | 1165596.6303
60 | 2565819.3208 | 1165584.403 | 2565818.9485 | 1165559.4034 | 2565817.3048 | 1165550.2562
61 | 2565825.6739 | 1165740.816 | 2565828.815 | 1165745.4315 | 2565831.084 | 1165747.6606
62 | 2565701.22 | 1165456.0015 | 2565698.7822 | 1165454.9475 | 2565688.9469 | 1165448.6266
63 | 2565701.22 | 1165456.0015 | 2565711.0237 | 1165460.2403
64 | 2565584.4781 | 1165382.6121 | 2565596.3021 | 1165382.9535 | 2565610.4879 | 1165385.1732 | 2565615.2175 | 1165386.3838
65 | 2565718.5246 | 1165463.4833 | 2565711.0237 | 1165460.2403
66 | 2565479.1233 | 1164929.2408 | 2565474.7297 | 1164932.1546 | 2565466.5143 | 1164941.6624 | 2565465.8544 | 1164944.0896 | 2565466.7373 | 1164945.9433
67 | 2565469.9626 | 1164952.7148 | 2565466.7373 | 1164945.9433
68 | 2565515.1139 | 1165009.6565 | 2565469.9626 | 1164952.7148
69 | 2565552.356 | 1164967.037 | 2565560.1569 | 1164980.6625
70 | 2565552.356 | 1164967.037 | 2565600.0104 | 1164905.9542
71 | 2565532.0122 | 1164998.0476 | 2565525.9984 | 1164984.264 | 2565552.356 | 1164967.037
72 | 2565566.991 | 1164992.5993 | 2565560.1569 | 1164980.6625
73 | 2565532.0122 | 1164998.0476 | 2565535.7678 | 1165005.5235
74 | 2565532.0122 | 1164998.0476 | 2565515.1139 | 1165009.6565
75 | 2565515.1139 | 1165009.6565 | 2565503.3564 | 1165017.7337
76 | 2565479.6642 | 1165031.0213 | 2565503.3564 | 1165017.7337
77 | 2565770.3758 | 1165254.6926 | 2565693.7839 | 1165133.011
78 | 2565693.7839 | 1165133.011 | 2565688.7041 | 1165128.6514
79 | 2565562.2996 | 1165058.3378 | 2565583.3492 | 1165099.538
80 | 2565562.2996 | 1165058.3378 | 2565541.7546 | 1165072.8062
81 | 2565585.1797 | 1165103.6074 | 2565583.3492 | 1165099.538
82 | 2565583.3492 | 1165099.538 | 2565577.4801 | 1165113.59 | 2565571.7979 | 1165125.4954 | 2565567.6083 | 1165129.3103 | 2565565.7347 | 1165130.7657
83 | 2565541.7546 | 1165072.8062 | 2565538.2305 | 1165075.288
84 | 2565566.991 | 1164992.5993 | 2565577.1564 | 1164987.9497 | 2565578.8055 | 1164987.2598
85 | 2565566.991 | 1164992.5993 | 2565576.2656 | 1165010.429
86 | 2565585.1797 | 1165103.6074 | 2565592.8546 | 1165118.671 | 2565599.6008 | 1165132.0058
87 | 2565585.1797 | 1165103.6074 | 2565608.8454 | 1165083.0388 | 2565605.9079 | 1165075.5629 | 2565605.0186 | 1165073.4198
88 | 2565557.7895 | 1165136.9373 | 2565565.7347 | 1165130.7657
89 | 2565511.5549 | 1165094.0737 | 2565538.2305 | 1165075.288
90 | 2565511.5549 | 1165094.0737 | 2565510.5885 | 1165094.7543
91 | 2565509.5548 | 1165095.4823 | 2565510.5885 | 1165094.7543
92 | 2565599.6008 | 1165132.0058 | 2565645.4273 | 1165091.5111
93 | 2565604.4579 | 1165072.0689 | 2565605.0186 | 1165073.4198
94 | 2565645.4273 | 1165091.5111 | 2565669.3579 | 1165070.3631 | 2565679.7833 | 1165060.9409
95 | 2565645.4273 | 1165091.5111 | 2565664.9773 | 1165108.2889
96 | 2565590.8267 | 1165039.2226 | 2565604.4579 | 1165072.0689
97 | 2565688.0942 | 1165053.4297 | 2565679.7833 | 1165060.9409
98 | 2565665.0404 | 1165108.3431 | 2565664.9773 | 1165108.2889
99 | 2565578.3366 | 1165014.4103 | 2565589.1824 | 1165035.2604 | 2565590.8267 | 1165039.2226
100 | 2565688.7041 | 1165128.6514 | 2565665.0404 | 1165108.3431
101 | 2565688.0942 | 1165053.4297 | 2565691.5552 | 1165050.3017
102 | 2565706.6625 | 1165032.5079 | 2565706.3145 | 1165033.2436 | 2565698.2377 | 1165044.2622 | 2565691.5552 | 1165050.3017
103 | 2565706.6625 | 1165032.5079 | 2565721.5069 | 1165044.0253
104 | 2565718.4087 | 1165005.6826 | 2565716.4456 | 1165011.8859 | 2565706.6625 | 1165032.5079
105 | 2565578.8055 | 1164987.2598 | 2565588.554 | 1164983.1818
106 | 2565578.3366 | 1165014.4103 | 2565576.2656 | 1165010.429
107 | 2565588.554 | 1164983.1818 | 2565588.554 | 1164983.1818 | 2565596.0306 | 1164986.3516 | 2565602.6595 | 1164992.5834
108 | 2565602.6595 | 1164992.5834 | 2565602.6595 | 1164992.5834 | 2565609.0317 | 1165004.5747
109 | 2565610.9589 | 1165008.2012 | 2565609.0317 | 1165004.5747
110 | 2565610.9589 | 1165008.2012 | 2565617.3651 | 1165020.2566
111 | 2565629.3704 | 1165042.8484 | 2565617.3651 | 1165020.2566
112 | 2565631.2473 | 1165046.3803 | 2565629.3704 | 1165042.8484
113 | 2565743.0273 | 1165060.7223 | 2565721.5069 | 1165044.0253
114 | 2565718.4087 | 1165005.6826 | 2565728.2436 | 1165007.4939 | 2565739.7488 | 1165008.1396 | 2565754.2421 | 1165010.4135 | 2565764.9338 | 1165013.4206 | 2565782.1493 | 1165019.8532
115 | 2565746.8433 | 1165063.6831 | 2565743.0273 | 1165060.7223
116 | 2565809.491 | 1165492.8025 | 2565809.9089 | 1165503.072
117 | 2565718.5246 | 1165463.4833 | 2565728.2227 | 1165476.3122 | 2565730.8103 | 1165478.921 | 2565734.4781 | 1165481.6125 | 2565752.0176 | 1165493.2627 | 2565755.068 | 1165496.458 | 2565757.001 | 1165499.7375 | 2565758.1346 | 1165503.8332
118 | 2565758.1346 | 1165503.8332 | 2565743.6841 | 1165512.4921
119 | 2565758.1346 | 1165503.8332 | 2565758.239 | 1165511.3698 | 2565757.4821 | 1165515.5874 | 2565753.2372 | 1165527.1175 | 2565750.7584 | 1165534.1575 | 2565749.7525 | 1165539.0213 | 2565750.2399 | 1165541.6792
120 | 2565743.6841 | 1165512.4921 | 2565716.1305 | 1165529.0025
121 | 2565782.1193 | 1165577.4607 | 2565780.7556 | 1165575.3295 | 2565776.9151 | 1165570.5379 | 2565757.5444 | 1165551.939 | 2565752.2145 | 1165546.4444 | 2565750.5507 | 1165543.3746 | 2565750.2399 | 1165541.6792
122 | 2565701.1763 | 1165537.9632 | 2565716.1305 | 1165529.0025
123 | 2565790.2394 | 1165628.4582 | 2565799.6086 | 1165615.9205 | 2565799.9787 | 1165608.3368 | 2565798.0843 | 1165602.4112 | 2565782.1193 | 1165577.4607
124 | 2565809.9089 | 1165503.072 | 2565810.226 | 1165510.8616 | 2565817.3048 | 1165550.2562
125 | 2565701.1763 | 1165537.9632 | 2565698.1659 | 1165539.7671
126 | 2565817.3048 | 1165550.2562 | 2565840.9743 | 1165526.7055
127 | 2565910.4702 | 1165467.9686 | 2565909.7671 | 1165522.0114 | 2565909.7671 | 1165522.0114
128 | 2565910.4702 | 1165467.9686 | 2565927.8267 | 1165478.1349
129 | 2565895.3772 | 1165521.1203 | 2565909.7671 | 1165522.0114
130 | 2565907.9445 | 1165556.1238 | 2565909.7671 | 1165522.0114
131 | 2565937.1366 | 1165483.1086 | 2565932.688 | 1165480.9823 | 2565927.8267 | 1165478.1349
132 | 2565840.9743 | 1165526.7055 | 2565855.8812 | 1165523.6182
133 | 2565855.8812 | 1165523.6182 | 2565874.2575 | 1165519.8124 | 2565876.1755 | 1165519.9312
134 | 2565880.4277 | 1165560.3045 | 2565866.2296 | 1165565.2267
135 | 2565880.4277 | 1165560.3045 | 2565887.0323 | 1165558.0148 | 2565888.0776 | 1165557.9203
136 | 2565876.1755 | 1165519.9312 | 2565895.3772 | 1165521.1203
137 | 2565907.9445 | 1165556.1238 | 2565902.8048 | 1165556.5886
138 | 2565891.5245 | 1165557.6086 | 2565902.8048 | 1165556.5886
139 | 2565891.5245 | 1165557.6086 | 2565888.0776 | 1165557.9203
140 | 2565841.4683 | 1165757.8621 | 2565831.084 | 1165747.6606
141 | 2565841.4683 | 1165757.8621 | 2565846.0622 | 1165762.3752 | 2565860.0159 | 1165772.8814
142 | 2565689.0162 | 1165545.2497 | 2565698.1659 | 1165539.7671

## bus_geodata
| x | y | coords
0 | 2565387.0026 | 1166222.1249
1 | 2565582.0155 | 1166031.8444
2 | 2565412.5186 | 1165795.3563
3 | 2565639.2322 | 1165851.003
4 | 2565370.0538 | 1165618.8775
5 | 2565651.8578 | 1165840.7695
6 | 2565614.7264 | 1165841.91
7 | 2565762.9418 | 1165722.9096
8 | 2565765.9045 | 1165717.1113
9 | 2565344.7446 | 1165620.7818
10 | 2565038.1021 | 1165642.0166
11 | 2565378.681 | 1165562.9101
12 | 2565369.4168 | 1165540.2584
13 | 2565402.6923 | 1165568.3584
14 | 2565365.0196 | 1165535.3178
15 | 2565452.4955 | 1165580.7155
16 | 2565361.9877 | 1165531.9113
17 | 2565494.0213 | 1165527.0611
18 | 2565811.4868 | 1165690.1798
19 | 2565811.5085 | 1165691.9643
20 | 2565811.7928 | 1165659.1857
21 | 2565820.9987 | 1165733.9463
22 | 2565811.8551 | 1165658.4075
23 | 2565733.5966 | 1165375.3384
24 | 2565749.2618 | 1165391.3073
25 | 2565724.279 | 1165363.8326
26 | 2565751.7094 | 1165393.8023
27 | 2565724.6448 | 1165344.7986
28 | 2565700.7335 | 1165372.5257
29 | 2565764.325 | 1165406.6591
30 | 2565768.0816 | 1165378.3046
31 | 2565744.2736 | 1165326.7104
32 | 2565720.5365 | 1165339.7846
33 | 2565685.7993 | 1165385.5244
34 | 2565787.489 | 1165428.2443
35 | 2565755.5693 | 1165417.2471
36 | 2565793.1825 | 1165379.5693
37 | 2565736.1441 | 1165311.8883
38 | 2565785.9407 | 1165306.9387
39 | 2565706.9462 | 1165323.1983
40 | 2565671.5134 | 1165402.41
41 | 2565809.2291 | 1165450.2362
42 | 2565747.0432 | 1165427.5576
43 | 2565723.6988 | 1165289.1977
44 | 2565793.1464 | 1165303.5194
45 | 2565706.2295 | 1165322.3237
46 | 2565616.8222 | 1165386.7946
47 | 2565654.3707 | 1165422.663
48 | 2565812.0002 | 1165656.5939
49 | 2565813.6034 | 1165639.8767
50 | 2565814.1762 | 1165635.196
51 | 2565818.8957 | 1165596.6303
52 | 2565819.3208 | 1165584.403
53 | 2565825.6739 | 1165740.816
54 | 2565636.4283 | 1165442.738
55 | 2565688.9469 | 1165448.6266
56 | 2565701.22 | 1165456.0015
57 | 2565615.2175 | 1165386.3838
58 | 2565711.0237 | 1165460.2403
59 | 2565479.1233 | 1164929.2408
60 | 2565466.7373 | 1164945.9433
61 | 2565469.9626 | 1164952.7148
62 | 2565552.356 | 1164967.037
63 | 2565560.1569 | 1164980.6625
64 | 2565600.0104 | 1164905.9542
65 | 2565532.0122 | 1164998.0476
66 | 2565515.1139 | 1165009.6565
67 | 2565503.3564 | 1165017.7337
68 | 2565770.3758 | 1165254.6926
69 | 2565693.7839 | 1165133.011
70 | 2565479.6642 | 1165031.0213
71 | 2565535.7678 | 1165005.5235
72 | 2565696.2302 | 1165309.3629
73 | 2565562.2996 | 1165058.3378
74 | 2565583.3492 | 1165099.538
75 | 2565541.7546 | 1165072.8062
76 | 2565566.991 | 1164992.5993
77 | 2565585.1797 | 1165103.6074
78 | 2565565.7347 | 1165130.7657
79 | 2565538.2305 | 1165075.288
80 | 2565511.5549 | 1165094.0737
81 | 2565510.5885 | 1165094.7543
82 | 2565509.5548 | 1165095.4823
83 | 2565599.6008 | 1165132.0058
84 | 2565605.0186 | 1165073.4198
85 | 2565557.7895 | 1165136.9373
86 | 2565645.4273 | 1165091.5111
87 | 2565604.4579 | 1165072.0689
88 | 2565679.7833 | 1165060.9409
89 | 2565664.9773 | 1165108.2889
90 | 2565590.8267 | 1165039.2226
91 | 2565665.0404 | 1165108.3431
92 | 2565688.7041 | 1165128.6514
93 | 2565688.0942 | 1165053.4297
94 | 2565691.5552 | 1165050.3017
95 | 2565706.6625 | 1165032.5079
96 | 2565578.8055 | 1164987.2598
97 | 2565576.2656 | 1165010.429
98 | 2565588.554 | 1164983.1818
99 | 2565578.3366 | 1165014.4103
100 | 2565602.6595 | 1164992.5834
101 | 2565609.0317 | 1165004.5747
102 | 2565610.9589 | 1165008.2012
103 | 2565617.3651 | 1165020.2566
104 | 2565629.3704 | 1165042.8484
105 | 2565631.2473 | 1165046.3803
106 | 2565721.5069 | 1165044.0253
107 | 2565718.4087 | 1165005.6826
108 | 2565743.0273 | 1165060.7223
109 | 2565782.1493 | 1165019.8532
110 | 2565746.8433 | 1165063.6831
111 | 2565814.7906 | 1165293.5983
112 | 2565809.491 | 1165492.8025
113 | 2565832.3577 | 1165450.4929
114 | 2565718.5246 | 1165463.4833
115 | 2565758.1346 | 1165503.8332
116 | 2565743.6841 | 1165512.4921
117 | 2565750.2399 | 1165541.6792
118 | 2565716.1305 | 1165529.0025
119 | 2565782.1193 | 1165577.4607
120 | 2565809.9089 | 1165503.072
121 | 2565584.4781 | 1165382.6121
122 | 2565701.1763 | 1165537.9632
123 | 2565790.2394 | 1165628.4582
124 | 2565817.3048 | 1165550.2562
125 | 2565910.4702 | 1165467.9686
126 | 2565909.7671 | 1165522.0114
127 | 2565927.8267 | 1165478.1349
128 | 2565840.9743 | 1165526.7055
129 | 2565855.8812 | 1165523.6182
130 | 2565866.2296 | 1165565.2267
131 | 2565880.4277 | 1165560.3045
132 | 2565895.3772 | 1165521.1203
133 | 2565907.9445 | 1165556.1238
134 | 2565937.1366 | 1165483.1086
135 | 2565876.1755 | 1165519.9312
136 | 2565902.8048 | 1165556.5886
137 | 2565891.5245 | 1165557.6086
138 | 2565888.0776 | 1165557.9203
139 | 2565831.084 | 1165747.6606
140 | 2565841.4683 | 1165757.8621
141 | 2565860.0159 | 1165772.8814
142 | 2565698.1659 | 1165539.7671
143 | 2565689.0161 | 1165545.2497
144 | 2565724.6448 | 1165344.7986

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97945 | -0.39488 | 0.00047685 | 0.00011951
1 | 0.97957 | -0.3925 | 0.000367 | 9.1978e-05
2 | 0.97477 | -0.48653 | 0.00074088 | 0.00018568
3 | 0.98285 | -0.32876 | 0 | 0
4 | 0.9719 | -0.54315 | 0 | 0
5 | 0.98314 | -0.3232 | 0.00076277 | 0.00019117
6 | 0.98285 | -0.32881 | 0.0001223 | 3.065e-05
7 | 0.98607 | -0.26655 | 0.00068753 | 0.00017231
8 | 0.9862 | -0.26419 | 0.003444 | 0.00086316
9 | 0.97184 | -0.54439 | 0.00034703 | 8.6973e-05
10 | 0.97118 | -0.55739 | 0.0022856 | 0.00057282
11 | 0.97113 | -0.55837 | 0 | 0
12 | 0.97089 | -0.56307 | 0.0068284 | 0.0017114
13 | 0.97103 | -0.56043 | 0.002583 | 0.00064736
14 | 0.97087 | -0.56345 | 0.0009868 | 0.00024732
15 | 0.97093 | -0.56229 | 0 | 0
16 | 0.97087 | -0.56363 | 0.0021323 | 0.0005344
17 | 0.97082 | -0.56452 | 0.001771 | 0.00044386
18 | 0.98743 | -0.24042 | 0 | 0
19 | 0.98743 | -0.24049 | 0.00063469 | 0.00015907
20 | 0.98818 | -0.22603 | 0.00019781 | 4.9575e-05
21 | 0.98736 | -0.24183 | 0.00070649 | 0.00017706
22 | 0.9882 | -0.22567 | 0.00048227 | 0.00012087
23 | 0.99528 | -0.089605 | 0.00035916 | 9.0013e-05
24 | 0.99456 | -0.10327 | 0.0019455 | 0.00048758
25 | 0.99575 | -0.080533 | 0 | 0
26 | 0.99445 | -0.10537 | 0 | 0
27 | 0.99646 | -0.066937 | 0 | 0
28 | 0.99542 | -0.08699 | 0.0014806 | 0.00037107
29 | 0.99391 | -0.11568 | 0 | 0
30 | 0.99436 | -0.10721 | 0.0021667 | 0.00054302
31 | 0.99537 | -0.087554 | 0 | 0
32 | 0.99696 | -0.057419 | 0.0013552 | 0.00033966
33 | 0.99517 | -0.091655 | 0.00097429 | 0.00024418
34 | 0.99298 | -0.13359 | 0.0019116 | 0.00047909
35 | 0.99389 | -0.11603 | 0.00040809 | 0.00010228
36 | 0.99427 | -0.10896 | 0.0024672 | 0.00061834
37 | 0.99532 | -0.088517 | 0.002191 | 0.00054913
38 | 0.99353 | -0.12245 | 0.00031388 | 7.8666e-05
39 | 0.99863 | -0.025829 | 0.00032451 | 8.133e-05
40 | 0.99493 | -0.096372 | 0 | 0
41 | 0.99208 | -0.15079 | 0 | 0
42 | 0.99388 | -0.11627 | 0.0010285 | 0.00025776
43 | 0.9953 | -0.088995 | 0.0010477 | 0.00026258
44 | 0.99321 | -0.12849 | 0 | 0
45 | 0.99872 | -0.024164 | 0.00028672 | 7.186e-05
46 | 0.99472 | -0.10041 | 0.00049722 | 0.00012461
47 | 0.99474 | -0.10016 | 0 | 0
48 | 0.98824 | -0.2248 | 0.0004155 | 0.00010413
49 | 0.98838 | -0.2221 | 0.0047449 | 0.0011892
50 | 0.98843 | -0.22121 | 0.0035165 | 0.00088133
51 | 0.98885 | -0.21306 | 0.0030021 | 0.0007524
52 | 0.98899 | -0.21027 | 0 | 0
53 | 0.98735 | -0.24197 | 0.00020025 | 5.0188e-05
54 | 0.99468 | -0.1012 | 0.0021867 | 0.00054805
55 | 0.9945 | -0.10468 | 0.00091566 | 0.00022949
56 | 0.99444 | -0.10595 | 0.00042767 | 0.00010718
57 | 0.99472 | -0.10051 | 0.0024178 | 0.00060595
58 | 0.99439 | -0.10681 | 0.00027613 | 6.9204e-05
59 | 0.97007 | -0.57789 | 0.0023748 | 0.00059519
60 | 0.97012 | -0.57691 | 0.0061584 | 0.0015435
61 | 0.97018 | -0.57572 | 0.0047728 | 0.0011962
62 | 0.97273 | -0.52523 | 0 | 0
63 | 0.97321 | -0.51588 | 0.0011938 | 0.0002992
64 | 0.97232 | -0.53338 | 0.0057097 | 0.001431
65 | 0.97158 | -0.54807 | 0 | 0
66 | 0.97108 | -0.55783 | 0.00094421 | 0.00023664
67 | 0.97093 | -0.56086 | 0.0016365 | 0.00041014
68 | 0.9911 | -0.16886 | 0.0035692 | 0.00089452
69 | 0.9856 | -0.27439 | 0.0033993 | 0.00085195
70 | 0.97068 | -0.56582 | 0.0098689 | 0.0024734
71 | 0.97157 | -0.54821 | 0.00086239 | 0.00021614
72 | 1 | 0 | -0.25887 | -0.066086
73 | 0.98026 | -0.37788 | 0.001174 | 0.00029423
74 | 0.98065 | -0.37019 | 0 | 0
75 | 0.98008 | -0.38152 | 0.0013761 | 0.00034488
76 | 0.97364 | -0.5074 | 0 | 0
77 | 0.98073 | -0.36873 | 0 | 0
78 | 0.98035 | -0.37608 | 0.0016742 | 0.0004196
79 | 0.98005 | -0.38204 | 0.0022233 | 0.00055721
80 | 0.97992 | -0.38464 | 0.0015754 | 0.00039483
81 | 0.97991 | -0.38471 | 0.0018736 | 0.00046957
82 | 0.97991 | -0.38473 | 0.00094587 | 0.00023706
83 | 0.98162 | -0.3514 | 0 | 0
84 | 0.97933 | -0.39602 | 0.00088616 | 0.00022209
85 | 0.98029 | -0.3774 | 0.0072373 | 0.0018138
86 | 0.98333 | -0.31824 | 0 | 0
87 | 0.97923 | -0.39791 | 0.0013801 | 0.0003459
88 | 0.9825 | -0.33446 | 0.00092834 | 0.00023266
89 | 0.98421 | -0.30127 | 0.0036285 | 0.00090938
90 | 0.97691 | -0.44316 | 0.0016123 | 0.00040409
91 | 0.98421 | -0.30121 | 0.0044925 | 0.0011259
92 | 0.98535 | -0.27919 | 0.0021152 | 0.00053013
93 | 0.98231 | -0.33822 | 0.0019421 | 0.00048673
94 | 0.98224 | -0.33963 | 0.0045438 | 0.0011388
95 | 0.98197 | -0.34477 | 0 | 0
96 | 0.97326 | -0.51492 | 0.00036413 | 9.1259e-05
97 | 0.97486 | -0.48338 | 0.001994 | 0.00049975
98 | 0.97295 | -0.52099 | 0.00088179 | 0.000221
99 | 0.97514 | -0.47786 | 0.0011541 | 0.00028924
100 | 0.97246 | -0.5306 | 0.013048 | 0.0032702
101 | 0.97225 | -0.53492 | 0.0094639 | 0.0023719
102 | 0.97222 | -0.53551 | 0.0010002 | 0.00025067
103 | 0.97213 | -0.53722 | 0.0010672 | 0.00026747
104 | 0.97199 | -0.53992 | 0.0036395 | 0.00091215
105 | 0.97199 | -0.54007 | 0.002081 | 0.00052156
106 | 0.98187 | -0.34686 | 0.0019432 | 0.00048702
107 | 0.98181 | -0.34794 | 0 | 0
108 | 0.98176 | -0.34892 | 0.0018696 | 0.00046857
109 | 0.98145 | -0.35505 | 0.0059805 | 0.0014989
110 | 0.98175 | -0.34913 | 0.0023264 | 0.00058305
111 | 0.99318 | -0.12913 | 0.0015137 | 0.00037936
112 | 0.99091 | -0.17325 | 0.0014079 | 0.00035285
113 | 0.99198 | -0.15279 | 0.0048836 | 0.001224
114 | 0.99436 | -0.10743 | 0 | 0
115 | 0.99413 | -0.11181 | 0 | 0
116 | 0.99409 | -0.11263 | 0.00056172 | 0.00014078
117 | 0.99408 | -0.11289 | 0.00057186 | 0.00014332
118 | 0.99403 | -0.11387 | 0.00043063 | 0.00010793
119 | 0.99404 | -0.11372 | 0.00068794 | 0.00017241
120 | 0.99064 | -0.17859 | 0.0036374 | 0.00091163
121 | 0.99469 | -0.10111 | 0.0010847 | 0.00027186
122 | 0.994 | -0.11441 | 0.00057433 | 0.00014394
123 | 0.99402 | -0.11402 | 0.00028525 | 7.1491e-05
124 | 0.9894 | -0.20247 | 0.0022483 | 0.00056349
125 | 0.9847 | -0.2939 | 0 | 0
126 | 0.98548 | -0.27868 | 0.0080403 | 0.0020151
127 | 0.9844 | -0.29956 | 0.010351 | 0.0025941
128 | 0.98806 | -0.22846 | 0.00064263 | 0.00016106
129 | 0.98745 | -0.24016 | 0.0014978 | 0.00037538
130 | 0.98488 | -0.29027 | 0.00089567 | 0.00022448
131 | 0.98489 | -0.29002 | 0.00089602 | 0.00022456
132 | 0.98597 | -0.26901 | 0.0016968 | 0.00042525
133 | 0.98505 | -0.28707 | 0.0034549 | 0.00086587
134 | 0.98435 | -0.30058 | 0.0053221 | 0.0013338
135 | 0.98666 | -0.25553 | 0.0024225 | 0.00060714
136 | 0.985 | -0.28802 | 0.0034562 | 0.00086621
137 | 0.98493 | -0.2894 | 0.00089567 | 0.00022448
138 | 0.98491 | -0.28976 | 0.0040849 | 0.0010238
139 | 0.98734 | -0.2421 | 0.00014557 | 3.6484e-05
140 | 0.98733 | -0.24227 | 0.00020158 | 5.052e-05
141 | 0.98732 | -0.24247 | 0.00045397 | 0.00011377
142 | 0.994 | -0.11448 | 0.00048439 | 0.0001214
143 | 0.99399 | -0.11462 | 0.00069722 | 0.00017474
144 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00047685 | -0.00011951 | 0.0004769 | 0.00011611 | 5.3532e-08 | -3.3953e-06 | 0.00072444 | 0.00072323 | 0.00072444 | 0.97945 | -0.39488 | 0.97957 | -0.3925 | 0.19902
1 | 0.017816 | 0.0045069 | -0.017736 | -0.0044593 | 8.0005e-05 | 4.7559e-05 | 0.027078 | 0.027079 | 0.027079 | 0.97957 | -0.3925 | 0.97477 | -0.48653 | 7.4394
2 | -0.01866 | -0.004715 | 0.018717 | 0.0047492 | 5.7202e-05 | 3.4213e-05 | 0.028359 | 0.028358 | 0.028359 | 0.97957 | -0.3925 | 0.98285 | -0.32876 | 7.7909
3 | 0.016995 | 0.0042736 | -0.016949 | -0.0042466 | 4.5834e-05 | 2.7077e-05 | 0.025949 | 0.025949 | 0.025949 | 0.97477 | -0.48653 | 0.9719 | -0.54315 | 7.1289
4 | -0.018839 | -0.0047795 | 0.018844 | 0.0047825 | 5.0313e-06 | 3.0113e-06 | 0.028543 | 0.028543 | 0.028543 | 0.98285 | -0.32876 | 0.98314 | -0.3232 | 7.8415
5 | 0.0001223 | 3.0319e-05 | -0.0001223 | -3.065e-05 | 3.3581e-10 | -3.3104e-07 | 0.00018504 | 0.00018515 | 0.00018515 | 0.98285 | -0.32876 | 0.98285 | -0.32881 | 0.050866
6 | 0.014315 | 0.0035899 | -0.014305 | -0.003584 | 1.038e-05 | 5.9299e-06 | 0.021918 | 0.021918 | 0.021918 | 0.9719 | -0.54315 | 0.97113 | -0.55837 | 6.0214
7 | 0.0026342 | 0.00065668 | -0.002634 | -0.0006569 | 1.5472e-07 | -2.1549e-07 | 0.0040318 | 0.0040319 | 0.0040319 | 0.9719 | -0.54315 | 0.97184 | -0.54439 | 1.1077
8 | -0.019607 | -0.0049737 | 0.019661 | 0.0050059 | 5.3563e-05 | 3.222e-05 | 0.029697 | 0.029697 | 0.029697 | 0.98314 | -0.3232 | 0.98607 | -0.26655 | 8.1586
9 | -0.020348 | -0.0051782 | 0.02035 | 0.0051796 | 2.3214e-06 | 1.4021e-06 | 0.030734 | 0.030734 | 0.030734 | 0.98607 | -0.26655 | 0.9862 | -0.26419 | 8.4435
10 | -0.023795 | -0.0060428 | 0.023822 | 0.0060595 | 2.7252e-05 | 1.6722e-05 | 0.035931 | 0.03593 | 0.035931 | 0.9862 | -0.26419 | 0.98743 | -0.24042 | 9.8711
11 | 0.002287 | 0.00056992 | -0.0022856 | -0.00057282 | 1.413e-06 | -2.9017e-06 | 0.0035006 | 0.0035019 | 0.0035019 | 0.97184 | -0.54439 | 0.97118 | -0.55739 | 0.96207
12 | 0.0099498 | 0.0024941 | -0.0099476 | -0.002493 | 2.2251e-06 | 1.1083e-06 | 0.015246 | 0.015246 | 0.015246 | 0.97113 | -0.55837 | 0.97089 | -0.56307 | 4.1884
13 | 0.0043548 | 0.0010899 | -0.0043543 | -0.0010899 | 4.2666e-07 | -4.3126e-08 | 0.006672 | 0.0066722 | 0.0066722 | 0.97113 | -0.55837 | 0.97103 | -0.56043 | 1.833
14 | 0.0031191 | 0.00078162 | -0.0031191 | -0.00078167 | 5.6681e-08 | -4.5517e-08 | 0.0047804 | 0.0047805 | 0.0047805 | 0.97089 | -0.56307 | 0.97087 | -0.56345 | 1.3133
15 | 0.0017714 | 0.00044254 | -0.0017712 | -0.00044314 | 1.567e-07 | -6.0138e-07 | 0.002714 | 0.0027142 | 0.0027142 | 0.97103 | -0.56043 | 0.97093 | -0.56229 | 0.74567
16 | 0.0021323 | 0.00053435 | -0.0021323 | -0.0005344 | 1.8264e-08 | -4.4704e-08 | 0.003268 | 0.0032681 | 0.0032681 | 0.97087 | -0.56345 | 0.97087 | -0.56363 | 0.89782
17 | 0.0017712 | 0.00044314 | -0.001771 | -0.00044386 | 1.8747e-07 | -7.1908e-07 | 0.0027142 | 0.0027145 | 0.0027145 | 0.97093 | -0.56229 | 0.97082 | -0.56452 | 0.74575
18 | 0.0023427 | 0.0005859 | -0.0023427 | -0.00058591 | 8.339e-09 | -1.7492e-08 | 0.0035299 | 0.0035299 | 0.0035299 | 0.98743 | -0.24042 | 0.98743 | -0.24049 | 0.96975
19 | -0.026164 | -0.0066454 | 0.026183 | 0.0066566 | 1.8126e-05 | 1.1204e-05 | 0.03946 | 0.03946 | 0.03946 | 0.98743 | -0.24042 | 0.98818 | -0.22603 | 10.8407
20 | 0.001708 | 0.00042684 | -0.0017079 | -0.00042733 | 1.0837e-07 | -4.8873e-07 | 0.0025734 | 0.0025736 | 0.0025736 | 0.98743 | -0.24049 | 0.98736 | -0.24183 | 0.70705
21 | -0.02638 | -0.0067062 | 0.026381 | 0.0067065 | 4.6277e-07 | 2.8617e-07 | 0.039758 | 0.039758 | 0.039758 | 0.98818 | -0.22603 | 0.9882 | -0.22567 | 10.9225
22 | 0.0010014 | 0.00025027 | -0.0010014 | -0.00025037 | 7.095e-09 | -1.0174e-07 | 0.0015089 | 0.001509 | 0.001509 | 0.98736 | -0.24183 | 0.98735 | -0.24197 | 0.41455
23 | -0.026863 | -0.0068273 | 0.026864 | 0.006828 | 1.1182e-06 | 6.9236e-07 | 0.040484 | 0.040484 | 0.040484 | 0.9882 | -0.22567 | 0.98824 | -0.2248 | 11.122
24 | 0.10502 | 0.02668 | -0.10496 | -0.026637 | 6.9053e-05 | 4.3323e-05 | 0.15715 | 0.15715 | 0.15715 | 0.99528 | -0.089605 | 0.99456 | -0.10327 | 14.3908
25 | -0.10538 | -0.02677 | 0.10543 | 0.026799 | 4.6039e-05 | 2.8887e-05 | 0.15768 | 0.15768 | 0.15768 | 0.99528 | -0.089605 | 0.99575 | -0.080533 | 14.4399
26 | 0.10301 | 0.026149 | -0.103 | -0.026143 | 1.0393e-05 | 6.5155e-06 | 0.15424 | 0.15424 | 0.15424 | 0.99456 | -0.10327 | 0.99445 | -0.10537 | 14.1242
27 | -0.12 | -0.030449 | 0.12008 | 0.030499 | 7.8522e-05 | 4.9493e-05 | 0.17946 | 0.17946 | 0.17946 | 0.99575 | -0.080533 | 0.99646 | -0.066937 | 16.4337
28 | 0.01457 | 0.0036502 | -0.014565 | -0.0036477 | 4.4792e-06 | 2.539e-06 | 0.021772 | 0.021772 | 0.021772 | 0.99575 | -0.080533 | 0.99542 | -0.08699 | 5.9814
29 | 0.098365 | 0.024982 | -0.098316 | -0.024951 | 4.8793e-05 | 3.0528e-05 | 0.1473 | 0.1473 | 0.1473 | 0.99445 | -0.10537 | 0.99391 | -0.11568 | 13.4892
30 | 0.0046345 | 0.0011609 | -0.0046341 | -0.001161 | 4.0664e-07 | -3.2285e-08 | 0.0069345 | 0.0069346 | 0.0069346 | 0.99445 | -0.10537 | 0.99436 | -0.10721 | 1.9051
31 | 0.13435 | 0.034564 | -0.13421 | -0.034479 | 0.00013452 | 8.5054e-05 | 0.20094 | 0.20094 | 0.20094 | 0.99646 | -0.066937 | 0.99537 | -0.087554 | 18.4013
32 | -0.25443 | -0.065063 | 0.25454 | 0.065137 | 0.00011725 | 7.4784e-05 | 0.3804 | 0.3804 | 0.3804 | 0.99646 | -0.066937 | 0.99696 | -0.057419 | 34.8348
33 | 0.013085 | 0.0032766 | -0.013082 | -0.003275 | 2.9051e-06 | 1.5961e-06 | 0.019559 | 0.019559 | 0.019559 | 0.99542 | -0.08699 | 0.99517 | -0.091655 | 5.3734
34 | 0.09688 | 0.024592 | -0.096796 | -0.024539 | 8.3387e-05 | 5.2138e-05 | 0.14515 | 0.14515 | 0.14515 | 0.99391 | -0.11568 | 0.99298 | -0.13359 | 13.2923
35 | 0.0014366 | 0.00035971 | -0.0014366 | -0.00035987 | 2.3831e-08 | -1.6281e-07 | 0.0021506 | 0.0021507 | 0.0021507 | 0.99391 | -0.11568 | 0.99389 | -0.11603 | 0.59085
36 | 0.0024674 | 0.00061796 | -0.0024672 | -0.00061834 | 2.051e-07 | -3.8907e-07 | 0.0036923 | 0.0036924 | 0.0036924 | 0.99436 | -0.10721 | 0.99427 | -0.10896 | 1.0144
37 | 0.0032389 | 0.00081126 | -0.0032387 | -0.00081138 | 1.4862e-07 | -1.2461e-07 | 0.0048418 | 0.0048418 | 0.0048418 | 0.99537 | -0.087554 | 0.99532 | -0.088517 | 1.3302
38 | 0.13098 | 0.033667 | -0.13075 | -0.033527 | 0.0002217 | 0.00014009 | 0.1961 | 0.1961 | 0.1961 | 0.99537 | -0.087554 | 0.99353 | -0.12245 | 17.9579
39 | -0.2559 | -0.065477 | 0.25629 | 0.065727 | 0.00039199 | 0.00025003 | 0.38242 | 0.38242 | 0.38242 | 0.99696 | -0.057419 | 0.99863 | -0.025829 | 35.0201
40 | 0.012108 | 0.0030308 | -0.012105 | -0.0030294 | 2.718e-06 | 1.4522e-06 | 0.018102 | 0.018102 | 0.018102 | 0.99517 | -0.091655 | 0.99493 | -0.096372 | 4.9732
41 | 0.094885 | 0.02406 | -0.094806 | -0.024011 | 7.837e-05 | 4.8956e-05 | 0.14229 | 0.14229 | 0.14229 | 0.99298 | -0.13359 | 0.99208 | -0.15079 | 13.0301
42 | 0.0010285 | 0.00025759 | -0.0010285 | -0.00025776 | 1.1895e-08 | -1.6577e-07 | 0.0015397 | 0.0015398 | 0.0015398 | 0.99389 | -0.11603 | 0.99388 | -0.11627 | 0.42302
43 | 0.0010477 | 0.00026225 | -0.0010477 | -0.00026258 | 2.3808e-08 | -3.2111e-07 | 0.0015662 | 0.0015663 | 0.0015663 | 0.99532 | -0.088517 | 0.9953 | -0.088995 | 0.43031
44 | 0.13044 | 0.033449 | -0.1304 | -0.033425 | 3.8156e-05 | 2.411e-05 | 0.19563 | 0.19563 | 0.19563 | 0.99353 | -0.12245 | 0.99321 | -0.12849 | 17.9149
45 | -0.25662 | -0.065808 | 0.25664 | 0.065822 | 2.0723e-05 | 1.3218e-05 | 0.3829 | 0.3829 | 0.3829 | 0.99863 | -0.025829 | 0.99872 | -0.024164 | 35.0643
46 | 0.0040005 | 0.0010018 | -0.0039998 | -0.001002 | 7.6911e-07 | -2.5168e-07 | 0.0059829 | 0.0059832 | 0.0059832 | 0.99493 | -0.096372 | 0.99472 | -0.10041 | 1.6437
47 | 0.0081043 | 0.0020276 | -0.0081029 | -0.002027 | 1.4599e-06 | 5.9022e-07 | 0.01212 | 0.01212 | 0.01212 | 0.99493 | -0.096372 | 0.99474 | -0.10016 | 3.3296
48 | 0.089922 | 0.022787 | -0.089825 | -0.022727 | 9.6933e-05 | 6.039e-05 | 0.13496 | 0.13496 | 0.13496 | 0.99208 | -0.15079 | 0.99091 | -0.17325 | 12.3593
49 | 0.0048841 | 0.001224 | -0.0048836 | -0.001224 | 4.6548e-07 | -7.278e-10 | 0.0073256 | 0.0073257 | 0.0073257 | 0.99208 | -0.15079 | 0.99198 | -0.15279 | 2.0126
50 | 0.0015137 | 0.00037908 | -0.0015137 | -0.00037936 | 4.5925e-08 | -2.7879e-07 | 0.0022677 | 0.0022678 | 0.0022678 | 0.99321 | -0.12849 | 0.99318 | -0.12913 | 0.62303
51 | 0.12889 | 0.033045 | -0.12864 | -0.032886 | 0.0002518 | 0.00015906 | 0.19336 | 0.19336 | 0.19336 | 0.99321 | -0.12849 | 0.9911 | -0.16886 | 17.7073
52 | -0.25692 | -0.065893 | 0.25722 | 0.066086 | 0.00030149 | 0.00019231 | 0.38333 | 0.38333 | 0.38333 | 0.99872 | -0.024164 | 1 | 0 | 35.1034
53 | 0.0035026 | 0.00087742 | -0.0035025 | -0.00087743 | 1.7051e-08 | -1.0589e-08 | 0.0052394 | 0.0052394 | 0.0052394 | 0.99472 | -0.10041 | 0.99472 | -0.10051 | 1.4394
54 | 0.005916 | 0.0014792 | -0.0059147 | -0.001479 | 1.2729e-06 | 2.5201e-07 | 0.0088485 | 0.0088487 | 0.0088487 | 0.99474 | -0.10016 | 0.9945 | -0.10468 | 2.431
55 | 0.0021869 | 0.00054777 | -0.0021867 | -0.00054805 | 1.0806e-07 | -2.8038e-07 | 0.0032712 | 0.0032713 | 0.0032713 | 0.99474 | -0.10016 | 0.99468 | -0.1012 | 0.89871
56 | -0.02728 | -0.0069322 | 0.027283 | 0.0069338 | 3.5484e-06 | 1.6253e-06 | 0.04111 | 0.04111 | 0.04111 | 0.98824 | -0.2248 | 0.98838 | -0.2221 | 3.7646
57 | -0.032028 | -0.008123 | 0.03203 | 0.0081237 | 1.3725e-06 | 6.9706e-07 | 0.048253 | 0.048253 | 0.048253 | 0.98838 | -0.2221 | 0.98843 | -0.22121 | 4.4188
58 | -0.035546 | -0.009005 | 0.03556 | 0.0090124 | 1.3925e-05 | 7.4175e-06 | 0.053547 | 0.053546 | 0.053547 | 0.98843 | -0.22121 | 0.98885 | -0.21306 | 4.9036
59 | -0.038562 | -0.0097648 | 0.038567 | 0.0097676 | 5.1671e-06 | 2.835e-06 | 0.058064 | 0.058064 | 0.058064 | 0.98885 | -0.21306 | 0.98899 | -0.21027 | 5.3172
60 | -0.038567 | -0.0097676 | 0.038582 | 0.0097756 | 1.4453e-05 | 7.9292e-06 | 0.058064 | 0.058063 | 0.058064 | 0.98899 | -0.21027 | 0.9894 | -0.20247 | 5.3172
61 | 0.00080113 | 0.00020018 | -0.00080112 | -0.00020029 | 4.7892e-09 | -1.0902e-07 | 0.0012072 | 0.0012072 | 0.0012072 | 0.98735 | -0.24197 | 0.98734 | -0.2421 | 0.33165
62 | 0.0049991 | 0.0012495 | -0.0049988 | -0.0012495 | 3.0092e-07 | 6.4383e-09 | 0.0074786 | 0.0074787 | 0.0074787 | 0.9945 | -0.10468 | 0.99444 | -0.10595 | 2.0546
63 | 0.0045711 | 0.0011423 | -0.0045709 | -0.0011423 | 1.8732e-07 | -1.8676e-08 | 0.0068388 | 0.0068388 | 0.0068388 | 0.99444 | -0.10595 | 0.99439 | -0.10681 | 1.8788
64 | 0.0010848 | 0.00027147 | -0.0010847 | -0.00027186 | 3.0677e-08 | -3.8367e-07 | 0.0016226 | 0.0016227 | 0.0016227 | 0.99472 | -0.10051 | 0.99469 | -0.10111 | 0.4458
65 | 0.0042948 | 0.0010731 | -0.0042947 | -0.0010732 | 1.2653e-07 | -2.5029e-08 | 0.0064256 | 0.0064256 | 0.0064256 | 0.99439 | -0.10681 | 0.99436 | -0.10743 | 1.7653
66 | -0.0023748 | -0.00059519 | 0.0023749 | 0.00059498 | 1.115e-07 | -2.0528e-07 | 0.0036428 | 0.0036427 | 0.0036428 | 0.97007 | -0.57789 | 0.97012 | -0.57691 | 1.0008
67 | -0.0085334 | -0.0021384 | 0.0085339 | 0.0021387 | 4.8186e-07 | 2.1577e-07 | 0.013089 | 0.013089 | 0.013089 | 0.97012 | -0.57691 | 0.97018 | -0.57572 | 3.5958
68 | -0.013307 | -0.0033348 | 0.013318 | 0.0033412 | 1.1351e-05 | 6.3664e-06 | 0.020409 | 0.020409 | 0.020409 | 0.97018 | -0.57572 | 0.97108 | -0.55783 | 5.6069
69 | -0.032387 | -0.0081363 | 0.032401 | 0.0081454 | 1.4456e-05 | 9.0567e-06 | 0.04955 | 0.04955 | 0.04955 | 0.97273 | -0.52523 | 0.97321 | -0.51588 | 13.6127
70 | 0.005712 | 0.0014315 | -0.0057097 | -0.001431 | 2.2181e-06 | 4.583e-07 | 0.0087377 | 0.008738 | 0.008738 | 0.97273 | -0.52523 | 0.97232 | -0.53338 | 2.4006
71 | 0.026675 | 0.0067049 | -0.026646 | -0.0066869 | 2.9062e-05 | 1.8023e-05 | 0.040813 | 0.040813 | 0.040813 | 0.97273 | -0.52523 | 0.97158 | -0.54807 | 11.2123
72 | -0.033595 | -0.0084446 | 0.033609 | 0.0084531 | 1.3614e-05 | 8.5421e-06 | 0.051375 | 0.051375 | 0.051375 | 0.97321 | -0.51588 | 0.97364 | -0.5074 | 14.1141
73 | 0.0008624 | 0.00021604 | -0.00086239 | -0.00021614 | 5.4729e-09 | -1.001e-07 | 0.0013208 | 0.0013208 | 0.0013208 | 0.97158 | -0.54807 | 0.97157 | -0.54821 | 0.36286
74 | 0.025784 | 0.0064708 | -0.025772 | -0.0064634 | 1.1991e-05 | 7.4202e-06 | 0.039492 | 0.039492 | 0.039492 | 0.97158 | -0.54807 | 0.97108 | -0.55783 | 10.8495
75 | 0.011509 | 0.0028856 | -0.011508 | -0.0028847 | 1.6639e-06 | 8.8842e-07 | 0.017636 | 0.017637 | 0.017637 | 0.97108 | -0.55783 | 0.97093 | -0.56086 | 4.8452
76 | 0.0098712 | 0.0024745 | -0.0098689 | -0.0024734 | 2.3314e-06 | 1.1562e-06 | 0.015129 | 0.015129 | 0.015129 | 0.97093 | -0.56086 | 0.97068 | -0.56582 | 4.1562
77 | 0.12507 | 0.031992 | -0.12443 | -0.031591 | 0.00063526 | 0.00040104 | 0.18801 | 0.18801 | 0.18801 | 0.9911 | -0.16886 | 0.9856 | -0.27439 | 17.2168
78 | 0.12103 | 0.030739 | -0.121 | -0.030721 | 2.7984e-05 | 1.7654e-05 | 0.18288 | 0.18288 | 0.18288 | 0.9856 | -0.27439 | 0.98535 | -0.27919 | 16.7468
79 | -0.0091703 | -0.0022983 | 0.0091737 | 0.0022999 | 3.3606e-06 | 1.5675e-06 | 0.01392 | 0.01392 | 0.01392 | 0.98026 | -0.37788 | 0.98065 | -0.37019 | 3.8243
80 | 0.0079963 | 0.0020041 | -0.007995 | -0.0020035 | 1.3884e-06 | 5.7185e-07 | 0.012138 | 0.012138 | 0.012138 | 0.98026 | -0.37788 | 0.98008 | -0.38152 | 3.3347
81 | -0.018088 | -0.0045346 | 0.018089 | 0.0045354 | 1.2602e-06 | 7.5026e-07 | 0.027447 | 0.027447 | 0.027447 | 0.98065 | -0.37019 | 0.98073 | -0.36873 | 7.5404
82 | 0.0089144 | 0.0022347 | -0.0089119 | -0.0022336 | 2.5016e-06 | 1.1412e-06 | 0.013527 | 0.013527 | 0.013527 | 0.98065 | -0.37019 | 0.98035 | -0.37608 | 3.7162
83 | 0.0066189 | 0.0016586 | -0.0066187 | -0.0016586 | 1.6323e-07 | 5.015e-08 | 0.010049 | 0.010049 | 0.010049 | 0.98008 | -0.38152 | 0.98005 | -0.38204 | 2.7607
84 | 0.031585 | 0.00793 | -0.031574 | -0.0079229 | 1.1332e-05 | 7.0914e-06 | 0.048277 | 0.048277 | 0.048277 | 0.97364 | -0.5074 | 0.97326 | -0.51492 | 13.2629
85 | -0.065194 | -0.016383 | 0.065269 | 0.016431 | 7.4843e-05 | 4.7649e-05 | 0.099652 | 0.099652 | 0.099652 | 0.97364 | -0.5074 | 0.97486 | -0.48338 | 27.377
86 | -0.090771 | -0.022972 | 0.090846 | 0.023019 | 7.5576e-05 | 4.7162e-05 | 0.1378 | 0.1378 | 0.1378 | 0.98073 | -0.36873 | 0.98162 | -0.3514 | 12.6193
87 | 0.072681 | 0.018437 | -0.072586 | -0.018377 | 9.5237e-05 | 5.9901e-05 | 0.11036 | 0.11036 | 0.11036 | 0.98073 | -0.36873 | 0.97933 | -0.39602 | 15.1588
88 | 0.0072377 | 0.001814 | -0.0072373 | -0.0018138 | 4.5531e-07 | 1.6456e-07 | 0.010986 | 0.010986 | 0.010986 | 0.98035 | -0.37608 | 0.98029 | -0.3774 | 3.0181
89 | 0.0043954 | 0.0011014 | -0.0043949 | -0.0011014 | 5.449e-07 | -6.2336e-08 | 0.0066735 | 0.0066736 | 0.0066736 | 0.98005 | -0.38204 | 0.97992 | -0.38464 | 1.8334
90 | 0.0028195 | 0.0007066 | -0.0028195 | -0.00070661 | 8.1256e-09 | -9.6909e-09 | 0.0042814 | 0.0042814 | 0.0042814 | 0.97992 | -0.38464 | 0.97991 | -0.38471 | 1.1762
91 | 0.00094587 | 0.00023704 | -0.00094587 | -0.00023706 | 9.7812e-10 | -1.5301e-08 | 0.0014363 | 0.0014363 | 0.0014363 | 0.97991 | -0.38471 | 0.97991 | -0.38473 | 0.39459
92 | -0.090846 | -0.023019 | 0.090991 | 0.02311 | 0.00014494 | 9.0441e-05 | 0.1378 | 0.1378 | 0.1378 | 0.98162 | -0.3514 | 0.98333 | -0.31824 | 12.6192
93 | 0.0717 | 0.018155 | -0.071693 | -0.018151 | 6.5177e-06 | 4.1529e-06 | 0.10901 | 0.10901 | 0.10901 | 0.97933 | -0.39602 | 0.97923 | -0.39791 | 29.9477
94 | 0.019561 | 0.0049097 | -0.019545 | -0.0049006 | 1.5112e-05 | 9.0891e-06 | 0.029602 | 0.029603 | 0.029603 | 0.98333 | -0.31824 | 0.9825 | -0.33446 | 8.1326
95 | -0.11055 | -0.028019 | 0.11064 | 0.028076 | 9.0245e-05 | 5.6776e-05 | 0.1674 | 0.1674 | 0.1674 | 0.98333 | -0.31824 | 0.98421 | -0.30127 | 15.33
96 | 0.070313 | 0.017805 | -0.070161 | -0.017708 | 0.00015243 | 9.7111e-05 | 0.10691 | 0.10691 | 0.10691 | 0.97923 | -0.39791 | 0.97691 | -0.44316 | 29.3716
97 | 0.018617 | 0.004668 | -0.018614 | -0.004666 | 3.3399e-06 | 1.9957e-06 | 0.028197 | 0.028197 | 0.028197 | 0.9825 | -0.33446 | 0.98231 | -0.33822 | 7.7463
98 | -0.11427 | -0.028986 | 0.11427 | 0.028986 | 3.1085e-07 | 1.9577e-07 | 0.17289 | 0.17289 | 0.17289 | 0.98421 | -0.30127 | 0.98421 | -0.30121 | 15.8323
99 | 0.068549 | 0.017304 | -0.068435 | -0.017231 | 0.00011372 | 7.2431e-05 | 0.10446 | 0.10446 | 0.10446 | 0.97691 | -0.44316 | 0.97514 | -0.47786 | 28.6969
100 | -0.11876 | -0.030112 | 0.11889 | 0.030191 | 0.00012584 | 7.935e-05 | 0.17968 | 0.17968 | 0.17968 | 0.98421 | -0.30121 | 0.98535 | -0.27919 | 16.4543
101 | 0.016672 | 0.0041792 | -0.016671 | -0.0041786 | 1.1158e-06 | 6.5503e-07 | 0.025255 | 0.025255 | 0.025255 | 0.98231 | -0.33822 | 0.98224 | -0.33963 | 6.9381
102 | 0.012127 | 0.0030398 | -0.012124 | -0.0030382 | 2.9721e-06 | 1.605e-06 | 0.018371 | 0.018371 | 0.018371 | 0.98224 | -0.33963 | 0.98197 | -0.34477 | 5.0471
103 | 0.0061403 | 0.0015387 | -0.0061397 | -0.0015385 | 6.0998e-07 | 1.5273e-07 | 0.0093045 | 0.0093046 | 0.0093046 | 0.98197 | -0.34477 | 0.98187 | -0.34686 | 2.5562
104 | 0.0059835 | 0.0014995 | -0.0059826 | -0.0014993 | 9.0399e-07 | 2.0766e-07 | 0.0090669 | 0.009067 | 0.009067 | 0.98197 | -0.34477 | 0.98181 | -0.34794 | 2.4909
105 | 0.03121 | 0.0078317 | -0.031201 | -0.007826 | 9.0238e-06 | 5.644e-06 | 0.04772 | 0.04772 | 0.04772 | 0.97326 | -0.51492 | 0.97295 | -0.52099 | 13.1099
106 | -0.067263 | -0.016931 | 0.067281 | 0.016942 | 1.7749e-05 | 1.1303e-05 | 0.1027 | 0.1027 | 0.1027 | 0.97486 | -0.48338 | 0.97514 | -0.47786 | 28.2131
107 | 0.030319 | 0.007605 | -0.030305 | -0.0075964 | 1.3885e-05 | 8.6726e-06 | 0.046372 | 0.046372 | 0.046372 | 0.97295 | -0.52099 | 0.97246 | -0.5306 | 12.7395
108 | 0.017257 | 0.0043262 | -0.017253 | -0.0043241 | 3.5507e-06 | 2.104e-06 | 0.026406 | 0.026406 | 0.026406 | 0.97246 | -0.5306 | 0.97225 | -0.53492 | 7.2544
109 | 0.0077894 | 0.0019522 | -0.0077892 | -0.0019521 | 2.1889e-07 | 8.9159e-08 | 0.011922 | 0.011922 | 0.011922 | 0.97225 | -0.53492 | 0.97222 | -0.53551 | 3.2752
110 | 0.0067891 | 0.0017015 | -0.0067885 | -0.0017013 | 5.5275e-07 | 1.8449e-07 | 0.010391 | 0.010391 | 0.010391 | 0.97222 | -0.53551 | 0.97213 | -0.53722 | 2.8547
111 | 0.0057213 | 0.0014338 | -0.0057206 | -0.0014337 | 7.3578e-07 | 1.5376e-07 | 0.0087574 | 0.0087575 | 0.0087575 | 0.97213 | -0.53722 | 0.97199 | -0.53992 | 2.4059
112 | 0.002081 | 0.00052152 | -0.002081 | -0.00052156 | 1.5223e-08 | -3.9832e-08 | 0.0031858 | 0.0031859 | 0.0031859 | 0.97199 | -0.53992 | 0.97199 | -0.54007 | 0.87524
113 | 0.0041965 | 0.0010515 | -0.0041961 | -0.0010516 | 4.1313e-07 | -8.0066e-08 | 0.0063596 | 0.0063598 | 0.0063598 | 0.98187 | -0.34686 | 0.98176 | -0.34892 | 1.7472
114 | 0.0059826 | 0.0014993 | -0.0059805 | -0.0014989 | 2.0249e-06 | 4.6563e-07 | 0.009067 | 0.0090673 | 0.0090673 | 0.98181 | -0.34794 | 0.98145 | -0.35505 | 2.491
115 | 0.0023264 | 0.000583 | -0.0023264 | -0.00058305 | 2.2519e-08 | -4.6662e-08 | 0.003526 | 0.0035261 | 0.0035261 | 0.98176 | -0.34892 | 0.98175 | -0.34913 | 0.9687
116 | 0.088417 | 0.022374 | -0.088395 | -0.02236 | 2.2674e-05 | 1.4114e-05 | 0.13285 | 0.13285 | 0.13285 | 0.99091 | -0.17325 | 0.99064 | -0.17859 | 12.1657
117 | 0.0042947 | 0.0010732 | -0.0042938 | -0.0010733 | 8.9439e-07 | -1.7669e-07 | 0.0064256 | 0.0064259 | 0.0064259 | 0.99436 | -0.10743 | 0.99413 | -0.11181 | 1.7654
118 | 0.0027486 | 0.00068793 | -0.0027485 | -0.00068808 | 1.0691e-07 | -1.4999e-07 | 0.0041138 | 0.0041138 | 0.0041138 | 0.99413 | -0.11181 | 0.99409 | -0.11263 | 1.1302
119 | 0.0015452 | 0.0003854 | -0.0015451 | -0.00038586 | 7.8677e-08 | -4.5842e-07 | 0.0023122 | 0.0023123 | 0.0023123 | 0.99413 | -0.11181 | 0.99408 | -0.11289 | 0.63526
120 | 0.0021868 | 0.0005473 | -0.0021866 | -0.00054763 | 1.2905e-07 | -3.3383e-07 | 0.003273 | 0.0032732 | 0.0032732 | 0.99409 | -0.11263 | 0.99403 | -0.11387 | 0.89922
121 | 0.00097323 | 0.00024254 | -0.0009732 | -0.00024314 | 3.8496e-08 | -6.0275e-07 | 0.0014563 | 0.0014566 | 0.0014566 | 0.99408 | -0.11289 | 0.99404 | -0.11372 | 0.40015
122 | 0.001756 | 0.00043971 | -0.001756 | -0.0004399 | 4.517e-08 | -1.9707e-07 | 0.0026285 | 0.0026286 | 0.0026286 | 0.99403 | -0.11387 | 0.994 | -0.11441 | 0.72214
123 | 0.00028526 | 7.0727e-05 | -0.00028525 | -7.1491e-05 | 4.0376e-09 | -7.6336e-07 | 0.00042674 | 0.00042701 | 0.00042701 | 0.99404 | -0.11372 | 0.99402 | -0.11402 | 0.11731
124 | 0.084757 | 0.021448 | -0.08466 | -0.021388 | 9.7001e-05 | 6.0236e-05 | 0.12739 | 0.12739 | 0.12739 | 0.99064 | -0.17859 | 0.9894 | -0.20247 | 11.6654
125 | 0.0011816 | 0.00029596 | -0.0011816 | -0.00029601 | 4.1177e-09 | -4.2856e-08 | 0.0017688 | 0.0017688 | 0.0017688 | 0.994 | -0.11441 | 0.994 | -0.11448 | 0.48595
126 | 0.04383 | 0.011049 | -0.043776 | -0.011015 | 5.4446e-05 | 3.4417e-05 | 0.065942 | 0.065942 | 0.065942 | 0.9894 | -0.20247 | 0.98806 | -0.22846 | 18.1158
127 | -0.015677 | -0.0039305 | 0.015689 | 0.0039371 | 1.1376e-05 | 6.5923e-06 | 0.023691 | 0.023691 | 0.023691 | 0.9847 | -0.2939 | 0.98548 | -0.27868 | 6.5086
128 | 0.015677 | 0.0039305 | -0.015673 | -0.003928 | 4.2337e-06 | 2.4538e-06 | 0.023691 | 0.023691 | 0.023691 | 0.9847 | -0.2939 | 0.9844 | -0.29956 | 6.5086
129 | -0.037419 | -0.0093847 | 0.037436 | 0.0093956 | 1.7261e-05 | 1.0863e-05 | 0.056503 | 0.056503 | 0.056503 | 0.98548 | -0.27868 | 0.98597 | -0.26901 | 15.5228
130 | 0.01369 | 0.0034326 | -0.013684 | -0.0034295 | 5.4741e-06 | 3.0684e-06 | 0.020672 | 0.020672 | 0.020672 | 0.98548 | -0.27868 | 0.98505 | -0.28707 | 5.679
131 | 0.0053223 | 0.0013339 | -0.0053221 | -0.0013338 | 2.5642e-07 | 2.9806e-08 | 0.0080452 | 0.0080452 | 0.0080452 | 0.9844 | -0.29956 | 0.98435 | -0.30058 | 2.2102
132 | 0.043133 | 0.010854 | -0.043109 | -0.010838 | 2.41e-05 | 1.5229e-05 | 0.064974 | 0.064974 | 0.064974 | 0.98806 | -0.22846 | 0.98745 | -0.24016 | 17.85
133 | 0.041611 | 0.010463 | -0.041581 | -0.010444 | 3.0515e-05 | 1.9265e-05 | 0.062717 | 0.062717 | 0.062717 | 0.98745 | -0.24016 | 0.98666 | -0.25553 | 17.2299
134 | -0.00089567 | -0.00022448 | 0.00089568 | 0.00022429 | 1.0319e-08 | -1.8463e-07 | 0.0013532 | 0.0013532 | 0.0013532 | 0.98488 | -0.29027 | 0.98489 | -0.29002 | 0.37177
135 | -0.0017917 | -0.00044886 | 0.0017917 | 0.00044877 | 2.2091e-08 | -8.8177e-08 | 0.0027069 | 0.0027069 | 0.0027069 | 0.98489 | -0.29002 | 0.98491 | -0.28976 | 0.74366
136 | -0.039133 | -0.0098208 | 0.039158 | 0.0098367 | 2.5168e-05 | 1.5862e-05 | 0.059064 | 0.059064 | 0.059064 | 0.98597 | -0.26901 | 0.98666 | -0.25553 | 16.2263
137 | 0.01023 | 0.0025636 | -0.010229 | -0.0025634 | 4.6212e-07 | 2.3006e-07 | 0.015453 | 0.015453 | 0.015453 | 0.98505 | -0.28707 | 0.985 | -0.28802 | 4.2453
138 | 0.0067729 | 0.0016972 | -0.0067724 | -0.001697 | 4.4464e-07 | 1.4041e-07 | 0.010232 | 0.010232 | 0.010232 | 0.985 | -0.28802 | 0.98493 | -0.2894 | 2.8109
139 | 0.0058768 | 0.0014726 | -0.0058767 | -0.0014726 | 1.0231e-07 | 2.143e-08 | 0.0088785 | 0.0088785 | 0.0088785 | 0.98493 | -0.2894 | 0.98491 | -0.28976 | 2.4391
140 | 0.00065555 | 0.00016381 | -0.00065555 | -0.00016399 | 5.3269e-09 | -1.8276e-07 | 0.0009878 | 0.00098787 | 0.00098787 | 0.98734 | -0.2421 | 0.98733 | -0.24227 | 0.27139
141 | 0.00045397 | 0.00011347 | -0.00045397 | -0.00011377 | 4.1959e-09 | -3.0305e-07 | 0.00068407 | 0.00068418 | 0.00068418 | 0.98733 | -0.24227 | 0.98732 | -0.24247 | 0.18796
142 | 0.00069723 | 0.00017461 | -0.00069722 | -0.00017474 | 4.3575e-09 | -1.3547e-07 | 0.0010437 | 0.0010438 | 0.0010438 | 0.994 | -0.11448 | 0.99399 | -0.11462 | 0.28675

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25921 | 0.066169

## res_load
| p_mw | q_mvar
0 | 0.00047685 | 0.00011951
1 | 0.000367 | 9.1978e-05
2 | 0.00074088 | 0.00018568
3 | 0.00076277 | 0.00019117
4 | 0.0001223 | 3.065e-05
5 | 0.00068753 | 0.00017231
6 | 0.003444 | 0.00086316
7 | 0.00034703 | 8.6973e-05
8 | 0.0022856 | 0.00057282
9 | 0.0068284 | 0.0017114
10 | 0.002583 | 0.00064736
11 | 0.0009868 | 0.00024732
12 | 0.0021323 | 0.0005344
13 | 0.001771 | 0.00044386
14 | 0.00063469 | 0.00015907
15 | 0.00019781 | 4.9575e-05
16 | 0.00070649 | 0.00017706
17 | 0.00048227 | 0.00012087
18 | 0.00035916 | 9.0013e-05
19 | 0.0019455 | 0.00048758
20 | 0.0014806 | 0.00037107
21 | 0.0021667 | 0.00054302
22 | 0.0013552 | 0.00033966
23 | 0.00097429 | 0.00024418
24 | 0.0019116 | 0.00047909
25 | 0.00040809 | 0.00010228
26 | 0.0024672 | 0.00061834
27 | 0.002191 | 0.00054913
28 | 0.00031388 | 7.8666e-05
29 | 0.00032451 | 8.133e-05
30 | 0.0010285 | 0.00025776
31 | 0.0010477 | 0.00026258
32 | 0.00028672 | 7.186e-05
33 | 0.00049722 | 0.00012461
34 | 0.0004155 | 0.00010413
35 | 0.0047449 | 0.0011892
36 | 0.0035165 | 0.00088133
37 | 0.0030021 | 0.0007524
38 | 0.00020025 | 5.0188e-05
39 | 0.0021867 | 0.00054805
40 | 0.00091566 | 0.00022949
41 | 0.00042767 | 0.00010718
42 | 0.0024178 | 0.00060595
43 | 0.00027613 | 6.9204e-05
44 | 0.0023748 | 0.00059519
45 | 0.0061584 | 0.0015435
46 | 0.0047728 | 0.0011962
47 | 0.0011938 | 0.0002992
48 | 0.0057097 | 0.001431
49 | 0.00094421 | 0.00023664
50 | 0.0016365 | 0.00041014
51 | 0.0035692 | 0.00089452
52 | 0.0033993 | 0.00085195
53 | 0.0098689 | 0.0024734
54 | 0.00086239 | 0.00021614
55 | 0.00033223 | 8.3266e-05
56 | 0.001174 | 0.00029423
57 | 0.0013761 | 0.00034488
58 | 0.0016742 | 0.0004196
59 | 0.0022233 | 0.00055721
60 | 0.0015754 | 0.00039483
61 | 0.0018736 | 0.00046957
62 | 0.00094587 | 0.00023706
63 | 0.00088616 | 0.00022209
64 | 0.0072373 | 0.0018138
65 | 0.0013801 | 0.0003459
66 | 0.00092834 | 0.00023266
67 | 0.0036285 | 0.00090938
68 | 0.0016123 | 0.00040409
69 | 0.0044925 | 0.0011259
70 | 0.0021152 | 0.00053013
71 | 0.0019421 | 0.00048673
72 | 0.0045438 | 0.0011388
73 | 0.00036413 | 9.1259e-05
74 | 0.001994 | 0.00049975
75 | 0.00088179 | 0.000221
76 | 0.0011541 | 0.00028924
77 | 0.013048 | 0.0032702
78 | 0.0094639 | 0.0023719
79 | 0.0010002 | 0.00025067
80 | 0.0010672 | 0.00026747
81 | 0.0036395 | 0.00091215
82 | 0.002081 | 0.00052156
83 | 0.0019432 | 0.00048702
84 | 0.0018696 | 0.00046857
85 | 0.0059805 | 0.0014989
86 | 0.0023264 | 0.00058305
87 | 0.0015137 | 0.00037936
88 | 0.0014079 | 0.00035285
89 | 0.0048836 | 0.001224
90 | 0.00056172 | 0.00014078
91 | 0.00057186 | 0.00014332
92 | 0.00043063 | 0.00010793
93 | 0.00068794 | 0.00017241
94 | 0.0036374 | 0.00091163
95 | 0.0010847 | 0.00027186
96 | 0.00057433 | 0.00014394
97 | 0.00028525 | 7.1491e-05
98 | 0.0022483 | 0.00056349
99 | 0.0080403 | 0.0020151
100 | 0.010351 | 0.0025941
101 | 0.00064263 | 0.00016106
102 | 0.0014978 | 0.00037538
103 | 0.00089567 | 0.00022448
104 | 0.00089602 | 0.00022456
105 | 0.0016968 | 0.00042525
106 | 0.0034549 | 0.00086587
107 | 0.0053221 | 0.0013338
108 | 0.0024225 | 0.00060714
109 | 0.0034562 | 0.00086621
110 | 0.00089567 | 0.00022448
111 | 0.0040849 | 0.0010238
112 | 0.00014557 | 3.6484e-05
113 | 0.00020158 | 5.052e-05
114 | 0.00045397 | 0.00011377
115 | 0.00048439 | 0.0001214
116 | 0.00069722 | 0.00017474

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1