## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2163-5_1_6_node_43 | 0.4 | n |  | TRUE
1 | bus_LV_2163-5_1_6_node_44 | 0.4 | n |  | TRUE
2 | bus_LV_2163-5_1_6_node_26 | 0.4 | n |  | TRUE
3 | bus_LV_2163-5_1_6_node_25 | 0.4 | n |  | TRUE
4 | bus_LV_2163-5_1_6_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_2163-5_1_6_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_2163-5_1_6_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_2163-5_1_6_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_2163-5_1_6_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_2163-5_1_6_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_2163-5_1_6_node_19 | 0.4 | n |  | TRUE
11 | bus_LV_2163-5_1_6_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_2163-5_1_6_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_2163-5_1_6_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_2163-5_1_6_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_2163-5_1_6_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_2163-5_1_6_node_46 | 0.4 | n |  | TRUE
17 | bus_LV_2163-5_1_6_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_2163-5_1_6_node_52 | 0.4 | n |  | TRUE
19 | bus_LV_2163-5_1_6_node_53 | 0.4 | n |  | TRUE
20 | bus_LV_2163-5_1_6_node_51 | 0.4 | n |  | TRUE
21 | bus_LV_2163-5_1_6_node_71 | 0.4 | n |  | TRUE
22 | bus_LV_2163-5_1_6_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_2163-5_1_6_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_2163-5_1_6_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_2163-5_1_6_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_2163-5_1_6_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_2163-5_1_6_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_2163-5_1_6_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_2163-5_1_6_node_68 | 0.4 | n |  | TRUE
30 | bus_LV_2163-5_1_6_node_73 | 0.4 | n |  | TRUE
31 | bus_LV_2163-5_1_6_node_55 | 0.4 | n |  | TRUE
32 | bus_LV_2163-5_1_6_node_54 | 0.4 | n |  | TRUE
33 | bus_LV_2163-5_1_6_node_42 | 0.4 | n |  | TRUE
34 | bus_LV_2163-5_1_6_node_57 | 0.4 | n |  | TRUE
35 | bus_LV_2163-5_1_6_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_2163-5_1_6_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_2163-5_1_6_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_2163-5_1_6_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_2163-5_1_6_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_2163-5_1_6_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_2163-5_1_6_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_2163-5_1_6_node_62 | 0.4 | n |  | TRUE
43 | bus_LV_2163-5_1_6_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_2163-5_1_6_node_220 | 0.4 | n |  | TRUE
45 | bus_LV_2163-5_1_6_node_60 | 0.4 | n |  | TRUE
46 | bus_LV_2163-5_1_6_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_2163-5_1_6_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_2163-5_1_6_node_48 | 0.4 | n |  | TRUE
49 | bus_LV_2163-5_1_6_node_66 | 0.4 | n |  | TRUE
50 | bus_LV_2163-5_1_6_node_72 | 0.4 | n |  | TRUE
51 | bus_LV_2163-5_1_6_node_64 | 0.4 | n |  | TRUE
52 | bus_LV_2163-5_1_6_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_2163-5_1_6_node_50 | 0.4 | n |  | TRUE
54 | bus_LV_2163-5_1_6_node_161 | 0.4 | n |  | TRUE
55 | bus_LV_2163-5_1_6_node_193 | 0.4 | n |  | TRUE
56 | bus_LV_2163-5_1_6_node_159 | 0.4 | n |  | TRUE
57 | bus_LV_2163-5_1_6_node_74 | 0.4 | n |  | TRUE
58 | bus_LV_2163-5_1_6_node_180 | 0.4 | n |  | TRUE
59 | bus_LV_2163-5_1_6_node_179 | 0.4 | n |  | TRUE
60 | bus_LV_2163-5_1_6_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_2163-5_1_6_node_192 | 0.4 | n |  | TRUE
62 | bus_LV_2163-5_1_6_node_197 | 0.4 | n |  | TRUE
63 | bus_LV_2163-5_1_6_node_190 | 0.4 | n |  | TRUE
64 | bus_LV_2163-5_1_6_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_2163-5_1_6_node_221 | 0.4 | n |  | TRUE
66 | bus_LV_2163-5_1_6_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_2163-5_1_6_node_65 | 0.4 | n |  | TRUE
68 | bus_LV_2163-5_1_6_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_2163-5_1_6_node_211 | 0.4 | n |  | TRUE
70 | bus_LV_2163-5_1_6_node_208 | 0.4 | n |  | TRUE
71 | bus_LV_2163-5_1_6_node_69 | 0.4 | n |  | TRUE
72 | bus_LV_2163-5_1_6_node_70 | 0.4 | n |  | TRUE
73 | bus_LV_2163-5_1_6_node_75 | 0.4 | n |  | TRUE
74 | bus_LV_2163-5_1_6_node_76 | 0.4 | n |  | TRUE
75 | bus_LV_2163-5_1_6_node_177 | 0.4 | n |  | TRUE
76 | bus_LV_2163-5_1_6_node_175 | 0.4 | n |  | TRUE
77 | bus_LV_2163-5_1_6_node_77 | 0.4 | n |  | TRUE
78 | bus_LV_2163-5_1_6_node_78 | 0.4 | n |  | TRUE
79 | bus_LV_2163-5_1_6_node_79 | 0.4 | n |  | TRUE
80 | bus_LV_2163-5_1_6_node_80 | 0.4 | n |  | TRUE
81 | bus_LV_2163-5_1_6_node_81 | 0.4 | n |  | TRUE
82 | bus_LV_2163-5_1_6_node_82 | 0.4 | n |  | TRUE
83 | bus_LV_2163-5_1_6_node_89 | 0.4 | n |  | TRUE
84 | bus_LV_2163-5_1_6_node_90 | 0.4 | n |  | TRUE
85 | bus_LV_2163-5_1_6_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_2163-5_1_6_node_97 | 0.4 | n |  | TRUE
87 | bus_LV_2163-5_1_6_node_96 | 0.4 | n |  | TRUE
88 | bus_LV_2163-5_1_6_node_198 | 0.4 | n |  | TRUE
89 | bus_LV_2163-5_1_6_node_91 | 0.4 | n |  | TRUE
90 | bus_LV_2163-5_1_6_node_290 | 0.4 | n |  | TRUE
91 | bus_LV_2163-5_1_6_node_289 | 0.4 | n |  | TRUE
92 | bus_LV_2163-5_1_6_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_2163-5_1_6_node_98 | 0.4 | n |  | TRUE
94 | bus_LV_2163-5_1_6_node_83 | 0.4 | n |  | TRUE
95 | bus_LV_2163-5_1_6_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_2163-5_1_6_node_85 | 0.4 | n |  | TRUE
97 | bus_LV_2163-5_1_6_node_99 | 0.4 | n |  | TRUE
98 | bus_LV_2163-5_1_6_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_2163-5_1_6_node_199 | 0.4 | n |  | TRUE
100 | bus_LV_2163-5_1_6_node_226 | 0.4 | n |  | TRUE
101 | bus_LV_2163-5_1_6_node_254 | 0.4 | n |  | TRUE
102 | bus_LV_2163-5_1_6_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_2163-5_1_6_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_2163-5_1_6_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_2163-5_1_6_node_95 | 0.4 | n |  | TRUE
106 | bus_LV_2163-5_1_6_node_288 | 0.4 | n |  | TRUE
107 | bus_LV_2163-5_1_6_node_200 | 0.4 | n |  | TRUE
108 | bus_LV_2163-5_1_6_node_298 | 0.4 | n |  | TRUE
109 | bus_LV_2163-5_1_6_node_291 | 0.4 | n |  | TRUE
110 | bus_LV_2163-5_1_6_node_101 | 0.4 | n |  | TRUE
111 | bus_LV_2163-5_1_6_node_138 | 0.4 | n |  | TRUE
112 | bus_LV_2163-5_1_6_node_149 | 0.4 | n |  | TRUE
113 | bus_LV_2163-5_1_6_node_151 | 0.4 | n |  | TRUE
114 | bus_LV_2163-5_1_6_node_137 | 0.4 | n |  | TRUE
115 | bus_LV_2163-5_1_6_node_147 | 0.4 | n |  | TRUE
116 | bus_LV_2163-5_1_6_node_102 | 0.4 | n |  | TRUE
117 | bus_LV_2163-5_1_6_node_103 | 0.4 | n |  | TRUE
118 | bus_LV_2163-5_1_6_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_2163-5_1_6_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_2163-5_1_6_node_106 | 0.4 | n |  | TRUE
121 | bus_LV_2163-5_1_6_node_107 | 0.4 | n |  | TRUE
122 | bus_LV_2163-5_1_6_node_110 | 0.4 | n |  | TRUE
123 | bus_LV_2163-5_1_6_node_146 | 0.4 | n |  | TRUE
124 | bus_LV_2163-5_1_6_node_150 | 0.4 | n |  | TRUE
125 | bus_LV_2163-5_1_6_node_134 | 0.4 | n |  | TRUE
126 | bus_LV_2163-5_1_6_node_115 | 0.4 | n |  | TRUE
127 | bus_LV_2163-5_1_6_node_108 | 0.4 | n |  | TRUE
128 | bus_LV_2163-5_1_6_node_109 | 0.4 | n |  | TRUE
129 | bus_LV_2163-5_1_6_node_144 | 0.4 | n |  | TRUE
130 | bus_LV_2163-5_1_6_node_145 | 0.4 | n |  | TRUE
131 | bus_LV_2163-5_1_6_node_143 | 0.4 | n |  | TRUE
132 | bus_LV_2163-5_1_6_node_135 | 0.4 | n |  | TRUE
133 | bus_LV_2163-5_1_6_node_111 | 0.4 | n |  | TRUE
134 | bus_LV_2163-5_1_6_node_112 | 0.4 | n |  | TRUE
135 | bus_LV_2163-5_1_6_node_113 | 0.4 | n |  | TRUE
136 | bus_LV_2163-5_1_6_node_114 | 0.4 | n |  | TRUE
137 | bus_LV_2163-5_1_6_node_130 | 0.4 | n |  | TRUE
138 | bus_LV_2163-5_1_6_node_131 | 0.4 | n |  | TRUE
139 | bus_LV_2163-5_1_6_node_127 | 0.4 | n |  | TRUE
140 | bus_LV_2163-5_1_6_node_129 | 0.4 | n |  | TRUE
141 | bus_LV_2163-5_1_6_node_125 | 0.4 | n |  | TRUE
142 | bus_LV_2163-5_1_6_node_116 | 0.4 | n |  | TRUE
143 | bus_LV_2163-5_1_6_node_117 | 0.4 | n |  | TRUE
144 | bus_LV_2163-5_1_6_node_118 | 0.4 | n |  | TRUE
145 | bus_LV_2163-5_1_6_node_119 | 0.4 | n |  | TRUE
146 | bus_LV_2163-5_1_6_node_140 | 0.4 | n |  | TRUE
147 | bus_LV_2163-5_1_6_node_141 | 0.4 | n |  | TRUE
148 | bus_LV_2163-5_1_6_node_155 | 0.4 | n |  | TRUE
149 | bus_LV_2163-5_1_6_node_156 | 0.4 | n |  | TRUE
150 | bus_LV_2163-5_1_6_node_120 | 0.4 | n |  | TRUE
151 | bus_LV_2163-5_1_6_node_121 | 0.4 | n |  | TRUE
152 | bus_LV_2163-5_1_6_node_122 | 0.4 | n |  | TRUE
153 | bus_LV_2163-5_1_6_node_123 | 0.4 | n |  | TRUE
154 | bus_LV_2163-5_1_6_node_124 | 0.4 | n |  | TRUE
155 | bus_LV_2163-5_1_6_node_136 | 0.4 | n |  | TRUE
156 | bus_LV_2163-5_1_6_node_152 | 0.4 | n |  | TRUE
157 | bus_LV_2163-5_1_6_node_153 | 0.4 | n |  | TRUE
158 | bus_LV_2163-5_1_6_node_126 | 0.4 | n |  | TRUE
159 | bus_LV_2163-5_1_6_node_128 | 0.4 | n |  | TRUE
160 | bus_LV_2163-5_1_6_node_132 | 0.4 | n |  | TRUE
161 | bus_LV_2163-5_1_6_node_133 | 0.4 | n |  | TRUE
162 | bus_LV_2163-5_1_6_node_185 | 0.4 | n |  | TRUE
163 | bus_LV_2163-5_1_6_node_148 | 0.4 | n |  | TRUE
164 | bus_LV_2163-5_1_6_node_182 | 0.4 | n |  | TRUE
165 | bus_LV_2163-5_1_6_node_139 | 0.4 | n |  | TRUE
166 | bus_LV_2163-5_1_6_node_154 | 0.4 | n |  | TRUE
167 | bus_LV_2163-5_1_6_node_142 | 0.4 | n |  | TRUE
168 | bus_LV_2163-5_1_6_node_157 | 0.4 | n |  | TRUE
169 | bus_LV_2163-5_1_6_node_308 | 0.4 | n |  | TRUE
170 | bus_LV_2163-5_1_6_node_309 | 0.4 | n |  | TRUE
171 | bus_LV_2163-5_1_6_node_307 | 0.4 | n |  | TRUE
172 | bus_LV_2163-5_1_6_node_158 | 0.4 | n |  | TRUE
173 | bus_LV_2163-5_1_6_node_160 | 0.4 | n |  | TRUE
174 | bus_LV_2163-5_1_6_node_162 | 0.4 | n |  | TRUE
175 | bus_LV_2163-5_1_6_node_194 | 0.4 | n |  | TRUE
176 | bus_LV_2163-5_1_6_node_163 | 0.4 | n |  | TRUE
177 | bus_LV_2163-5_1_6_node_164 | 0.4 | n |  | TRUE
178 | bus_LV_2163-5_1_6_node_165 | 0.4 | n |  | TRUE
179 | bus_LV_2163-5_1_6_node_166 | 0.4 | n |  | TRUE
180 | bus_LV_2163-5_1_6_node_167 | 0.4 | n |  | TRUE
181 | bus_LV_2163-5_1_6_node_168 | 0.4 | n |  | TRUE
182 | bus_LV_2163-5_1_6_node_263 | 0.4 | n |  | TRUE
183 | bus_LV_2163-5_1_6_node_260 | 0.4 | n |  | TRUE
184 | bus_LV_2163-5_1_6_node_219 | 0.4 | n |  | TRUE
185 | bus_LV_2163-5_1_6_node_201 | 0.4 | n |  | TRUE
186 | bus_LV_2163-5_1_6_node_202 | 0.4 | n |  | TRUE
187 | bus_LV_2163-5_1_6_node_204 | 0.4 | n |  | TRUE
188 | bus_LV_2163-5_1_6_node_231 | 0.4 | n |  | TRUE
189 | bus_LV_2163-5_1_6_node_261 | 0.4 | n |  | TRUE
190 | bus_LV_2163-5_1_6_node_217 | 0.4 | n |  | TRUE
191 | bus_LV_2163-5_1_6_node_169 | 0.4 | n |  | TRUE
192 | bus_LV_2163-5_1_6_node_170 | 0.4 | n |  | TRUE
193 | bus_LV_2163-5_1_6_node_171 | 0.4 | n |  | TRUE
194 | bus_LV_2163-5_1_6_node_172 | 0.4 | n |  | TRUE
195 | bus_LV_2163-5_1_6_node_173 | 0.4 | n |  | TRUE
196 | bus_LV_2163-5_1_6_node_174 | 0.4 | n |  | TRUE
197 | bus_LV_2163-5_1_6_node_214 | 0.4 | n |  | TRUE
198 | bus_LV_2163-5_1_6_node_191 | 0.4 | n |  | TRUE
199 | bus_LV_2163-5_1_6_node_310 | 0.4 | n |  | TRUE
200 | bus_LV_2163-5_1_6_node_223 | 0.4 | n |  | TRUE
201 | bus_LV_2163-5_1_6_node_284 | 0.4 | n |  | TRUE
202 | bus_LV_2163-5_1_6_node_176 | 0.4 | n |  | TRUE
203 | bus_LV_2163-5_1_6_node_178 | 0.4 | n |  | TRUE
204 | bus_LV_2163-5_1_6_node_222 | 0.4 | n |  | TRUE
205 | bus_LV_2163-5_1_6_node_209 | 0.4 | n |  | TRUE
206 | bus_LV_2163-5_1_6_node_181 | 0.4 | n |  | TRUE
207 | bus_LV_2163-5_1_6_node_183 | 0.4 | n |  | TRUE
208 | bus_LV_2163-5_1_6_node_184 | 0.4 | n |  | TRUE
209 | bus_LV_2163-5_1_6_node_186 | 0.4 | n |  | TRUE
210 | bus_LV_2163-5_1_6_node_187 | 0.4 | n |  | TRUE
211 | bus_LV_2163-5_1_6_node_293 | 0.4 | n |  | TRUE
212 | bus_LV_2163-5_1_6_node_311 | 0.4 | n |  | TRUE
213 | bus_LV_2163-5_1_6_node_240 | 0.4 | n |  | TRUE
214 | bus_LV_2163-5_1_6_node_237 | 0.4 | n |  | TRUE
215 | bus_LV_2163-5_1_6_node_294 | 0.4 | n |  | TRUE
216 | bus_LV_2163-5_1_6_node_292 | 0.4 | n |  | TRUE
217 | bus_LV_2163-5_1_6_node_246 | 0.4 | n |  | TRUE
218 | bus_LV_2163-5_1_6_node_238 | 0.4 | n |  | TRUE
219 | bus_LV_2163-5_1_6_node_188 | 0.4 | n |  | TRUE
220 | bus_LV_2163-5_1_6_node_189 | 0.4 | n |  | TRUE
221 | bus_LV_2163-5_1_6_node_258 | 0.4 | n |  | TRUE
222 | bus_LV_2163-5_1_6_node_195 | 0.4 | n |  | TRUE
223 | bus_LV_2163-5_1_6_node_196 | 0.4 | n |  | TRUE
224 | bus_LV_2163-5_1_6_node_212 | 0.4 | n |  | TRUE
225 | bus_LV_2163-5_1_6_node_248 | 0.4 | n |  | TRUE
226 | bus_LV_2163-5_1_6_node_213 | 0.4 | n |  | TRUE
227 | bus_LV_2163-5_1_6_node_249 | 0.4 | n |  | TRUE
228 | bus_LV_2163-5_1_6_node_229 | 0.4 | n |  | TRUE
229 | bus_LV_2163-5_1_6_node_203 | 0.4 | n |  | TRUE
230 | bus_LV_2163-5_1_6_node_277 | 0.4 | n |  | TRUE
231 | bus_LV_2163-5_1_6_node_285 | 0.4 | n |  | TRUE
232 | bus_LV_2163-5_1_6_node_245 | 0.4 | n |  | TRUE
233 | bus_LV_2163-5_1_6_node_228 | 0.4 | n |  | TRUE
234 | bus_LV_2163-5_1_6_node_270 | 0.4 | n |  | TRUE
235 | bus_LV_2163-5_1_6_node_205 | 0.4 | n |  | TRUE
236 | bus_LV_2163-5_1_6_node_206 | 0.4 | n |  | TRUE
237 | bus_LV_2163-5_1_6_node_207 | 0.4 | n |  | TRUE
238 | bus_LV_2163-5_1_6_node_210 | 0.4 | n |  | TRUE
239 | bus_LV_2163-5_1_6_node_227 | 0.4 | n |  | TRUE
240 | bus_LV_2163-5_1_6_node_224 | 0.4 | n |  | TRUE
241 | bus_LV_2163-5_1_6_node_225 | 0.4 | n |  | TRUE
242 | bus_LV_2163-5_1_6_node_312 | 0.4 | n |  | TRUE
243 | bus_LV_2163-5_1_6_node_215 | 0.4 | n |  | TRUE
244 | bus_LV_2163-5_1_6_node_216 | 0.4 | n |  | TRUE
245 | bus_LV_2163-5_1_6_node_218 | 0.4 | n |  | TRUE
246 | bus_LV_2163-5_1_6_node_280 | 0.4 | n |  | TRUE
247 | bus_LV_2163-5_1_6_node_282 | 0.4 | n |  | TRUE
248 | bus_LV_2163-5_1_6_node_278 | 0.4 | n |  | TRUE
249 | bus_LV_2163-5_1_6_node_257 | 0.4 | n |  | TRUE
250 | bus_LV_2163-5_1_6_node_276 | 0.4 | n |  | TRUE
251 | bus_LV_2163-5_1_6_node_275 | 0.4 | n |  | TRUE
252 | bus_LV_2163-5_1_6_node_230 | 0.4 | n |  | TRUE
253 | bus_LV_2163-5_1_6_node_232 | 0.4 | n |  | TRUE
254 | bus_LV_2163-5_1_6_node_233 | 0.4 | n |  | TRUE
255 | bus_LV_2163-5_1_6_node_234 | 0.4 | n |  | TRUE
256 | bus_LV_2163-5_1_6_node_235 | 0.4 | n |  | TRUE
257 | bus_LV_2163-5_1_6_node_236 | 0.4 | n |  | TRUE
258 | bus_LV_2163-5_1_6_node_255 | 0.4 | n |  | TRUE
259 | bus_LV_2163-5_1_6_node_273 | 0.4 | n |  | TRUE
260 | bus_LV_2163-5_1_6_node_241 | 0.4 | n |  | TRUE
261 | bus_LV_2163-5_1_6_node_242 | 0.4 | n |  | TRUE
262 | bus_LV_2163-5_1_6_node_274 | 0.4 | n |  | TRUE
263 | bus_LV_2163-5_1_6_node_239 | 0.4 | n |  | TRUE
264 | bus_LV_2163-5_1_6_node_247 | 0.4 | n |  | TRUE
265 | bus_LV_2163-5_1_6_node_243 | 0.4 | n |  | TRUE
266 | bus_LV_2163-5_1_6_node_256 | 0.4 | n |  | TRUE
267 | bus_LV_2163-5_1_6_node_250 | 0.4 | n |  | TRUE
268 | bus_LV_2163-5_1_6_node_251 | 0.4 | n |  | TRUE
269 | bus_LV_2163-5_1_6_node_252 | 0.4 | n |  | TRUE
270 | bus_LV_2163-5_1_6_node_253 | 0.4 | n |  | TRUE
271 | bus_LV_2163-5_1_6_node_259 | 0.4 | n |  | TRUE
272 | bus_LV_2163-5_1_6_node_299 | 0.4 | n |  | TRUE
273 | bus_LV_2163-5_1_6_node_262 | 0.4 | n |  | TRUE
274 | bus_LV_2163-5_1_6_node_264 | 0.4 | n |  | TRUE
275 | bus_LV_2163-5_1_6_node_265 | 0.4 | n |  | TRUE
276 | bus_LV_2163-5_1_6_node_266 | 0.4 | n |  | TRUE
277 | bus_LV_2163-5_1_6_node_281 | 0.4 | n |  | TRUE
278 | bus_LV_2163-5_1_6_node_279 | 0.4 | n |  | TRUE
279 | bus_LV_2163-5_1_6_node_267 | 0.4 | n |  | TRUE
280 | bus_LV_2163-5_1_6_node_268 | 0.4 | n |  | TRUE
281 | bus_LV_2163-5_1_6_node_269 | 0.4 | n |  | TRUE
282 | bus_LV_2163-5_1_6_node_272 | 0.4 | n |  | TRUE
283 | bus_LV_2163-5_1_6_node_283 | 0.4 | n |  | TRUE
284 | bus_LV_2163-5_1_6_node_287 | 0.4 | n |  | TRUE
285 | bus_LV_2163-5_1_6_node_286 | 0.4 | n |  | TRUE
286 | bus_LV_2163-5_1_6_node_296 | 0.4 | n |  | TRUE
287 | bus_LV_2163-5_1_6_node_295 | 0.4 | n |  | TRUE
288 | bus_LV_2163-5_1_6_node_297 | 0.4 | n |  | TRUE
289 | bus_MV_28_0_node_50 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2163-5_1_6_load_43 | 0 | 0.00050943 | 0.00012767 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2163-5_1_6_load_25 | 3 | 0.00091685 | 0.00022978 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2163-5_1_6_load_13 | 4 | 0.0019324 | 0.0004843 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2163-5_1_6_load_14 | 5 | 0.0010961 | 0.00027472 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2163-5_1_6_load_16 | 7 | 0.00010388 | 2.6035e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2163-5_1_6_load_17 | 8 | 0.00079014 | 0.00019803 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2163-5_1_6_load_18 | 9 | 0.00063442 | 0.000159 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2163-5_1_6_load_19 | 10 | 0.00032818 | 8.225e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2163-5_1_6_load_20 | 12 | 0.0012317 | 0.00030869 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2163-5_1_6_load_22 | 14 | 0.00032216 | 8.0742e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2163-5_1_6_load_24 | 15 | 0.00038491 | 9.6468e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2163-5_1_6_load_40 | 17 | 0.00026586 | 6.6631e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2163-5_1_6_load_53 | 19 | 0.00014929 | 3.7417e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2163-5_1_6_load_51 | 20 | 0.0002502 | 6.2707e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2163-5_1_6_load_71 | 21 | 0.00062146 | 0.00015575 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2163-5_1_6_load_27 | 22 | 0.0025325 | 0.00063471 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2163-5_1_6_load_31 | 26 | 0.0017796 | 0.00044601 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2163-5_1_6_load_32 | 27 | 0.00061586 | 0.00015435 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2163-5_1_6_load_33 | 28 | 0.00079681 | 0.0001997 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2163-5_1_6_load_68 | 29 | 0.00035953 | 9.0106e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2163-5_1_6_load_73 | 30 | 0.00031105 | 7.7957e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2163-5_1_6_load_55 | 31 | 0.0024246 | 0.00060765 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2163-5_1_6_load_54 | 32 | 0.00043126 | 0.00010809 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2163-5_1_6_load_41 | 35 | 0.00065231 | 0.00016348 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2163-5_1_6_load_38 | 36 | 0.0010742 | 0.00026921 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2163-5_1_6_load_34 | 37 | 0.0024133 | 0.00060484 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2163-5_1_6_load_35 | 38 | 0.0011737 | 0.00029416 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2163-5_1_6_load_37 | 39 | 0.0006683 | 0.00016749 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2163-5_1_6_load_45 | 41 | 0.0052587 | 0.001318 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2163-5_1_6_load_62 | 42 | 0.00095687 | 0.00023982 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2163-5_1_6_load_59 | 43 | 0.00065773 | 0.00016484 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2163-5_1_6_load_220 | 44 | 0.00032855 | 8.2342e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2163-5_1_6_load_39 | 46 | 0.00022 | 5.5138e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2163-5_1_6_load_47 | 47 | 0.002661 | 0.0006669 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2163-5_1_6_load_48 | 48 | 0.0004861 | 0.00012183 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2163-5_1_6_load_66 | 49 | 0.0032224 | 0.00080761 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2163-5_1_6_load_72 | 50 | 0.00015687 | 3.9315e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2163-5_1_6_load_64 | 51 | 0.0016988 | 0.00042575 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2163-5_1_6_load_49 | 52 | 0.0016491 | 0.00041331 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2163-5_1_6_load_50 | 53 | 0.0042842 | 0.0010737 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2163-5_1_6_load_193 | 55 | 0.0034979 | 0.00087667 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2163-5_1_6_load_159 | 56 | 0.00044891 | 0.00011251 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2163-5_1_6_load_74 | 57 | 0.00071492 | 0.00017918 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2163-5_1_6_load_180 | 58 | 0.00064713 | 0.00016219 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2163-5_1_6_load_179 | 59 | 0.00276 | 0.00069172 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2163-5_1_6_load_197 | 62 | 0.0091122 | 0.0022837 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2163-5_1_6_load_190 | 63 | 0.0016881 | 0.00042309 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2163-5_1_6_load_61 | 64 | 0.00087222 | 0.0002186 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2163-5_1_6_load_221 | 65 | 0.0010225 | 0.00025627 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2163-5_1_6_load_63 | 66 | 0.00042215 | 0.0001058 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2163-5_1_6_load_67 | 68 | 0.00046589 | 0.00011676 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2163-5_1_6_load_211 | 69 | 0.0044891 | 0.0011251 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2163-5_1_6_load_208 | 70 | 0.0050233 | 0.001259 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2163-5_1_6_load_69 | 71 | 0.0004707 | 0.00011797 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2163-5_1_6_load_75 | 73 | 0.0014657 | 0.00036734 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2163-5_1_6_load_76 | 74 | 0.00044431 | 0.00011135 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2163-5_1_6_load_177 | 75 | 0.0027355 | 0.00068559 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2163-5_1_6_load_175 | 76 | 0.0049524 | 0.0012412 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2163-5_1_6_load_77 | 77 | 0.0019902 | 0.0004988 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2163-5_1_6_load_78 | 78 | 0.00038374 | 9.6173e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2163-5_1_6_load_81 | 81 | 0.00075897 | 0.00019021 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2163-5_1_6_load_82 | 82 | 0.0088918 | 0.0022285 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2163-5_1_6_load_89 | 83 | 0.00066198 | 0.00016591 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2163-5_1_6_load_90 | 84 | 0.00044271 | 0.00011095 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2163-5_1_6_load_87 | 85 | 0.0013079 | 0.0003278 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2163-5_1_6_load_96 | 87 | 0.0015011 | 0.00037622 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2163-5_1_6_load_198 | 88 | 0.0042813 | 0.001073 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2163-5_1_6_load_290 | 90 | 0.0032811 | 0.00082231 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2163-5_1_6_load_289 | 91 | 0.0022743 | 0.00057 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2163-5_1_6_load_86 | 92 | 0.00062691 | 0.00015712 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2163-5_1_6_load_98 | 93 | 0.0010929 | 0.0002739 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2163-5_1_6_load_83 | 94 | 0.00094098 | 0.00023583 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2163-5_1_6_load_84 | 95 | 0.0004373 | 0.0001096 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2163-5_1_6_load_99 | 97 | 0.0017742 | 0.00044466 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2163-5_1_6_load_88 | 98 | 0.00245 | 0.00061403 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2163-5_1_6_load_199 | 99 | 0.0025365 | 0.0006357 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2163-5_1_6_load_254 | 101 | 0.002844 | 0.00071278 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2163-5_1_6_load_92 | 102 | 0.0013824 | 0.00034647 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2163-5_1_6_load_95 | 105 | 0.0016536 | 0.00041443 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2163-5_1_6_load_288 | 106 | 0.0028417 | 0.00071218 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2163-5_1_6_load_200 | 107 | 0.0012386 | 0.00031042 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2163-5_1_6_load_298 | 108 | 0.0056192 | 0.0014083 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2163-5_1_6_load_291 | 109 | 0.0023787 | 0.00059617 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2163-5_1_6_load_138 | 111 | 0.0058496 | 0.0014661 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2163-5_1_6_load_149 | 112 | 0.0017772 | 0.0004454 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2163-5_1_6_load_151 | 113 | 0.002935 | 0.00073559 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2163-5_1_6_load_137 | 114 | 0.0014849 | 0.00037214 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2163-5_1_6_load_102 | 116 | 0.0027912 | 0.00069953 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2163-5_1_6_load_103 | 117 | 0.0029312 | 0.00073464 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2163-5_1_6_load_105 | 119 | 0.0028893 | 0.00072413 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2163-5_1_6_load_106 | 120 | 0.0021759 | 0.00054533 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2163-5_1_6_load_107 | 121 | 0.0042322 | 0.0010607 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2163-5_1_6_load_110 | 122 | 0.0031762 | 0.00079603 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2163-5_1_6_load_146 | 123 | 0.0020922 | 0.00052436 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2163-5_1_6_load_150 | 124 | 0.0015638 | 0.00039193 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2163-5_1_6_load_134 | 125 | 0.0030847 | 0.0007731 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2163-5_1_6_load_108 | 127 | 0.0027797 | 0.00069666 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2163-5_1_6_load_109 | 128 | 0.0029292 | 0.00073412 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2163-5_1_6_load_144 | 129 | 0.0023792 | 0.00059628 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2163-5_1_6_load_145 | 130 | 0.0018724 | 0.00046926 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2163-5_1_6_load_143 | 131 | 0.0026147 | 0.00065529 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2163-5_1_6_load_135 | 132 | 0.0030996 | 0.00077683 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2163-5_1_6_load_111 | 133 | 0.0031711 | 0.00079474 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2163-5_1_6_load_112 | 134 | 0.0028559 | 0.00071576 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2163-5_1_6_load_113 | 135 | 0.0027529 | 0.00068995 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2163-5_1_6_load_114 | 136 | 0.0020728 | 0.0005195 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2163-5_1_6_load_130 | 137 | 0.0034858 | 0.00087362 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2163-5_1_6_load_131 | 138 | 0.0033219 | 0.00083254 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2163-5_1_6_load_129 | 140 | 0.0022186 | 0.00055603 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2163-5_1_6_load_125 | 141 | 0.00062031 | 0.00015546 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2163-5_1_6_load_116 | 142 | 0.002267 | 0.00056817 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2163-5_1_6_load_117 | 143 | 0.0016137 | 0.00040442 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2163-5_1_6_load_118 | 144 | 0.0025114 | 0.00062942 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2163-5_1_6_load_140 | 146 | 0.002074 | 0.0005198 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2163-5_1_6_load_141 | 147 | 0.0013574 | 0.00034019 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2163-5_1_6_load_155 | 148 | 0.00082841 | 0.00020762 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2163-5_1_6_load_156 | 149 | 0.0018249 | 0.00045736 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2163-5_1_6_load_120 | 150 | 0.0010776 | 0.00027007 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2163-5_1_6_load_121 | 151 | 0.0013936 | 0.00034926 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2163-5_1_6_load_122 | 152 | 0.001646 | 0.00041252 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2163-5_1_6_load_123 | 153 | 0.0038568 | 0.00096659 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2163-5_1_6_load_124 | 154 | 0.0029547 | 0.00074052 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2163-5_1_6_load_136 | 155 | 0.0027882 | 0.00069879 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2163-5_1_6_load_152 | 156 | 0.0032011 | 0.00080228 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2163-5_1_6_load_153 | 157 | 0.0016447 | 0.0004122 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2163-5_1_6_load_126 | 158 | 0.0015132 | 0.00037923 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2163-5_1_6_load_132 | 160 | 0.002661 | 0.00066691 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2163-5_1_6_load_133 | 161 | 0.0022688 | 0.00056862 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2163-5_1_6_load_185 | 162 | 0.00061877 | 0.00015508 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2163-5_1_6_load_139 | 165 | 0.0025933 | 0.00064994 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2163-5_1_6_load_154 | 166 | 0.0029585 | 0.00074146 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2163-5_1_6_load_142 | 167 | 0.0037994 | 0.00095222 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2163-5_1_6_load_157 | 168 | 0.0018089 | 0.00045335 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2163-5_1_6_load_308 | 169 | 0.00072372 | 0.00018138 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2163-5_1_6_load_309 | 170 | 0.0042144 | 0.0010562 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2163-5_1_6_load_307 | 171 | 0.0047338 | 0.0011864 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2163-5_1_6_load_158 | 172 | 0.002729 | 0.00068395 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2163-5_1_6_load_160 | 173 | 0.0003679 | 9.2205e-05 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_2163-5_1_6_load_162 | 174 | 0.00072452 | 0.00018158 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_2163-5_1_6_load_163 | 176 | 0.0039002 | 0.00097747 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_2163-5_1_6_load_164 | 177 | 0.0024268 | 0.00060821 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_2163-5_1_6_load_166 | 179 | 0.0022115 | 0.00055426 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_2163-5_1_6_load_168 | 181 | 0.0013854 | 0.00034721 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_2163-5_1_6_load_263 | 182 | 0.0019917 | 0.00049918 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_2163-5_1_6_load_260 | 183 | 0.0025611 | 0.00064187 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_2163-5_1_6_load_219 | 184 | 0.0023736 | 0.00059489 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_2163-5_1_6_load_202 | 186 | 0.0028924 | 0.00072492 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_2163-5_1_6_load_231 | 188 | 0.001961 | 0.00049147 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_2163-5_1_6_load_261 | 189 | 0.0020894 | 0.00052365 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_2163-5_1_6_load_169 | 191 | 0.0042212 | 0.0010579 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_2163-5_1_6_load_170 | 192 | 0.0012796 | 0.00032069 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_2163-5_1_6_load_172 | 194 | 0.0019822 | 0.0004968 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_2163-5_1_6_load_173 | 195 | 0.0051939 | 0.0013017 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_2163-5_1_6_load_174 | 196 | 0.0039275 | 0.00098432 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_2163-5_1_6_load_214 | 197 | 0.0013752 | 0.00034467 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_2163-5_1_6_load_310 | 199 | 0.0039483 | 0.00098953 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_2163-5_1_6_load_223 | 200 | 0.00066188 | 0.00016588 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_2163-5_1_6_load_284 | 201 | 0.0020685 | 0.00051842 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_2163-5_1_6_load_176 | 202 | 0.0027991 | 0.00070153 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_2163-5_1_6_load_178 | 203 | 0.0033472 | 0.0008389 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_2163-5_1_6_load_222 | 204 | 0.0037062 | 0.00092886 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_2163-5_1_6_load_209 | 205 | 0.0028417 | 0.00071221 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_2163-5_1_6_load_181 | 206 | 0.0022575 | 0.00056578 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_2163-5_1_6_load_186 | 209 | 0.0010345 | 0.00025927 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_2163-5_1_6_load_311 | 212 | 0.00057251 | 0.00014349 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_2163-5_1_6_load_240 | 213 | 0.0017543 | 0.00043967 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_2163-5_1_6_load_237 | 214 | 0.0021483 | 0.00053842 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_2163-5_1_6_load_294 | 215 | 0.0031974 | 0.00080134 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_2163-5_1_6_load_292 | 216 | 0.00095144 | 0.00023845 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_2163-5_1_6_load_238 | 218 | 0.0026267 | 0.00065832 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_2163-5_1_6_load_188 | 219 | 0.006905 | 0.0017305 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_2163-5_1_6_load_189 | 220 | 0.0040024 | 0.0010031 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_2163-5_1_6_load_258 | 221 | 0.0018266 | 0.00045778 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_2163-5_1_6_load_195 | 222 | 0.002394 | 0.0006 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_2163-5_1_6_load_196 | 223 | 0.00099236 | 0.00024871 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_2163-5_1_6_load_212 | 224 | 0.0021884 | 0.00054847 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_2163-5_1_6_load_248 | 225 | 0.0037541 | 0.00094086 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_2163-5_1_6_load_213 | 226 | 0.00158 | 0.000396 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_2163-5_1_6_load_249 | 227 | 0.0010761 | 0.00026969 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_2163-5_1_6_load_229 | 228 | 0.0054812 | 0.0013737 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_2163-5_1_6_load_277 | 230 | 0.0046759 | 0.0011719 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_2163-5_1_6_load_285 | 231 | 0.0041484 | 0.0010397 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_2163-5_1_6_load_245 | 232 | 0.0036536 | 0.00091569 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_2163-5_1_6_load_228 | 233 | 0.0021843 | 0.00054743 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_2163-5_1_6_load_205 | 235 | 0.0011255 | 0.00028207 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_2163-5_1_6_load_206 | 236 | 0.0021898 | 0.00054881 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_2163-5_1_6_load_224 | 240 | 0.0020195 | 0.00050615 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_2163-5_1_6_load_312 | 242 | 0.0046247 | 0.001159 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_2163-5_1_6_load_215 | 243 | 0.0017055 | 0.00042743 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_2163-5_1_6_load_216 | 244 | 0.0010708 | 0.00026837 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_2163-5_1_6_load_218 | 245 | 0.0015345 | 0.00038457 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_2163-5_1_6_load_278 | 248 | 0.0011597 | 0.00029064 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_2163-5_1_6_load_276 | 250 | 0.002951 | 0.0007396 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_2163-5_1_6_load_275 | 251 | 0.0044809 | 0.001123 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_2163-5_1_6_load_232 | 253 | 0.00063854 | 0.00016003 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_2163-5_1_6_load_233 | 254 | 0.00079583 | 0.00019945 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_2163-5_1_6_load_234 | 255 | 0.00077543 | 0.00019434 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_2163-5_1_6_load_235 | 256 | 0.0007074 | 0.00017729 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_2163-5_1_6_load_236 | 257 | 0.0024579 | 0.000616 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_2163-5_1_6_load_255 | 258 | 0.00098433 | 0.0002467 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_2163-5_1_6_load_273 | 259 | 0.0015364 | 0.00038507 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_2163-5_1_6_load_241 | 260 | 0.00062387 | 0.00015636 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_2163-5_1_6_load_242 | 261 | 0.00099846 | 0.00025024 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_2163-5_1_6_load_274 | 262 | 0.0028572 | 0.00071609 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_2163-5_1_6_load_239 | 263 | 0.006779 | 0.001699 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_2163-5_1_6_load_247 | 264 | 0.0045297 | 0.0011352 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_2163-5_1_6_load_243 | 265 | 0.00079218 | 0.00019854 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_2163-5_1_6_load_256 | 266 | 0.0068761 | 0.0017233 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_2163-5_1_6_load_250 | 267 | 0.0017428 | 0.00043678 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_2163-5_1_6_load_251 | 268 | 0.0032153 | 0.00080583 | 0 | 0 |  | 1 | TRUE | wye
210 | LV_2163-5_1_6_load_252 | 269 | 0.0032087 | 0.00080417 | 0 | 0 |  | 1 | TRUE | wye
211 | LV_2163-5_1_6_load_253 | 270 | 0.0029128 | 0.00073002 | 0 | 0 |  | 1 | TRUE | wye
212 | LV_2163-5_1_6_load_259 | 271 | 0.011376 | 0.0028512 | 0 | 0 |  | 1 | TRUE | wye
213 | LV_2163-5_1_6_load_299 | 272 | 0.0068892 | 0.0017266 | 0 | 0 |  | 1 | TRUE | wye
214 | LV_2163-5_1_6_load_262 | 273 | 0.0025237 | 0.00063249 | 0 | 0 |  | 1 | TRUE | wye
215 | LV_2163-5_1_6_load_264 | 274 | 0.0010232 | 0.00025644 | 0 | 0 |  | 1 | TRUE | wye
216 | LV_2163-5_1_6_load_265 | 275 | 0.0020225 | 0.00050688 | 0 | 0 |  | 1 | TRUE | wye
217 | LV_2163-5_1_6_load_266 | 276 | 0.0042675 | 0.0010695 | 0 | 0 |  | 1 | TRUE | wye
218 | LV_2163-5_1_6_load_281 | 277 | 0.0016596 | 0.00041593 | 0 | 0 |  | 1 | TRUE | wye
219 | LV_2163-5_1_6_load_279 | 278 | 0.0015693 | 0.0003933 | 0 | 0 |  | 1 | TRUE | wye
220 | LV_2163-5_1_6_load_267 | 279 | 0.0018955 | 0.00047506 | 0 | 0 |  | 1 | TRUE | wye
221 | LV_2163-5_1_6_load_268 | 280 | 0.0034126 | 0.00085527 | 0 | 0 |  | 1 | TRUE | wye
222 | LV_2163-5_1_6_load_272 | 282 | 0.0025805 | 0.00064672 | 0 | 0 |  | 1 | TRUE | wye
223 | LV_2163-5_1_6_load_283 | 283 | 0.0014865 | 0.00037254 | 0 | 0 |  | 1 | TRUE | wye
224 | LV_2163-5_1_6_load_287 | 284 | 0.0012638 | 0.00031674 | 0 | 0 |  | 1 | TRUE | wye
225 | LV_2163-5_1_6_load_286 | 285 | 0.0012041 | 0.00030176 | 0 | 0 |  | 1 | TRUE | wye
226 | LV_2163-5_1_6_load_295 | 287 | 0.0012941 | 0.00032433 | 0 | 0 |  | 1 | TRUE | wye
227 | LV_2163-5_1_6_load_297 | 288 | 0.0016653 | 0.00041737 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 263 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2163-5_1_6_line_0 |  | 0 | 1 | 0.14473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2163-5_1_6_line_1 |  | 0 | 2 | 0.32988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2163-5_1_6_line_2 |  | 1 | 41 | 0.099037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2163-5_1_6_line_3 |  | 2 | 3 | 0.057039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2163-5_1_6_line_4 |  | 4 | 5 | 0.0085856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2163-5_1_6_line_5 |  | 4 | 6 | 0.029887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2163-5_1_6_line_6 |  | 5 | 7 | 0.10134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2163-5_1_6_line_7 |  | 6 | 8 | 0.010672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2163-5_1_6_line_8 |  | 7 | 9 | 0.11345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2163-5_1_6_line_9 |  | 9 | 10 | 0.043678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2163-5_1_6_line_10 |  | 9 | 11 | 0.20076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2163-5_1_6_line_11 |  | 10 | 12 | 0.003353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2163-5_1_6_line_12 |  | 11 | 14 | 0.087133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2163-5_1_6_line_13 |  | 12 | 13 | 0.062836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2163-5_1_6_line_14 |  | 13 | 15 | 0.014239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2163-5_1_6_line_15 |  | 14 | 16 | 0.07046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2163-5_1_6_line_16 |  | 16 | 17 | 0.13297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2163-5_1_6_line_17 |  | 17 | 46 | 0.05785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2163-5_1_6_line_18 |  | 18 | 19 | 0.00030784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2163-5_1_6_line_19 |  | 18 | 20 | 0.080446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2163-5_1_6_line_20 |  | 19 | 21 | 0.012098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2163-5_1_6_line_21 |  | 20 | 46 | 0.185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2163-5_1_6_line_22 |  | 22 | 23 | 0.050267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2163-5_1_6_line_23 |  | 22 | 24 | 0.067276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2163-5_1_6_line_24 |  | 23 | 25 | 0.094905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2163-5_1_6_line_25 |  | 23 | 26 | 0.076503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2163-5_1_6_line_26 |  | 24 | 27 | 0.06725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2163-5_1_6_line_27 |  | 24 | 28 | 0.054109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2163-5_1_6_line_28 |  | 25 | 31 | 0.10384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2163-5_1_6_line_29 |  | 25 | 32 | 0.058242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2163-5_1_6_line_30 |  | 28 | 33 | 0.15421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2163-5_1_6_line_31 |  | 29 | 30 | 0.11208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2163-5_1_6_line_32 |  | 30 | 50 | 0.094479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2163-5_1_6_line_33 |  | 30 | 57 | 0.27665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2163-5_1_6_line_34 |  | 32 | 34 | 0.15839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_2163-5_1_6_line_35 |  | 33 | 35 | 0.01089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2163-5_1_6_line_36 |  | 34 | 58 | 0.014507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_2163-5_1_6_line_37 |  | 34 | 59 | 0.092281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2163-5_1_6_line_38 |  | 35 | 36 | 0.21182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2163-5_1_6_line_39 |  | 36 | 46 | 0.003519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2163-5_1_6_line_40 |  | 37 | 38 | 0.099797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2163-5_1_6_line_41 |  | 37 | 39 | 0.13341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2163-5_1_6_line_42 |  | 38 | 40 | 0.044836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2163-5_1_6_line_43 |  | 39 | 41 | 0.053526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2163-5_1_6_line_44 |  | 40 | 42 | 0.026879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2163-5_1_6_line_45 |  | 40 | 43 | 0.03058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2163-5_1_6_line_46 |  | 42 | 44 | 0.0062736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2163-5_1_6_line_47 |  | 43 | 45 | 0.036358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2163-5_1_6_line_48 |  | 44 | 65 | 0.011014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2163-5_1_6_line_49 |  | 45 | 64 | 0.085825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2163-5_1_6_line_50 |  | 47 | 48 | 0.10212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2163-5_1_6_line_51 |  | 47 | 49 | 0.064646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2163-5_1_6_line_52 |  | 48 | 50 | 0.11141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2163-5_1_6_line_53 |  | 49 | 51 | 0.03526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2163-5_1_6_line_54 |  | 51 | 66 | 0.024813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2163-5_1_6_line_55 |  | 52 | 53 | 0.02423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2163-5_1_6_line_56 |  | 53 | 54 | 0.02813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2163-5_1_6_line_57 |  | 54 | 55 | 0.040874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2163-5_1_6_line_58 |  | 54 | 56 | 0.026966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2163-5_1_6_line_59 |  | 55 | 175 | 0.0097756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_2163-5_1_6_line_60 |  | 56 | 172 | 0.001376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2163-5_1_6_line_61 |  | 58 | 62 | 0.014898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_2163-5_1_6_line_62 |  | 60 | 61 | 0.005165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_2163-5_1_6_line_63 |  | 60 | 62 | 0.025126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_2163-5_1_6_line_64 |  | 61 | 63 | 0.01669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_2163-5_1_6_line_65 |  | 63 | 198 | 0.040539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_2163-5_1_6_line_66 |  | 63 | 219 | 0.058436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_2163-5_1_6_line_67 |  | 65 | 174 | 0.019357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2163-5_1_6_line_68 |  | 66 | 67 | 0.015875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2163-5_1_6_line_69 |  | 67 | 68 | 0.037611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2163-5_1_6_line_70 |  | 68 | 69 | 0.042229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2163-5_1_6_line_71 |  | 69 | 70 | 0.01905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2163-5_1_6_line_72 |  | 70 | 236 | 0.021042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2163-5_1_6_line_73 |  | 71 | 72 | 0.028043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2163-5_1_6_line_74 |  | 72 | 73 | 0.020657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2163-5_1_6_line_75 |  | 72 | 74 | 0.0504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2163-5_1_6_line_76 |  | 74 | 75 | 0.014137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2163-5_1_6_line_77 |  | 75 | 76 | 0.036103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2163-5_1_6_line_78 |  | 76 | 202 | 0.037863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2163-5_1_6_line_79 |  | 77 | 78 | 0.021432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2163-5_1_6_line_80 |  | 77 | 79 | 0.0066258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2163-5_1_6_line_81 |  | 78 | 80 | 0.031174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2163-5_1_6_line_82 |  | 79 | 81 | 0.027349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2163-5_1_6_line_83 |  | 79 | 82 | 0.12498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2163-5_1_6_line_84 |  | 80 | 83 | 0.036578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2163-5_1_6_line_85 |  | 80 | 84 | 0.040939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2163-5_1_6_line_86 |  | 81 | 85 | 0.02241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2163-5_1_6_line_87 |  | 82 | 86 | 0.02486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2163-5_1_6_line_88 |  | 83 | 87 | 0.015503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2163-5_1_6_line_89 |  | 84 | 88 | 0.00068996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2163-5_1_6_line_90 |  | 85 | 92 | 0.02151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2163-5_1_6_line_91 |  | 86 | 93 | 0.066797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2163-5_1_6_line_92 |  | 87 | 96 | 0.019427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2163-5_1_6_line_93 |  | 88 | 99 | 0.037639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_2163-5_1_6_line_94 |  | 89 | 90 | 0.0205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_2163-5_1_6_line_95 |  | 89 | 91 | 0.045056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_2163-5_1_6_line_96 |  | 90 | 100 | 0.042095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_2163-5_1_6_line_97 |  | 91 | 101 | 0.0011376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_2163-5_1_6_line_98 |  | 92 | 98 | 0.026473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2163-5_1_6_line_99 |  | 94 | 95 | 0.03775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2163-5_1_6_line_100 |  | 95 | 96 | 0.017063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2163-5_1_6_line_101 |  | 96 | 97 | 0.03 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2163-5_1_6_line_102 |  | 99 | 107 | 0.015626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_2163-5_1_6_line_103 |  | 100 | 241 | 0.0267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_2163-5_1_6_line_104 |  | 101 | 269 | 0.024931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_2163-5_1_6_line_105 |  | 102 | 103 | 0.14137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2163-5_1_6_line_106 |  | 103 | 104 | 0.01945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2163-5_1_6_line_107 |  | 103 | 105 | 0.074235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2163-5_1_6_line_108 |  | 104 | 106 | 0.0030281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_2163-5_1_6_line_109 |  | 104 | 107 | 0.034727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_2163-5_1_6_line_110 |  | 105 | 108 | 0.029022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2163-5_1_6_line_111 |  | 106 | 109 | 0.019377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_2163-5_1_6_line_112 |  | 109 | 227 | 0.012492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
113 | LV_2163-5_1_6_line_113 |  | 110 | 111 | 0.021653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2163-5_1_6_line_114 |  | 110 | 112 | 0.024581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2163-5_1_6_line_115 |  | 110 | 113 | 0.029339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2163-5_1_6_line_116 |  | 111 | 114 | 0.024002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2163-5_1_6_line_117 |  | 112 | 115 | 0.027855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2163-5_1_6_line_118 |  | 114 | 155 | 0.0098706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2163-5_1_6_line_119 |  | 115 | 123 | 0.016782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2163-5_1_6_line_120 |  | 115 | 163 | 0.012546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_2163-5_1_6_line_121 |  | 116 | 117 | 0.00102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2163-5_1_6_line_122 |  | 116 | 118 | 0.017206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2163-5_1_6_line_123 |  | 117 | 119 | 0.01784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2163-5_1_6_line_124 |  | 118 | 120 | 0.027594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2163-5_1_6_line_125 |  | 118 | 121 | 0.016831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2163-5_1_6_line_126 |  | 119 | 122 | 0.01387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2163-5_1_6_line_127 |  | 120 | 123 | 0.024077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2163-5_1_6_line_128 |  | 121 | 124 | 0.033908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2163-5_1_6_line_129 |  | 122 | 125 | 0.024052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2163-5_1_6_line_130 |  | 124 | 126 | 0.0081263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2163-5_1_6_line_131 |  | 125 | 132 | 0.0033086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2163-5_1_6_line_132 |  | 126 | 135 | 0.0069473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2163-5_1_6_line_133 |  | 127 | 128 | 0.012193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2163-5_1_6_line_134 |  | 128 | 129 | 0.067278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2163-5_1_6_line_135 |  | 129 | 131 | 0.021121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2163-5_1_6_line_136 |  | 129 | 130 | 8.8151e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2163-5_1_6_line_137 |  | 131 | 167 | 0.0047637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2163-5_1_6_line_138 |  | 132 | 167 | 0.019961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2163-5_1_6_line_139 |  | 133 | 134 | 0.015321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2163-5_1_6_line_140 |  | 133 | 135 | 0.020243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2163-5_1_6_line_141 |  | 134 | 136 | 0.014552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2163-5_1_6_line_142 |  | 136 | 137 | 0.024367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2163-5_1_6_line_143 |  | 137 | 138 | 0.0052815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2163-5_1_6_line_144 |  | 138 | 165 | 0.021569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2163-5_1_6_line_145 |  | 139 | 140 | 0.056999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
146 | LV_2163-5_1_6_line_146 |  | 139 | 141 | 0.030875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
147 | LV_2163-5_1_6_line_147 |  | 140 | 162 | 0.025885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
148 | LV_2163-5_1_6_line_148 |  | 141 | 158 | 0.0064152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
149 | LV_2163-5_1_6_line_149 |  | 142 | 143 | 0.0036717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2163-5_1_6_line_150 |  | 142 | 144 | 0.01532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_2163-5_1_6_line_151 |  | 143 | 145 | 0.018957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2163-5_1_6_line_152 |  | 145 | 146 | 0.01995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2163-5_1_6_line_153 |  | 145 | 147 | 0.005998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_2163-5_1_6_line_154 |  | 146 | 148 | 0.020016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_2163-5_1_6_line_155 |  | 147 | 149 | 0.026225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_2163-5_1_6_line_156 |  | 148 | 166 | 0.0056859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_2163-5_1_6_line_157 |  | 149 | 168 | 0.012609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_2163-5_1_6_line_158 |  | 150 | 151 | 0.0092108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_2163-5_1_6_line_159 |  | 150 | 152 | 0.015398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_2163-5_1_6_line_160 |  | 151 | 153 | 0.00442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_2163-5_1_6_line_161 |  | 152 | 154 | 0.0021101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_2163-5_1_6_line_162 |  | 153 | 155 | 0.027035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_2163-5_1_6_line_163 |  | 154 | 156 | 0.027698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_2163-5_1_6_line_164 |  | 156 | 157 | 0.0019058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_2163-5_1_6_line_165 |  | 157 | 169 | 0.017911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_2163-5_1_6_line_166 |  | 158 | 159 | 0.028058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
167 | LV_2163-5_1_6_line_167 |  | 159 | 160 | 0.03514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_2163-5_1_6_line_168 |  | 159 | 161 | 0.0075102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
169 | LV_2163-5_1_6_line_169 |  | 161 | 163 | 0.030403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
170 | LV_2163-5_1_6_line_170 |  | 162 | 164 | 0.010588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
171 | LV_2163-5_1_6_line_171 |  | 163 | 166 | 0.022142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_2163-5_1_6_line_172 |  | 164 | 208 | 0.035234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_2163-5_1_6_line_173 |  | 164 | 206 | 0.0091829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
174 | LV_2163-5_1_6_line_174 |  | 168 | 171 | 0.0026512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_2163-5_1_6_line_175 |  | 169 | 170 | 0.0054763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_2163-5_1_6_line_176 |  | 172 | 173 | 0.0086384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_2163-5_1_6_line_177 |  | 173 | 174 | 0.036011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_2163-5_1_6_line_178 |  | 175 | 222 | 0.034856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
179 | LV_2163-5_1_6_line_179 |  | 175 | 223 | 0.020643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
180 | LV_2163-5_1_6_line_180 |  | 176 | 177 | 0.023113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_2163-5_1_6_line_181 |  | 176 | 178 | 0.032429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_2163-5_1_6_line_182 |  | 177 | 179 | 0.024634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_2163-5_1_6_line_183 |  | 178 | 180 | 0.034949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_2163-5_1_6_line_184 |  | 178 | 181 | 0.0056663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_2163-5_1_6_line_185 |  | 180 | 182 | 0.0033064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_2163-5_1_6_line_186 |  | 180 | 183 | 0.017642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_2163-5_1_6_line_187 |  | 181 | 184 | 0.036946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_2163-5_1_6_line_188 |  | 182 | 188 | 0.023046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
189 | LV_2163-5_1_6_line_189 |  | 183 | 189 | 0.016865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_2163-5_1_6_line_190 |  | 184 | 190 | 0.0022673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_2163-5_1_6_line_191 |  | 185 | 186 | 0.029874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
192 | LV_2163-5_1_6_line_192 |  | 185 | 187 | 0.01103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
193 | LV_2163-5_1_6_line_193 |  | 186 | 228 | 0.020667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
194 | LV_2163-5_1_6_line_194 |  | 187 | 232 | 0.030199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
195 | LV_2163-5_1_6_line_195 |  | 187 | 229 | 0.046558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
196 | LV_2163-5_1_6_line_196 |  | 188 | 252 | 0.014755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
197 | LV_2163-5_1_6_line_197 |  | 189 | 273 | 0.0022045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_2163-5_1_6_line_198 |  | 190 | 245 | 0.013212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_2163-5_1_6_line_199 |  | 190 | 243 | 0.011911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_2163-5_1_6_line_200 |  | 191 | 192 | 0.0025325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_2163-5_1_6_line_201 |  | 191 | 193 | 0.029765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
202 | LV_2163-5_1_6_line_202 |  | 192 | 194 | 0.032044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_2163-5_1_6_line_203 |  | 193 | 195 | 0.0062104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
204 | LV_2163-5_1_6_line_204 |  | 193 | 196 | 0.029647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
205 | LV_2163-5_1_6_line_205 |  | 194 | 197 | 0.018435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_2163-5_1_6_line_206 |  | 195 | 198 | 0.036799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
207 | LV_2163-5_1_6_line_207 |  | 196 | 199 | 0.029963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
208 | LV_2163-5_1_6_line_208 |  | 198 | 200 | 0.027902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
209 | LV_2163-5_1_6_line_209 |  | 199 | 201 | 0.029264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
210 | LV_2163-5_1_6_line_210 |  | 200 | 221 | 0.016114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
211 | LV_2163-5_1_6_line_211 |  | 201 | 239 | 0.043676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
212 | LV_2163-5_1_6_line_212 |  | 202 | 203 | 0.027626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_2163-5_1_6_line_213 |  | 203 | 204 | 0.0051484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_2163-5_1_6_line_214 |  | 204 | 205 | 0.024729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_2163-5_1_6_line_215 |  | 205 | 237 | 0.014612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_2163-5_1_6_line_216 |  | 206 | 207 | 0.0087958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
217 | LV_2163-5_1_6_line_217 |  | 207 | 209 | 0.03575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_2163-5_1_6_line_218 |  | 207 | 210 | 0.028488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
219 | LV_2163-5_1_6_line_219 |  | 208 | 211 | 0.018176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_2163-5_1_6_line_220 |  | 208 | 212 | 0.011371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_2163-5_1_6_line_221 |  | 210 | 213 | 0.0092547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
222 | LV_2163-5_1_6_line_222 |  | 210 | 214 | 0.021087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
223 | LV_2163-5_1_6_line_223 |  | 211 | 215 | 0.0067907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_2163-5_1_6_line_224 |  | 211 | 216 | 0.029702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_2163-5_1_6_line_225 |  | 213 | 217 | 0.044332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
226 | LV_2163-5_1_6_line_226 |  | 214 | 218 | 0.018751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
227 | LV_2163-5_1_6_line_227 |  | 215 | 286 | 0.073718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_2163-5_1_6_line_228 |  | 217 | 264 | 0.0028575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
229 | LV_2163-5_1_6_line_229 |  | 217 | 232 | 0.012792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
230 | LV_2163-5_1_6_line_230 |  | 218 | 263 | 0.030491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
231 | LV_2163-5_1_6_line_231 |  | 219 | 220 | 0.054224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_2163-5_1_6_line_232 |  | 221 | 249 | 0.0075631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
233 | LV_2163-5_1_6_line_233 |  | 222 | 224 | 0.00072365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
234 | LV_2163-5_1_6_line_234 |  | 223 | 225 | 0.015191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
235 | LV_2163-5_1_6_line_235 |  | 224 | 226 | 0.036693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
236 | LV_2163-5_1_6_line_236 |  | 225 | 227 | 0.031195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
237 | LV_2163-5_1_6_line_237 |  | 226 | 240 | 0.077816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
238 | LV_2163-5_1_6_line_238 |  | 228 | 233 | 0.019891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
239 | LV_2163-5_1_6_line_239 |  | 229 | 230 | 0.045135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
240 | LV_2163-5_1_6_line_240 |  | 229 | 231 | 0.017878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_2163-5_1_6_line_241 |  | 230 | 234 | 0.028971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
242 | LV_2163-5_1_6_line_242 |  | 233 | 252 | 0.01307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
243 | LV_2163-5_1_6_line_243 |  | 234 | 280 | 0.006005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
244 | LV_2163-5_1_6_line_244 |  | 235 | 236 | 0.024609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_2163-5_1_6_line_245 |  | 235 | 237 | 0.02969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
246 | LV_2163-5_1_6_line_246 |  | 237 | 238 | 0.023253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
247 | LV_2163-5_1_6_line_247 |  | 238 | 239 | 0.014723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
248 | LV_2163-5_1_6_line_248 |  | 238 | 240 | 0.061183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
249 | LV_2163-5_1_6_line_249 |  | 239 | 241 | 0.076326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
250 | LV_2163-5_1_6_line_250 |  | 241 | 242 | 0.021024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_2163-5_1_6_line_251 |  | 243 | 244 | 0.019099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
252 | LV_2163-5_1_6_line_252 |  | 245 | 246 | 0.011074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_2163-5_1_6_line_253 |  | 246 | 247 | 0.025628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_2163-5_1_6_line_254 |  | 246 | 248 | 0.0061094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
255 | LV_2163-5_1_6_line_255 |  | 247 | 284 | 0.008766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_2163-5_1_6_line_256 |  | 247 | 285 | 0.0092166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_2163-5_1_6_line_257 |  | 248 | 278 | 0.0057796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_2163-5_1_6_line_258 |  | 249 | 271 | 0.049909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
259 | LV_2163-5_1_6_line_259 |  | 249 | 266 | 0.035775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
260 | LV_2163-5_1_6_line_260 |  | 250 | 251 | 0.012757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
261 | LV_2163-5_1_6_line_261 |  | 251 | 263 | 0.010778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_2163-5_1_6_line_262 |  | 253 | 254 | 0.014924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
263 | LV_2163-5_1_6_line_263 |  | 253 | 255 | 0.0084608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
264 | LV_2163-5_1_6_line_264 |  | 254 | 256 | 0.020777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
265 | LV_2163-5_1_6_line_265 |  | 255 | 257 | 0.022227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
266 | LV_2163-5_1_6_line_266 |  | 256 | 258 | 0.013357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
267 | LV_2163-5_1_6_line_267 |  | 257 | 259 | 0.021065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
268 | LV_2163-5_1_6_line_268 |  | 258 | 260 | 0.04318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
269 | LV_2163-5_1_6_line_269 |  | 259 | 262 | 0.0079699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
270 | LV_2163-5_1_6_line_270 |  | 260 | 265 | 0.016686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
271 | LV_2163-5_1_6_line_271 |  | 260 | 261 | 0.015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
272 | LV_2163-5_1_6_line_272 |  | 262 | 283 | 0.014313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
273 | LV_2163-5_1_6_line_273 |  | 264 | 266 | 0.033073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
274 | LV_2163-5_1_6_line_274 |  | 267 | 268 | 0.030413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
275 | LV_2163-5_1_6_line_275 |  | 267 | 269 | 4.4223e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
276 | LV_2163-5_1_6_line_276 |  | 268 | 270 | 0.00211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
277 | LV_2163-5_1_6_line_277 |  | 271 | 272 | 0.013404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
278 | LV_2163-5_1_6_line_278 |  | 274 | 275 | 0.023011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
279 | LV_2163-5_1_6_line_279 |  | 275 | 276 | 0.031394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
280 | LV_2163-5_1_6_line_280 |  | 276 | 277 | 0.019105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
281 | LV_2163-5_1_6_line_281 |  | 277 | 278 | 0.0098445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
282 | LV_2163-5_1_6_line_282 |  | 279 | 280 | 0.023816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
283 | LV_2163-5_1_6_line_283 |  | 279 | 281 | 0.0026154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
284 | LV_2163-5_1_6_line_284 |  | 281 | 282 | 0.029989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
285 | LV_2163-5_1_6_line_285 |  | 282 | 283 | 0.023143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
286 | LV_2163-5_1_6_line_286 |  | 286 | 287 | 0.038868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
287 | LV_2163-5_1_6_line_287 |  | 287 | 288 | 0.01563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2163-5_1_6_trafo_239 | 0.63 MVA 20/0.4 kV | 289 | 263 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2579934.6187 | 1164051.0851 | 2580067.9245 | 1164107.4514
1 | 2580292.931 | 1164348.6883 | 2580067.9245 | 1164107.4514
2 | 2579934.6187 | 1164051.0851 | 2579877.1377 | 1164029.4895 | 2579857.8001 | 1164022.74 | 2579843.828 | 1164012.7931
3 | 2580292.931 | 1164348.6883 | 2580327.4078 | 1164388.2169 | 2580330.4764 | 1164391.6269
4 | 2580234.5711 | 1165342.9282 | 2580227.4888 | 1165338.075
5 | 2580261.0594 | 1165356.2989 | 2580255.7639 | 1165354.9046 | 2580243.1866 | 1165348.8319 | 2580234.5711 | 1165342.9282
6 | 2580150.7174 | 1165271.9644 | 2580155.5784 | 1165275.5294 | 2580226.073 | 1165337.1048 | 2580227.4888 | 1165338.075
7 | 2580261.0594 | 1165356.2989 | 2580271.4079 | 1165358.9075
8 | 2580150.7174 | 1165271.9644 | 2580186.4515 | 1165164.2939
9 | 2580186.4515 | 1165164.2939 | 2580190.4682 | 1165154.3863 | 2580200.4173 | 1165143.5924 | 2580203.3969 | 1165139.2359 | 2580203.785 | 1165133.8987 | 2580201.3945 | 1165126.6022
10 | 2580186.4515 | 1165164.2939 | 2579995.6711 | 1165101.7968
11 | 2580201.3945 | 1165126.6022 | 2580200.3506 | 1165123.4159
12 | 2579995.6711 | 1165101.7968 | 2579945.6954 | 1165054.6737 | 2579935.2238 | 1165039.4906
13 | 2580247.0643 | 1165092.4682 | 2580219.9623 | 1165098.4829 | 2580213.0251 | 1165100.8515 | 2580205.8691 | 1165106.5225 | 2580201.8797 | 1165111.1491 | 2580200.3638 | 1165115.8565 | 2580200.3506 | 1165123.4159 | 2580200.3506 | 1165123.4159
14 | 2580247.0643 | 1165092.4682 | 2580258.2026 | 1165101.338
15 | 2579905.7584 | 1164975.857 | 2579914.5735 | 1164989.9678 | 2579921.7392 | 1165005.4849 | 2579927.1357 | 1165023.1757 | 2579933.9995 | 1165037.7155 | 2579935.2238 | 1165039.4906
16 | 2579905.7584 | 1164975.857 | 2579818.5517 | 1164875.4819
17 | 2579818.5517 | 1164875.4819 | 2579773.7146 | 1164838.9277
18 | 2580015.1386 | 1164885.8469 | 2580014.896 | 1164885.6574
19 | 2580014.896 | 1164885.6574 | 2580010.1283 | 1164881.927 | 2579974.6731 | 1164842.737 | 2579958.4258 | 1164828.5892
20 | 2580015.1386 | 1164885.8469 | 2580024.671 | 1164893.2968
21 | 2579958.4258 | 1164828.5892 | 2579773.7146 | 1164838.9277
22 | 2579340.1732 | 1164502.0668 | 2579371.1175 | 1164541.6806
23 | 2579421.9708 | 1164585.2713 | 2579409.0589 | 1164573.9211 | 2579392.7087 | 1164562.6384 | 2579382.4882 | 1164554.5362 | 2579374.4253 | 1164545.9152 | 2579371.1175 | 1164541.6806
24 | 2579288.1858 | 1164423.1513 | 2579298.8024 | 1164446.0149 | 2579306.4284 | 1164458.8839 | 2579340.1732 | 1164502.0668
25 | 2579282.1536 | 1164552.1147 | 2579340.1732 | 1164502.0668
26 | 2579421.9708 | 1164585.2713 | 2579384.7477 | 1164641.3386
27 | 2579421.9708 | 1164585.2713 | 2579426.1877 | 1164588.9809 | 2579460.5844 | 1164623.1632
28 | 2579288.1858 | 1164423.1513 | 2579236.5436 | 1164468.3862 | 2579211.2663 | 1164492.8645
29 | 2579288.1858 | 1164423.1513 | 2579268.2843 | 1164368.4149
30 | 2579460.5844 | 1164623.1632 | 2579587.7081 | 1164710.4555
31 | 2579482.1944 | 1164313.1136 | 2579496.3821 | 1164424.2915
32 | 2579420.3747 | 1164241.8171 | 2579425.3246 | 1164246.6898 | 2579465.6365 | 1164290.9292 | 2579482.1944 | 1164313.1136
33 | 2579482.1944 | 1164313.1136 | 2579758.1112 | 1164292.9229
34 | 2579191.2905 | 1164230.0015 | 2579268.2843 | 1164368.4149
35 | 2579587.7081 | 1164710.4555 | 2579595.5248 | 1164718.0377
36 | 2579191.2905 | 1164230.0015 | 2579184.298 | 1164217.2909
37 | 2579191.2905 | 1164230.0015 | 2579179.13 | 1164236.8806 | 2579173.8979 | 1164238.6441 | 2579170.8116 | 1164238.6548 | 2579168.1427 | 1164237.5413 | 2579148.155 | 1164220.1022 | 2579139.8092 | 1164211.8382 | 2579128.1565 | 1164199.5949 | 2579128.2519 | 1164196.2151 | 2579131.6219 | 1164191.9012 | 2579133.5962 | 1164189.9422
38 | 2579595.5248 | 1164718.0377 | 2579770.9872 | 1164836.7041
39 | 2579770.9872 | 1164836.7041 | 2579773.7146 | 1164838.9277
40 | 2579667.1294 | 1163959.7775 | 2579647.2629 | 1163945.3133 | 2579635.9382 | 1163939.271 | 2579624.8209 | 1163937.9415 | 2579586.7315 | 1163934.8919 | 2579580.0641 | 1163931.3796 | 2579577.6809 | 1163926.4853
41 | 2579667.1294 | 1163959.7775 | 2579790.3342 | 1164010.9504
42 | 2579612.3089 | 1163902.6553 | 2579609.4977 | 1163907.0226 | 2579600.7646 | 1163910.8765 | 2579582.6583 | 1163917.2859 | 2579579.1162 | 1163920.6663 | 2579577.6809 | 1163926.4853 | 2579577.6809 | 1163926.4853
43 | 2579843.828 | 1164012.7931 | 2579790.3342 | 1164010.9504
44 | 2579612.3089 | 1163902.6553 | 2579610.929 | 1163897.7575 | 2579605.4492 | 1163894.419 | 2579598.6794 | 1163892.3076 | 2579590.4024 | 1163892.0112
45 | 2579612.3089 | 1163902.6553 | 2579634.5223 | 1163905.8146 | 2579642.6334 | 1163905.0928
46 | 2579590.4024 | 1163892.0112 | 2579584.1329 | 1163891.7867
47 | 2579678.2277 | 1163898.1956 | 2579663.6225 | 1163900.4463 | 2579658.7027 | 1163901.8526 | 2579649.46 | 1163904.4853 | 2579642.6334 | 1163905.0928
48 | 2579584.1329 | 1163891.7867 | 2579577.7072 | 1163891.5566 | 2579573.1462 | 1163892.0145
49 | 2579643.3823 | 1163822.1759 | 2579647.6975 | 1163841.1707 | 2579654.9518 | 1163852.8297 | 2579678.0047 | 1163886.6572 | 2579679.1198 | 1163892.5008 | 2579678.2277 | 1163898.1956
50 | 2579422.1443 | 1164063.4755 | 2579422.1443 | 1164063.4755 | 2579420.3045 | 1164074.0871 | 2579422.7675 | 1164088.786 | 2579426.3627 | 1164096.4664 | 2579474.5056 | 1164144.4392
51 | 2579358.8096 | 1164050.5204 | 2579422.1443 | 1164063.4755
52 | 2579420.3747 | 1164241.8171 | 2579474.5056 | 1164144.4392
53 | 2579358.8096 | 1164050.5204 | 2579356.8117 | 1164061.8996 | 2579356.1094 | 1164069.2168 | 2579356.7746 | 1164082.2211 | 2579356.562 | 1164085.5489
54 | 2579356.562 | 1164085.5489 | 2579356.3313 | 1164089.1594 | 2579353.1372 | 1164104.5448 | 2579352.3669 | 1164109.9724
55 | 2579477.3947 | 1163897.3481 | 2579475.1464 | 1163901.9681 | 2579473.7598 | 1163906.3195 | 2579473.6806 | 1163912.256 | 2579475.578 | 1163920.6315 | 2579475.578 | 1163920.6315
56 | 2579484.987 | 1163870.4519 | 2579481.1445 | 1163882.2599 | 2579479.6334 | 1163892.7481 | 2579477.3947 | 1163897.3481
57 | 2579484.987 | 1163870.4519 | 2579467.2102 | 1163867.9894 | 2579457.9092 | 1163864.8197 | 2579451.0581 | 1163861.3748 | 2579446.6039 | 1163858.2651
58 | 2579484.987 | 1163870.4519 | 2579498.9715 | 1163872.5606 | 2579511.4544 | 1163875.4949
59 | 2579439.1928 | 1163851.9108 | 2579444.8626 | 1163857.0495 | 2579446.6039 | 1163858.2651
60 | 2579512.7939 | 1163875.8098 | 2579511.4544 | 1163875.4949
61 | 2579177.1172 | 1164204.2378 | 2579184.298 | 1164217.2909
62 | 2579194.0403 | 1164183.891 | 2579194.5942 | 1164189.025
63 | 2579194.5942 | 1164189.025 | 2579179.8628 | 1164196.5578 | 2579177.7113 | 1164198.9109 | 2579177.1083 | 1164201.681 | 2579177.1172 | 1164204.2378
64 | 2579194.0403 | 1164183.891 | 2579192.7724 | 1164167.2537
65 | 2579192.7724 | 1164167.2537 | 2579192.6999 | 1164164.0301 | 2579193.5635 | 1164145.8736 | 2579196.6608 | 1164126.9978
66 | 2579192.7724 | 1164167.2537 | 2579180.7012 | 1164168.9966 | 2579173.2579 | 1164169.1892 | 2579169.618 | 1164168.5571 | 2579166.3274 | 1164167.0789 | 2579162.6583 | 1164164.6905 | 2579150.9263 | 1164151.6693 | 2579144.5054 | 1164144.5494
67 | 2579553.8789 | 1163892.4422 | 2579561.7748 | 1163893.1562 | 2579573.1462 | 1163892.0145
68 | 2579350.192 | 1164125.4766 | 2579351.2128 | 1164123.9056 | 2579351.4624 | 1164116.3454 | 2579352.3669 | 1164109.9724
69 | 2579350.192 | 1164125.4766 | 2579349.3283 | 1164125.9576 | 2579347.4292 | 1164126.0197 | 2579345.4579 | 1164125.115 | 2579344.2866 | 1164123.0291 | 2579333.0327 | 1164095.0462
70 | 2579333.0327 | 1164095.0462 | 2579328.8524 | 1164084.652 | 2579321.7366 | 1164059.953 | 2579320.5856 | 1164054.7565
71 | 2579316.3938 | 1164036.1742 | 2579317.901 | 1164042.6354 | 2579320.5856 | 1164054.7565
72 | 2579306.0447 | 1164018.2632 | 2579313.1447 | 1164027.0329 | 2579315.3279 | 1164031.6054 | 2579316.3938 | 1164036.1742
73 | 2579285.8657 | 1164177.6806 | 2579302.5335 | 1164183.0256 | 2579312.0678 | 1164187.5163
74 | 2579285.8657 | 1164177.6806 | 2579265.2088 | 1164177.5509
75 | 2579285.8657 | 1164177.6806 | 2579302.4939 | 1164156.1011 | 2579304.5296 | 1164149.0239 | 2579301.0663 | 1164133.6155
76 | 2579301.0663 | 1164133.6155 | 2579297.9661 | 1164119.8224
77 | 2579290.0489 | 1164084.5983 | 2579297.9661 | 1164119.8224
78 | 2579290.0489 | 1164084.5983 | 2579286.733 | 1164069.8457 | 2579281.0111 | 1164054.0687 | 2579279.4731 | 1164048.3105
79 | 2579260.7916 | 1163674.4961 | 2579261.1628 | 1163679.1605 | 2579260.8192 | 1163695.9098
80 | 2579260.2659 | 1163667.8912 | 2579260.7916 | 1163674.4961
81 | 2579260.18 | 1163727.0768 | 2579260.8192 | 1163695.9098
82 | 2579260.2659 | 1163667.8912 | 2579277.6254 | 1163666.864 | 2579282.3322 | 1163663.6572 | 2579284.4524 | 1163659.9578
83 | 2579260.2659 | 1163667.8912 | 2579259.7534 | 1163661.4565 | 2579255.5038 | 1163648.5425 | 2579227.4836 | 1163599.0148 | 2579209.4499 | 1163560.358 | 2579207.589 | 1163555.3214
84 | 2579260.18 | 1163727.0768 | 2579225.96 | 1163714.1557
85 | 2579260.18 | 1163727.0768 | 2579263.3425 | 1163729.1113 | 2579288.228 | 1163745.0554 | 2579294.9584 | 1163748.6352
86 | 2579284.4524 | 1163659.9578 | 2579285.8114 | 1163657.5865 | 2579286.3844 | 1163648.3355 | 2579283.2237 | 1163638.4187
87 | 2579198.9732 | 1163532.0024 | 2579207.589 | 1163555.3214
88 | 2579225.96 | 1163714.1557 | 2579222.6632 | 1163712.9109 | 2579211.3581 | 1163708.9506
89 | 2579294.9584 | 1163748.6352 | 2579295.5676 | 1163748.9592
90 | 2579276.6916 | 1163617.9247 | 2579283.2237 | 1163638.4187
91 | 2579198.9732 | 1163532.0024 | 2579211.5711 | 1163542.5973 | 2579221.7818 | 1163547.3087 | 2579233.451 | 1163548.5132 | 2579260.8542 | 1163545.928
92 | 2579192.46 | 1163705.1897 | 2579203.0553 | 1163706.0422 | 2579211.3581 | 1163708.9506
93 | 2579295.5676 | 1163748.9592 | 2579305.1932 | 1163754.079 | 2579311.3647 | 1163755.8474 | 2579318.343 | 1163756.1457 | 2579331.6661 | 1163756.6217
94 | 2579258.5586 | 1163807.2893 | 2579258.3086 | 1163827.7873
95 | 2579258.5586 | 1163807.2893 | 2579262.3069 | 1163808.1768 | 2579302.3956 | 1163817.6984
96 | 2579257.7952 | 1163869.8789 | 2579258.3086 | 1163827.7873
97 | 2579302.3956 | 1163817.6984 | 2579303.4732 | 1163818.0629
98 | 2579268.6525 | 1163592.7023 | 2579276.6916 | 1163617.9247
99 | 2579185.2722 | 1163720.6651 | 2579178.419 | 1163735.4203 | 2579174.8366 | 1163749.1841 | 2579176.3167 | 1163754.137 | 2579177.5802 | 1163755.801
100 | 2579192.46 | 1163705.1897 | 2579185.2722 | 1163720.6651
101 | 2579192.46 | 1163705.1897 | 2579188.4518 | 1163700.0566 | 2579185.3877 | 1163695.5094 | 2579172.0528 | 1163683.4128
102 | 2579347.282 | 1163757.1797 | 2579347.282 | 1163757.1797 | 2579331.6661 | 1163756.6217
103 | 2579257.7952 | 1163869.8789 | 2579249.2839 | 1163875.8114 | 2579239.0348 | 1163888.5644
104 | 2579303.4732 | 1163818.0629 | 2579327.0896 | 1163826.0514
105 | 2579386.4014 | 1163760.9578 | 2579474.1215 | 1163650.0897
106 | 2579386.4014 | 1163760.9578 | 2579384.6666 | 1163762.0421 | 2579383.1417 | 1163764.0595 | 2579378.9622 | 1163771.3776 | 2579374.713 | 1163776.2502
107 | 2579386.4014 | 1163760.9578 | 2579389.0219 | 1163761.2934 | 2579392.5499 | 1163762.7042 | 2579438.8884 | 1163792.3042 | 2579447.9846 | 1163801.3211
108 | 2579374.713 | 1163776.2502 | 2579376.338 | 1163778.8053
109 | 2579374.713 | 1163776.2502 | 2579364.3614 | 1163763.8574 | 2579360.3924 | 1163761.1364 | 2579355.437 | 1163758.9191 | 2579347.282 | 1163757.1797
110 | 2579458.2286 | 1163828.467 | 2579448.0413 | 1163801.3773 | 2579447.9846 | 1163801.3211
111 | 2579376.338 | 1163778.8053 | 2579386.737 | 1163795.156
112 | 2579395.4581 | 1163803.9995 | 2579391.9624 | 1163801.17 | 2579387.7501 | 1163796.7489 | 2579386.737 | 1163795.156
113 | 2578972.251 | 1163701.446 | 2578975.2865 | 1163699.9902 | 2578991.809 | 1163692.1533
114 | 2578972.251 | 1163701.446 | 2578981.0527 | 1163724.3969
115 | 2578972.251 | 1163701.446 | 2578968.2481 | 1163702.216 | 2578953.5068 | 1163705.047 | 2578943.2581 | 1163705.2953
116 | 2578991.809 | 1163692.1533 | 2579013.4949 | 1163681.8672
117 | 2578991.0266 | 1163750.4047 | 2578981.0527 | 1163724.3969
118 | 2579022.4131 | 1163677.6371 | 2579013.4949 | 1163681.8672
119 | 2578991.0266 | 1163750.4047 | 2578987.6386 | 1163751.7839 | 2578975.7639 | 1163757.3729 | 2578975.7639 | 1163757.3729
120 | 2578995.9994 | 1163761.9264 | 2578991.0266 | 1163750.4047
121 | 2578918.9818 | 1163792.6521 | 2578917.9865 | 1163792.8748
122 | 2578935.7727 | 1163788.8959 | 2578918.9818 | 1163792.6521
123 | 2578917.9865 | 1163792.8748 | 2578912.4469 | 1163794.114 | 2578901.0888 | 1163798.4673 | 2578901.0888 | 1163798.4673
124 | 2578935.7727 | 1163788.8959 | 2578938.1535 | 1163784.2185 | 2578941.7548 | 1163780.3261 | 2578953.4473 | 1163770.858 | 2578955.1569 | 1163769.825
125 | 2578935.7727 | 1163788.8959 | 2578935.6793 | 1163794.9993 | 2578937.4809 | 1163802.0187 | 2578938.5028 | 1163805.3455
126 | 2578891.5108 | 1163808.0837 | 2578891.5108 | 1163808.0837 | 2578895.0678 | 1163802.4905 | 2578901.0888 | 1163798.4673
127 | 2578975.7639 | 1163757.3729 | 2578955.1569 | 1163769.825
128 | 2578938.5028 | 1163805.3455 | 2578948.4593 | 1163837.7588
129 | 2578891.5108 | 1163808.0837 | 2578887.4733 | 1163818.5587 | 2578884.5425 | 1163831.0448
130 | 2578950.8455 | 1163845.5269 | 2578948.4593 | 1163837.7588
131 | 2578884.5425 | 1163831.0448 | 2578883.7864 | 1163834.2659
132 | 2578950.8455 | 1163845.5269 | 2578947.3128 | 1163851.509
133 | 2578802.3531 | 1163860.516 | 2578809.9947 | 1163851.0151
134 | 2578871.4579 | 1163878.375 | 2578809.9947 | 1163851.0151
135 | 2578877.9219 | 1163858.2794 | 2578874.4592 | 1163870.1527 | 2578871.4579 | 1163878.375
136 | 2578871.4579 | 1163878.375 | 2578871.4277 | 1163878.4578
137 | 2578879.2252 | 1163853.6983 | 2578879.0904 | 1163854.2729 | 2578877.9219 | 1163858.2794
138 | 2578879.2252 | 1163853.6983 | 2578883.7864 | 1163834.2659
139 | 2578940.6154 | 1163870.6122 | 2578935.5464 | 1163885.0703
140 | 2578940.6154 | 1163870.6122 | 2578947.3128 | 1163851.509
141 | 2578930.732 | 1163898.8026 | 2578935.5464 | 1163885.0703
142 | 2578930.732 | 1163898.8026 | 2578922.6701 | 1163921.7976
143 | 2578920.9227 | 1163926.7817 | 2578922.6701 | 1163921.7976
144 | 2578920.9227 | 1163926.7817 | 2578918.1122 | 1163934.798 | 2578910.8058 | 1163945.6402
145 | 2579046.1892 | 1163851.8734 | 2579058.9773 | 1163870.9827 | 2579065.2825 | 1163882.4886 | 2579071.8466 | 1163895.8057 | 2579074.0062 | 1163901.4448
146 | 2579046.1892 | 1163851.8734 | 2579029.398 | 1163826.9308 | 2579028.9887 | 1163826.2352
147 | 2579083.2634 | 1163925.6178 | 2579074.0062 | 1163901.4448
148 | 2579028.9887 | 1163826.2352 | 2579025.7356 | 1163820.706
149 | 2579054.6652 | 1163767.242 | 2579055.4115 | 1163763.6469
150 | 2579051.5517 | 1163782.2419 | 2579054.6652 | 1163767.242
151 | 2579059.2644 | 1163745.0852 | 2579055.4115 | 1163763.6469
152 | 2579059.2644 | 1163745.0852 | 2579043.2629 | 1163742.3398 | 2579039.5618 | 1163742.6579
153 | 2579059.2644 | 1163745.0852 | 2579065.1819 | 1163746.0643
154 | 2579020.9853 | 1163749.6745 | 2579031.8963 | 1163744.325 | 2579037.7348 | 1163742.8149 | 2579039.5618 | 1163742.6579
155 | 2579091.0554 | 1163750.3454 | 2579065.1819 | 1163746.0643
156 | 2579015.8801 | 1163752.1776 | 2579020.9853 | 1163749.6745
157 | 2579091.0554 | 1163750.3454 | 2579103.4948 | 1163752.4037
158 | 2579061.8552 | 1163674.8734 | 2579052.8095 | 1163673.1373
159 | 2579061.8552 | 1163674.8734 | 2579076.9769 | 1163677.7756
160 | 2579048.4283 | 1163672.5979 | 2579051.2223 | 1163672.8326 | 2579052.8095 | 1163673.1373
161 | 2579079.0492 | 1163678.1733 | 2579076.9769 | 1163677.7756
162 | 2579048.4283 | 1163672.5979 | 2579043.0937 | 1163672.1496 | 2579037.8249 | 1163672.3459 | 2579032.7728 | 1163673.1529 | 2579026.2643 | 1163675.8104 | 2579022.4131 | 1163677.6371
163 | 2579106.2509 | 1163683.394 | 2579079.0492 | 1163678.1733
164 | 2579108.1226 | 1163683.7533 | 2579106.2509 | 1163683.394
165 | 2579108.1226 | 1163683.7533 | 2579125.7124 | 1163687.1292
166 | 2579011.5075 | 1163796.5227 | 2579025.7356 | 1163820.706
167 | 2579011.5075 | 1163796.5227 | 2579006.2607 | 1163800.7432 | 2578992.5852 | 1163825.6703
168 | 2579011.5075 | 1163796.5227 | 2579008.4355 | 1163789.6695
169 | 2578995.9994 | 1163761.9264 | 2579008.4355 | 1163789.6695
170 | 2579087.0501 | 1163935.5058 | 2579083.2634 | 1163925.6178
171 | 2578995.9994 | 1163761.9264 | 2578998.7366 | 1163760.5827 | 2579015.8801 | 1163752.1776
172 | 2579087.0501 | 1163935.5058 | 2579083.8369 | 1163936.4731 | 2579075.9631 | 1163938.4905 | 2579052.2294 | 1163940.8413
173 | 2579087.0501 | 1163935.5058 | 2579089.5237 | 1163942.0338 | 2579090.3401 | 1163944.0788
174 | 2579106.1105 | 1163752.8365 | 2579103.4948 | 1163752.4037
175 | 2579131.0905 | 1163688.1614 | 2579125.7124 | 1163687.1292
176 | 2579512.7939 | 1163875.8098 | 2579515.6121 | 1163876.4723 | 2579520.9914 | 1163878.4848
177 | 2579553.8789 | 1163892.4422 | 2579550.2831 | 1163892.1171 | 2579542.3921 | 1163889.1426 | 2579528.0965 | 1163881.143 | 2579520.9914 | 1163878.4848
178 | 2579439.1928 | 1163851.9108 | 2579406.1228 | 1163862.9243
179 | 2579439.1928 | 1163851.9108 | 2579436.6902 | 1163847.9841 | 2579433.9452 | 1163842.613 | 2579431.3809 | 1163836.3409 | 2579429.8864 | 1163833.535
180 | 2579031.7416 | 1164102.1437 | 2579045.7758 | 1164085.9367 | 2579046.9396 | 1164084.7339
181 | 2579010.5134 | 1164126.6585 | 2579031.7416 | 1164102.1437
182 | 2579065.2549 | 1164068.3663 | 2579055.8562 | 1164075.5185 | 2579046.9396 | 1164084.7339
183 | 2579010.5134 | 1164126.6585 | 2579036.0386 | 1164150.6033
184 | 2579010.5134 | 1164126.6585 | 2579006.5683 | 1164130.7257
185 | 2579036.0386 | 1164150.6033 | 2579038.6853 | 1164148.6216
186 | 2579036.0386 | 1164150.6033 | 2579022.7153 | 1164162.1672
187 | 2579006.5683 | 1164130.7257 | 2578986.9265 | 1164150.9757 | 2578984.3619 | 1164153.4303 | 2578980.3504 | 1164156.7162
188 | 2579057.1335 | 1164134.8085 | 2579038.6853 | 1164148.6216
189 | 2579022.7153 | 1164162.1672 | 2579021.9441 | 1164162.8366 | 2579019.848 | 1164165.6676 | 2579018.9603 | 1164168.0608 | 2579018.8768 | 1164170.4511 | 2579019.6151 | 1164173.5168 | 2579021.8353 | 1164177.1093
190 | 2578978.5964 | 1164158.1529 | 2578980.3504 | 1164156.7162
191 | 2579102.2176 | 1164072.4104 | 2579101.9148 | 1164077.8031 | 2579096.5438 | 1164083.6915 | 2579094.9079 | 1164082.3632 | 2579092.0536 | 1164085.2301 | 2579085.0111 | 1164092.8152
192 | 2579102.2176 | 1164072.4104 | 2579104.2123 | 1164071.214 | 2579106.4469 | 1164068.5382 | 2579109.1415 | 1164068.173 | 2579111.4124 | 1164067.1313
193 | 2579085.0111 | 1164092.8152 | 2579081.2117 | 1164096.9072 | 2579083.9446 | 1164100.9441 | 2579091.4893 | 1164107.8212 | 2579091.4893 | 1164107.8212
194 | 2579111.4124 | 1164067.1313 | 2579112.9922 | 1164065.5583 | 2579114.0035 | 1164063.4648 | 2579117.6671 | 1164048.9114 | 2579119.1811 | 1164043.8369 | 2579121.1494 | 1164038.8708
195 | 2579075.3686 | 1164042.2335 | 2579081.2834 | 1164045.1032 | 2579089.5175 | 1164052.0223 | 2579100.7675 | 1164065.0563 | 2579103.7557 | 1164067.6582 | 2579106.4469 | 1164068.5382 | 2579109.1415 | 1164068.173 | 2579111.4124 | 1164067.1313
196 | 2579068.9449 | 1164125.9647 | 2579057.1335 | 1164134.8085
197 | 2579022.9942 | 1164178.9846 | 2579021.8353 | 1164177.1093
198 | 2578978.5964 | 1164158.1529 | 2578968.1383 | 1164166.227
199 | 2578978.5964 | 1164158.1529 | 2578970.9562 | 1164149.0154
200 | 2579230.8075 | 1164105.5171 | 2579231.6335 | 1164107.9111
201 | 2579209.6449 | 1164085.9988 | 2579223.4576 | 1164093.8992 | 2579229.8061 | 1164102.6149 | 2579230.8075 | 1164105.5171
202 | 2579231.6335 | 1164107.9111 | 2579234.6026 | 1164116.5164 | 2579239.9495 | 1164138.8255
203 | 2579209.6449 | 1164085.9988 | 2579207.7268 | 1164091.9056
204 | 2579209.6449 | 1164085.9988 | 2579218.9657 | 1164057.8551
205 | 2579240.4637 | 1164156.9274 | 2579241.8995 | 1164146.9619 | 2579239.9495 | 1164138.8255
206 | 2579196.6608 | 1164126.9978 | 2579199.3018 | 1164117.8507 | 2579207.7268 | 1164091.9056
207 | 2579218.9657 | 1164057.8551 | 2579228.3859 | 1164029.4114
208 | 2579196.6608 | 1164126.9978 | 2579193.4165 | 1164125.6195 | 2579190.4633 | 1164124.2846 | 2579185.8097 | 1164120.6768 | 2579181.0657 | 1164115.2683 | 2579176.6046 | 1164108.5629
209 | 2579228.3859 | 1164029.4114 | 2579237.5862 | 1164001.6316
210 | 2579176.6046 | 1164108.5629 | 2579167.6787 | 1164095.1464
211 | 2579250.5713 | 1163959.938 | 2579244.4255 | 1163980.981 | 2579237.5862 | 1164001.6316
212 | 2579279.4731 | 1164048.3105 | 2579275.0753 | 1164031.8447 | 2579273.2946 | 1164021.857 | 2579273.282 | 1164021.4197
213 | 2579273.1335 | 1164016.2734 | 2579273.282 | 1164021.4197
214 | 2579273.1335 | 1164016.2734 | 2579272.4206 | 1163991.5545
215 | 2579270.8801 | 1163977.0429 | 2579272.2936 | 1163987.1542 | 2579272.4206 | 1163991.5545
216 | 2579093.6032 | 1163952.2469 | 2579092.8383 | 1163950.3375 | 2579090.3401 | 1163944.0788
217 | 2579093.6032 | 1163952.2469 | 2579087.5443 | 1163956.3701 | 2579085.0879 | 1163959.1356 | 2579082.6397 | 1163964.269 | 2579075.4103 | 1163981.9031
218 | 2579093.6032 | 1163952.2469 | 2579104.3562 | 1163978.6337
219 | 2579034.2496 | 1163943.8058 | 2579041.2755 | 1163942.4471 | 2579052.2294 | 1163940.8413
220 | 2579052.2294 | 1163940.8413 | 2579045.8223 | 1163931.4475
221 | 2579104.3562 | 1163978.6337 | 2579108.2081 | 1163987.0487
222 | 2579104.3562 | 1163978.6337 | 2579112.4028 | 1163975.6708 | 2579116.58 | 1163974.4111 | 2579124.5938 | 1163972.9326
223 | 2579034.2496 | 1163943.8058 | 2579027.6825 | 1163945.534
224 | 2579034.2496 | 1163943.8058 | 2579034.945 | 1163947.7498 | 2579035.9531 | 1163953.5047 | 2579035.7779 | 1163955.9621 | 2579034.1594 | 1163957.4129 | 2579028.5252 | 1163960.323 | 2579021.0233 | 1163965.0675
225 | 2579126.6596 | 1164027.3581 | 2579108.2081 | 1163987.0487
226 | 2579124.5938 | 1163972.9326 | 2579131.9946 | 1163971.5671 | 2579139.4893 | 1163970.6961 | 2579143.169 | 1163970.7469
227 | 2578967.7248 | 1163984.7819 | 2578973.1336 | 1163976.581 | 2578983.227 | 1163965.4733 | 2578996.0051 | 1163957.7468 | 2579027.2713 | 1163945.6422 | 2579027.6825 | 1163945.534
228 | 2579126.6596 | 1164027.3581 | 2579128.032 | 1164029.8645
229 | 2579126.6596 | 1164027.3581 | 2579123.4477 | 1164033.0722 | 2579121.1494 | 1164038.8708
230 | 2579172.6691 | 1163978.0287 | 2579167.1967 | 1163976.836 | 2579151.0345 | 1163971.7119 | 2579144.6285 | 1163970.7671 | 2579143.169 | 1163970.7469
231 | 2579144.5054 | 1164144.5494 | 2579141.762 | 1164141.5072 | 2579129.7531 | 1164130.399 | 2579127.705 | 1164129.4279 | 2579125.7658 | 1164128.9789 | 2579122.957 | 1164129.5223 | 2579120.3054 | 1164131.1879 | 2579108.699 | 1164141.0667 | 2579103.4373 | 1164145.3428 | 2579102.156 | 1164146.119
232 | 2579163.4894 | 1164088.8496 | 2579167.6787 | 1164095.1464
233 | 2579405.4362 | 1163863.1529 | 2579406.1228 | 1163862.9243
234 | 2579429.8864 | 1163833.535 | 2579427.0487 | 1163828.2073 | 2579421.7002 | 1163820.7775
235 | 2579375.5475 | 1163882.9494 | 2579381.0946 | 1163876.7786 | 2579387.6439 | 1163870.4084 | 2579396.0543 | 1163866.2774 | 2579405.4362 | 1163863.1529
236 | 2579395.4581 | 1163803.9995 | 2579397.3232 | 1163805.5092 | 2579415.2505 | 1163816.0195 | 2579421.7002 | 1163820.7775 | 2579421.7002 | 1163820.7775
237 | 2579316.1277 | 1163932.4374 | 2579333.7935 | 1163920.9639 | 2579356.5353 | 1163904.0992 | 2579375.5475 | 1163882.9494
238 | 2579075.078 | 1164115.9827 | 2579079.3328 | 1164111.51 | 2579080.22 | 1164111.1512 | 2579081.5288 | 1164110.9242 | 2579086.4324 | 1164111.5408 | 2579087.3893 | 1164111.4262 | 2579088.1847 | 1164111.1344 | 2579091.4893 | 1164107.8212
239 | 2579075.3686 | 1164042.2335 | 2579068.4307 | 1164040.279 | 2579055.4802 | 1164038.101 | 2579047.0365 | 1164036.9744 | 2579039.0023 | 1164036.8803 | 2579030.7984 | 1164037.6656
240 | 2579075.3686 | 1164042.2335 | 2579073.9198 | 1164030.8996 | 2579070.4085 | 1164025.4869
241 | 2579002.7581 | 1164044.4889 | 2579011.2175 | 1164041.3576 | 2579026.2245 | 1164038.1034 | 2579030.7984 | 1164037.6656
242 | 2579068.9449 | 1164125.9647 | 2579067.8949 | 1164123.5338 | 2579075.078 | 1164115.9827
243 | 2579002.7581 | 1164044.4889 | 2578997.8503 | 1164047.9492
244 | 2579290.6458 | 1163999.0676 | 2579299.054 | 1164009.6284 | 2579306.0447 | 1164018.2632
245 | 2579270.8801 | 1163977.0429 | 2579278.5855 | 1163983.9197 | 2579290.6458 | 1163999.0676
246 | 2579260.0802 | 1163956.8146 | 2579262.8614 | 1163959.3507 | 2579264.9705 | 1163962.4227 | 2579270.0368 | 1163974.6001 | 2579270.8801 | 1163977.0429
247 | 2579250.5713 | 1163959.938 | 2579252.3497 | 1163953.7732 | 2579260.0802 | 1163956.8146
248 | 2579260.0802 | 1163956.8146 | 2579272.5767 | 1163951.691 | 2579299.1457 | 1163940.9492 | 2579313.5052 | 1163934.1406 | 2579316.1277 | 1163932.4374
249 | 2579239.0348 | 1163888.5644 | 2579240.6153 | 1163898.186 | 2579246.8574 | 1163911.5155 | 2579255.9692 | 1163924.1791 | 2579255.2381 | 1163931.9967 | 2579254.0709 | 1163944.3625 | 2579252.3497 | 1163953.7732 | 2579250.5713 | 1163959.938
250 | 2579239.0348 | 1163888.5644 | 2579228.5931 | 1163898.7724 | 2579224.5283 | 1163903.7779
251 | 2578961.8464 | 1164133.8996 | 2578960.6539 | 1164136.6941 | 2578970.9562 | 1164149.0154
252 | 2578959.3724 | 1164172.9946 | 2578968.1383 | 1164166.227
253 | 2578943.2349 | 1164153.0524 | 2578959.3724 | 1164172.9946
254 | 2578959.3724 | 1164172.9946 | 2578954.5357 | 1164176.7272
255 | 2578946.9952 | 1164146.5248 | 2578948.027 | 1164148.1109 | 2578943.2349 | 1164153.0524
256 | 2578943.2349 | 1164153.0524 | 2578937.262 | 1164153.2402 | 2578934.7023 | 1164155.2277
257 | 2578954.5357 | 1164176.7272 | 2578949.9602 | 1164180.2582
258 | 2579163.4894 | 1164088.8496 | 2579169.5988 | 1164081.658 | 2579181.9446 | 1164055.3352 | 2579182.4971 | 1164051.2312 | 2579178.6006 | 1164045.1084
259 | 2579163.4894 | 1164088.8496 | 2579144.4953 | 1164058.5334
260 | 2579196.0195 | 1163975.6401 | 2579183.3902 | 1163977.4404
261 | 2579172.6691 | 1163978.0287 | 2579172.6691 | 1163978.0287 | 2579178.0691 | 1163978.1989 | 2579183.3902 | 1163977.4404
262 | 2578871.7922 | 1164126.0026 | 2578871.779 | 1164126.1907 | 2578871.9546 | 1164128.2244 | 2578873.1193 | 1164130.5548 | 2578878.1844 | 1164139.2799
263 | 2578871.7922 | 1164126.0026 | 2578871.9394 | 1164123.9112 | 2578872.7458 | 1164122.3965 | 2578875.1675 | 1164120.6649 | 2578876.7158 | 1164120.036
264 | 2578888.6156 | 1164157.2482 | 2578878.1844 | 1164139.2799
265 | 2578898.5483 | 1164116.0917 | 2578883.1705 | 1164118.4688 | 2578878.2876 | 1164119.3977 | 2578876.7158 | 1164120.036
266 | 2578888.6156 | 1164157.2482 | 2578895.3218 | 1164168.8002
267 | 2578898.5483 | 1164116.0917 | 2578902.0842 | 1164115.5451 | 2578904.0196 | 1164114.938 | 2578918.8841 | 1164110.6922
268 | 2578895.3218 | 1164168.8002 | 2578862.2008 | 1164196.5041
269 | 2578925.9463 | 1164107.0267 | 2578919.4665 | 1164110.5258 | 2578918.8841 | 1164110.6922
270 | 2578862.2008 | 1164196.5041 | 2578871.647 | 1164210.259
271 | 2578862.2008 | 1164196.5041 | 2578854.9963 | 1164186.0133 | 2578853.3132 | 1164184.4853
272 | 2578925.9463 | 1164107.0267 | 2578938.5399 | 1164100.2259
273 | 2579144.4953 | 1164058.5334 | 2579138.4215 | 1164048.839 | 2579128.032 | 1164029.8645
274 | 2579327.1315 | 1163826.0656 | 2579346.7691 | 1163832.7082 | 2579355.0431 | 1163837.7363
275 | 2579327.0896 | 1163826.0514 | 2579327.1315 | 1163826.0656
276 | 2579356.8463 | 1163838.8321 | 2579355.0431 | 1163837.7363
277 | 2579173.7628 | 1164032.6078 | 2579178.6006 | 1164045.1084
278 | 2578996.9482 | 1164200.9563 | 2578977.4097 | 1164213.112
279 | 2578977.4097 | 1164213.112 | 2578966.9954 | 1164219.5912 | 2578955.8618 | 1164204.037
280 | 2578945.3038 | 1164188.185 | 2578945.3038 | 1164188.185 | 2578946.4775 | 1164190.9267 | 2578955.8618 | 1164204.037
281 | 2578945.3038 | 1164188.185 | 2578945.2117 | 1164185.9509 | 2578945.9856 | 1164183.9138 | 2578947.4195 | 1164182.219 | 2578949.9602 | 1164180.2582
282 | 2578978.386 | 1164061.6731 | 2578997.8503 | 1164047.9492
283 | 2578976.2486 | 1164063.1802 | 2578978.386 | 1164061.6731
284 | 2578976.2486 | 1164063.1802 | 2578955.6252 | 1164084.9516
285 | 2578955.6252 | 1164084.9516 | 2578943.8966 | 1164097.3332 | 2578938.5399 | 1164100.2259
286 | 2578967.7248 | 1163984.7819 | 2578956.2073 | 1163993.7935 | 2578946.1649 | 1164001.9663 | 2578939.978 | 1164011.4173
287 | 2578936.1876 | 1164026.4137 | 2578938.6082 | 1164013.5098 | 2578939.978 | 1164011.4173

## bus_geodata
| x | y | coords
0 | 2580067.9245 | 1164107.4514
1 | 2579934.6187 | 1164051.0851
2 | 2580292.931 | 1164348.6883
3 | 2580330.4764 | 1164391.6269
4 | 2580234.5711 | 1165342.9282
5 | 2580227.4888 | 1165338.075
6 | 2580261.0594 | 1165356.2989
7 | 2580150.7174 | 1165271.9644
8 | 2580271.4079 | 1165358.9075
9 | 2580186.4515 | 1165164.2939
10 | 2580201.3945 | 1165126.6022
11 | 2579995.6711 | 1165101.7968
12 | 2580200.3506 | 1165123.4159
13 | 2580247.0643 | 1165092.4682
14 | 2579935.2238 | 1165039.4906
15 | 2580258.2026 | 1165101.338
16 | 2579905.7584 | 1164975.857
17 | 2579818.5517 | 1164875.4819
18 | 2580014.896 | 1164885.6574
19 | 2580015.1386 | 1164885.8469
20 | 2579958.4258 | 1164828.5892
21 | 2580024.671 | 1164893.2968
22 | 2579371.1175 | 1164541.6806
23 | 2579340.1732 | 1164502.0668
24 | 2579421.9708 | 1164585.2713
25 | 2579288.1858 | 1164423.1513
26 | 2579282.1536 | 1164552.1147
27 | 2579384.7477 | 1164641.3386
28 | 2579460.5844 | 1164623.1632
29 | 2579496.3821 | 1164424.2915
30 | 2579482.1944 | 1164313.1136
31 | 2579211.2663 | 1164492.8645
32 | 2579268.2843 | 1164368.4149
33 | 2579587.7081 | 1164710.4555
34 | 2579191.2905 | 1164230.0015
35 | 2579595.5248 | 1164718.0377
36 | 2579770.9872 | 1164836.7041
37 | 2579667.1294 | 1163959.7775
38 | 2579577.6809 | 1163926.4853
39 | 2579790.3342 | 1164010.9504
40 | 2579612.3089 | 1163902.6553
41 | 2579843.828 | 1164012.7931
42 | 2579590.4024 | 1163892.0112
43 | 2579642.6334 | 1163905.0928
44 | 2579584.1329 | 1163891.7867
45 | 2579678.2277 | 1163898.1956
46 | 2579773.7146 | 1164838.9277
47 | 2579422.1443 | 1164063.4755
48 | 2579474.5056 | 1164144.4392
49 | 2579358.8096 | 1164050.5204
50 | 2579420.3747 | 1164241.8171
51 | 2579356.562 | 1164085.5489
52 | 2579475.578 | 1163920.6315
53 | 2579477.3947 | 1163897.3481
54 | 2579484.987 | 1163870.4519
55 | 2579446.6039 | 1163858.2651
56 | 2579511.4544 | 1163875.4949
57 | 2579758.1112 | 1164292.9229
58 | 2579184.298 | 1164217.2909
59 | 2579133.5962 | 1164189.9422
60 | 2579194.5942 | 1164189.025
61 | 2579194.0403 | 1164183.891
62 | 2579177.1172 | 1164204.2378
63 | 2579192.7724 | 1164167.2537
64 | 2579643.3823 | 1163822.1759
65 | 2579573.1462 | 1163892.0145
66 | 2579352.3669 | 1164109.9724
67 | 2579350.192 | 1164125.4766
68 | 2579333.0327 | 1164095.0462
69 | 2579320.5856 | 1164054.7565
70 | 2579316.3938 | 1164036.1742
71 | 2579312.0678 | 1164187.5163
72 | 2579285.8657 | 1164177.6806
73 | 2579265.2087 | 1164177.5509
74 | 2579301.0663 | 1164133.6155
75 | 2579297.9661 | 1164119.8224
76 | 2579290.0489 | 1164084.5983
77 | 2579260.7916 | 1163674.4961
78 | 2579260.8192 | 1163695.9098
79 | 2579260.2659 | 1163667.8912
80 | 2579260.18 | 1163727.0768
81 | 2579284.4524 | 1163659.9578
82 | 2579207.589 | 1163555.3214
83 | 2579225.96 | 1163714.1557
84 | 2579294.9584 | 1163748.6352
85 | 2579283.2237 | 1163638.4187
86 | 2579198.9732 | 1163532.0024
87 | 2579211.3581 | 1163708.9506
88 | 2579295.5676 | 1163748.9592
89 | 2579258.5586 | 1163807.2893
90 | 2579258.3086 | 1163827.7873
91 | 2579302.3956 | 1163817.6984
92 | 2579276.6916 | 1163617.9247
93 | 2579260.8542 | 1163545.928
94 | 2579177.5802 | 1163755.801
95 | 2579185.2722 | 1163720.6651
96 | 2579192.46 | 1163705.1897
97 | 2579172.0528 | 1163683.4128
98 | 2579268.6525 | 1163592.7023
99 | 2579331.6661 | 1163756.6217
100 | 2579257.7952 | 1163869.8789
101 | 2579303.4732 | 1163818.0629
102 | 2579474.1215 | 1163650.0897
103 | 2579386.4014 | 1163760.9578
104 | 2579374.713 | 1163776.2502
105 | 2579447.9846 | 1163801.3211
106 | 2579376.338 | 1163778.8053
107 | 2579347.282 | 1163757.1797
108 | 2579458.2286 | 1163828.467
109 | 2579386.737 | 1163795.156
110 | 2578972.251 | 1163701.446
111 | 2578991.809 | 1163692.1533
112 | 2578981.0527 | 1163724.3969
113 | 2578943.2581 | 1163705.2953
114 | 2579013.4949 | 1163681.8672
115 | 2578991.0266 | 1163750.4047
116 | 2578918.9818 | 1163792.6521
117 | 2578917.9865 | 1163792.8748
118 | 2578935.7727 | 1163788.8959
119 | 2578901.0888 | 1163798.4673
120 | 2578955.1569 | 1163769.825
121 | 2578938.5028 | 1163805.3455
122 | 2578891.5108 | 1163808.0837
123 | 2578975.7639 | 1163757.3729
124 | 2578948.4593 | 1163837.7588
125 | 2578884.5425 | 1163831.0448
126 | 2578950.8455 | 1163845.5269
127 | 2578802.3531 | 1163860.516
128 | 2578809.9947 | 1163851.0151
129 | 2578871.4579 | 1163878.375
130 | 2578871.4277 | 1163878.4578
131 | 2578877.9219 | 1163858.2794
132 | 2578883.7864 | 1163834.2659
133 | 2578940.6154 | 1163870.6122
134 | 2578935.5464 | 1163885.0703
135 | 2578947.3128 | 1163851.509
136 | 2578930.732 | 1163898.8026
137 | 2578922.6701 | 1163921.7976
138 | 2578920.9227 | 1163926.7817
139 | 2579046.1892 | 1163851.8734
140 | 2579074.0062 | 1163901.4448
141 | 2579028.9887 | 1163826.2352
142 | 2579054.6652 | 1163767.242
143 | 2579055.4115 | 1163763.6469
144 | 2579051.5517 | 1163782.2419
145 | 2579059.2644 | 1163745.0852
146 | 2579039.5618 | 1163742.6579
147 | 2579065.1819 | 1163746.0643
148 | 2579020.9853 | 1163749.6745
149 | 2579091.0554 | 1163750.3454
150 | 2579061.8552 | 1163674.8734
151 | 2579052.8095 | 1163673.1373
152 | 2579076.9769 | 1163677.7756
153 | 2579048.4283 | 1163672.5979
154 | 2579079.0492 | 1163678.1733
155 | 2579022.4131 | 1163677.6371
156 | 2579106.2509 | 1163683.394
157 | 2579108.1226 | 1163683.7533
158 | 2579025.7356 | 1163820.706
159 | 2579011.5075 | 1163796.5227
160 | 2578992.5852 | 1163825.6703
161 | 2579008.4355 | 1163789.6695
162 | 2579083.2634 | 1163925.6178
163 | 2578995.9994 | 1163761.9264
164 | 2579087.0501 | 1163935.5058
165 | 2578910.8058 | 1163945.6402
166 | 2579015.8801 | 1163752.1776
167 | 2578879.2252 | 1163853.6983
168 | 2579103.4948 | 1163752.4037
169 | 2579125.7124 | 1163687.1292
170 | 2579131.0905 | 1163688.1614
171 | 2579106.1105 | 1163752.8365
172 | 2579512.7939 | 1163875.8098
173 | 2579520.9914 | 1163878.4848
174 | 2579553.8789 | 1163892.4422
175 | 2579439.1928 | 1163851.9108
176 | 2579031.7416 | 1164102.1437
177 | 2579046.9396 | 1164084.7339
178 | 2579010.5134 | 1164126.6585
179 | 2579065.2549 | 1164068.3663
180 | 2579036.0386 | 1164150.6033
181 | 2579006.5683 | 1164130.7257
182 | 2579038.6853 | 1164148.6216
183 | 2579022.7153 | 1164162.1672
184 | 2578980.3504 | 1164156.7162
185 | 2579102.2176 | 1164072.4104
186 | 2579085.0111 | 1164092.8152
187 | 2579111.4124 | 1164067.1313
188 | 2579057.1335 | 1164134.8085
189 | 2579021.8353 | 1164177.1093
190 | 2578978.5964 | 1164158.1529
191 | 2579230.8075 | 1164105.5171
192 | 2579231.6335 | 1164107.9111
193 | 2579209.6449 | 1164085.9988
194 | 2579239.9495 | 1164138.8255
195 | 2579207.7268 | 1164091.9056
196 | 2579218.9657 | 1164057.8551
197 | 2579240.4637 | 1164156.9274
198 | 2579196.6608 | 1164126.9978
199 | 2579228.3859 | 1164029.4114
200 | 2579176.6046 | 1164108.5629
201 | 2579237.5862 | 1164001.6316
202 | 2579279.4731 | 1164048.3105
203 | 2579273.282 | 1164021.4197
204 | 2579273.1335 | 1164016.2734
205 | 2579272.4206 | 1163991.5545
206 | 2579090.3401 | 1163944.0788
207 | 2579093.6032 | 1163952.2469
208 | 2579052.2294 | 1163940.8413
209 | 2579075.4103 | 1163981.9031
210 | 2579104.3562 | 1163978.6337
211 | 2579034.2496 | 1163943.8058
212 | 2579045.8223 | 1163931.4475
213 | 2579108.2081 | 1163987.0487
214 | 2579124.5938 | 1163972.9326
215 | 2579027.6825 | 1163945.534
216 | 2579021.0233 | 1163965.0675
217 | 2579126.6596 | 1164027.3581
218 | 2579143.169 | 1163970.7469
219 | 2579144.5054 | 1164144.5494
220 | 2579102.156 | 1164146.119
221 | 2579167.6787 | 1164095.1464
222 | 2579406.1228 | 1163862.9243
223 | 2579429.8864 | 1163833.535
224 | 2579405.4362 | 1163863.1529
225 | 2579421.7002 | 1163820.7775
226 | 2579375.5475 | 1163882.9494
227 | 2579395.4581 | 1163803.9995
228 | 2579091.4893 | 1164107.8212
229 | 2579075.3686 | 1164042.2335
230 | 2579030.7984 | 1164037.6656
231 | 2579070.4085 | 1164025.4869
232 | 2579121.1494 | 1164038.8708
233 | 2579075.078 | 1164115.9827
234 | 2579002.7581 | 1164044.4889
235 | 2579290.6458 | 1163999.0676
236 | 2579306.0447 | 1164018.2632
237 | 2579270.8801 | 1163977.0429
238 | 2579260.0802 | 1163956.8146
239 | 2579250.5713 | 1163959.938
240 | 2579316.1277 | 1163932.4374
241 | 2579239.0348 | 1163888.5644
242 | 2579224.5283 | 1163903.7779
243 | 2578970.9562 | 1164149.0154
244 | 2578961.8464 | 1164133.8996
245 | 2578968.1383 | 1164166.227
246 | 2578959.3724 | 1164172.9946
247 | 2578943.2349 | 1164153.0524
248 | 2578954.5357 | 1164176.7272
249 | 2579163.4894 | 1164088.8496
250 | 2579196.0195 | 1163975.6401
251 | 2579183.3902 | 1163977.4404
252 | 2579068.9449 | 1164125.9647
253 | 2578871.7922 | 1164126.0026
254 | 2578878.1844 | 1164139.2799
255 | 2578876.7158 | 1164120.036
256 | 2578888.6156 | 1164157.2482
257 | 2578898.5483 | 1164116.0917
258 | 2578895.3218 | 1164168.8002
259 | 2578918.8841 | 1164110.6922
260 | 2578862.2008 | 1164196.504
261 | 2578853.3132 | 1164184.4853
262 | 2578925.9463 | 1164107.0267
263 | 2579172.6691 | 1163978.0287
264 | 2579128.032 | 1164029.8645
265 | 2578871.647 | 1164210.259
266 | 2579144.4953 | 1164058.5334
267 | 2579327.1315 | 1163826.0656
268 | 2579355.0431 | 1163837.7363
269 | 2579327.0896 | 1163826.0514
270 | 2579356.8463 | 1163838.8321
271 | 2579178.6006 | 1164045.1084
272 | 2579173.7628 | 1164032.6078
273 | 2579022.9942 | 1164178.9846
274 | 2578996.9482 | 1164200.9563
275 | 2578977.4097 | 1164213.112
276 | 2578955.8618 | 1164204.037
277 | 2578945.3038 | 1164188.185
278 | 2578949.9602 | 1164180.2582
279 | 2578978.386 | 1164061.6731
280 | 2578997.8503 | 1164047.9492
281 | 2578976.2486 | 1164063.1802
282 | 2578955.6252 | 1164084.9516
283 | 2578938.5399 | 1164100.2259
284 | 2578946.9952 | 1164146.5248
285 | 2578934.7023 | 1164155.2277
286 | 2578967.7248 | 1163984.7819
287 | 2578939.978 | 1164011.4173
288 | 2578936.1876 | 1164026.4137
289 | 2579104.3562 | 1163978.6337

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97034 | -0.57467 | 0.00050943 | 0.00012767
1 | 0.97053 | -0.57082 | 0 | 0
2 | 0.97006 | -0.58032 | 0 | 0
3 | 0.97001 | -0.58129 | 0.00091685 | 0.00022978
4 | 0.97063 | -0.56944 | 0.0019324 | 0.0004843
5 | 0.97065 | -0.569 | 0.0010961 | 0.00027472
6 | 0.9706 | -0.56987 | 0 | 0
7 | 0.97101 | -0.56184 | 0.00010388 | 2.6035e-05
8 | 0.9706 | -0.57003 | 0.00079014 | 0.00019803
9 | 0.97143 | -0.5536 | 0.00063442 | 0.000159
10 | 0.97135 | -0.55518 | 0.00032818 | 8.225e-05
11 | 0.97264 | -0.52947 | 0 | 0
12 | 0.97134 | -0.55528 | 0.0012317 | 0.00030869
13 | 0.97132 | -0.55573 | 0 | 0
14 | 0.97317 | -0.51901 | 0.00032216 | 8.0742e-05
15 | 0.97131 | -0.55583 | 0.00038491 | 9.6468e-05
16 | 0.97362 | -0.51013 | 0 | 0
17 | 0.97447 | -0.4934 | 0.00026586 | 6.6631e-05
18 | 0.97462 | -0.49047 | 0 | 0
19 | 0.97462 | -0.49047 | 0.00014929 | 3.7417e-05
20 | 0.97467 | -0.48933 | 0.0002502 | 6.2707e-05
21 | 0.97461 | -0.49061 | 0.00062146 | 0.00015575
22 | 0.97955 | -0.39341 | 0.0025325 | 0.00063471
23 | 0.9802 | -0.38058 | 0 | 0
24 | 0.97883 | -0.4075 | 0 | 0
25 | 0.9816 | -0.35334 | 0 | 0
26 | 0.98008 | -0.38305 | 0.0017796 | 0.00044601
27 | 0.97879 | -0.40826 | 0.00061586 | 0.00015435
28 | 0.97828 | -0.41824 | 0.00079681 | 0.0001997
29 | 0.97387 | -0.50489 | 0.00035953 | 9.0106e-05
30 | 0.97391 | -0.50415 | 0.00031105 | 7.7957e-05
31 | 0.98136 | -0.35789 | 0.0024246 | 0.00060765
32 | 0.98258 | -0.3341 | 0.00043126 | 0.00010809
33 | 0.97684 | -0.44667 | 0 | 0
34 | 0.98395 | -0.30739 | 0 | 0
35 | 0.97673 | -0.44867 | 0.00065231 | 0.00016348
36 | 0.97488 | -0.4853 | 0.0010742 | 0.00026921
37 | 0.97191 | -0.54335 | 0.0024133 | 0.00060484
38 | 0.97282 | -0.52534 | 0.0011737 | 0.00029416
39 | 0.971 | -0.56153 | 0.0006683 | 0.00016749
40 | 0.97328 | -0.51628 | 0 | 0
41 | 0.97066 | -0.56817 | 0.0052587 | 0.001318
42 | 0.97359 | -0.5101 | 0.00095687 | 0.00023982
43 | 0.97324 | -0.51714 | 0.00065773 | 0.00016484
44 | 0.97367 | -0.50855 | 0.00032855 | 8.2342e-05
45 | 0.97321 | -0.51773 | 0 | 0
46 | 0.97485 | -0.48584 | 0.00022 | 5.5138e-05
47 | 0.97439 | -0.49469 | 0.002661 | 0.0006669
48 | 0.97419 | -0.49853 | 0.0004861 | 0.00012183
49 | 0.97467 | -0.48909 | 0.0032224 | 0.00080761
50 | 0.97403 | -0.50172 | 0.00015687 | 3.9315e-05
51 | 0.97493 | -0.48396 | 0.0016988 | 0.00042575
52 | 0.97504 | -0.48157 | 0.0016491 | 0.00041331
53 | 0.97507 | -0.48084 | 0.0042842 | 0.0010737
54 | 0.97523 | -0.47778 | 0 | 0
55 | 0.97547 | -0.47309 | 0.0034979 | 0.00087667
56 | 0.97475 | -0.48722 | 0.00044891 | 0.00011251
57 | 0.97373 | -0.50781 | 0.00071492 | 0.00017918
58 | 0.98401 | -0.30626 | 0.00064713 | 0.00016219
59 | 0.98372 | -0.31197 | 0.00276 | 0.00069172
60 | 0.98421 | -0.30225 | 0 | 0
61 | 0.98424 | -0.30167 | 0 | 0
62 | 0.98407 | -0.30508 | 0.0091122 | 0.0022837
63 | 0.98434 | -0.29979 | 0.0016881 | 0.00042309
64 | 0.97314 | -0.51911 | 0.00087222 | 0.0002186
65 | 0.97381 | -0.50575 | 0.0010225 | 0.00025627
66 | 0.97515 | -0.47958 | 0.00042215 | 0.0001058
67 | 0.9753 | -0.47665 | 0 | 0
68 | 0.97565 | -0.46972 | 0.00046589 | 0.00011676
69 | 0.97606 | -0.46158 | 0.0044891 | 0.0011251
70 | 0.97632 | -0.45635 | 0.0050233 | 0.001259
71 | 0.97603 | -0.46208 | 0.0004707 | 0.00011797
72 | 0.97605 | -0.46184 | 0 | 0
73 | 0.97602 | -0.46239 | 0.0014657 | 0.00036734
74 | 0.97614 | -0.46005 | 0.00044431 | 0.00011135
75 | 0.97617 | -0.45944 | 0.0027355 | 0.00068559
76 | 0.97634 | -0.45606 | 0.0049524 | 0.0012412
77 | 0.97212 | -0.53915 | 0.0019902 | 0.0004988
78 | 0.97246 | -0.53238 | 0.00038374 | 9.6173e-05
79 | 0.97202 | -0.541 | 0 | 0
80 | 0.97297 | -0.52233 | 0 | 0
81 | 0.97189 | -0.5436 | 0.00075897 | 0.00019021
82 | 0.97086 | -0.56406 | 0.0088918 | 0.0022285
83 | 0.97279 | -0.52591 | 0.00066198 | 0.00016591
84 | 0.97384 | -0.50513 | 0.00044271 | 0.00011095
85 | 0.9718 | -0.54541 | 0.0013079 | 0.0003278
86 | 0.97083 | -0.56456 | 0 | 0
87 | 0.97272 | -0.52724 | 0.0015011 | 0.00037622
88 | 0.97386 | -0.50483 | 0.0042813 | 0.001073
89 | 0.97858 | -0.41209 | 0 | 0
90 | 0.97864 | -0.41088 | 0.0032811 | 0.00082231
91 | 0.97844 | -0.41475 | 0.0022743 | 0.00057
92 | 0.97174 | -0.54663 | 0.00062691 | 0.00015712
93 | 0.97077 | -0.56591 | 0.0010929 | 0.0002739
94 | 0.97261 | -0.52946 | 0.00094098 | 0.00023583
95 | 0.97264 | -0.5288 | 0.0004373 | 0.0001096
96 | 0.97266 | -0.52837 | 0 | 0
97 | 0.97261 | -0.52935 | 0.0017742 | 0.00044466
98 | 0.97168 | -0.54783 | 0.00245 | 0.00061403
99 | 0.97434 | -0.49531 | 0.0025365 | 0.0006357
100 | 0.97879 | -0.4079 | 0 | 0
101 | 0.97844 | -0.41481 | 0.002844 | 0.00071278
102 | 0.97429 | -0.49627 | 0.0013824 | 0.00034647
103 | 0.97447 | -0.49268 | 0 | 0
104 | 0.97463 | -0.48958 | 0 | 0
105 | 0.97397 | -0.50259 | 0.0016536 | 0.00041443
106 | 0.97465 | -0.48914 | 0.0028417 | 0.00071218
107 | 0.97443 | -0.49358 | 0.0012386 | 0.00031042
108 | 0.97382 | -0.50559 | 0.0056192 | 0.0014083
109 | 0.97481 | -0.48609 | 0.0023787 | 0.00059617
110 | 0.98443 | -0.29864 | 0 | 0
111 | 0.98381 | -0.31065 | 0.0058496 | 0.0014661
112 | 0.98519 | -0.28372 | 0.0017772 | 0.0004454
113 | 0.98435 | -0.30019 | 0.002935 | 0.00073559
114 | 0.98326 | -0.32146 | 0.0014849 | 0.00037214
115 | 0.98611 | -0.26595 | 0 | 0
116 | 0.98162 | -0.35328 | 0.0027912 | 0.00069953
117 | 0.98159 | -0.35386 | 0.0029312 | 0.00073464
118 | 0.98217 | -0.3426 | 0 | 0
119 | 0.98112 | -0.36311 | 0.0028893 | 0.00072413
120 | 0.98371 | -0.31253 | 0.0021759 | 0.00054533
121 | 0.98176 | -0.35052 | 0.0042322 | 0.0010607
122 | 0.98079 | -0.36957 | 0.0031762 | 0.00079603
123 | 0.9851 | -0.28542 | 0.0020922 | 0.00052436
124 | 0.98108 | -0.36391 | 0.0015638 | 0.00039193
125 | 0.98029 | -0.37941 | 0.0030847 | 0.0007731
126 | 0.98092 | -0.36689 | 0 | 0
127 | 0.97929 | -0.39902 | 0.0027797 | 0.00069666
128 | 0.97932 | -0.3984 | 0.0029292 | 0.00073412
129 | 0.97967 | -0.39142 | 0.0023792 | 0.00059628
130 | 0.97967 | -0.39142 | 0.0018724 | 0.00046926
131 | 0.97987 | -0.3876 | 0.0026147 | 0.00065529
132 | 0.98023 | -0.38058 | 0.0030996 | 0.00077683
133 | 0.98047 | -0.37587 | 0.0031711 | 0.00079474
134 | 0.98026 | -0.37985 | 0.0028559 | 0.00071576
135 | 0.98079 | -0.36944 | 0.0027529 | 0.00068995
136 | 0.98011 | -0.38288 | 0.0020728 | 0.0005195
137 | 0.9799 | -0.38704 | 0.0034858 | 0.00087362
138 | 0.97987 | -0.3876 | 0.0033219 | 0.00083254
139 | 0.99012 | -0.18828 | 0 | 0
140 | 0.99148 | -0.16211 | 0.0022186 | 0.00055603
141 | 0.98939 | -0.20249 | 0.00062031 | 0.00015546
142 | 0.98538 | -0.28013 | 0.002267 | 0.00056817
143 | 0.9854 | -0.27981 | 0.0016137 | 0.00040442
144 | 0.98535 | -0.28082 | 0.0025114 | 0.00062942
145 | 0.98551 | -0.27764 | 0 | 0
146 | 0.9858 | -0.27187 | 0.002074 | 0.0005198
147 | 0.98545 | -0.27869 | 0.0013574 | 0.00034019
148 | 0.98614 | -0.26534 | 0.00082841 | 0.00020762
149 | 0.98525 | -0.28263 | 0.0018249 | 0.00045736
150 | 0.98232 | -0.33967 | 0.0010776 | 0.00027007
151 | 0.98246 | -0.3371 | 0.0013936 | 0.00034926
152 | 0.98212 | -0.34367 | 0.001646 | 0.00041252
153 | 0.98252 | -0.33575 | 0.0038568 | 0.00096659
154 | 0.9821 | -0.34416 | 0.0029547 | 0.00074052
155 | 0.98304 | -0.32564 | 0.0027882 | 0.00069879
156 | 0.98185 | -0.34906 | 0.0032011 | 0.00080228
157 | 0.98183 | -0.34928 | 0.0016447 | 0.0004122
158 | 0.98923 | -0.20543 | 0.0015132 | 0.00037923
159 | 0.98857 | -0.21814 | 0 | 0
160 | 0.98849 | -0.21981 | 0.002661 | 0.00066691
161 | 0.9884 | -0.22148 | 0.0022688 | 0.00056862
162 | 0.99211 | -0.15005 | 0.00061877 | 0.00015508
163 | 0.98669 | -0.25468 | 0 | 0
164 | 0.99237 | -0.14509 | 0 | 0
165 | 0.97982 | -0.38862 | 0.0025933 | 0.00064994
166 | 0.98624 | -0.2634 | 0.0029585 | 0.00074146
167 | 0.97992 | -0.38651 | 0.0037994 | 0.00095222
168 | 0.98518 | -0.28411 | 0.0018089 | 0.00045335
169 | 0.98175 | -0.35088 | 0.00072372 | 0.00018138
170 | 0.98173 | -0.3513 | 0.0042144 | 0.0010562
171 | 0.98516 | -0.28433 | 0.0047338 | 0.0011864
172 | 0.97473 | -0.48769 | 0.002729 | 0.00068395
173 | 0.9746 | -0.49021 | 0.0003679 | 9.2205e-05
174 | 0.97408 | -0.50048 | 0.00072452 | 0.00018158
175 | 0.97552 | -0.47207 | 0 | 0
176 | 0.98661 | -0.25645 | 0.0039002 | 0.00097747
177 | 0.98651 | -0.25837 | 0.0024268 | 0.00060821
178 | 0.98686 | -0.25149 | 0 | 0
179 | 0.98646 | -0.25934 | 0.0022115 | 0.00055426
180 | 0.98785 | -0.23225 | 0 | 0
181 | 0.98675 | -0.25374 | 0.0013854 | 0.00034721
182 | 0.98797 | -0.23001 | 0.0019917 | 0.00049918
183 | 0.98774 | -0.23451 | 0.0025611 | 0.00064187
184 | 0.98604 | -0.26755 | 0.0023736 | 0.00059489
185 | 0.98939 | -0.20249 | 0 | 0
186 | 0.9891 | -0.20807 | 0.0028924 | 0.00072492
187 | 0.98949 | -0.20043 | 0 | 0
188 | 0.98839 | -0.22179 | 0.001961 | 0.00049147
189 | 0.98767 | -0.2359 | 0.0020894 | 0.00052365
190 | 0.986 | -0.2683 | 0 | 0
191 | 0.9831 | -0.32386 | 0.0042212 | 0.0010579
192 | 0.98309 | -0.32408 | 0.0012796 | 0.00032069
193 | 0.98322 | -0.32149 | 0 | 0
194 | 0.98299 | -0.32602 | 0.0019822 | 0.0004968
195 | 0.98342 | -0.31752 | 0.0051939 | 0.0013017
196 | 0.9823 | -0.33947 | 0.0039275 | 0.00098432
197 | 0.98297 | -0.32647 | 0.0013752 | 0.00034467
198 | 0.98467 | -0.2934 | 0 | 0
199 | 0.98138 | -0.35725 | 0.0039483 | 0.00098953
200 | 0.98584 | -0.27076 | 0.00066188 | 0.00016588
201 | 0.98051 | -0.37423 | 0.0020685 | 0.00051842
202 | 0.97669 | -0.44908 | 0.0027991 | 0.00070153
203 | 0.97702 | -0.44259 | 0.0033472 | 0.0008389
204 | 0.9771 | -0.44106 | 0.0037062 | 0.00092886
205 | 0.97756 | -0.43207 | 0.0028417 | 0.00071221
206 | 0.99261 | -0.14055 | 0.0022575 | 0.00056578
207 | 0.99284 | -0.13613 | 0 | 0
208 | 0.99212 | -0.14989 | 0 | 0
209 | 0.9928 | -0.13678 | 0.0010345 | 0.00025927
210 | 0.99359 | -0.12172 | 0 | 0
211 | 0.992 | -0.15218 | 0 | 0
212 | 0.99212 | -0.15 | 0.00057251 | 0.00014349
213 | 0.993 | -0.13308 | 0.0017543 | 0.00043967
214 | 0.9955 | -0.085255 | 0.0021483 | 0.00053842
215 | 0.99197 | -0.15292 | 0.0031974 | 0.00080134
216 | 0.99198 | -0.15268 | 0.00095144 | 0.00023845
217 | 0.99016 | -0.18742 | 0 | 0
218 | 0.99721 | -0.052807 | 0.0026267 | 0.00065832
219 | 0.98422 | -0.30209 | 0.006905 | 0.0017305
220 | 0.98402 | -0.306 | 0.0040024 | 0.0010031
221 | 0.98652 | -0.25766 | 0.0018266 | 0.00045778
222 | 0.97604 | -0.46191 | 0.002394 | 0.0006
223 | 0.97532 | -0.47593 | 0.00099236 | 0.00024871
224 | 0.97605 | -0.4617 | 0.0021884 | 0.00054847
225 | 0.97518 | -0.47872 | 0.0037541 | 0.00094086
226 | 0.97662 | -0.4504 | 0.00158 | 0.000396
227 | 0.97491 | -0.48402 | 0.0010761 | 0.00026969
228 | 0.98891 | -0.21173 | 0.0054812 | 0.0013737
229 | 0.98922 | -0.20564 | 0 | 0
230 | 0.989 | -0.21002 | 0.0046759 | 0.0011719
231 | 0.98916 | -0.20696 | 0.0041484 | 0.0010397
232 | 0.98996 | -0.19141 | 0.0036536 | 0.00091569
233 | 0.98875 | -0.21485 | 0.0021843 | 0.00054743
234 | 0.98888 | -0.21235 | 0 | 0
235 | 0.97722 | -0.43865 | 0.0011255 | 0.00028207
236 | 0.97672 | -0.44864 | 0.0021898 | 0.00054881
237 | 0.97787 | -0.426 | 0 | 0
238 | 0.97886 | -0.40647 | 0 | 0
239 | 0.97923 | -0.3993 | 0 | 0
240 | 0.97786 | -0.42604 | 0.0020195 | 0.00050615
241 | 0.97889 | -0.406 | 0 | 0
242 | 0.9788 | -0.40777 | 0.0046247 | 0.001159
243 | 0.98597 | -0.26889 | 0.0017055 | 0.00042743
244 | 0.98595 | -0.26926 | 0.0010708 | 0.00026837
245 | 0.98581 | -0.27202 | 0.0015345 | 0.00038457
246 | 0.98567 | -0.27484 | 0 | 0
247 | 0.98561 | -0.27597 | 0 | 0
248 | 0.9856 | -0.27612 | 0.0011597 | 0.00029064
249 | 0.98684 | -0.25148 | 0 | 0
250 | 0.99989 | -0.0020526 | 0.002951 | 0.0007396
251 | 0.99993 | -0.0013963 | 0.0044809 | 0.001123
252 | 0.98858 | -0.21811 | 0 | 0
253 | 0.98849 | -0.21998 | 0.00063854 | 0.00016003
254 | 0.98847 | -0.22024 | 0.00079583 | 0.00019945
255 | 0.9885 | -0.21981 | 0.00077543 | 0.00019434
256 | 0.98846 | -0.22054 | 0.0007074 | 0.00017729
257 | 0.98852 | -0.21931 | 0.0024579 | 0.000616
258 | 0.98845 | -0.22082 | 0.00098433 | 0.0002467
259 | 0.98856 | -0.21865 | 0.0015364 | 0.00038507
260 | 0.98835 | -0.22268 | 0.00062387 | 0.00015636
261 | 0.98834 | -0.22294 | 0.00099846 | 0.00025024
262 | 0.98857 | -0.21835 | 0.0028572 | 0.00071609
263 | 1 | 0 | -0.51242 | -0.13109
264 | 0.99003 | -0.19005 | 0.0045297 | 0.0011352
265 | 0.98834 | -0.22291 | 0.00079218 | 0.00019854
266 | 0.98847 | -0.21993 | 0.0068761 | 0.0017233
267 | 0.97839 | -0.41582 | 0.0017428 | 0.00043678
268 | 0.97835 | -0.4165 | 0.0032153 | 0.00080583
269 | 0.97839 | -0.41582 | 0.0032087 | 0.00080417
270 | 0.97835 | -0.41653 | 0.0029128 | 0.00073002
271 | 0.98667 | -0.25474 | 0.011376 | 0.0028512
272 | 0.98665 | -0.25507 | 0.0068892 | 0.0017266
273 | 0.98766 | -0.236 | 0.0025237 | 0.00063249
274 | 0.98522 | -0.28345 | 0.0010232 | 0.00025644
275 | 0.98525 | -0.28303 | 0.0020225 | 0.00050688
276 | 0.98533 | -0.28131 | 0.0042675 | 0.0010695
277 | 0.98546 | -0.2788 | 0.0016596 | 0.00041593
278 | 0.98554 | -0.27722 | 0.0015693 | 0.0003933
279 | 0.98877 | -0.21446 | 0.0018955 | 0.00047506
280 | 0.98885 | -0.21284 | 0.0034126 | 0.00085527
281 | 0.98876 | -0.21462 | 0 | 0
282 | 0.98867 | -0.21647 | 0.0025805 | 0.00064672
283 | 0.98861 | -0.21768 | 0.0014865 | 0.00037254
284 | 0.9856 | -0.27617 | 0.0012638 | 0.00031674
285 | 0.9856 | -0.27617 | 0.0012041 | 0.00030176
286 | 0.99177 | -0.15679 | 0 | 0
287 | 0.99166 | -0.15883 | 0.0012941 | 0.00032433
288 | 0.99164 | -0.15929 | 0.0016653 | 0.00041737
289 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0014266 | -0.00035287 | 0.0014268 | 0.00035124 | 2.5927e-07 | -1.6222e-06 | 0.002186 | 0.0021853 | 0.002186 | 0.97034 | -0.57467 | 0.97053 | -0.57082 | 0.60054
1 | 0.00091714 | 0.00022519 | -0.00091689 | -0.00022911 | 2.4437e-07 | -3.9173e-06 | 0.0014048 | 0.0014062 | 0.0014062 | 0.97034 | -0.57467 | 0.97006 | -0.58032 | 0.38632
2 | -0.0014268 | -0.00035124 | 0.001427 | 0.00035013 | 1.7733e-07 | -1.1105e-06 | 0.0021853 | 0.0021849 | 0.0021853 | 0.97053 | -0.57082 | 0.97066 | -0.56817 | 0.60037
3 | 0.00091689 | 0.00022911 | -0.00091685 | -0.00022978 | 4.2305e-08 | -6.7706e-07 | 0.0014062 | 0.0014065 | 0.0014065 | 0.97006 | -0.58032 | 0.97001 | -0.58129 | 0.38639
4 | -0.0027225 | -0.00068184 | 0.0027226 | 0.00068177 | 5.6082e-08 | -7.0228e-08 | 0.0041736 | 0.0041736 | 0.0041736 | 0.97063 | -0.56944 | 0.97065 | -0.569 | 1.1466
5 | 0.00079016 | 0.00019754 | -0.00079015 | -0.0001979 | 1.6443e-08 | -3.5887e-07 | 0.0012112 | 0.0012113 | 0.0012113 | 0.97063 | -0.56944 | 0.9706 | -0.56987 | 0.33278
6 | -0.0038187 | -0.00095649 | 0.00382 | 0.00095607 | 1.3023e-06 | -4.1969e-07 | 0.005854 | 0.0058535 | 0.005854 | 0.97065 | -0.569 | 0.97101 | -0.56184 | 1.6082
7 | 0.00079015 | 0.0001979 | -0.00079014 | -0.00019803 | 5.8724e-09 | -1.2814e-07 | 0.0012113 | 0.0012114 | 0.0012114 | 0.9706 | -0.56987 | 0.9706 | -0.57003 | 0.33279
8 | -0.0039239 | -0.0009821 | 0.0039255 | 0.00098168 | 1.5379e-06 | -4.1964e-07 | 0.0060127 | 0.0060122 | 0.0060127 | 0.97101 | -0.56184 | 0.97143 | -0.5536 | 1.6518
9 | 0.0019449 | 0.00048598 | -0.0019448 | -0.00048642 | 1.4534e-07 | -4.4768e-07 | 0.0029787 | 0.0029789 | 0.0029789 | 0.97143 | -0.5536 | 0.97135 | -0.55518 | 0.81838
10 | -0.0065048 | -0.0016267 | 0.0065123 | 0.001629 | 7.4716e-06 | 2.2933e-06 | 0.0099627 | 0.0099618 | 0.0099627 | 0.97143 | -0.5536 | 0.97264 | -0.52947 | 2.737
11 | 0.0016166 | 0.00040417 | -0.0016166 | -0.00040421 | 7.7094e-09 | -3.657e-08 | 0.0024762 | 0.0024762 | 0.0024762 | 0.97135 | -0.55518 | 0.97134 | -0.55528 | 0.68027
12 | -0.0065123 | -0.001629 | 0.0065155 | 0.0016299 | 3.2424e-06 | 9.9313e-07 | 0.0099618 | 0.0099614 | 0.0099618 | 0.97264 | -0.52947 | 0.97317 | -0.51901 | 2.7368
13 | 0.00038492 | 9.552e-05 | -0.00038491 | -9.6292e-05 | 8.1876e-09 | -7.7254e-07 | 0.00058932 | 0.0005896 | 0.0005896 | 0.97134 | -0.55528 | 0.97132 | -0.55573 | 0.16198
14 | 0.00038491 | 9.6292e-05 | -0.00038491 | -9.6468e-05 | 1.8564e-09 | -1.7505e-07 | 0.0005896 | 0.00058967 | 0.00058967 | 0.97132 | -0.55573 | 0.97131 | -0.55583 | 0.162
15 | -0.0068377 | -0.0017107 | 0.0068406 | 0.0017117 | 2.8875e-06 | 9.7216e-07 | 0.010454 | 0.010454 | 0.010454 | 0.97317 | -0.51901 | 0.97362 | -0.51013 | 2.872
16 | -0.0068406 | -0.0017117 | 0.006846 | 0.0017135 | 5.4486e-06 | 1.8321e-06 | 0.010454 | 0.010453 | 0.010454 | 0.97362 | -0.51013 | 0.97447 | -0.4934 | 2.8719
17 | -0.0071119 | -0.0017801 | 0.0071144 | 0.001781 | 2.558e-06 | 9.1617e-07 | 0.010859 | 0.010859 | 0.010859 | 0.97447 | -0.4934 | 0.97485 | -0.48584 | 2.9833
18 | 0.00077076 | 0.00019302 | -0.00077076 | -0.00019302 | 1.598e-10 | -3.7338e-09 | 0.0011767 | 0.0011767 | 0.0011767 | 0.97462 | -0.49047 | 0.97462 | -0.49047 | 0.32327
19 | -0.00077076 | -0.00019302 | 0.0007708 | 0.00019204 | 4.1759e-08 | -9.7583e-07 | 0.0011767 | 0.0011764 | 0.0011767 | 0.97462 | -0.49047 | 0.97467 | -0.48933 | 0.32327
20 | 0.00062147 | 0.0001556 | -0.00062146 | -0.00015575 | 4.0842e-09 | -1.4815e-07 | 0.00094878 | 0.00094884 | 0.00094884 | 0.97462 | -0.49047 | 0.97461 | -0.49061 | 0.26067
21 | -0.001021 | -0.00025475 | 0.0010212 | 0.00025255 | 1.6838e-07 | -2.1983e-06 | 0.0015583 | 0.0015575 | 0.0015583 | 0.97467 | -0.48933 | 0.97485 | -0.48584 | 0.42811
22 | -0.014072 | -0.0035316 | 0.014081 | 0.0035365 | 8.615e-06 | 4.8804e-06 | 0.021378 | 0.021378 | 0.021378 | 0.97955 | -0.39341 | 0.9802 | -0.38058 | 5.8731
23 | 0.011539 | 0.0028969 | -0.011532 | -0.0028928 | 7.7539e-06 | 4.1163e-06 | 0.017531 | 0.017531 | 0.017531 | 0.97955 | -0.39341 | 0.97883 | -0.4075 | 4.8163
24 | -0.01586 | -0.0039817 | 0.015881 | 0.0039937 | 2.0635e-05 | 1.2009e-05 | 0.02408 | 0.024079 | 0.02408 | 0.9802 | -0.38058 | 0.9816 | -0.35334 | 6.6153
25 | 0.0017798 | 0.00044518 | -0.0017796 | -0.00044601 | 2.0941e-07 | -8.3017e-07 | 0.0027016 | 0.0027019 | 0.0027019 | 0.9802 | -0.38058 | 0.98008 | -0.38305 | 0.74228
26 | 0.00061588 | 0.00015352 | -0.00061586 | -0.00015435 | 2.21e-08 | -8.3113e-07 | 0.00093597 | 0.00093627 | 0.00093627 | 0.97883 | -0.4075 | 0.97879 | -0.40826 | 0.25722
27 | 0.010916 | 0.0027393 | -0.01091 | -0.0027364 | 5.5884e-06 | 2.8968e-06 | 0.016595 | 0.016596 | 0.016596 | 0.97883 | -0.4075 | 0.97828 | -0.41824 | 4.5593
28 | 0.0024251 | 0.00060668 | -0.0024246 | -0.00060765 | 5.2621e-07 | -9.7553e-07 | 0.0036758 | 0.0036763 | 0.0036763 | 0.9816 | -0.35334 | 0.98136 | -0.35789 | 1.01
29 | -0.018306 | -0.0046004 | 0.018323 | 0.0046104 | 1.6825e-05 | 1.0031e-05 | 0.027755 | 0.027755 | 0.027755 | 0.9816 | -0.35334 | 0.98258 | -0.3341 | 7.625
30 | 0.010113 | 0.0025367 | -0.0101 | -0.0025299 | 1.3686e-05 | 6.8259e-06 | 0.015384 | 0.015384 | 0.015384 | 0.97828 | -0.41824 | 0.97684 | -0.44667 | 4.2265
31 | -0.00035953 | -9.0106e-05 | 0.00035954 | 8.8719e-05 | 1.2672e-08 | -1.3865e-06 | 0.00054933 | 0.00054884 | 0.00054933 | 0.97387 | -0.50489 | 0.97391 | -0.50415 | 0.15092
32 | -0.0013856 | -0.00034249 | 0.0013858 | 0.00034142 | 1.5851e-07 | -1.0744e-06 | 0.0021154 | 0.002115 | 0.0021154 | 0.97391 | -0.50415 | 0.97403 | -0.50172 | 0.58115
33 | 0.00071505 | 0.00017581 | -0.00071492 | -0.00017918 | 1.2369e-07 | -3.3628e-06 | 0.0010913 | 0.0010925 | 0.0010925 | 0.97391 | -0.50415 | 0.97373 | -0.50781 | 0.30014
34 | -0.018754 | -0.0047185 | 0.018778 | 0.0047298 | 2.3965e-05 | 1.132e-05 | 0.028408 | 0.028406 | 0.028408 | 0.98258 | -0.3341 | 0.98395 | -0.30739 | 3.9022
35 | 0.0101 | 0.0025299 | -0.010099 | -0.0025294 | 9.6654e-07 | 4.8227e-07 | 0.015384 | 0.015384 | 0.015384 | 0.97684 | -0.44667 | 0.97673 | -0.44867 | 4.2265
36 | -0.021539 | -0.0054208 | 0.02154 | 0.0054206 | 1.1549e-06 | -1.822e-07 | 0.032581 | 0.032581 | 0.032581 | 0.98395 | -0.30739 | 0.98401 | -0.30626 | 1.7902
37 | 0.0027606 | 0.00069094 | -0.00276 | -0.00069172 | 6.031e-07 | -7.8585e-07 | 0.0041745 | 0.0041749 | 0.0041749 | 0.98395 | -0.30739 | 0.98372 | -0.31197 | 1.147
38 | 0.0094464 | 0.0023659 | -0.00943 | -0.002358 | 1.6451e-05 | 7.8826e-06 | 0.014391 | 0.014392 | 0.014392 | 0.97673 | -0.44867 | 0.97488 | -0.4853 | 3.9538
39 | 0.0083558 | 0.0020888 | -0.0083556 | -0.0020887 | 2.1459e-07 | 9.3465e-08 | 0.012752 | 0.012752 | 0.012752 | 0.97488 | -0.4853 | 0.97485 | -0.48584 | 3.5033
40 | -0.0097758 | -0.0024435 | 0.0097842 | 0.0024477 | 8.3805e-06 | 4.1256e-06 | 0.014965 | 0.014964 | 0.014965 | 0.97191 | -0.54335 | 0.97282 | -0.52534 | 4.1112
41 | 0.0073625 | 0.0018387 | -0.0073561 | -0.0018363 | 6.3543e-06 | 2.415e-06 | 0.01127 | 0.01127 | 0.01127 | 0.97191 | -0.54335 | 0.971 | -0.56153 | 3.0963
42 | -0.010958 | -0.0027418 | 0.010963 | 0.0027443 | 4.7226e-06 | 2.4655e-06 | 0.01676 | 0.016759 | 0.01676 | 0.97282 | -0.52534 | 0.97328 | -0.51628 | 4.6043
43 | 0.0066878 | 0.0016688 | -0.0066857 | -0.0016681 | 2.1073e-06 | 6.8683e-07 | 0.010246 | 0.010246 | 0.010246 | 0.971 | -0.56153 | 0.97066 | -0.56817 | 2.815
44 | -0.012493 | -0.0031259 | 0.012496 | 0.0031279 | 3.6763e-06 | 2.0187e-06 | 0.019098 | 0.019098 | 0.019098 | 0.97328 | -0.51628 | 0.97359 | -0.5101 | 5.2467
45 | 0.0015301 | 0.00038164 | -0.00153 | -0.00038198 | 6.2723e-08 | -3.3988e-07 | 0.0023387 | 0.0023388 | 0.0023388 | 0.97328 | -0.51628 | 0.97324 | -0.51714 | 0.64252
46 | -0.013453 | -0.0033678 | 0.013454 | 0.0033683 | 9.945e-07 | 5.5846e-07 | 0.02056 | 0.02056 | 0.02056 | 0.97359 | -0.5101 | 0.97367 | -0.50855 | 5.6484
47 | 0.0008723 | 0.00021713 | -0.00087228 | -0.00021757 | 2.4236e-08 | -4.3628e-07 | 0.0013332 | 0.0013333 | 0.0013333 | 0.97324 | -0.51714 | 0.97321 | -0.51773 | 0.3663
48 | -0.013783 | -0.0034507 | 0.013785 | 0.0034517 | 1.8322e-06 | 1.0356e-06 | 0.021062 | 0.021062 | 0.021062 | 0.97367 | -0.50855 | 0.97381 | -0.50575 | 5.7864
49 | 0.00087228 | 0.00021757 | -0.00087222 | -0.0002186 | 5.7232e-08 | -1.0297e-06 | 0.0013333 | 0.0013337 | 0.0013337 | 0.97321 | -0.51773 | 0.97314 | -0.51911 | 0.3664
50 | 0.0020294 | 0.00050028 | -0.002029 | -0.00050132 | 3.6714e-07 | -1.0367e-06 | 0.0030961 | 0.0030966 | 0.0030966 | 0.97439 | -0.49469 | 0.97419 | -0.49853 | 0.85071
51 | -0.0046903 | -0.0011672 | 0.0046916 | 0.0011672 | 1.2427e-06 | -1.0144e-08 | 0.0071598 | 0.0071595 | 0.0071598 | 0.97439 | -0.49469 | 0.97467 | -0.48909 | 1.967
52 | 0.0015429 | 0.00037949 | -0.0015427 | -0.00038073 | 2.3158e-07 | -1.2387e-06 | 0.0023541 | 0.0023546 | 0.0023546 | 0.97419 | -0.49853 | 0.97403 | -0.50172 | 0.64687
53 | -0.007914 | -0.0019748 | 0.0079159 | 0.0019756 | 1.9292e-06 | 7.9512e-07 | 0.012079 | 0.012079 | 0.012079 | 0.97467 | -0.48909 | 0.97493 | -0.48396 | 3.3184
54 | -0.0096147 | -0.0024013 | 0.0096167 | 0.0024023 | 2.003e-06 | 9.7242e-07 | 0.014672 | 0.014672 | 0.014672 | 0.97493 | -0.48396 | 0.97515 | -0.47958 | 4.0307
55 | -0.0016491 | -0.00041331 | 0.0016492 | 0.00041304 | 5.755e-08 | -2.6539e-07 | 0.0025168 | 0.0025166 | 0.0025168 | 0.97504 | -0.48157 | 0.97507 | -0.48084 | 0.69142
56 | -0.0059334 | -0.0014868 | 0.0059343 | 0.001487 | 8.6483e-07 | 2.0256e-07 | 0.0090546 | 0.0090545 | 0.0090546 | 0.97507 | -0.48084 | 0.97523 | -0.47778 | 2.4875
57 | -0.025034 | -0.0062783 | 0.02504 | 0.0062798 | 5.5912e-06 | 1.5379e-06 | 0.038199 | 0.038198 | 0.038199 | 0.97523 | -0.47778 | 0.97547 | -0.47309 | 2.6235
58 | 0.0191 | 0.0047913 | -0.019091 | -0.0047861 | 8.5892e-06 | 5.1608e-06 | 0.029144 | 0.029144 | 0.029144 | 0.97523 | -0.47778 | 0.97475 | -0.48722 | 8.0067
59 | -0.028538 | -0.0071565 | 0.028539 | 0.0071567 | 1.3895e-06 | 2.7908e-07 | 0.043534 | 0.043534 | 0.043534 | 0.97547 | -0.47309 | 0.97552 | -0.47207 | 2.392
60 | 0.018642 | 0.0046736 | -0.018642 | -0.0046734 | 4.1793e-07 | 2.5032e-07 | 0.028459 | 0.028459 | 0.028459 | 0.97475 | -0.48722 | 0.97473 | -0.48769 | 7.8184
61 | -0.022187 | -0.0055828 | 0.022188 | 0.0055826 | 1.2584e-06 | -1.4096e-07 | 0.033559 | 0.033559 | 0.033559 | 0.98401 | -0.30626 | 0.98407 | -0.30508 | 1.8439
62 | -0.031305 | -0.0078675 | 0.031306 | 0.0078677 | 8.6802e-07 | 2.2733e-07 | 0.047337 | 0.047337 | 0.047337 | 0.98421 | -0.30225 | 0.98424 | -0.30167 | 2.6009
63 | 0.031305 | 0.0078675 | -0.031301 | -0.0078664 | 4.2227e-06 | 1.1062e-06 | 0.047337 | 0.047337 | 0.047337 | 0.98421 | -0.30225 | 0.98407 | -0.30508 | 2.601
64 | -0.031306 | -0.0078677 | 0.031308 | 0.0078684 | 2.8049e-06 | 7.3443e-07 | 0.047337 | 0.047336 | 0.047337 | 0.98424 | -0.30167 | 0.98434 | -0.29979 | 2.6009
65 | -0.043906 | -0.011022 | 0.043919 | 0.011028 | 1.3396e-05 | 5.9961e-06 | 0.066378 | 0.066378 | 0.066378 | 0.98434 | -0.29979 | 0.98467 | -0.2934 | 3.6472
66 | 0.010909 | 0.0027305 | -0.010908 | -0.0027334 | 1.1919e-06 | -2.9509e-06 | 0.01649 | 0.016491 | 0.016491 | 0.98434 | -0.29979 | 0.98422 | -0.30209 | 0.90613
67 | -0.014807 | -0.003708 | 0.014811 | 0.0037101 | 3.7156e-06 | 2.1371e-06 | 0.022625 | 0.022625 | 0.022625 | 0.97381 | -0.50575 | 0.97408 | -0.50048 | 6.2156
68 | -0.010039 | -0.0025081 | 0.01004 | 0.0025088 | 1.3964e-06 | 6.9563e-07 | 0.015316 | 0.015316 | 0.015316 | 0.97515 | -0.47958 | 0.9753 | -0.47665 | 4.2076
69 | -0.01004 | -0.0025088 | 0.010044 | 0.0025104 | 3.3084e-06 | 1.6479e-06 | 0.015316 | 0.015316 | 0.015316 | 0.9753 | -0.47665 | 0.97565 | -0.46972 | 4.2076
70 | -0.010509 | -0.0026272 | 0.010513 | 0.0026293 | 4.0672e-06 | 2.0754e-06 | 0.016026 | 0.016026 | 0.016026 | 0.97565 | -0.46972 | 0.97606 | -0.46158 | 4.4028
71 | -0.015003 | -0.0037544 | 0.015006 | 0.0037565 | 3.7362e-06 | 2.153e-06 | 0.02287 | 0.022869 | 0.02287 | 0.97606 | -0.46158 | 0.97632 | -0.45635 | 6.2829
72 | -0.02003 | -0.0050155 | 0.020037 | 0.0050199 | 7.3527e-06 | 4.4425e-06 | 0.030526 | 0.030525 | 0.030526 | 0.97632 | -0.45635 | 0.97672 | -0.44864 | 8.3861
73 | -0.0004707 | -0.00011797 | 0.00047071 | 0.00011762 | 5.4144e-09 | -3.4702e-07 | 0.00071761 | 0.00071748 | 0.00071761 | 0.97603 | -0.46208 | 0.97605 | -0.46184 | 0.19715
74 | 0.0014657 | 0.00036711 | -0.0014657 | -0.00036734 | 3.8679e-08 | -2.3342e-07 | 0.0022345 | 0.0022346 | 0.0022346 | 0.97605 | -0.46184 | 0.97602 | -0.46239 | 0.61389
75 | -0.0019364 | -0.00048473 | 0.0019366 | 0.0004842 | 1.6468e-07 | -5.2457e-07 | 0.002952 | 0.0029517 | 0.002952 | 0.97605 | -0.46184 | 0.97614 | -0.46005 | 0.81098
76 | -0.0023809 | -0.00059556 | 0.002381 | 0.00059542 | 6.9818e-08 | -1.3205e-07 | 0.003629 | 0.003629 | 0.003629 | 0.97614 | -0.46005 | 0.97617 | -0.45944 | 0.99699
77 | -0.0051165 | -0.001281 | 0.0051173 | 0.0012811 | 8.2343e-07 | 7.558e-08 | 0.0077989 | 0.0077987 | 0.0077989 | 0.97617 | -0.45944 | 0.97634 | -0.45606 | 2.1425
78 | -0.01007 | -0.0025223 | 0.010073 | 0.0025239 | 3.344e-06 | 1.6665e-06 | 0.015347 | 0.015346 | 0.015347 | 0.97634 | -0.45606 | 0.97669 | -0.44908 | 4.2161
79 | -0.017132 | -0.0042952 | 0.017138 | 0.0042984 | 5.5274e-06 | 3.2717e-06 | 0.026225 | 0.026225 | 0.026225 | 0.97212 | -0.53915 | 0.97246 | -0.53238 | 7.2047
80 | 0.015142 | 0.0037964 | -0.015141 | -0.0037956 | 1.3349e-06 | 7.7218e-07 | 0.023179 | 0.023179 | 0.023179 | 0.97212 | -0.53915 | 0.97202 | -0.541 | 6.3677
81 | -0.017522 | -0.0043946 | 0.01753 | 0.0043996 | 8.4038e-06 | 4.9915e-06 | 0.026812 | 0.026812 | 0.026812 | 0.97246 | -0.53238 | 0.97297 | -0.52233 | 7.366
82 | 0.0051451 | 0.0012888 | -0.0051445 | -0.0012887 | 6.3623e-07 | 6.8223e-08 | 0.0078762 | 0.0078763 | 0.0078763 | 0.97202 | -0.541 | 0.97189 | -0.5436 | 2.1638
83 | 0.0099957 | 0.0025068 | -0.0099847 | -0.0025013 | 1.0975e-05 | 5.4768e-06 | 0.015302 | 0.015303 | 0.015303 | 0.97202 | -0.541 | 0.97086 | -0.56406 | 4.2041
84 | 0.0053171 | 0.0013312 | -0.0053162 | -0.0013311 | 9.0695e-07 | 1.2624e-07 | 0.0081313 | 0.0081315 | 0.0081315 | 0.97297 | -0.52233 | 0.97279 | -0.52591 | 2.2339
85 | -0.022847 | -0.0057309 | 0.022866 | 0.0057423 | 1.8745e-05 | 1.1488e-05 | 0.034943 | 0.034943 | 0.034943 | 0.97297 | -0.52233 | 0.97384 | -0.50513 | 9.5998
86 | 0.0043855 | 0.0010985 | -0.0043852 | -0.0010986 | 3.7886e-07 | -3.5213e-08 | 0.0067143 | 0.0067144 | 0.0067144 | 0.97189 | -0.5436 | 0.9718 | -0.54541 | 1.8446
87 | 0.001093 | 0.00027283 | -0.0010929 | -0.00027312 | 2.615e-08 | -2.9067e-07 | 0.0016748 | 0.0016749 | 0.0016749 | 0.97086 | -0.56406 | 0.97083 | -0.56456 | 0.46013
88 | 0.0046543 | 0.0011652 | -0.004654 | -0.0011652 | 2.9462e-07 | -3.8947e-09 | 0.0071189 | 0.0071189 | 0.0071189 | 0.97279 | -0.52591 | 0.97272 | -0.52724 | 1.9558
89 | -0.023309 | -0.0058533 | 0.023309 | 0.0058535 | 3.2827e-07 | 2.0151e-07 | 0.03562 | 0.03562 | 0.03562 | 0.97384 | -0.50513 | 0.97386 | -0.50483 | 9.7856
90 | 0.0030772 | 0.00077076 | -0.0030771 | -0.00077091 | 1.7907e-07 | -1.5188e-07 | 0.0047117 | 0.0047118 | 0.0047118 | 0.9718 | -0.54541 | 0.97174 | -0.54663 | 1.2944
91 | 0.0010929 | 0.00027312 | -0.0010929 | -0.0002739 | 7.028e-08 | -7.8092e-07 | 0.0016749 | 0.0016752 | 0.0016752 | 0.97083 | -0.56456 | 0.97077 | -0.56591 | 0.46021
92 | 0.0031528 | 0.000789 | -0.0031526 | -0.00078913 | 1.6943e-07 | -1.327e-07 | 0.0048226 | 0.0048227 | 0.0048227 | 0.97272 | -0.52724 | 0.97266 | -0.52837 | 1.3249
93 | -0.02759 | -0.0069265 | 0.027603 | 0.0069336 | 1.2545e-05 | 7.0915e-06 | 0.042161 | 0.042161 | 0.042161 | 0.97386 | -0.50483 | 0.97434 | -0.49531 | 5.7914
94 | -0.016201 | -0.0040549 | 0.016202 | 0.0040542 | 9.3287e-07 | -6.9075e-07 | 0.024633 | 0.024632 | 0.024633 | 0.97858 | -0.41209 | 0.97864 | -0.41088 | 1.3534
95 | 0.016201 | 0.0040549 | -0.016199 | -0.0040564 | 2.0505e-06 | -1.5175e-06 | 0.024633 | 0.024634 | 0.024634 | 0.97858 | -0.41209 | 0.97844 | -0.41475 | 1.3535
96 | -0.019483 | -0.0048765 | 0.019485 | 0.0048757 | 2.77e-06 | -8.7219e-07 | 0.029621 | 0.02962 | 0.029621 | 0.97864 | -0.41088 | 0.97879 | -0.4079 | 1.6275
97 | 0.013924 | 0.0034864 | -0.013924 | -0.0034865 | 3.8256e-08 | -4.6956e-08 | 0.021175 | 0.021175 | 0.021175 | 0.97844 | -0.41475 | 0.97844 | -0.41481 | 1.1635
98 | 0.0024501 | 0.00061379 | -0.00245 | -0.00061403 | 1.3974e-07 | -2.385e-07 | 0.0037518 | 0.0037519 | 0.0037519 | 0.97174 | -0.54663 | 0.97168 | -0.54783 | 1.0307
99 | -0.00094098 | -0.00023583 | 0.00094101 | 0.00023538 | 2.9336e-08 | -4.4974e-07 | 0.0014396 | 0.0014395 | 0.0014396 | 0.97261 | -0.52946 | 0.97264 | -0.5288 | 0.3955
100 | -0.0013783 | -0.00034498 | 0.0013783 | 0.00034479 | 2.8446e-08 | -1.9358e-07 | 0.0021085 | 0.0021084 | 0.0021085 | 0.97264 | -0.5288 | 0.97266 | -0.52837 | 0.57925
101 | 0.0017743 | 0.00044434 | -0.0017742 | -0.00044466 | 8.2885e-08 | -3.1929e-07 | 0.0027143 | 0.0027144 | 0.0027144 | 0.97266 | -0.52837 | 0.97261 | -0.52935 | 0.74571
102 | -0.030139 | -0.0075693 | 0.030142 | 0.0075699 | 2.4835e-06 | 6.163e-07 | 0.046035 | 0.046034 | 0.046035 | 0.97434 | -0.49531 | 0.97443 | -0.49358 | 2.5294
103 | -0.019485 | -0.0048757 | 0.019487 | 0.0048751 | 1.7569e-06 | -5.537e-07 | 0.02962 | 0.02962 | 0.02962 | 0.97879 | -0.4079 | 0.97889 | -0.406 | 1.6275
104 | 0.01108 | 0.0027737 | -0.01108 | -0.0027749 | 5.3089e-07 | -1.2258e-06 | 0.01685 | 0.01685 | 0.01685 | 0.97844 | -0.41481 | 0.97839 | -0.41582 | 0.92584
105 | -0.0013824 | -0.00034647 | 0.0013827 | 0.00034486 | 2.3627e-07 | -1.6097e-06 | 0.0021114 | 0.0021107 | 0.0021114 | 0.97429 | -0.49627 | 0.97447 | -0.49268 | 0.58005
106 | -0.0086597 | -0.002169 | 0.008661 | 0.0021696 | 1.2753e-06 | 5.7381e-07 | 0.013223 | 0.013223 | 0.013223 | 0.97447 | -0.49268 | 0.97463 | -0.48958 | 3.6326
107 | 0.007277 | 0.0018242 | -0.0072736 | -0.0018229 | 3.4375e-06 | 1.2757e-06 | 0.011112 | 0.011112 | 0.011112 | 0.97447 | -0.49268 | 0.97397 | -0.50259 | 3.0529
108 | -0.040047 | -0.010052 | 0.040048 | 0.010052 | 8.4915e-07 | 3.5477e-07 | 0.061148 | 0.061148 | 0.061148 | 0.97463 | -0.48958 | 0.97465 | -0.48914 | 3.3598
109 | 0.031386 | 0.007882 | -0.03138 | -0.0078803 | 5.9821e-06 | 1.6652e-06 | 0.047925 | 0.047926 | 0.047926 | 0.97463 | -0.48958 | 0.97443 | -0.49358 | 2.6333
110 | 0.00562 | 0.0014085 | -0.0056192 | -0.0014083 | 8.0233e-07 | 1.5237e-07 | 0.0085861 | 0.0085862 | 0.0085862 | 0.97397 | -0.50259 | 0.97382 | -0.50559 | 2.3589
111 | -0.04289 | -0.010764 | 0.042896 | 0.010767 | 6.2323e-06 | 2.781e-06 | 0.065486 | 0.065485 | 0.065486 | 0.97465 | -0.48914 | 0.97481 | -0.48609 | 3.5981
112 | -0.045275 | -0.011363 | 0.045279 | 0.011365 | 4.4755e-06 | 2.0856e-06 | 0.069117 | 0.069116 | 0.069117 | 0.97481 | -0.48609 | 0.97491 | -0.48402 | 3.7976
113 | 0.030889 | 0.0077605 | -0.030872 | -0.0077495 | 1.7707e-05 | 1.1057e-05 | 0.046698 | 0.046698 | 0.046698 | 0.98443 | -0.29864 | 0.98381 | -0.31065 | 12.8291
114 | -0.033825 | -0.0084959 | 0.033849 | 0.008511 | 2.4102e-05 | 1.5112e-05 | 0.051134 | 0.051134 | 0.051134 | 0.98443 | -0.29864 | 0.98519 | -0.28372 | 14.0479
115 | 0.0029353 | 0.00073536 | -0.002935 | -0.00073559 | 2.1657e-07 | -2.3437e-07 | 0.0044367 | 0.0044368 | 0.0044368 | 0.98443 | -0.29864 | 0.98435 | -0.30019 | 1.2189
116 | 0.025022 | 0.0062834 | -0.025009 | -0.0062755 | 1.2895e-05 | 7.948e-06 | 0.03785 | 0.03785 | 0.03785 | 0.98381 | -0.31065 | 0.98326 | -0.32146 | 10.3984
117 | -0.035626 | -0.0089564 | 0.035656 | 0.0089754 | 3.0255e-05 | 1.9008e-05 | 0.053819 | 0.053818 | 0.053819 | 0.98519 | -0.28372 | 0.98611 | -0.26595 | 14.7853
118 | 0.023524 | 0.0059033 | -0.02352 | -0.0059005 | 4.6919e-06 | 2.8777e-06 | 0.035603 | 0.035603 | 0.035603 | 0.98326 | -0.32146 | 0.98304 | -0.32564 | 9.7811
119 | 0.064994 | 0.016412 | -0.064934 | -0.016373 | 6.0588e-05 | 3.8563e-05 | 0.098119 | 0.098119 | 0.098119 | 0.98611 | -0.26595 | 0.9851 | -0.28542 | 26.9558
120 | -0.10065 | -0.025387 | 0.1007 | 0.025422 | 5.4305e-05 | 3.4435e-05 | 0.15194 | 0.15194 | 0.15194 | 0.98611 | -0.26595 | 0.98669 | -0.25468 | 20.8705
121 | 0.031598 | 0.0079332 | -0.031597 | -0.0079327 | 8.7773e-07 | 5.4885e-07 | 0.047903 | 0.047903 | 0.047903 | 0.98162 | -0.35328 | 0.98159 | -0.35386 | 13.1603
122 | -0.034389 | -0.0086328 | 0.034406 | 0.0086438 | 1.7537e-05 | 1.1006e-05 | 0.052134 | 0.052134 | 0.052134 | 0.98162 | -0.35328 | 0.98217 | -0.3426 | 14.3226
123 | 0.028666 | 0.0071981 | -0.028653 | -0.0071902 | 1.2636e-05 | 7.8616e-06 | 0.04346 | 0.04346 | 0.04346 | 0.98159 | -0.35386 | 0.98112 | -0.36311 | 11.9395
124 | -0.060497 | -0.015197 | 0.060584 | 0.015252 | 8.6952e-05 | 5.5299e-05 | 0.091668 | 0.091668 | 0.091668 | 0.98217 | -0.3426 | 0.98371 | -0.31253 | 25.1834
125 | 0.026091 | 0.0065528 | -0.026081 | -0.0065467 | 9.8645e-06 | 6.1004e-06 | 0.039533 | 0.039533 | 0.039533 | 0.98217 | -0.3426 | 0.98176 | -0.35052 | 10.8608
126 | 0.025764 | 0.0064661 | -0.025756 | -0.0064611 | 7.9426e-06 | 4.9082e-06 | 0.039078 | 0.039078 | 0.039078 | 0.98112 | -0.36311 | 0.98079 | -0.36957 | 10.7357
127 | -0.06276 | -0.015797 | 0.062841 | 0.015849 | 8.1415e-05 | 5.18e-05 | 0.094959 | 0.094959 | 0.094959 | 0.98371 | -0.31253 | 0.9851 | -0.28542 | 26.0876
128 | 0.021849 | 0.005486 | -0.021835 | -0.0054775 | 1.3947e-05 | 8.4977e-06 | 0.033119 | 0.033119 | 0.033119 | 0.98176 | -0.35052 | 0.98108 | -0.36391 | 9.0986
129 | 0.02258 | 0.0056651 | -0.022569 | -0.0056586 | 1.0586e-05 | 6.4716e-06 | 0.034259 | 0.034259 | 0.034259 | 0.98079 | -0.36957 | 0.98029 | -0.37941 | 9.4119
130 | 0.020271 | 0.0050856 | -0.020268 | -0.0050839 | 2.8809e-06 | 1.7412e-06 | 0.030747 | 0.030747 | 0.030747 | 0.98108 | -0.36391 | 0.98092 | -0.36689 | 8.447
131 | 0.019484 | 0.0048855 | -0.019483 | -0.0048849 | 1.0854e-06 | 6.5293e-07 | 0.029577 | 0.029577 | 0.029577 | 0.98029 | -0.37941 | 0.98023 | -0.38058 | 8.1255
132 | 0.020268 | 0.0050839 | -0.020266 | -0.0050824 | 2.463e-06 | 1.4886e-06 | 0.030747 | 0.030747 | 0.030747 | 0.98092 | -0.36689 | 0.98079 | -0.36944 | 8.447
133 | -0.0027797 | -0.00069666 | 0.0027798 | 0.00069656 | 8.1568e-08 | -1.012e-07 | 0.0042237 | 0.0042237 | 0.0042237 | 0.97929 | -0.39902 | 0.97932 | -0.3984 | 1.1604
134 | -0.005709 | -0.0014307 | 0.0057109 | 0.001431 | 1.8983e-06 | 3.681e-07 | 0.0086744 | 0.0086741 | 0.0086744 | 0.97932 | -0.3984 | 0.97967 | -0.39142 | 2.3831
135 | -0.0099624 | -0.0024966 | 0.0099643 | 0.0024975 | 1.8135e-06 | 8.9465e-07 | 0.015132 | 0.015132 | 0.015132 | 0.97967 | -0.39142 | 0.97987 | -0.3876 | 4.1571
136 | 0.0018724 | 0.00046926 | -0.0018724 | -0.00046926 | 2.6691e-10 | -9.3911e-10 | 0.0028439 | 0.0028439 | 0.0028439 | 0.97967 | -0.39142 | 0.97967 | -0.39142 | 0.7813
137 | -0.012579 | -0.0031528 | 0.01258 | 0.0031531 | 6.5184e-07 | 3.5717e-07 | 0.019102 | 0.019102 | 0.019102 | 0.97987 | -0.3876 | 0.97992 | -0.38651 | 5.2479
138 | 0.016384 | 0.0041081 | -0.016379 | -0.0041054 | 4.6303e-06 | 2.7119e-06 | 0.024872 | 0.024872 | 0.024872 | 0.98023 | -0.38058 | 0.97992 | -0.38651 | 6.8329
139 | 0.014336 | 0.0035945 | -0.014334 | -0.003593 | 2.72e-06 | 1.5476e-06 | 0.021758 | 0.021758 | 0.021758 | 0.98047 | -0.37587 | 0.98026 | -0.37985 | 5.9775
140 | -0.017507 | -0.0043893 | 0.017513 | 0.0043924 | 5.3594e-06 | 3.1746e-06 | 0.026571 | 0.026571 | 0.026571 | 0.98047 | -0.37587 | 0.98079 | -0.36944 | 7.2996
141 | 0.011478 | 0.0028772 | -0.011476 | -0.0028763 | 1.6565e-06 | 8.7674e-07 | 0.017423 | 0.017423 | 0.017423 | 0.98026 | -0.37985 | 0.98011 | -0.38288 | 4.7865
142 | 0.0094031 | 0.0023568 | -0.0094013 | -0.0023559 | 1.8623e-06 | 8.8486e-07 | 0.014276 | 0.014276 | 0.014276 | 0.98011 | -0.38288 | 0.9799 | -0.38704 | 3.922
143 | 0.0059155 | 0.0014823 | -0.0059153 | -0.0014823 | 1.5981e-07 | 3.5751e-08 | 0.0089828 | 0.0089828 | 0.0089828 | 0.9799 | -0.38704 | 0.97987 | -0.3876 | 2.4678
144 | 0.0025934 | 0.00064975 | -0.0025933 | -0.00064994 | 1.2545e-07 | -1.9139e-07 | 0.0039382 | 0.0039383 | 0.0039383 | 0.97987 | -0.3876 | 0.97982 | -0.38862 | 1.082
145 | -0.13017 | -0.032964 | 0.13033 | 0.033066 | 0.00016381 | 0.00010117 | 0.19575 | 0.19575 | 0.19575 | 0.99012 | -0.18828 | 0.99148 | -0.16211 | 10.7555
146 | 0.13017 | 0.032964 | -0.13008 | -0.03291 | 8.8731e-05 | 5.4804e-05 | 0.19575 | 0.19575 | 0.19575 | 0.99012 | -0.18828 | 0.98939 | -0.20249 | 10.7555
147 | -0.13255 | -0.033622 | 0.13263 | 0.033669 | 7.6941e-05 | 4.7572e-05 | 0.19908 | 0.19908 | 0.19908 | 0.99148 | -0.16211 | 0.99211 | -0.15005 | 10.9384
148 | 0.12946 | 0.032754 | -0.12944 | -0.032743 | 1.8261e-05 | 1.1275e-05 | 0.19482 | 0.19482 | 0.19482 | 0.98939 | -0.20249 | 0.98923 | -0.20543 | 10.7043
149 | -0.0047785 | -0.0011974 | 0.0047786 | 0.0011974 | 7.1694e-08 | -8.8829e-10 | 0.007216 | 0.0072159 | 0.007216 | 0.98538 | -0.28013 | 0.9854 | -0.27981 | 1.9824
150 | 0.0025115 | 0.00062928 | -0.0025114 | -0.00062942 | 8.2632e-08 | -1.4226e-07 | 0.0037925 | 0.0037926 | 0.0037926 | 0.98538 | -0.28013 | 0.98535 | -0.28082 | 1.0419
151 | -0.0063922 | -0.0016019 | 0.0063929 | 0.001602 | 6.6237e-07 | 1.8239e-07 | 0.0096527 | 0.0096526 | 0.0096527 | 0.9854 | -0.27981 | 0.98551 | -0.27764 | 2.6518
152 | -0.01612 | -0.0040404 | 0.016125 | 0.004043 | 4.4323e-06 | 2.5824e-06 | 0.02434 | 0.02434 | 0.02434 | 0.98551 | -0.27764 | 0.9858 | -0.27187 | 6.6869
153 | 0.0097276 | 0.0024384 | -0.0097271 | -0.0024381 | 4.8523e-07 | 2.3413e-07 | 0.014688 | 0.014688 | 0.014688 | 0.98551 | -0.27764 | 0.98545 | -0.27869 | 4.0351
154 | -0.018199 | -0.0045628 | 0.018205 | 0.0045662 | 5.6644e-06 | 3.3699e-06 | 0.027471 | 0.027471 | 0.027471 | 0.9858 | -0.27187 | 0.98614 | -0.26534 | 7.5469
155 | 0.0083697 | 0.0020979 | -0.0083681 | -0.0020973 | 1.5708e-06 | 6.7127e-07 | 0.012638 | 0.012638 | 0.012638 | 0.98545 | -0.27869 | 0.98525 | -0.28263 | 3.4721
156 | -0.019033 | -0.0047738 | 0.019035 | 0.0047748 | 1.7588e-06 | 1.0531e-06 | 0.028721 | 0.028721 | 0.028721 | 0.98614 | -0.26534 | 0.98624 | -0.2634 | 7.8903
157 | 0.0065432 | 0.0016399 | -0.0065428 | -0.0016398 | 4.6174e-07 | 1.3496e-07 | 0.0098822 | 0.0098822 | 0.0098822 | 0.98525 | -0.28263 | 0.98518 | -0.28411 | 2.7149
158 | -0.015468 | -0.003878 | 0.01547 | 0.0038791 | 1.8964e-06 | 1.0971e-06 | 0.023431 | 0.023431 | 0.023431 | 0.98232 | -0.33967 | 0.98246 | -0.3371 | 6.4372
159 | 0.01439 | 0.003608 | -0.014388 | -0.0036064 | 2.7438e-06 | 1.5612e-06 | 0.021799 | 0.021799 | 0.021799 | 0.98232 | -0.33967 | 0.98212 | -0.34367 | 5.9888
160 | -0.016863 | -0.0042284 | 0.016865 | 0.004229 | 1.0813e-06 | 6.3608e-07 | 0.025542 | 0.025542 | 0.025542 | 0.98246 | -0.3371 | 0.98252 | -0.33575 | 7.017
161 | 0.012742 | 0.0031939 | -0.012741 | -0.0031937 | 2.9491e-07 | 1.6204e-07 | 0.019305 | 0.019305 | 0.019305 | 0.98212 | -0.34367 | 0.9821 | -0.34416 | 5.3036
162 | -0.020721 | -0.0051956 | 0.020731 | 0.0052017 | 9.9847e-06 | 6.0477e-06 | 0.031383 | 0.031383 | 0.031383 | 0.98252 | -0.33575 | 0.98304 | -0.32564 | 8.6217
163 | 0.0097867 | 0.0024532 | -0.0097844 | -0.0024521 | 2.2839e-06 | 1.1113e-06 | 0.014828 | 0.014829 | 0.014829 | 0.9821 | -0.34416 | 0.98185 | -0.34906 | 4.0738
164 | 0.0065833 | 0.0016498 | -0.0065832 | -0.0016498 | 7.1141e-08 | 2.1428e-08 | 0.0099772 | 0.0099772 | 0.0099772 | 0.98185 | -0.34906 | 0.98183 | -0.34928 | 2.741
165 | 0.0049386 | 0.0012376 | -0.0049382 | -0.0012376 | 3.7626e-07 | 1.4307e-08 | 0.0074846 | 0.0074847 | 0.0074847 | 0.98183 | -0.34928 | 0.98175 | -0.35088 | 2.0562
166 | 0.12793 | 0.032364 | -0.12785 | -0.032315 | 7.8015e-05 | 4.8129e-05 | 0.19254 | 0.19254 | 0.19254 | 0.98923 | -0.20543 | 0.98857 | -0.21814 | 10.5793
167 | 0.0026612 | 0.0006666 | -0.002661 | -0.00066691 | 2.1144e-07 | -3.1518e-07 | 0.0040056 | 0.0040058 | 0.0040058 | 0.98857 | -0.21814 | 0.98849 | -0.21981 | 1.1005
168 | 0.12519 | 0.031649 | -0.12517 | -0.031637 | 2.0022e-05 | 1.2333e-05 | 0.18854 | 0.18854 | 0.18854 | 0.98857 | -0.21814 | 0.9884 | -0.22148 | 10.3592
169 | 0.1229 | 0.031068 | -0.12271 | -0.030944 | 0.00019536 | 0.00012425 | 0.18512 | 0.18512 | 0.18512 | 0.9884 | -0.22148 | 0.98669 | -0.25468 | 25.4288
170 | -0.13325 | -0.033824 | 0.13328 | 0.033844 | 3.1767e-05 | 1.9647e-05 | 0.20001 | 0.20001 | 0.20001 | 0.99211 | -0.15005 | 0.99237 | -0.14509 | 10.9893
171 | 0.022002 | 0.0055219 | -0.021993 | -0.0055163 | 9.1437e-06 | 5.5693e-06 | 0.033184 | 0.033184 | 0.033184 | 0.98669 | -0.25468 | 0.98624 | -0.2634 | 9.1166
172 | 0.0076844 | 0.0019243 | -0.0076826 | -0.0019237 | 1.754e-06 | 6.6749e-07 | 0.011522 | 0.011522 | 0.011522 | 0.99237 | -0.14509 | 0.99212 | -0.14989 | 3.1654
173 | -0.14097 | -0.035768 | 0.141 | 0.035787 | 3.0816e-05 | 1.9129e-05 | 0.21153 | 0.21153 | 0.21153 | 0.99237 | -0.14509 | 0.99261 | -0.14055 | 11.6224
174 | 0.0047339 | 0.0011864 | -0.0047338 | -0.0011864 | 5.0828e-08 | -1.2285e-09 | 0.0071501 | 0.0071501 | 0.0071501 | 0.98518 | -0.28411 | 0.98516 | -0.28433 | 1.9643
175 | 0.0042145 | 0.0010562 | -0.0042144 | -0.0010562 | 8.3794e-08 | -1.5617e-08 | 0.0063877 | 0.0063878 | 0.0063878 | 0.98175 | -0.35088 | 0.98173 | -0.3513 | 1.7549
176 | 0.015913 | 0.0039894 | -0.015911 | -0.0039883 | 1.9117e-06 | 1.1159e-06 | 0.024293 | 0.024293 | 0.024293 | 0.97473 | -0.48769 | 0.9746 | -0.49021 | 6.6739
177 | 0.015543 | 0.0038961 | -0.015535 | -0.0038917 | 7.6053e-06 | 4.4189e-06 | 0.023731 | 0.023731 | 0.023731 | 0.9746 | -0.49021 | 0.97408 | -0.50048 | 6.5196
178 | -0.079669 | -0.019995 | 0.079707 | 0.020017 | 3.8612e-05 | 2.2535e-05 | 0.12153 | 0.12153 | 0.12153 | 0.97552 | -0.47207 | 0.97604 | -0.46191 | 6.6776
179 | 0.05113 | 0.012838 | -0.05112 | -0.012833 | 9.4195e-06 | 4.7401e-06 | 0.077999 | 0.078 | 0.078 | 0.97552 | -0.47207 | 0.97532 | -0.47593 | 4.2857
180 | 0.0046389 | 0.0011622 | -0.0046384 | -0.0011622 | 4.2425e-07 | -2.3607e-08 | 0.0069963 | 0.0069964 | 0.0069964 | 0.98661 | -0.25645 | 0.98651 | -0.25837 | 1.9221
181 | -0.008539 | -0.0021397 | 0.008541 | 0.0021406 | 2.0169e-06 | 8.7659e-07 | 0.012879 | 0.012878 | 0.012879 | 0.98661 | -0.25645 | 0.98686 | -0.25149 | 3.5381
182 | 0.0022116 | 0.00055401 | -0.0022115 | -0.00055426 | 1.028e-07 | -2.4871e-07 | 0.0033359 | 0.003336 | 0.003336 | 0.98651 | -0.25837 | 0.98646 | -0.25934 | 0.91648
183 | -0.030805 | -0.0077271 | 0.030833 | 0.0077447 | 2.8278e-05 | 1.7651e-05 | 0.046451 | 0.046451 | 0.046451 | 0.98686 | -0.25149 | 0.98785 | -0.23225 | 12.7613
184 | 0.022264 | 0.0055865 | -0.022262 | -0.005585 | 2.395e-06 | 1.4604e-06 | 0.033573 | 0.033573 | 0.033573 | 0.98686 | -0.25149 | 0.98675 | -0.25374 | 9.2232
185 | -0.038009 | -0.009543 | 0.038013 | 0.0095455 | 4.0651e-06 | 2.5593e-06 | 0.057259 | 0.057259 | 0.057259 | 0.98785 | -0.23225 | 0.98797 | -0.23001 | 15.7305
186 | 0.0071752 | 0.0017982 | -0.0071745 | -0.001798 | 7.7283e-07 | 2.6878e-07 | 0.010808 | 0.010808 | 0.010808 | 0.98785 | -0.23225 | 0.98774 | -0.23451 | 2.9693
187 | 0.020876 | 0.0052378 | -0.020863 | -0.0052295 | 1.3733e-05 | 8.3176e-06 | 0.031483 | 0.031484 | 0.031484 | 0.98675 | -0.25374 | 0.98604 | -0.26755 | 8.6494
188 | -0.040004 | -0.010045 | 0.04002 | 0.010054 | 1.5691e-05 | 9.4516e-06 | 0.060259 | 0.060259 | 0.060259 | 0.98797 | -0.23001 | 0.98839 | -0.22179 | 8.2773
189 | 0.0046134 | 0.0011561 | -0.0046131 | -0.0011561 | 3.0548e-07 | -2.0337e-08 | 0.00695 | 0.0069501 | 0.0069501 | 0.98774 | -0.23451 | 0.98767 | -0.2359 | 1.9094
190 | 0.018489 | 0.0046346 | -0.018488 | -0.0046342 | 6.6191e-07 | 3.947e-07 | 0.027902 | 0.027902 | 0.027902 | 0.98604 | -0.26755 | 0.986 | -0.2683 | 7.6653
191 | 0.052582 | 0.013214 | -0.052568 | -0.013207 | 1.4017e-05 | 7.0533e-06 | 0.079095 | 0.079096 | 0.079096 | 0.98939 | -0.20249 | 0.9891 | -0.20807 | 4.3459
192 | -0.052582 | -0.013214 | 0.052587 | 0.013216 | 5.1752e-06 | 2.6038e-06 | 0.079095 | 0.079095 | 0.079095 | 0.98939 | -0.20249 | 0.98949 | -0.20043 | 4.3459
193 | 0.049676 | 0.012482 | -0.049667 | -0.012478 | 8.6598e-06 | 4.2162e-06 | 0.074744 | 0.074745 | 0.074745 | 0.9891 | -0.20807 | 0.98891 | -0.21173 | 4.1069
194 | -0.083976 | -0.02107 | 0.084013 | 0.021091 | 3.6126e-05 | 2.118e-05 | 0.12629 | 0.12629 | 0.12629 | 0.98949 | -0.20043 | 0.98996 | -0.19141 | 6.9392
195 | 0.031389 | 0.0078535 | -0.031381 | -0.0078515 | 7.7791e-06 | 1.9892e-06 | 0.047199 | 0.0472 | 0.0472 | 0.98949 | -0.20043 | 0.98922 | -0.20564 | 2.5934
196 | -0.041981 | -0.010546 | 0.041988 | 0.01055 | 7.3696e-06 | 4.1491e-06 | 0.063211 | 0.063211 | 0.063211 | 0.98839 | -0.22179 | 0.98858 | -0.21811 | 5.7885
197 | 0.0025237 | 0.00063247 | -0.0025237 | -0.00063249 | 1.1951e-08 | -2.0564e-08 | 0.0038022 | 0.0038022 | 0.0038022 | 0.98767 | -0.2359 | 0.98766 | -0.236 | 1.0446
198 | 0.015712 | 0.0039388 | -0.015709 | -0.0039372 | 2.7857e-06 | 1.6144e-06 | 0.023712 | 0.023712 | 0.023712 | 0.986 | -0.2683 | 0.98581 | -0.27202 | 6.5142
199 | 0.0027764 | 0.00069547 | -0.0027763 | -0.00069557 | 7.841e-08 | -1.0173e-07 | 0.0041898 | 0.0041899 | 0.0041899 | 0.986 | -0.2683 | 0.98597 | -0.26889 | 1.1511
200 | 0.0046375 | 0.0011617 | -0.0046374 | -0.0011617 | 4.679e-08 | -2.166e-09 | 0.0070191 | 0.0070191 | 0.0070191 | 0.9831 | -0.32386 | 0.98309 | -0.32408 | 1.9283
201 | -0.0088587 | -0.0022197 | 0.0088597 | 0.0022196 | 1.0033e-06 | -1.1277e-07 | 0.013408 | 0.013408 | 0.013408 | 0.9831 | -0.32386 | 0.98322 | -0.32149 | 1.8418
202 | 0.0033578 | 0.00084105 | -0.0033575 | -0.00084125 | 3.1039e-07 | -2.0761e-07 | 0.0050823 | 0.0050824 | 0.0050824 | 0.98309 | -0.32408 | 0.98299 | -0.32602 | 1.3963
203 | -0.1779 | -0.044969 | 0.17794 | 0.04499 | 3.3799e-05 | 2.1237e-05 | 0.26938 | 0.26938 | 0.26938 | 0.98322 | -0.32149 | 0.98342 | -0.31752 | 14.8009
204 | 0.16904 | 0.042749 | -0.1689 | -0.042658 | 0.00014569 | 9.136e-05 | 0.25597 | 0.25597 | 0.25597 | 0.98322 | -0.32149 | 0.9823 | -0.33947 | 14.0642
205 | 0.0013753 | 0.00034445 | -0.0013752 | -0.00034467 | 2.9961e-08 | -2.1452e-07 | 0.0020818 | 0.0020819 | 0.0020819 | 0.98299 | -0.32602 | 0.98297 | -0.32647 | 0.57194
206 | -0.18313 | -0.046292 | 0.18334 | 0.046425 | 0.00021213 | 0.00013342 | 0.27724 | 0.27723 | 0.27724 | 0.98342 | -0.31752 | 0.98467 | -0.2934 | 15.2327
207 | 0.16497 | 0.041673 | -0.16483 | -0.041585 | 0.00014047 | 8.8009e-05 | 0.25002 | 0.25002 | 0.25002 | 0.9823 | -0.33947 | 0.98138 | -0.35725 | 13.7374
208 | -0.22726 | -0.057453 | 0.22751 | 0.057609 | 0.00024708 | 0.00015635 | 0.34361 | 0.34361 | 0.34361 | 0.98467 | -0.2934 | 0.98584 | -0.27076 | 18.8798
209 | 0.16088 | 0.040596 | -0.16075 | -0.040514 | 0.0001307 | 8.1804e-05 | 0.24403 | 0.24403 | 0.24403 | 0.98138 | -0.35725 | 0.98051 | -0.37423 | 13.4085
210 | -0.22817 | -0.057775 | 0.22831 | 0.057866 | 0.00014353 | 9.0828e-05 | 0.34461 | 0.34461 | 0.34461 | 0.98584 | -0.27076 | 0.98652 | -0.25766 | 18.9346
211 | 0.15868 | 0.039996 | -0.15849 | -0.039877 | 0.00019009 | 0.00011891 | 0.2409 | 0.2409 | 0.2409 | 0.98051 | -0.37423 | 0.97923 | -0.3993 | 13.2361
212 | -0.012872 | -0.0032255 | 0.012876 | 0.0032277 | 3.9842e-06 | 2.204e-06 | 0.019611 | 0.019611 | 0.019611 | 0.97669 | -0.44908 | 0.97702 | -0.44259 | 5.3876
213 | -0.016223 | -0.0040666 | 0.016225 | 0.0040673 | 1.1787e-06 | 6.8988e-07 | 0.024709 | 0.024709 | 0.024709 | 0.97702 | -0.44259 | 0.9771 | -0.44106 | 6.7881
214 | -0.019931 | -0.0049961 | 0.019939 | 0.0050013 | 8.5435e-06 | 5.158e-06 | 0.030353 | 0.030353 | 0.030353 | 0.9771 | -0.44106 | 0.97756 | -0.43207 | 8.3387
215 | -0.022781 | -0.0057135 | 0.022788 | 0.0057175 | 6.5895e-06 | 4.034e-06 | 0.034678 | 0.034678 | 0.034678 | 0.97756 | -0.43207 | 0.97787 | -0.426 | 9.527
216 | -0.14325 | -0.036353 | 0.14328 | 0.036372 | 3.0469e-05 | 1.8931e-05 | 0.21491 | 0.21491 | 0.21491 | 0.99261 | -0.14055 | 0.99284 | -0.13613 | 11.8083
217 | 0.0010345 | 0.00025882 | -0.0010345 | -0.00025927 | 3.2225e-08 | -4.4168e-07 | 0.0015503 | 0.0015505 | 0.0015505 | 0.99284 | -0.13613 | 0.9928 | -0.13678 | 0.42596
218 | -0.14432 | -0.036631 | 0.14442 | 0.036693 | 0.00010011 | 6.2228e-05 | 0.21646 | 0.21646 | 0.21646 | 0.99284 | -0.13613 | 0.99359 | -0.12172 | 11.8935
219 | 0.0071101 | 0.0017803 | -0.0071093 | -0.0017801 | 7.7503e-07 | 2.6134e-07 | 0.010663 | 0.010663 | 0.010663 | 0.99212 | -0.14989 | 0.992 | -0.15218 | 2.9295
220 | 0.00057252 | 0.00014334 | -0.00057251 | -0.00014349 | 3.1438e-09 | -1.4482e-07 | 0.00085863 | 0.00085868 | 0.00085868 | 0.99212 | -0.14989 | 0.99212 | -0.15 | 0.2359
221 | 0.3512 | 0.089455 | -0.35101 | -0.089332 | 0.00019239 | 0.00012253 | 0.52648 | 0.52648 | 0.52648 | 0.99359 | -0.12172 | 0.993 | -0.13308 | 28.9274
222 | -0.49562 | -0.12615 | 0.4965 | 0.12671 | 0.00087293 | 0.00055731 | 0.74294 | 0.74294 | 0.74294 | 0.99359 | -0.12172 | 0.9955 | -0.085255 | 40.8209
223 | 0.0061578 | 0.001542 | -0.0061576 | -0.0015419 | 2.1724e-07 | 5.137e-08 | 0.0092364 | 0.0092364 | 0.0092364 | 0.992 | -0.15218 | 0.99197 | -0.15292 | 2.5375
224 | 0.00095146 | 0.00023808 | -0.00095144 | -0.00023845 | 2.2686e-08 | -3.6894e-07 | 0.0014271 | 0.0014272 | 0.0014272 | 0.992 | -0.15218 | 0.99198 | -0.15268 | 0.39209
225 | 0.34926 | 0.088892 | -0.34834 | -0.088311 | 0.00091241 | 0.00058109 | 0.52385 | 0.52385 | 0.52385 | 0.993 | -0.13308 | 0.99016 | -0.18742 | 28.783
226 | -0.49864 | -0.12724 | 0.49943 | 0.12774 | 0.00078295 | 0.00049987 | 0.74615 | 0.74615 | 0.74615 | 0.9955 | -0.085255 | 0.99721 | -0.052807 | 40.9973
227 | 0.0029603 | 0.0007406 | -0.0029597 | -0.0007412 | 5.4504e-07 | -6.0263e-07 | 0.0044401 | 0.0044405 | 0.0044405 | 0.99197 | -0.15292 | 0.99177 | -0.15679 | 1.2199
228 | 0.26066 | 0.066295 | -0.26063 | -0.066274 | 3.2943e-05 | 2.09e-05 | 0.39207 | 0.39207 | 0.39207 | 0.99016 | -0.18742 | 0.99003 | -0.19005 | 21.5422
229 | 0.087683 | 0.022017 | -0.087666 | -0.022007 | 1.6663e-05 | 9.8415e-06 | 0.13178 | 0.13178 | 0.13178 | 0.99016 | -0.18742 | 0.98996 | -0.19141 | 7.2409
230 | -0.50205 | -0.1284 | 0.50334 | 0.12922 | 0.0012866 | 0.00082141 | 0.75007 | 0.75007 | 0.75007 | 0.99721 | -0.052807 | 1 | 0 | 41.2126
231 | 0.0040032 | 0.0010029 | -0.0040024 | -0.0010031 | 7.4483e-07 | -2.1228e-07 | 0.0060521 | 0.0060524 | 0.0060524 | 0.98422 | -0.30209 | 0.98402 | -0.306 | 1.6627
232 | -0.23014 | -0.058324 | 0.23021 | 0.058367 | 6.8444e-05 | 4.3321e-05 | 0.34736 | 0.34736 | 0.34736 | 0.98652 | -0.25766 | 0.98684 | -0.25148 | 19.086
233 | -0.082101 | -0.020617 | 0.082102 | 0.020618 | 8.505e-07 | 4.991e-07 | 0.12518 | 0.12518 | 0.12518 | 0.97604 | -0.46191 | 0.97605 | -0.4617 | 6.8781
234 | 0.050128 | 0.012585 | -0.050121 | -0.012581 | 6.6652e-06 | 3.3179e-06 | 0.076486 | 0.076486 | 0.076486 | 0.97532 | -0.47593 | 0.97518 | -0.47872 | 4.2025
235 | -0.084291 | -0.021166 | 0.084336 | 0.021193 | 4.5454e-05 | 2.6796e-05 | 0.12852 | 0.12852 | 0.12852 | 0.97605 | -0.4617 | 0.97662 | -0.4504 | 7.0615
236 | 0.046367 | 0.01164 | -0.046355 | -0.011635 | 1.1714e-05 | 5.5515e-06 | 0.070758 | 0.070759 | 0.070759 | 0.97518 | -0.47872 | 0.97491 | -0.48402 | 3.8878
237 | -0.085916 | -0.021589 | 0.086016 | 0.021648 | 0.00010004 | 5.9151e-05 | 0.13093 | 0.13092 | 0.13093 | 0.97662 | -0.4504 | 0.97786 | -0.42604 | 7.1937
238 | 0.044186 | 0.011104 | -0.044179 | -0.011101 | 6.5968e-06 | 2.9461e-06 | 0.066497 | 0.066498 | 0.066498 | 0.98891 | -0.21173 | 0.98875 | -0.21485 | 3.6537
239 | 0.027233 | 0.0068119 | -0.027227 | -0.0068111 | 5.6792e-06 | 7.3814e-07 | 0.040959 | 0.04096 | 0.04096 | 0.98922 | -0.20564 | 0.989 | -0.21002 | 2.2506
240 | 0.0041486 | 0.0010396 | -0.0041484 | -0.0010397 | 2.6109e-07 | -6.2407e-08 | 0.0062404 | 0.0062405 | 0.0062405 | 0.98922 | -0.20564 | 0.98916 | -0.20696 | 1.7144
241 | 0.022551 | 0.0056392 | -0.022549 | -0.0056395 | 2.5008e-06 | -2.5809e-07 | 0.033925 | 0.033926 | 0.033926 | 0.989 | -0.21002 | 0.98888 | -0.21235 | 1.8641
242 | 0.041995 | 0.010553 | -0.041988 | -0.01055 | 6.5277e-06 | 3.6749e-06 | 0.06321 | 0.063211 | 0.063211 | 0.98875 | -0.21485 | 0.98858 | -0.21811 | 5.7885
243 | 0.022549 | 0.0056395 | -0.022548 | -0.0056396 | 5.1836e-07 | -5.3432e-08 | 0.033926 | 0.033926 | 0.033926 | 0.98888 | -0.21235 | 0.98885 | -0.21284 | 1.8641
244 | 0.022237 | 0.0055752 | -0.022227 | -0.0055687 | 1.0581e-05 | 6.4639e-06 | 0.033861 | 0.033862 | 0.033862 | 0.97722 | -0.43865 | 0.97672 | -0.44864 | 9.3026
245 | -0.023363 | -0.0058573 | 0.023377 | 0.0058659 | 1.4091e-05 | 8.646e-06 | 0.035575 | 0.035575 | 0.035575 | 0.97722 | -0.43865 | 0.97787 | -0.426 | 9.7734
246 | -0.046165 | -0.011583 | 0.046208 | 0.011611 | 4.3037e-05 | 2.7252e-05 | 0.070253 | 0.070253 | 0.070253 | 0.97787 | -0.426 | 0.97886 | -0.40647 | 19.3004
247 | -0.13433 | -0.033814 | 0.13437 | 0.033842 | 4.6067e-05 | 2.8557e-05 | 0.20425 | 0.20425 | 0.20425 | 0.97886 | -0.40647 | 0.97923 | -0.3993 | 11.2224
248 | 0.088118 | 0.022203 | -0.088036 | -0.022154 | 8.239e-05 | 4.8888e-05 | 0.134 | 0.134 | 0.134 | 0.97886 | -0.40647 | 0.97786 | -0.42604 | 7.3624
249 | 0.02412 | 0.0060343 | -0.024112 | -0.0060341 | 7.6888e-06 | 1.2166e-07 | 0.036648 | 0.03665 | 0.03665 | 0.97923 | -0.3993 | 0.97889 | -0.406 | 2.0137
250 | 0.004625 | 0.001159 | -0.0046247 | -0.001159 | 3.897e-07 | -1.4866e-08 | 0.0070305 | 0.0070306 | 0.0070306 | 0.97889 | -0.406 | 0.9788 | -0.40777 | 1.9315
251 | 0.0010708 | 0.00026814 | -0.0010708 | -0.00026837 | 1.8705e-08 | -2.3161e-07 | 0.001616 | 0.0016161 | 0.0016161 | 0.98597 | -0.26889 | 0.98595 | -0.26926 | 0.44398
252 | 0.014175 | 0.0035526 | -0.014173 | -0.0035515 | 1.9011e-06 | 1.0755e-06 | 0.021396 | 0.021396 | 0.021396 | 0.98581 | -0.27202 | 0.98567 | -0.27484 | 5.878
253 | 0.002468 | 0.00061804 | -0.0024679 | -0.00061829 | 1.334e-07 | -2.4125e-07 | 0.0037257 | 0.0037258 | 0.0037258 | 0.98567 | -0.27484 | 0.98561 | -0.27597 | 1.0236
254 | 0.011705 | 0.0029335 | -0.011704 | -0.0029331 | 7.1534e-07 | 3.7995e-07 | 0.01767 | 0.01767 | 0.01767 | 0.98567 | -0.27484 | 0.9856 | -0.27612 | 4.8544
255 | 0.0012638 | 0.00031663 | -0.0012638 | -0.00031674 | 1.1967e-08 | -1.0406e-07 | 0.001908 | 0.001908 | 0.001908 | 0.98561 | -0.27597 | 0.9856 | -0.27617 | 0.52418
256 | 0.0012041 | 0.00030165 | -0.0012041 | -0.00030176 | 1.1421e-08 | -1.1015e-07 | 0.0018178 | 0.0018178 | 0.0018178 | 0.98561 | -0.27597 | 0.9856 | -0.27617 | 0.4994
257 | 0.010544 | 0.0026424 | -0.010544 | -0.0026422 | 5.4926e-07 | 2.7787e-07 | 0.015919 | 0.015919 | 0.015919 | 0.9856 | -0.27612 | 0.98554 | -0.27722 | 4.3734
258 | 0.018269 | 0.0045756 | -0.018266 | -0.004577 | 2.8403e-06 | -1.3699e-06 | 0.027546 | 0.027547 | 0.027547 | 0.98684 | -0.25148 | 0.98667 | -0.25474 | 1.5136
259 | -0.24848 | -0.062943 | 0.24885 | 0.063182 | 0.00037713 | 0.00023908 | 0.37491 | 0.37491 | 0.37491 | 0.98684 | -0.25148 | 0.98847 | -0.21993 | 20.5995
260 | -0.002951 | -0.0007396 | 0.0029511 | 0.00073949 | 9.2265e-08 | -1.0828e-07 | 0.0043917 | 0.0043916 | 0.0043917 | 0.99989 | -0.0020526 | 0.99993 | -0.0013963 | 1.2065
261 | -0.0074321 | -0.0018625 | 0.0074326 | 0.0018627 | 4.9436e-07 | 1.7501e-07 | 0.01106 | 0.01106 | 0.01106 | 0.99993 | -0.0013963 | 1 | 0 | 3.0384
262 | 0.0049025 | 0.0012251 | -0.0049024 | -0.001226 | 6.0941e-08 | -9.1753e-07 | 0.0073786 | 0.007379 | 0.007379 | 0.98849 | -0.21998 | 0.98847 | -0.22024 | 0.40544
263 | -0.005541 | -0.0013851 | 0.005541 | 0.0013846 | 4.4135e-08 | -5.1405e-07 | 0.0083398 | 0.0083396 | 0.0083398 | 0.98849 | -0.21998 | 0.9885 | -0.21981 | 0.45823
264 | 0.0041066 | 0.0010265 | -0.0041065 | -0.0010278 | 5.9536e-08 | -1.2935e-06 | 0.0061809 | 0.0061814 | 0.0061814 | 0.98847 | -0.22024 | 0.98846 | -0.22054 | 0.33964
265 | -0.0063165 | -0.0015789 | 0.0063166 | 0.0015776 | 1.5066e-07 | -1.3283e-06 | 0.0095069 | 0.0095064 | 0.0095069 | 0.9885 | -0.21981 | 0.98852 | -0.21931 | 0.52236
266 | 0.0033991 | 0.00085053 | -0.0033991 | -0.00085102 | 4.3712e-08 | -4.8567e-07 | 0.0051165 | 0.0051167 | 0.0051167 | 0.98846 | -0.22054 | 0.98845 | -0.22082 | 0.46856
267 | -0.0087745 | -0.0021936 | 0.0087748 | 0.0021924 | 2.7553e-07 | -1.174e-06 | 0.013206 | 0.013206 | 0.013206 | 0.98852 | -0.21931 | 0.98856 | -0.21865 | 0.72562
268 | 0.0024147 | 0.00060432 | -0.0024145 | -0.00060474 | 2.1395e-07 | -4.1649e-07 | 0.0036349 | 0.0036351 | 0.0036351 | 0.98845 | -0.22082 | 0.98835 | -0.22268 | 0.99864
269 | -0.010311 | -0.0025775 | 0.010311 | 0.0025771 | 1.4395e-07 | -4.1878e-07 | 0.015518 | 0.015518 | 0.015518 | 0.98856 | -0.21865 | 0.98857 | -0.21835 | 0.85266
270 | 0.00079219 | 0.00019833 | -0.00079218 | -0.00019854 | 8.9004e-09 | -2.0814e-07 | 0.0011926 | 0.0011927 | 0.0011927 | 0.98835 | -0.22268 | 0.98834 | -0.22291 | 0.32766
271 | 0.00099847 | 0.00025005 | -0.00099846 | -0.00025024 | 1.271e-08 | -1.8409e-07 | 0.0015032 | 0.0015033 | 0.0015033 | 0.98835 | -0.22268 | 0.98834 | -0.22294 | 0.41298
272 | -0.013169 | -0.0032932 | 0.013169 | 0.0032925 | 4.2164e-07 | -6.477e-07 | 0.019819 | 0.019819 | 0.019819 | 0.98857 | -0.21835 | 0.98861 | -0.21768 | 1.089
273 | 0.2561 | 0.065139 | -0.25573 | -0.064905 | 0.00036816 | 0.0002335 | 0.38526 | 0.38526 | 0.38526 | 0.99003 | -0.19005 | 0.98847 | -0.21993 | 21.1681
274 | 0.0061283 | 0.001534 | -0.0061281 | -0.0015358 | 1.9813e-07 | -1.7828e-06 | 0.0093198 | 0.0093205 | 0.0093205 | 0.97839 | -0.41582 | 0.97835 | -0.4165 | 0.51211
275 | -0.0078711 | -0.0019708 | 0.0078711 | 0.0019708 | 4.5499e-10 | -2.4863e-09 | 0.01197 | 0.01197 | 0.01197 | 0.97839 | -0.41582 | 0.97839 | -0.41582 | 0.65771
276 | 0.0029128 | 0.00072995 | -0.0029128 | -0.00073002 | 5.1765e-09 | -7.6174e-08 | 0.0044302 | 0.0044302 | 0.0044302 | 0.97835 | -0.4165 | 0.97835 | -0.41653 | 0.4057
277 | 0.0068893 | 0.0017258 | -0.0068892 | -0.0017266 | 1.0852e-07 | -7.865e-07 | 0.01039 | 0.01039 | 0.01039 | 0.98667 | -0.25474 | 0.98665 | -0.25507 | 0.57088
278 | -0.0010232 | -0.00025644 | 0.0010232 | 0.00025616 | 2.0607e-08 | -2.7985e-07 | 0.0015454 | 0.0015453 | 0.0015454 | 0.98522 | -0.28345 | 0.98525 | -0.28303 | 0.42455
279 | -0.0030457 | -0.00076304 | 0.0030459 | 0.00076279 | 2.4908e-07 | -2.4042e-07 | 0.0045998 | 0.0045997 | 0.0045998 | 0.98525 | -0.28303 | 0.98533 | -0.28131 | 1.2637
280 | -0.0073134 | -0.0018323 | 0.0073143 | 0.0018326 | 8.7387e-07 | 3.159e-07 | 0.011044 | 0.011044 | 0.011044 | 0.98533 | -0.28131 | 0.98546 | -0.2788 | 3.0341
281 | -0.0089738 | -0.0022486 | 0.0089745 | 0.0022489 | 6.7781e-07 | 3.0836e-07 | 0.01355 | 0.01355 | 0.01355 | 0.98546 | -0.2788 | 0.98554 | -0.27722 | 3.7225
282 | -0.019134 | -0.0047849 | 0.019135 | 0.0047843 | 1.4806e-06 | -5.7989e-07 | 0.028791 | 0.028791 | 0.028791 | 0.98877 | -0.21446 | 0.98885 | -0.21284 | 1.5819
283 | 0.017238 | 0.0043098 | -0.017238 | -0.0043099 | 1.3197e-07 | -8.3263e-08 | 0.025939 | 0.025939 | 0.025939 | 0.98877 | -0.21446 | 0.98876 | -0.21462 | 1.4252
284 | 0.017238 | 0.0043099 | -0.017237 | -0.0043108 | 1.5133e-06 | -9.5449e-07 | 0.025939 | 0.025939 | 0.025939 | 0.98876 | -0.21462 | 0.98867 | -0.21647 | 1.4252
285 | 0.014656 | 0.0036641 | -0.014655 | -0.0036651 | 8.4435e-07 | -9.4339e-07 | 0.022056 | 0.022056 | 0.022056 | 0.98867 | -0.21647 | 0.98861 | -0.21768 | 1.2119
286 | 0.0029597 | 0.0007412 | -0.0029594 | -0.00074152 | 2.8741e-07 | -3.1756e-07 | 0.0044405 | 0.0044406 | 0.0044406 | 0.99177 | -0.15679 | 0.99166 | -0.15883 | 1.22
287 | 0.0016653 | 0.00041719 | -0.0016653 | -0.00041737 | 3.6599e-08 | -1.7822e-07 | 0.0024988 | 0.0024989 | 0.0024989 | 0.99166 | -0.15883 | 0.99164 | -0.15929 | 0.68651

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.5192 | 0.13278

## res_load
| p_mw | q_mvar
0 | 0.00050943 | 0.00012767
1 | 0.00091685 | 0.00022978
2 | 0.0019324 | 0.0004843
3 | 0.0010961 | 0.00027472
4 | 0.00010388 | 2.6035e-05
5 | 0.00079014 | 0.00019803
6 | 0.00063442 | 0.000159
7 | 0.00032818 | 8.225e-05
8 | 0.0012317 | 0.00030869
9 | 0.00032216 | 8.0742e-05
10 | 0.00038491 | 9.6468e-05
11 | 0.00026586 | 6.6631e-05
12 | 0.00014929 | 3.7417e-05
13 | 0.0002502 | 6.2707e-05
14 | 0.00062146 | 0.00015575
15 | 0.0025325 | 0.00063471
16 | 0.0017796 | 0.00044601
17 | 0.00061586 | 0.00015435
18 | 0.00079681 | 0.0001997
19 | 0.00035953 | 9.0106e-05
20 | 0.00031105 | 7.7957e-05
21 | 0.0024246 | 0.00060765
22 | 0.00043126 | 0.00010809
23 | 0.00065231 | 0.00016348
24 | 0.0010742 | 0.00026921
25 | 0.0024133 | 0.00060484
26 | 0.0011737 | 0.00029416
27 | 0.0006683 | 0.00016749
28 | 0.0052587 | 0.001318
29 | 0.00095687 | 0.00023982
30 | 0.00065773 | 0.00016484
31 | 0.00032855 | 8.2342e-05
32 | 0.00022 | 5.5138e-05
33 | 0.002661 | 0.0006669
34 | 0.0004861 | 0.00012183
35 | 0.0032224 | 0.00080761
36 | 0.00015687 | 3.9315e-05
37 | 0.0016988 | 0.00042575
38 | 0.0016491 | 0.00041331
39 | 0.0042842 | 0.0010737
40 | 0.0034979 | 0.00087667
41 | 0.00044891 | 0.00011251
42 | 0.00071492 | 0.00017918
43 | 0.00064713 | 0.00016219
44 | 0.00276 | 0.00069172
45 | 0.0091122 | 0.0022837
46 | 0.0016881 | 0.00042309
47 | 0.00087222 | 0.0002186
48 | 0.0010225 | 0.00025627
49 | 0.00042215 | 0.0001058
50 | 0.00046589 | 0.00011676
51 | 0.0044891 | 0.0011251
52 | 0.0050233 | 0.001259
53 | 0.0004707 | 0.00011797
54 | 0.0014657 | 0.00036734
55 | 0.00044431 | 0.00011135
56 | 0.0027355 | 0.00068559
57 | 0.0049524 | 0.0012412
58 | 0.0019902 | 0.0004988
59 | 0.00038374 | 9.6173e-05
60 | 0.00075897 | 0.00019021
61 | 0.0088918 | 0.0022285
62 | 0.00066198 | 0.00016591
63 | 0.00044271 | 0.00011095
64 | 0.0013079 | 0.0003278
65 | 0.0015011 | 0.00037622
66 | 0.0042813 | 0.001073
67 | 0.0032811 | 0.00082231
68 | 0.0022743 | 0.00057
69 | 0.00062691 | 0.00015712
70 | 0.0010929 | 0.0002739
71 | 0.00094098 | 0.00023583
72 | 0.0004373 | 0.0001096
73 | 0.0017742 | 0.00044466
74 | 0.00245 | 0.00061403
75 | 0.0025365 | 0.0006357
76 | 0.002844 | 0.00071278
77 | 0.0013824 | 0.00034647
78 | 0.0016536 | 0.00041443
79 | 0.0028417 | 0.00071218
80 | 0.0012386 | 0.00031042
81 | 0.0056192 | 0.0014083
82 | 0.0023787 | 0.00059617
83 | 0.0058496 | 0.0014661
84 | 0.0017772 | 0.0004454
85 | 0.002935 | 0.00073559
86 | 0.0014849 | 0.00037214
87 | 0.0027912 | 0.00069953
88 | 0.0029312 | 0.00073464
89 | 0.0028893 | 0.00072413
90 | 0.0021759 | 0.00054533
91 | 0.0042322 | 0.0010607
92 | 0.0031762 | 0.00079603
93 | 0.0020922 | 0.00052436
94 | 0.0015638 | 0.00039193
95 | 0.0030847 | 0.0007731
96 | 0.0027797 | 0.00069666
97 | 0.0029292 | 0.00073412
98 | 0.0023792 | 0.00059628
99 | 0.0018724 | 0.00046926
100 | 0.0026147 | 0.00065529
101 | 0.0030996 | 0.00077683
102 | 0.0031711 | 0.00079474
103 | 0.0028559 | 0.00071576
104 | 0.0027529 | 0.00068995
105 | 0.0020728 | 0.0005195
106 | 0.0034858 | 0.00087362
107 | 0.0033219 | 0.00083254
108 | 0.0022186 | 0.00055603
109 | 0.00062031 | 0.00015546
110 | 0.002267 | 0.00056817
111 | 0.0016137 | 0.00040442
112 | 0.0025114 | 0.00062942
113 | 0.002074 | 0.0005198
114 | 0.0013574 | 0.00034019
115 | 0.00082841 | 0.00020762
116 | 0.0018249 | 0.00045736
117 | 0.0010776 | 0.00027007
118 | 0.0013936 | 0.00034926
119 | 0.001646 | 0.00041252
120 | 0.0038568 | 0.00096659
121 | 0.0029547 | 0.00074052
122 | 0.0027882 | 0.00069879
123 | 0.0032011 | 0.00080228
124 | 0.0016447 | 0.0004122
125 | 0.0015132 | 0.00037923
126 | 0.002661 | 0.00066691
127 | 0.0022688 | 0.00056862
128 | 0.00061877 | 0.00015508
129 | 0.0025933 | 0.00064994
130 | 0.0029585 | 0.00074146
131 | 0.0037994 | 0.00095222
132 | 0.0018089 | 0.00045335
133 | 0.00072372 | 0.00018138
134 | 0.0042144 | 0.0010562
135 | 0.0047338 | 0.0011864
136 | 0.002729 | 0.00068395
137 | 0.0003679 | 9.2205e-05
138 | 0.00072452 | 0.00018158
139 | 0.0039002 | 0.00097747
140 | 0.0024268 | 0.00060821
141 | 0.0022115 | 0.00055426
142 | 0.0013854 | 0.00034721
143 | 0.0019917 | 0.00049918
144 | 0.0025611 | 0.00064187
145 | 0.0023736 | 0.00059489
146 | 0.0028924 | 0.00072492
147 | 0.001961 | 0.00049147
148 | 0.0020894 | 0.00052365
149 | 0.0042212 | 0.0010579
150 | 0.0012796 | 0.00032069
151 | 0.0019822 | 0.0004968
152 | 0.0051939 | 0.0013017
153 | 0.0039275 | 0.00098432
154 | 0.0013752 | 0.00034467
155 | 0.0039483 | 0.00098953
156 | 0.00066188 | 0.00016588
157 | 0.0020685 | 0.00051842
158 | 0.0027991 | 0.00070153
159 | 0.0033472 | 0.0008389
160 | 0.0037062 | 0.00092886
161 | 0.0028417 | 0.00071221
162 | 0.0022575 | 0.00056578
163 | 0.0010345 | 0.00025927
164 | 0.00057251 | 0.00014349
165 | 0.0017543 | 0.00043967
166 | 0.0021483 | 0.00053842
167 | 0.0031974 | 0.00080134
168 | 0.00095144 | 0.00023845
169 | 0.0026267 | 0.00065832
170 | 0.006905 | 0.0017305
171 | 0.0040024 | 0.0010031
172 | 0.0018266 | 0.00045778
173 | 0.002394 | 0.0006
174 | 0.00099236 | 0.00024871
175 | 0.0021884 | 0.00054847
176 | 0.0037541 | 0.00094086
177 | 0.00158 | 0.000396
178 | 0.0010761 | 0.00026969
179 | 0.0054812 | 0.0013737
180 | 0.0046759 | 0.0011719
181 | 0.0041484 | 0.0010397
182 | 0.0036536 | 0.00091569
183 | 0.0021843 | 0.00054743
184 | 0.0011255 | 0.00028207
185 | 0.0021898 | 0.00054881
186 | 0.0020195 | 0.00050615
187 | 0.0046247 | 0.001159
188 | 0.0017055 | 0.00042743
189 | 0.0010708 | 0.00026837
190 | 0.0015345 | 0.00038457
191 | 0.0011597 | 0.00029064
192 | 0.002951 | 0.0007396
193 | 0.0044809 | 0.001123
194 | 0.00063854 | 0.00016003
195 | 0.00079583 | 0.00019945
196 | 0.00077543 | 0.00019434
197 | 0.0007074 | 0.00017729
198 | 0.0024579 | 0.000616
199 | 0.00098433 | 0.0002467
200 | 0.0015364 | 0.00038507
201 | 0.00062387 | 0.00015636
202 | 0.00099846 | 0.00025024
203 | 0.0028572 | 0.00071609
204 | 0.006779 | 0.001699
205 | 0.0045297 | 0.0011352
206 | 0.00079218 | 0.00019854
207 | 0.0068761 | 0.0017233
208 | 0.0017428 | 0.00043678
209 | 0.0032153 | 0.00080583
210 | 0.0032087 | 0.00080417
211 | 0.0029128 | 0.00073002
212 | 0.011376 | 0.0028512
213 | 0.0068892 | 0.0017266
214 | 0.0025237 | 0.00063249
215 | 0.0010232 | 0.00025644
216 | 0.0020225 | 0.00050688
217 | 0.0042675 | 0.0010695
218 | 0.0016596 | 0.00041593
219 | 0.0015693 | 0.0003933
220 | 0.0018955 | 0.00047506
221 | 0.0034126 | 0.00085527
222 | 0.0025805 | 0.00064672
223 | 0.0014865 | 0.00037254
224 | 0.0012638 | 0.00031674
225 | 0.0012041 | 0.00030176
226 | 0.0012941 | 0.00032433
227 | 0.0016653 | 0.00041737

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1